## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-02-2025 | during | 02-02-2025 | during | 02-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 20 | 20 | 97.3 | 97.3 | 97.3 | 97.3 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 358 | 404 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 313 | 279 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 45 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 210 | 210 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 82 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 20 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 15 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16.5 | 33 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 26 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 53 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 115 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 14 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 17 | 17 | 17 | 17 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1816.5 | 2254 | 4574.99 | 4558.99 | 3344.51 | 3328.51
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 152 | 0 | 0 | 151 | 151 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 78 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 41 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 17 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 15 | 2 | 11 | 2 | 11 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 11 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 2.03 | 0 | 2.03 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 33 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 54 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 108 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 2 | 2 | 2 | 2 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 286 | 235 | 220 | 220 | 220 | 220 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1697 | 2178 | 2892.75 | 2882.72 | 3043.75 | 3033.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 219 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 255 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 28 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 23 | 24 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 43 | 51 | 43 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 121 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 31 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 72 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 59 | 105 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 53 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1124 | 1214 | 1720.97 | 1678.97 | 1704.97 | 1662.97
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-02-2025 | during | 02-02-2025 | during | 02-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 43 | 210 | 210 | 210 | 210 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 58 | 58 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.05 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 139.05 | 151 | 638.2 | 601.5 | 390.2 | 353.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 42 | 41 | 41 | 42 | 41 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 113 | 113 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 33 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 318 | 382 | 315 | 315 | 287 | 287 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 383 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 976 | 1034 | 1419 | 1420 | 974 | 975
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 696 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 55 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 962 | 696 | 3160 | 3095 | 1255.02 | 1190.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 134 | 132 | 136 | 136 | 136 | 136 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1110 | 1110 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 72 | 150 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 299 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.44 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1840.44 | 1926 | 2178.12 | 2177.12 | 2138.12 | 2137.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 42 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 32 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 110 | 187 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 397 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 28 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 59 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 1.29 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 725 | 730.04 | 748 | 748 | 749 | 749 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.06 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 84 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1383.85 | 1512.54 | 2508.79 | 2359.24 | 2254 | 2104.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 66 | 67 | 69 | 69 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 158 | 160 | 160 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.1 | 0 | 4.1 | 0 | 4.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 26.5 | 0 | 26.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 61 | 0 | 62.7 | 0 | 62.7 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 341.1 | 420 | 584.3 | 491 | 541.32 | 448.02
System Total |  |  |  |  | 27884.66 | 27066.248 | 10279.94 | 11385.54 | 19677.12 | 19264.54 | 15645.89 | 15233.31
Forecast Scenario (02-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9080 |  | 0 |  | 9080
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8100 |  | 0 |  | 8100
|  |  |  | 3:00 | 7750 |  | 0 |  | 7750
|  |  |  | 4:00 | 7630 |  | 0 |  | 7630
|  |  |  | 5:00 | 7480 |  | 0 |  | 7480
|  |  |  | 6:00 | 7900 |  | 0 |  | 7900
|  |  |  | 7:00 | 8800 |  | 0 |  | 8800
|  |  |  | 8:00 | 9790 |  | 0 |  | 9790
|  |  |  | 9:00 | 10320 |  | 0 |  | 10320
|  |  |  | 10:00 | 10090 |  | 0 |  | 10090
|  |  |  | 11:00 | 10150 |  | 0 |  | 10150
|  |  |  | 12:00 | 10650 |  | 0 |  | 10650
|  |  |  | 13:00 | 10820 |  | 0 |  | 10820
|  |  |  | 14:00 | 10300 |  | 0 |  | 10300
|  |  |  | 15:00 | 10000 |  | 0 |  | 10000
|  |  |  | 16:00 | 9700 |  | 0 |  | 9700
|  |  |  | 17:00 | 9900 |  | 0 |  | 9900
|  |  |  | 18:00 | 10850 |  | 0 |  | 10850
|  |  |  | 18:30 | 11050 |  | 0 |  | 11050
|  |  |  | 19:00 | 11250 |  | 0 |  | 11250
|  |  |  | 19:30 | 11100 |  | 0 |  | 11100
|  |  |  | 20:00 | 10940 |  | 0 |  | 10940
|  |  |  | 21:00 | 10710 |  | 0 |  | 10710
|  |  |  | 22:00 | 10150 |  | 0 |  | 10150
|  |  |  | 23:00 | 9700 |  | 0 |  | 9700
Probable Maximum Temperature: |  |  | 30.20°C
Probable Maximum Demand at Day Peak: |  |  | 10650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11250.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11250.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 230.56 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:03 hrs on 02-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-02-2025 | [28 empty] | Date: | 01-02-2025 | [28 empty] | Date: | 01-02-2025 | [28 empty] | Date: | 01-02-2025 | [28 empty] | Date: | 01-02-2025 | [19 empty] | Date: | 01-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [19 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 300 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 197 | 0 | 0 | 50 | 29 | 185 | 29 | 0 | 70 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 310 | 0 | 312 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 59 | 11 | 0 | 0 | 12 | 4519.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 170 | 0 | 395 | 0 | 0 | 2.5 | 165 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 132 | 220 | 0 | 0 | 1000 | 0 | 4096.33 | 8615.83 | 91.78
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 290 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 197 | 0 | 0 | 50 | 29 | 186 | 26 | 0 | 70 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 300 | 0 | 312 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 19 | 33 | 0 | 0 | 6 | 4354.5 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 160 | 0 | 396 | 0 | 0 | 2.5 | 165 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 132 | 220 | 0 | 0 | 1000 | 0 | 3796.5 | 8151 | 91.77
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 273 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 197 | 0 | 0 | 50 | 29 | 183 | 26 | 0 | 70 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 300 | 0 | 312 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 19 | 33 | 0 | 0 | 0 | 4334.5 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 153 | 0 | 313 | 0 | 0 | 2.5 | 165 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 900 | 0 | 3392.5 | 7727 | 91.77
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 107 | 0 | 0 | 50 | 29 | 191 | 26 | 0 | 80 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 300 | 0 | 312 | 5 | 42 | 0 | 5 | 113 | 23 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4090.5 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 148 | 0 | 327 | 0 | 0 | 2.5 | 166 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 800 | 0 | 3300.5 | 7391 | 91.76
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 292 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 51 | 0 | 108 | 0 | 0 | 50 | 29 | 186 | 26 | 0 | 80 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 295 | 0 | 312 | 5 | 42 | 0 | 5 | 113 | 23 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4059.5 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 148 | 0 | 320 | 0 | 0 | 2.5 | 163 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 800 | 0 | 3149.5 | 7209 | 91.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 108 | 0 | 0 | 50 | 29 | 191 | 26 | 0 | 85 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 300 | 0 | 312 | 5 | 42 | 0 | 5 | 113 | 23 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 3981.5 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 142 | 0 | 325 | 0 | 0 | 2.5 | 166 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 6 | 80 | 180 | 0 | 0 | 800 | 0 | 3095.5 | 7077 | 91.75
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 300 | 313 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 189 | 0 | 0 | 50 | 29 | 208 | 26 | 0 | 91 | 0 | 0 | 15 | 0 | 54 | 0 | 0 | 0 | 315 | 0 | 301 | 5 | 42 | 0 | 5 | 113 | 23 | 0 | 21 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4171.5 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 414 | 0 | 0 | 2.5 | 164 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 6 | 136 | 220 | 0 | 0 | 810 | 0 | 3273.5 | 7445 | 91.75
07:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 400 | 311 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 1 | 51 | 0 | 199 | 0 | 0 | 50 | 29 | 206 | 26 | 0 | 90 | 0 | 0 | 15 | 0 | 54 | 0 | 2 | 0 | 325 | 0 | 315 | 30 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 12 | 24 | 49 | 0 | 0.62 | 0 | 4623.62 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 110 | 0 | 414 | 0 | 0.02 | 2.5 | 164 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 6 | 136 | 220 | 0 | 0 | 940 | 0 | 3558.02 | 8181.64 | 91.74
08:00 | 0 | 17 | 26 | 0 | 0 | 0 | 0 | 20 | 333 | 0 | 0 | 0 | 0 | 0 | 10 | 32 | 0 | 0 | 18 | 54 | 15 | 0 | 400 | 296 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 1 | 0 | 16 | 22 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 407 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 4 | 51 | 0 | 197 | 0 | 0 | 51 | 29 | 202 | 26 | 6 | 95 | 11 | 1 | 11 | 0 | 48 | 0 | 14 | 0 | 330 | 0 | 315 | 33 | 42 | 0 | 5 | 113 | 0 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 55 | 50 | 0 | 2.98 | 0 | 4959.98 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 4.12 | 0 | 0 | 0 | 0 | 109 | 0 | 414 | 0 | 0.38 | 2.5 | 161 | 67 | 0 | 1 | 0 | 0 | 0 | 0.6 | 8 | 0.04 | 0 | 307 | 5 | 134 | 220 | 0 | 0 | 1090 | 35 | 4055.64 | 9015.62 | 91.74
09:00 | 0 | 30 | 26 | 0 | 0 | 0 | 0 | 20 | 324 | 0 | 0 | 32 | 0 | 0 | 50 | 32 | 0 | 0 | 54 | 90 | 15 | 0 | 400 | 304 | 0 | 0 | 0 | 32 | 270 | 0 | 0 | 3 | 0 | 24 | 22 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 3 | 408 | 0 | 0 | 4 | 0 | 13 | 0 | 0 | 0 | 0 | 1224 | 10 | 51 | 0 | 197 | 0 | 0 | 50 | 29 | 216 | 29 | 50 | 90 | 51 | 37 | 11 | 0 | 56 | 0 | 16 | 0 | 325 | 0 | 318 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 55 | 48 | 0 | 4.9 | 6 | 5462.9 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 9.02 | 0 | 0 | 0 | 0 | 109 | 0 | 414 | 0 | 0.26 | 2.5 | 158 | 66 | 35 | 2 | 0 | 0 | 0 | 1 | 18 | 0.07 | 0 | 307 | 5 | 134 | 220 | 0 | 0 | 1132 | 35 | 4051.85 | 9514.75 | 91.74
10:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 20 | 330 | 0 | 0 | 35 | 0 | 0 | 50 | 32 | 0 | 0 | 55 | 90 | 0 | 0 | 400 | 273 | 0 | 0 | 0 | 16.5 | 270 | 0 | 0 | 4 | 0 | 20 | 22 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 406 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1224 | 14 | 51 | 0 | 197 | 0 | 0 | 80 | 24 | 184 | 30 | 50 | 70 | 51 | 53 | 11 | 0 | 60 | 0 | 32 | 0 | 320 | 0 | 318 | 30 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 45 | 0 | 10.78 | 6 | 5476.28 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11.8 | 0 | 0 | 0 | 0 | 109 | 0 | 387 | 0 | 0.29 | 2.5 | 158 | 66 | 35 | 4 | 0 | 0 | 0 | 2.4 | 24 | 0.16 | 0 | 250 | 5 | 100 | 180 | 0 | 0 | 1110 | 35 | 4130.15 | 9606.43 | 91.73
11:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 20 | 355 | 0 | 0 | 35 | 0 | 0 | 50 | 32 | 0 | 0 | 55 | 90 | 15 | 0 | 400 | 285 | 0 | 0 | 0 | 16.5 | 270 | 0 | 0 | 8 | 0 | 20 | 22 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 364 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1224 | 16 | 51 | 0 | 197 | 0 | 0 | 140 | 23 | 186 | 30 | 50 | 50 | 51 | 53 | 11 | 0 | 60 | 0 | 44 | 0 | 300 | 0 | 318 | 30 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 44 | 1 | 21.18 | 6 | 5536.68 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 30.66 | 0 | 0 | 0 | 0 | 109 | 0 | 389 | 0 | 0.49 | 2.5 | 161 | 68 | 35 | 8 | 0 | 0 | 0 | 3.7 | 51 | 0.25 | 0 | 250 | 5 | 100 | 180 | 0 | 0 | 1100 | 35 | 4230.6 | 9767.28 | 91.73
12:00 | 0 | 53 | 26 | 0 | 0 | 0 | 0 | 20 | 358 | 0 | 0 | 35 | 0 | 0 | 52 | 32 | 0 | 0 | 55 | 115 | 15 | 0 | 400 | 313 | 0 | 0 | 0 | 16.5 | 270 | 0 | 0 | 14 | 0 | 20 | 22 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 5 | 286 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1224 | 17 | 51 | 0 | 197 | 0 | 0 | 255 | 23 | 219 | 30 | 51 | 50 | 51 | 59 | 17 | 0 | 68 | 0 | 53 | 0 | 325 | 0 | 318 | 33 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 33 | 2 | 31.05 | 6 | 5752.55 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 47.06 | 0 | 0 | 0 | 0 | 110 | 0 | 414 | 0 | 1.29 | 2.5 | 160 | 66 | 35 | 15 | 0 | 0 | 0 | 4.1 | 61 | 0.44 | 0 | 299 | 5 | 134 | 220 | 0 | 0 | 1110 | 72 | 4527.39 | 10279.94 | 91.73
13:00 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 20 | 366 | 0 | 0 | 51 | 0 | 0 | 58 | 32 | 0 | 0 | 55 | 155 | 15 | 0 | 400 | 286 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 20 | 0 | 19 | 22 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3 | 40 | 17 | 8 | 234 | 0 | 0 | 19 | 0 | 56 | 0 | 0 | 0 | 0 | 1224 | 15 | 51 | 0 | 187 | 0 | 0 | 260 | 23 | 191 | 30 | 80 | 50 | 77 | 68 | 11 | 0 | 76 | 0 | 56 | 0 | 330 | 0 | 223 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 33 | 2 | 34.32 | 6 | 5816.82 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 47.48 | 0 | 0 | 0 | 0 | 136 | 0 | 393 | 0 | 1.22 | 2.5 | 162 | 66 | 70 | 15 | 0 | 0 | 0 | 3.8 | 110 | 0.43 | 0 | 307 | 5 | 134 | 220 | 0 | 0 | 1110 | 108 | 4650.43 | 10467.25 | 91.72
14:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 20 | 380 | 0 | 0 | 54 | 0 | 0 | 59 | 16 | 0 | 0 | 55 | 162 | 25 | 0 | 300 | 285 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 22 | 0 | 18.5 | 22 | 0 | 0 | 35 | 16 | 0 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 3 | 40 | 51 | 6 | 234 | 0 | 0 | 19 | 0 | 51 | 0 | 0 | 0 | 0 | 1224 | 14 | 51 | 0 | 187 | 0 | 0 | 255 | 24 | 193 | 27 | 96 | 50 | 100 | 91 | 17 | 0 | 70 | 0 | 49 | 0 | 305 | 0 | 214 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 33 | 2 | 26.69 | 6 | 5776.69 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.88 | 0 | 0 | 724.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 36.31 | 0 | 0 | 0 | 0 | 130 | 0 | 400 | 0 | 0 | 2.5 | 162 | 68 | 35 | 14 | 0 | 0 | 0 | 3.4 | 114 | 0.42 | 0 | 297 | 5 | 80 | 220 | 0 | 0 | 1122 | 108 | 4520.26 | 10296.95 | 91.72
15:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 20 | 380 | 0 | 0 | 54 | 0 | 0 | 59 | 16 | 0 | 0 | 55 | 162 | 25 | 0 | 300 | 291 | 0 | 0 | 35 | 33 | 300 | 0 | 0 | 16 | 0 | 19 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 17 | 0 | 0 | 0 | 0 | 2 | 40 | 42 | 2 | 240 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1192 | 11 | 51 | 0 | 187 | 0 | 0 | 253 | 24 | 204 | 27 | 95 | 50 | 51 | 75 | 17 | 0 | 68 | 0 | 29 | 0 | 305 | 0 | 214 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 33 | 1 | 23.11 | 6 | 5646.11 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 719.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 28.02 | 0 | 0 | 0 | 0 | 130 | 0 | 339 | 0 | 2.55 | 2.5 | 155 | 68 | 35 | 12 | 0 | 0 | 0 | 2.3 | 80 | 0.27 | 0 | 250 | 4 | 80 | 220 | 0 | 0 | 1130 | 108 | 4350.6 | 9996.71 | 91.72
16:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 20 | 380 | 0 | 0 | 54 | 0 | 0 | 76 | 16 | 0 | 0 | 55 | 126 | 25 | 0 | 300 | 281 | 0 | 0 | 35 | 33 | 300 | 0 | 0 | 9 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 1 | 40 | 17 | 3 | 236 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1150 | 6 | 51 | 0 | 195 | 0 | 0 | 255 | 24 | 183 | 27 | 99 | 50 | 34 | 75 | 17 | 0 | 66 | 0 | 13 | 0 | 310 | 0 | 223 | 33 | 40 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 34 | 1 | 11.81 | 6 | 5479.81 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.74 | 0 | 0 | 719.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 12.55 | 0 | 0 | 0 | 0 | 145 | 0 | 313 | 0 | 1.15 | 2.5 | 157 | 67 | 35 | 6 | 0 | 0 | 0 | 1 | 46 | 0.18 | 0 | 250 | 4 | 80 | 220 | 0 | 0 | 1120 | 108 | 4241.69 | 9721.5 | 91.71
17:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 20 | 381 | 0 | 0 | 54 | 0 | 0 | 76 | 40 | 0 | 0 | 55 | 126 | 17 | 0 | 300 | 294 | 0 | 0 | 35 | 32 | 300 | 0 | 0 | 2 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 7 | 233 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1150 | 1 | 51 | 0 | 195 | 0 | 0 | 0 | 24 | 194 | 23 | 115 | 50 | 34 | 75 | 17 | 0 | 60 | 0 | 3 | 0 | 310 | 0 | 326 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 34 | 0 | 2.82 | 6 | 5346.82 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 719.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2.96 | 0 | 0 | 0 | 0 | 159 | 0 | 414 | 0 | 0.26 | 2.5 | 160 | 67 | 35 | 2 | 0 | 0 | 0 | 0.3 | 12 | 0.03 | 0 | 250 | 5 | 132 | 220 | 0 | 0 | 1110 | 108 | 4317.39 | 9664.21 | 91.7
18:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 20 | 410 | 0 | 0 | 54 | 0 | 0 | 102 | 82 | 0 | 19 | 55 | 126 | 25 | 0 | 420 | 311 | 0 | 0 | 35 | 32 | 329 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 3 | 17 | 32 | 0 | 12 | 12 | 0 | 40 | 26 | 4 | 233 | 17 | 0 | 24 | 0 | 54 | 25 | 0 | 0 | 0 | 1180 | 0 | 51 | 46 | 197 | 0 | 0 | 40 | 24 | 206 | 25 | 115 | 70 | 136 | 95 | 17 | 0 | 68 | 0 | 0 | 40 | 305 | 0 | 372 | 33 | 41 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 18 | 9 | 58 | 34 | 0 | 0 | 6 | 6151 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721.63 | 0 | 0 | 42 | 0 | 5 | 0 | 51 | 0 | 10 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 432 | 0 | 0 | 2.5 | 160 | 67 | 76 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 132 | 220 | 0 | 0 | 1110 | 116 | 4570.13 | 10721.13 | 91.7
19:00 | 0 | 105 | 26 | 0 | 0 | 0 | 0 | 20 | 404 | 0 | 0 | 54 | 0 | 0 | 132 | 82 | 0 | 45 | 55 | 162 | 25 | 0 | 420 | 279 | 0 | 0 | 35 | 33 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 33 | 11 | 0 | 2 | 17 | 41 | 0 | 50 | 50 | 0 | 40 | 54 | 15 | 235 | 108 | 0 | 33 | 0 | 78 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 121 | 197 | 0 | 0 | 0 | 24 | 183 | 28 | 115 | 70 | 200 | 105 | 17 | 0 | 72 | 0 | 0 | 31 | 320 | 0 | 382 | 33 | 41 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 43 | 0 | 0 | 6 | 6831 | 696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730.04 | 0 | 0 | 42 | 0 | 35 | 0 | 59 | 0 | 32 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 397 | 0 | 0 | 2.5 | 158 | 67 | 115 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1110 | 150 | 4554.54 | 11385.54 | 91.69
19:30 | 0 | 105 | 26 | 0 | 0 | 0 | 0 | 20 | 404 | 0 | 0 | 54 | 0 | 0 | 132 | 48 | 0 | 55 | 55 | 162 | 25 | 0 | 380 | 286 | 0 | 0 | 35 | 33 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 30 | 0 | 0 | 1 | 17 | 41 | 0 | 50 | 50 | 0 | 40 | 68 | 26 | 237 | 108 | 0 | 33 | 0 | 85 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 197 | 0 | 0 | 0 | 25 | 184 | 30 | 115 | 70 | 200 | 105 | 17 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 345 | 33 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 43 | 0 | 0 | 6 | 6719 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.72 | 0 | 0 | 0 | 0 | 35 | 0 | 59 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 313 | 0 | 0 | 2.5 | 166 | 67 | 115 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1120 | 136 | 4276.22 | 10995.22
20:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 20 | 403 | 0 | 0 | 54 | 0 | 0 | 132 | 16 | 0 | 55 | 55 | 162 | 25 | 0 | 380 | 300 | 0 | 0 | 35 | 33 | 335 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 41 | 0 | 50 | 50 | 0 | 40 | 68 | 18 | 236 | 108 | 0 | 33 | 0 | 87 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 195 | 0 | 0 | 0 | 26 | 189 | 30 | 115 | 70 | 200 | 105 | 17 | 0 | 72 | 0 | 0 | 0 | 295 | 0 | 348 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 84 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 43 | 0 | 0 | 6 | 6619 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.21 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 319 | 0 | 0 | 2.5 | 171 | 68 | 115 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 150 | 4275.71 | 10894.71 | 91.69
21:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 41 | 403 | 0 | 0 | 54 | 0 | 0 | 117 | 16 | 0 | 55 | 17 | 162 | 25 | 0 | 400 | 289 | 0 | 0 | 35 | 33 | 335 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 33 | 237 | 0 | 0 | 31 | 0 | 103 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 115 | 70 | 200 | 106 | 17 | 0 | 72 | 0 | 0 | 0 | 305 | 0 | 347 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 84 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 48 | 0 | 0 | 6 | 6255 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 378 | 0 | 0 | 2.5 | 177 | 68 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 150 | 4483.5 | 10738.5 | 91.68
22:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 403 | 0 | 0 | 54 | 0 | 0 | 114 | 16 | 0 | 0 | 0 | 162 | 25 | 0 | 400 | 306 | 0 | 0 | 17 | 33 | 335 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 220 | 0 | 0 | 19 | 0 | 51 | 151 | 0 | 0 | 0 | 1227 | 0 | 51 | 80 | 197 | 0 | 0 | 0 | 29 | 188 | 30 | 115 | 70 | 100 | 73 | 17 | 0 | 62 | 0 | 0 | 0 | 305 | 0 | 350 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 54 | 0 | 0 | 6 | 5951.5 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 395 | 0 | 0 | 2.5 | 172 | 68 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 150 | 4361.5 | 10313 | 91.68
23:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 61 | 401 | 0 | 0 | 54 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 126 | 17 | 0 | 400 | 310 | 0 | 0 | 17 | 33 | 335 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 215 | 0 | 0 | 19 | 0 | 0 | 151 | 0 | 0 | 0 | 1226 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 28 | 196 | 30 | 115 | 51 | 51 | 55 | 17 | 0 | 58 | 0 | 0 | 0 | 295 | 0 | 300 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 35 | 70 | 0 | 0 | 6 | 5534.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 334 | 0 | 0 | 2.5 | 174 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 150 | 4266.5 | 9801 | 91.67
Total KWH | 0 | 1016813 | 321048 | 0 | 0 | 0 | 0 | 603227.28 | 8910000 | 0 | 0 | 779940 | 0 | 0 | 1249056 | 493920 | 0 | 189977 | 734168 | 2113920 | 408600 | 0 | 8655500 | 7030807 | 0 | 0 | 377194 | 702800 | 7094667 | 0 | 0 | 97514 | 0 | 417600 | 527400 | 0 | 0 | 569125 | 168611 | 12384 | 0 | 10560 | 168953 | 55041 | 0 | 105600 | 99840 | 20520 | 960000 | 401450 | 427200 | 7585454.55 | 220800 | 0 | 346560 | 0 | 853927 | 848145 | 0 | 0 | 0 | 26132725 | 104760 | 1218080 | 516872 | 4416000 | 0 | 0 | 1902000 | 640800 | 4740000 | 667008 | 1501440 | 1645850 | 1459680 | 1259160 | 377930 | 0 | 1464000 | 0 | 313427 | 62240 | 7536000 | 0 | 7706000 | 724392 | 988000 | 0 | 114528 | 2685354 | 550368 | 0 | 1805760 | 716928 | 0 | 0 | 0 | 172080 | 224400 | 1029600 | 954240 | 8000 | 167840 | 108960 | 128492743.83 | 17059118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251280 | 0 | 0 | 16050784 | 0 | 0 | 70929 | 0 | 70656 | 0 | 228176 | 0 | 33309 | 10574 | 520970 | 77639 | 232500 | 696273 | 0 | 0 | 0 | 3475382 | 0 | 9138109 | 0 | 8700 | 65628 | 4007000 | 1525527 | 832951 | 82333 | 189955 | 0 | 0 | 23328.6 | 510480 | 2107.5 | 0 | 6305000 | 142571 | 2791000 | 5189140 | 0 | 0 | 25403636.36 | 1694400 | 96689456.46 | 225182200.29

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10279.94 | MW | 12:00 Hr. | Energy Generated |  |  | 225.1822 |  | MKWHr.
| Day Peak Demand |  |  | 10326.94 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.225 |  | MKWHr.
| Evening Peak Generation |  |  | 11385.54 | MW | 19:00 Hr. | Energy Demand |  |  | 225.4072 |  | MKWHr.
| Evening Peak Demand |  |  | 11385.54 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.4 |  | °C
| Minimum Generation of the Day |  |  | 7077 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 759.37 |  | MMCFD
| Maximum Generation of the Day |  |  | 11385.54 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.349 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.3506 | 0 | 7.276 | 0 | 0 | 0.097514 | 0 | 0 | 41.7242 | Gas | 96.5133 | Gas | 346396519.838
| Chattogram Zone |  |  | 1.2753 | 33.7182 | 3.0023 | 0 | 0.96 | 0.12528 | 0 | 0.01056 | 39.0917 | Coal | 70.9593 | Coal | 500047159.1968
| Cumilla Zone |  |  | 15.6077 | 0 | 4.7994 | 0 | 0 | 0.31343 | 1.464 | 0 | 22.1845 | HFO | 19.8213 | HFO | 359435126.49
| Mymensingh Zone |  |  | 0.95424 | 0 | 1.535 | 0 | 0 | 0.17584 | 0 | 0 | 2.6651 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 22.8273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8273 | Hydro | 0.96 | Hydro | 96000
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.25128 | 17.0591 | 0 | 17.3104 | Solar | 2.3438 | Solar | 35491687.575
| Barishal Zone |  |  | 8.1227 | 31.7086 | 1.6944 | 0 | 0 | 0.0021075 | 0 | 0 | 41.5279 | Import | 34.5739 | Import | 188055929.4
| Rajshahi Zone |  |  | 13.3754 | 0 | 0.49128 | 0 | 0 | 0.76217 | 16.0508 | 0 | 30.6796 | Wind | 0.01056 | Wind | 164736
| Rangpur Zone |  |  | 0 | 5.5325 | 1.0229 | 0 | 0 | 0.61614 | 0 | 0 | 7.1716
| Total |  |  | 96.5133 | 70.9593 | 19.8213 | 0 | 0.96 | 2.3438 | 34.5739 | 0.01056 | 225.1822
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 346396519.838 |  | Hydro | 96000
|  |  |  | Coal | 500047159.1968 |  | Solar | 35491687.575
|  |  |  | HFO | 359435126.49 |  | Import | 188055929.4
|  |  |  | HSD | 0 |  | Wind | 164736
[5 empty] | Total: | 142,96,87,158 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.0591 | Peak Hr Flow | 696.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6500272.778 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.0508 | Peak Hr Flow | 730.04 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 188 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.464 | Peak Hr Flow | 72.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 602 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 34.5739 | Peak Hr Flow | 1498.04 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3997
|  |  |  | Chattogram |  | 0 |  | 1097
|  |  |  | Cumilla |  | 0 |  | 935
|  |  |  | Mymensingh |  | 0 |  | 972
|  |  |  | Sylhet |  | 0 |  | 388
|  |  |  | Khulna |  | 0 |  | 1204
|  |  |  | Barishal |  | 0 |  | 307
|  |  |  | Rajshahi |  | 0 |  | 1080
|  |  |  | Rangpur |  | 0 |  | 804
|  |  |  | Total |  | 0 |  | 10784
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 720.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1512.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
| 08:17 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 08:21 | 10:10 | Kushtia 132/33kV S/S T-1 HT Scheduled S/D Due to 33 kv busbar maintenance work and 33 kv | [7 empty] | 10.0MW load
|  |  | all feeder annual maintenance work will be done by WZPDCL | [7 empty] | interrup.
| 08:22 | 11:23 | Kushtia 132/33kV S/S T2 HT Scheduled S/D Due to 33 kv busbar maintenance work and 33 kv | [7 empty] | 30.0MW load
|  |  | all feeder annual maintenance work will be done by WZPDCL | [7 empty] | interrup.
| 08:27 | 17:19 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Annual maintenance
( Dead line cheaking)
| 08:29 | 16:07 | Kachua 132/33kV S/S Main Bus-2 Project Work S/D Due to For project work
| 08:34 | 14:51 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to Annual maintenance
dead line checking (Khulshi Demand)
| 08:46 |  | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance
| 08:48 | 14:44 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Annual Maintenance
| 08:48 | 14:44 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Scheduled S/D Due to Annual Maintenance
| 09:05 | 14:35 | Chandpur 132/33kV S/S Bus A Scheduled S/D Due to Annual maintenance
| 09:17 | 17:35 | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Nawabganj 132/33kV end Due to
Deadline checking. and from Keranigonj 230/132/33kV end Due to Dead line checking at
Nawabganj end.
| 09:20 | 17:45 | Hathazari 230/132/33kV S/S MT-02 HT Scheduled S/D Due to Annual Maintenace
| 09:20 | 17:45 | Hathazari 230/132/33kV S/S MT-01 LT Scheduled S/D Due to Annual Maintenace
| 09:25 |  | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Project Work S/D from Jamalpur 132/33kV end
Due to Project work bus D/S change.
| 10:17 | 11:37 | Jamalpur 132/33kV S/S T-1 LT Project Work S/D Due to Project work bus D/S change
| 10:17 | 11:37 | Jamalpur 132/33kV S/S T-1 HT Project Work S/D Due to Project work bus D/S change
| 10:21 |  | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) HT Scheduled S/D Due to For
Annual Maintenance, S/D taken by BSRM SS.
|  | 10:25 | Jamalpur 132/33kV S/S Bus-A is restored.
| 10:30 |  | Jamalpur 132/33kV S/S Bus-B Project Work S/D Due to Project work bus D/S change
| 10:33 | 14:52 | Rajbari 132/33kV S/S Faridpur - 2 Scheduled S/D Due to Annual Maintenance
| 10:34 | 14:51 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 Scheduled S/D Due to Annual maintenance for
rajbary end
| 10:58 | 17:43 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end Due
to Maintenance work from EPVTL End.
| 11:15 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due
to Tower painting for LILO Ckt
| 11:50 | 20:42 | BIPTC S/S Baharampur-4 Scheduled S/D
| 11:56 | 12:28 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) LT Forced S/D Due to Core Bushing Oil
leakage
| 11:57 | 12:26 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) HT Forced S/D Due to Core Bushing Oil
leakage
| 12:10 | 13:30 | Rangpur 132/33kV S/S Rangpur-GTPS Scheduled S/D Due to Project work
| 12:28 | 13:10 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Project Work S/D Due to 33 kv bus PT
rearrange
| 12:32 |  | Bibiyana-III 400 MW CCPP, FGMO is OFF with remarks:-
| 13:24 | 14:49 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Project Work S/D Due to 33 kv bus PT
rearrange
|  | 13:43 | Jashore 132/33kV S/S T-3 HT is restored.
| 13:43 |  | TR-3 (132/33 kv, 80/120 MVA ) new Transformer Commissioning / close at Jashore S/S.
|  | 14:26 | Naogaon 132/33kV S/S T-2 HT is restored.
|  | 14:26 | Naogaon 132/33kV S/S T-1 HT is restored.
|  | 14:28 | Naogaon 132/33kV S/S T-2 LT is restored.
|  | 14:28 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 14:29 | Naogaon 132/33kV S/S T-3 LT is restored.
|  | 14:30 | Naogaon 132/33kV S/S T-1 LT is restored.
| 16:25 | 18:52 | Bheramara(GK) 132/33kV S/S TR-2 LT Forced S/D Due to 33 kV BUS PT change
| 16:28 | 18:47 | Bheramara(GK) 132/33kV S/S TR-2 HT Forced S/D Due to 33 kV BUS PT change
| 16:29 | 18:16 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Forced S/D Due to Red hot maintenance
| 16:30 | 18:15 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Forced S/D Due to Red hot maintenance
| 17:40 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 18:22 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 18:35 | 19:40 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Forced S/D
| 18:36 | 19:39 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Forced S/D
| 19:00 |  | Evening peak Generation is 11385 MW
| 01:02 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 03:08 |  | Sirajgonj Gas 225MW Unit-1 ST was sync.
| 03:12 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 05:00 |  | Minimum Generation: 7652 MW.
| 06:10 |  | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Tripped showing Over current relay. relays.
| 06:10 |  | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Tripped showing Over current and earth | [7 empty] | 20.0MW load
|  |  | fault. relays Due to R Phase Under Ground Cable Fault. | [7 empty] | interrup.
| 06:13 | 06:33 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing distance
Relay relays Due to unknown
| 06:21 | 07:42 | Coxsbazar 132/33kV S/S 405T-T1 LT Tripped showing No signal relays Due to Ukhiya 33kv
feeder tripped
| 07:46 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 07:46 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 20 | 603227.28 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 404 | 8910000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8655500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 279 | 7030807 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 45 | 189977 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7094667 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 779940 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 82 | 493920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 734168 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 377194 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 417600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527400 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 408600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 33 | 702800 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 26 | 321048 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1249056 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1016813 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2113920 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 97514 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 2254 | 41724151.28
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104760 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 346560 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 152 | 848145 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 78 | 853927 | -
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 41 | 55041 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 168953 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 105600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 427200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 11 | 12384 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 33 | 168611 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 401450 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 99840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 569125 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 108 | 220800 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26132725 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 2 | 10560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 235 | 7585454.55 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2178 | 39091655.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4740000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 1902000 | schedule outage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 28 | 667008 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 24 | 640800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4416000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1218080 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 121 | 516872 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 31 | 62240 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1645850 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 1459680 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1464000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 377930 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1259160 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1501440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 313427 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1214 | 22184487
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 43 | 954240 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1029600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 224400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 167840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 108960 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 172080 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 151 | 2665120
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 988000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2685354 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 33 | 724392 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 114528 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 716928 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1805760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 550368 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7536000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 382 | 7706000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2368.568 | 1034 | 22827330
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 696 | 17059118 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 251280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 696 | 17310398
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 142571 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 2791000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 25403636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5189140 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1694400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6305000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2107.5 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1926 | 41527854.86
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 42 | 70929 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 32 | 33309 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 696273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 187 | 3475382 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 397 | 9138109 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 28 | 77639 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 65628 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 10574 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 59 | 228176 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 70656 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 8700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 730.04 | 16050784 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 232500 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 520970 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1512.54 | 30679629
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 67 | 1525527 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 4007000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 80 | 189955 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23328.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 832951 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 82333 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 510480 | -
Rangpur Area Total |  |  |  |  | 950 | 420 | 7171574.6
Eastern Grid Total |  |  |  |  | 16771.748 | 6831 | 128492743.83
Western Grid Total |  |  |  |  | 10294.5 | 4554.54 | 96689456.46
National Grid Total |  |  |  |  | 27066.248 | 11385.54 | 225182200.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7389.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3394.5 | MW
i) Dhaka area |  |  | 3997.24 |  | MW | i) Khulna area |  |  |  | 1203.7 | MW
ii) Chattogram area |  |  | 1097.4 |  | MW | ii) Barishal area |  |  |  | 307 | MW
iii) Cumilla area |  |  | 935 |  | MW | iii) Rajshahi area |  |  |  | 1079.8 | MW
iv) Mymensingh area |  |  | 972 |  | MW | iv) Rangpur area |  |  |  | 804 | MW
v) Sylhet area |  |  | 388 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10784.14 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 63 | 18:30 | 133 | Purbachal | 14 | 19:00
2 | AKSML | 113.1 | 05:00 | 68 | Jamalpur | 104 | 09:00 | 134 | Purbasadipur | 116 | 18:30
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 115 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 75 | 13:00 | 70 | Jhenaidah | 93 | 08:00 | 136 | Rahim | 25 | 07:00
5 | Agrabad | 70 | 19:00 | 71 | Joydebpur | 138 | 11:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 48 | 10:00 | 72 | Joypurhat | 56 | 09:00 | 138 | Rajendrapur | 110 | 15:00
7 | Ashuganj | 70 | 13:00 | 73 | Juldah | 11 | 10:00 | 139 | Rajshahi | 83 | 13:00
8 | BSRM | 193 | 02:00 | 74 | KSRM | 31 | 01:00 | 140 | Rajshahi-230 | 60 | 13:00
9 | Bagerhat | 61 | 18:30 | 75 | Kabirpur | 216 | 11:00 | 141 | Ramganj | 84 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 20:00 | 142 | Rampur | 27 | 18:00
11 | Bakulia | 68 | 19:00 | 77 | Kallyanpur | 66 | 13:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 31 | 13:00 | 78 | Kalurghat | 30 | 16:00 | 144 | Rangpur | 100 | 18:30
13 | Bangabhaban | 3 | 09:00 | 79 | Kamrangirchar | 55 | 13:00 | 145 | Ruppur | 3 | 12:00
14 | Barapukuria | 64 | 18:30 | 80 | Kaptai | N/A | N/A | 146 | SSM | 0 | 00:00
15 | Barguna | 16 | 18:00 | 81 | Kazla | 96 | 13:00 | 147 | Saidpur | 98 | 13:00
16 | Barishal | 75 | 09:00 | 82 | Keranigonj | 60 | 19:00 | 148 | Satkhira | 86 | 18:30
17 | Barishal-230 | 74 | 18:30 | 83 | Khagrachori | 26 | 18:00 | 149 | Satmasjid | 88 | 13:00
18 | Baroaulia | 53 | 14:00 | 84 | Khulna | 68 | 19:30 | 150 | Savar | 143 | 15:00
19 | Baroirhat | 55 | 18:00 | 85 | Khulshi | 161 | 14:00 | 151 | SevenRings | 17.73 | 13:00
20 | Bashundhara | 135 | 13:00 | 86 | Kishoreganj | 130 | 14:00 | 152 | ShahCement | 23 | 12:00
21 | BashundharaCement | 12 | 10:00 | 87 | Kodda | 242 | 18:30 | 153 | Shahjadpur | 58 | 19:30
22 | Beanibazar | 52 | 18:00 | 88 | Kulaura | 28 | 18:00 | 154 | Shahjibazar | 90 | 21:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 62 | 18:30 | 155 | Shahmirpur | 46 | 14:00
24 | Bhaluka | 116 | 15:00 | 90 | Kushtia | 104 | 13:00 | 156 | Shariatpur | 53 | 21:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 53 | 13:00 | 157 | Sherpur | 126 | 19:00
26 | Bhangura | 27 | 19:30 | 92 | Lalmonirhat | 49 | 18:30 | 158 | Shikalbaha | 25 | 19:00
27 | Bheramara(GK) | 41 | 19:00 | 93 | MI_Cement | 10.2 | 01:00 | 159 | Shitalakhya | 62.7 | 15:00
28 | Bhulta | 227 | 20:00 | 94 | Madanganj | 19 | 12:00 | 160 | Sholosohor | 34 | 15:00
29 | Bog-Sherpur | 62 | 13:00 | 95 | Madaripur | 62 | 20:00 | 161 | Shyampur | 152 | 11:00
30 | Bogura | 111 | 18:30 | 96 | Madartek | 53.2 | 14:00 | 162 | Siddhirganj | 105 | 10:00
31 | Borhanuddin | 52 | 19:00 | 97 | Madunaghat | 37 | 18:30 | 163 | Sirajganj | 80 | 19:00
32 | Brahmanbaria | 107 | 18:00 | 98 | Magura | 45 | 18:30 | 164 | Sonargaon | 93 | 23:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 60 | 10:00 | 165 | Sreemongol | 42 | 19:30
34 | Chandpur | 47 | 21:00 | 100 | Manikganj | 100 | 18:30 | 166 | Sreepur | 79 | 18:00
35 | Chandraghona | 27 | 18:00 | 101 | Maniknagar | 44 | 13:00 | 167 | Srinagar | 30.28 | 13:00
36 | Chapai | 65 | 13:00 | 102 | Matarbari | 33 | 18:30 | 168 | Sunamganj | 42 | 18:30
37 | Charsaidpur | 41 | 16:00 | 103 | Matuail | 62 | 12:00 | 169 | Sylhet | 26 | 18:00
38 | Chauddagram | 48 | 13:00 | 104 | Millgate | 71 | 12:00 | 170 | Sylhet-132 | 80 | 18:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 101 | 13:00 | 171 | TK | 25 | 18:00
40 | Chowmuhani | 150 | 18:00 | 106 | Mirsorai | 9 | 18:30 | 172 | Tangail | 152 | 19:00
41 | Chuadanga | 76 | 13:00 | 107 | Mirzapur | 34 | 13:00 | 173 | Thakurgaon | 78 | 18:30
42 | Coxsbazar | 112 | 18:00 | 108 | Mithapukur | 72 | 18:00 | 174 | Tongi | 103 | 12:00
43 | Cumilla(N) | 113 | 19:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 24 | 18:30
44 | Cumilla(S) | 136 | 14:00 | 110 | Mogbazar | 99.7 | 14:00 | 176 | Ullon | 38 | 14:00
45 | Daudkandi | 110 | 20:00 | 111 | Mongla | 29 | 12:00 | 177 | Uttara | 63 | 13:00
46 | Dhaka | 32 | 12:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 35 | 13:00
47 | Dhamrai | 104 | 18:00 | 113 | Muktagacha | 30 | 07:00 | 179 | Zigatola | 56 | 13:00
48 | Dhanmondi | 94 | 13:00 | 114 | Munshiganj | 70 | 18:00
49 | Dohazari | 74 | 20:00 | 115 | Mymensingh | 167 | 18:00
50 | Faridpur | 110 | 19:00 | 116 | Naogaon | 110 | 18:30
51 | Fatullah | 68 | 12:00 | 117 | Narail | 42 | 19:00
52 | Fenchuganj | 28 | 18:00 | 118 | Narinda | 56 | 13:00
53 | Feni | 68 | 18:00 | 119 | Narshingdi | 162 | 19:30
54 | GPH | 86 | 05:00 | 120 | Natore | 103 | 13:00
55 | Ghatail | 42 | 08:00 | 121 | Nawabganj | 31 | 13:00
56 | Ghorashal | 14 | 12:00 | 122 | Netrakona | 130 | 10:00
57 | Ghorashal-230 | 58 | 09:00 | 123 | New | 65.9 | 12:00
58 | Goalpara | 26 | 13:00 | 124 | Niamatpur | 84 | 13:00
59 | Gollamari | 52 | 13:00 | 125 | Noapara | 35 | 19:00
60 | Gopalganj | 76.8 | 18:30 | 126 | PHP | 9 | 00:00
61 | Gulshan | 66 | 13:00 | 127 | Pabna | 64 | 18:30
62 | Halishahar | 40 | 18:30 | 128 | Palashbari | 92 | 09:00
63 | HaripurSBU | 154 | 12:00 | 129 | Panchagarh | 43 | 18:30
64 | Hasnabad | 69 | 14:00 | 130 | Patuakhali | 57 | 13:00
65 | Hathazari | 53 | 17:00 | 131 | Payra | 18 | 12:00
66 | Ishurdi | 62 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8615.83 | 0 |  | 8615.83
1:00 | 8151 | 0 |  | 8151
2:00 | 7727 | 0 |  | 7727
3:00 | 7391 | 0 |  | 7391
4:00 | 7209 | 0 |  | 7209
5:00 | 7077 | 0 |  | 7077
6:00 | 7445 | 0 |  | 7445
7:00 | 8181.64 | 0 |  | 8181.64
8:00 | 9015.62 | 12 |  | 9028.62
9:00 | 9514.75 | 25 |  | 9540.88
10:00 | 9606.43 | 14 |  | 9621.43
11:00 | 9767.28 | 39 |  | 9808.04
12:00 | 10279.94 | 45 |  | 10326.94
13:00 | 10467.25 | 54 |  | 10523.25
14:00 | 10296.95 | 36 |  | 10334.95
15:00 | 9996.71 | 0 |  | 9996.71
16:00 | 9721.5 | 0 |  | 9721.5
17:00 | 9664.21 | 0 |  | 9664.21
18:00 | 10721.13 | 0 |  | 10721.13
19:00 | 11385.54 | 0 |  | 11385.54
19:30 | 10995.22 | 0 |  | 10995.22
20:00 | 10894.71 | 0 |  | 10894.71
21:00 | 10738.5 | 0 |  | 10738.5
22:00 | 10313 | 0 |  | 10313
23:00 | 9801 | 0 |  | 9801
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4519.5 | 4096.33 | 8615.83 | DAILY GENERATION CURVE
00:30 | 4437 | 3946.415 | 8383.415
01:00 | 4354.5 | 3796.5 | 8151 | 01-02-2025
01:30 | 4344.5 | 3594.5 | 7939
02:00 | 4334.5 | 3392.5 | 7727
02:30 | 4212.5 | 3346.5 | 7559
03:00 | 4090.5 | 3300.5 | 7391
03:30 | 4075 | 3225 | 7300
04:00 | 4059.5 | 3149.5 | 7209
04:30 | 4020.5 | 3122.5 | 7143
05:00 | 3981.5 | 3095.5 | 7077
05:30 | 4076.5 | 3184.5 | 7261
06:00 | 4171.5 | 3273.5 | 7445
06:30 | 4397.56 | 3415.76 | 7813.32
07:00 | 4623.62 | 3558.02 | 8181.64
07:30 | 4791.8 | 3806.83 | 8598.63
08:00 | 4959.98 | 4055.64 | 9015.62
08:30 | 5211.44 | 4053.745 | 9265.185
09:00 | 5462.9 | 4051.85 | 9514.75
09:30 | 5469.59 | 4091 | 9560.59
10:00 | 5476.28 | 4130.15 | 9606.43
10:30 | 5506.48 | 4180.375 | 9686.855
11:00 | 5536.68 | 4230.6 | 9767.28
11:30 | 5644.615 | 4378.995 | 10023.61
12:00 | 5752.55 | 4527.39 | 10279.94
12:30 | 5784.685 | 4588.91 | 10373.595
13:00 | 5816.82 | 4650.43 | 10467.25
13:30 | 5796.755 | 4585.345 | 10382.1
14:00 | 5776.69 | 4520.26 | 10296.95
14:30 | 5711.4 | 4435.43 | 10146.83
15:00 | 5646.11 | 4350.6 | 9996.71
15:30 | 5562.96 | 4296.145 | 9859.105
16:00 | 5479.81 | 4241.69 | 9721.5
16:30 | 5413.315 | 4279.54 | 9692.855
17:00 | 5346.82 | 4317.39 | 9664.21
17:30 | 5748.91 | 4443.76 | 10192.67
18:00 | 6151 | 4570.13 | 10721.13
18:30 | 6491 | 4562.335 | 11053.335
19:00 | 6831 | 4554.54 | 11385.54
19:30 | 6719 | 4276.22 | 10995.22
20:00 | 6619 | 4275.71 | 10894.71
20:30 | 6437 | 4379.605 | 10816.605 |  | Executive Engineer
21:00 | 6255 | 4483.5 | 10738.5 |  | Network Operation Division
21:30 | 6103.25 | 4422.5 | 10525.75
22:00 | 5951.5 | 4361.5 | 10313
22:30 | 5743 | 4314 | 10057
23:00 | 5534.5 | 4266.5 | 9801

## En-Curve
QF-LDC-12
Date | 01-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2167 | 1800 | 906 | 0 | 62 | 659.83 | 40 | 2892 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2172.5 | 1790 | 837 | 0 | 58 | 607.915 | 40 | 2816.5 | 0 | 0 | 61.5 | 0 | 0 | 0 | 0 | 01-02-2025
01:00 | 2178 | 1780 | 768 | 0 | 54 | 556 | 40 | 2741 | 0 | 0 | 34 | 0 | 0 | 0 | 0
01:30 | 2115.5 | 1756 | 742.5 | 0 | 52 | 511 | 40 | 2691 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | Energy Generated | 225.1822 |  | MKWHr
02:00 | 2053 | 1732 | 717 | 0 | 50 | 466 | 40 | 2641 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | Energy not Served | 0.225 |  | MKWHr
02:30 | 2074.5 | 1658 | 717 | 0 | 49 | 465.5 | 40 | 2541 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | Total Energy Requirement | 225.4072 |  | MKWHr
03:00 | 2096 | 1584 | 717 | 0 | 48 | 465 | 40 | 2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2090 | 1587.5 | 670 | 0 | 49 | 441 | 40 | 2422.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2084 | 1591 | 623 | 0 | 50 | 417 | 40 | 2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2070 | 1588.5 | 623 | 0 | 50 | 414.5 | 40 | 2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2056 | 1586 | 623 | 0 | 50 | 412 | 40 | 2310 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2063 | 1668.5 | 670 | 0 | 52 | 412.5 | 40 | 2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2070 | 1751 | 717 | 0 | 54 | 413 | 40 | 2400 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2073.5 | 1851.25 | 717 | 0 | 54 | 457 | 40 | 2599 | 2.57 | 1 | 18 | 0 | 0 | 0 | 0
07:00 | 2077 | 1951.5 | 717 | 0 | 54 | 501 | 40 | 2798 | 5.14 | 2 | 36 | 0 | 0 | 0 | 0
07:30 | 2074 | 1920.5 | 735 | 0 | 51 | 612 | 40 | 2978 | 31.13 | 38.5 | 118.5 | 0 | 0 | 0 | 6
08:00 | 2071 | 1889.5 | 753 | 0 | 48 | 723 | 40 | 3158 | 57.12 | 75 | 201 | 0 | 0 | 0 | 12
08:30 | 2072.5 | 1906.5 | 688 | 0 | 52 | 726.5 | 40 | 3226.5 | 86.685 | 81.5 | 385 | 0 | 0 | 0 | 18.5
09:00 | 2074 | 1923.5 | 623 | 0 | 56 | 730 | 40 | 3295 | 116.25 | 88 | 569 | 0 | 0 | 0 | 25
09:30 | 2034.5 | 1862.25 | 765 | 0 | 58 | 696.5 | 40 | 3254.5 | 151.34 | 98.5 | 600 | 0 | 0 | 0 | 19.5
10:00 | 1995 | 1801 | 907 | 0 | 60 | 663 | 40 | 3214 | 186.43 | 109 | 631 | 0 | 0 | 0 | 14
10:30 | 2029 | 1804.5 | 907 | 0 | 60 | 663.5 | 40 | 3190.5 | 252.355 | 109 | 631 | 0 | 0 | 0 | 26.5
11:00 | 2063 | 1808 | 907 | 0 | 60 | 664 | 40 | 3167 | 318.28 | 109 | 631 | 0 | 0 | 0 | 39
11:30 | 2163 | 1860.5 | 907 | 0 | 64 | 694.5 | 40 | 3156 | 353.61 | 118.5 | 666.5 | 0 | 0 | 0 | 42
12:00 | 2263 | 1913 | 907 | 0 | 68 | 725 | 40 | 3145 | 388.94 | 128 | 702 | 0 | 0 | 0 | 45
12:30 | 2225.5 | 1896.5 | 906.5 | 0 | 72 | 728 | 40 | 3124 | 409.595 | 134 | 837.5 | 0 | 0 | 0 | 49.5
13:00 | 2188 | 1880 | 906 | 0 | 76 | 731 | 40 | 3103 | 430.25 | 140 | 973 | 0 | 0 | 0 | 54
13:30 | 2161 | 1824.25 | 906 | 0 | 73 | 727.875 | 40 | 3105 | 403.475 | 134.5 | 1006.5 | 0 | 0 | 0.5 | 45
14:00 | 2134 | 1768.5 | 906 | 0 | 70 | 724.75 | 40 | 3107 | 376.7 | 129 | 1040 | 0 | 0 | 1 | 36
14:30 | 2108 | 1777.5 | 906 | 0 | 69 | 722.355 | 40 | 3071 | 330.975 | 129 | 990.5 | 0 | 0 | 2.5 | 18
15:00 | 2082 | 1786.5 | 906 | 0 | 68 | 719.96 | 40 | 3035 | 285.25 | 129 | 941 | 0 | 0 | 4 | 0
15:30 | 2071 | 1787.5 | 906.5 | 0 | 67 | 719.765 | 40 | 3007.5 | 220.34 | 129 | 908 | 0 | 0 | 2.5 | 0
16:00 | 2060 | 1788.5 | 907 | 0 | 66 | 719.57 | 40 | 2980 | 155.43 | 129 | 875 | 0 | 0 | 1 | 0
16:30 | 2072 | 1794.5 | 907 | 0 | 63 | 719.455 | 40 | 2975 | 96.4 | 141 | 883 | 0 | 0 | 1.5 | 0
17:00 | 2084 | 1800.5 | 907 | 0 | 60 | 719.34 | 40 | 2970 | 37.37 | 153 | 891 | 0 | 0 | 2 | 0
17:30 | 2217 | 1869 | 906.5 | 0 | 64 | 720.485 | 40 | 2985 | 18.685 | 273.5 | 1096 | 0 | 0 | 2.5 | 0
18:00 | 2350 | 1937.5 | 906 | 0 | 68 | 721.63 | 40 | 3000 | 0 | 394 | 1301 | 0 | 0 | 3 | 0
18:30 | 2367 | 1935.5 | 801 | 0 | 70 | 725.835 | 40 | 3050.5 | 0 | 428.5 | 1632.5 | 0 | 0 | 2.5 | 0
19:00 | 2384 | 1933.5 | 696 | 0 | 72 | 730.04 | 40 | 3101 | 0 | 463 | 1964 | 0 | 0 | 2 | 0
19:30 | 2218 | 1897.5 | 623 | 0 | 70 | 726.72 | 40 | 3121 | 0 | 324 | 1974 | 0 | 0 | 1 | 0
20:00 | 2232 | 1887.5 | 623 | 0 | 72 | 726.21 | 40 | 3136 | 0 | 257 | 1921 | 0 | 0 | 0 | 0
20:30 | 2248.5 | 1921 | 764 | 0 | 72 | 727.605 | 40 | 3139.5 | 0 | 199.5 | 1704.5 | 0 | 0 | 0 | 0
21:00 | 2265 | 1954.5 | 905 | 0 | 72 | 729 | 40 | 3143 | 0 | 142 | 1488 | 0 | 0 | 0 | 0
21:30 | 2277.5 | 1969.25 | 906 | 0 | 67 | 727.5 | 40 | 3133.5 | 0 | 104 | 1301 | 0 | 0 | 0 | 0
22:00 | 2290 | 1984 | 907 | 0 | 62 | 726 | 40 | 3124 | 0 | 66 | 1114 | 0 | 0 | 0 | 0
22:30 | 2236 | 1982.5 | 906.5 | 0 | 60 | 726 | 40 | 3122 | 0 | 50.5 | 933.5 | 0 | 0 | 0 | 0
23:00 | 2182 | 1981 | 906 | 0 | 58 | 726 | 40 | 3120 | 0 | 35 | 753 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 411 | 01:00 | 390 | 11:00 | Payra | 416 | 03:00 | 406 | 12:00
Ashuganj | 414 | 4:00 | 388 | 7:00 | Rahanpur | 419 | 03:00 | 404 | 12:00
Bhulta | 412 | 04:00 | 392 | 12:00 | Rampal | 415 | 05:00 | 392 | 14:00
Bibiana | 405 | 04:00 | 395 | 11:00
BIPTC | 408 | 04:00 | 386 | 13:00
Bogura | 417 | 05:00 | 400 | 08:00
Gopalganj | 416 | 05:00 | 393 | 12:00
Kaliakoir | 396 | 06:00 | 380 | 12:00
Madunaghat | 412 | 05:00 | 401 | 12:00
Meghnaghat | 412 | 05:00 | 390 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 05:00 | 222 | 17:00 | Keranigonj | 238 | 05:00 | 224 | 12:00
AKSML | 238 | 19:00 | 229 | 11:00 | Khulna(S) | 242 | 03:00 | 223 | 12:00
Aminbazar | 238 | 01:00 | 228 | 11:00 | Madunaghat | 237 | 05:00 | 229 | 12:00
Ashuganj | 241 | 02:00 | 233 | 11:00 | Madunaghat-400 | 237 | 05:00 | 231 | 12:00
Ashuganj-400 | 241 | 02:00 | 233 | 11:00 | Maniknagar | 240 | 05:00 | 227 | 12:00
Baghabari | 239 | 04:00 | 228 | 12:00 | Meghnaghat | 241 | 00:00 | 235 | 10:00
Barapukuria | 227 | 02:00 | 218 | 08:00 | Meghnaghat-400 | 241 | 05:00 | 229 | 12:00
Barapukuria-230 | 227 | 02:00 | 218 | 08:00 | Mirsorai | 237 | 05:00 | 229 | 23:00
Barishal | 246 | 04:00 | 234 | 12:00 | Rajshahi | 241 | 03:00 | 223 | 12:00
Bheramara | 240 | 02:00 | 223 | 12:00 | Rampal | 240 | 05:00 | 220 | 12:00
Bhulta | 240 | 04:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 237 | 02:00 | 225 | 11:00 | Rampura | 240 | 04:00 | 226 | 12:00
BIPTC | 242 | 02:00 | 223 | 12:00 | Shikalbaha | 236 | 06:00 | 228 | 12:00
Bogura | 241 | 02:00 | 230 | 12:00 | Shyampur | 238 | 02:00 | 226 | 12:00
Bogura-400 | 240 | 02:00 | 230 | 08:00 | Siddhirganj | 237 | 00:00 | 228 | 12:00
Borhanuddin | 248 | 02:00 | 242 | 11:00 | Sirajgonj | 246 | 02:00 | 237 | 12:00
BSRM | 237 | 05:00 | 227 | 23:00 | Sreepur | 239 | 02:00 | 229 | 12:00
Cumilla(N) | 235 | 01:00 | 229 | 12:00 | Tongi | 236 | 04:00 | 221 | 12:00
Faridpur | 246 | 03:00 | 233 | 12:00
Fenchuganj | 234 | 06:00 | 225 | 13:00
Ghorashal | 240 | 00:00 | 235 | 08:00
Ghorashal-230 | 237 | 02:00 | 226 | 12:00
Gopalganj | 246 | 04:00 | 233 | 12:00
GPH | 237 | 05:00 | 228 | 12:00
Haripur | 240 | 04:00 | 227 | 13:00
Hasnabad | 237 | 05:00 | 226 | 12:00
Hathazari | 237 | 19:00 | 232 | 12:00
Ishurdi | 242 | 02:00 | 225 | 12:00
Jhenaidah | 240 | 02:00 | 218 | 12:00
Kaliakoir | 235 | 06:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 128 | 12:00 | Magura | 140 | 02:00 | 126 | 13:00
Agargaon | 138 | 02:00 | 130 | 12:00 | Mahasthangarh | 136 | 03:00 | 128 | 08:00
Agrabad | 135 | 19:00 | 130 | 11:00 | Manikganj | 138 | 04:00 | 130 | 05:00
AKS | 132 | 03:00 | 129 | 07:00 | Maniknagar | 136 | 03:00 | 128 | 12:00
Aminbazar | 137 | 01:00 | 131 | 11:00 | Matarbari | 128 | 05:00 | 120 | 18:00
Amnura | 138 | 19:30 | 130 | 12:00 | Matuail | 137 | 02:00 | 130.2 | 12:00
Ashuganj | 141 | 01:00 | 138 | 08:00 | Millgate | 140 | 04:00 | 128 | 12:00
Bagerhat | 139 | 01:00 | 125 | 12:00 | Mirpur | 135 | 01:00 | 129 | 12:00
Bajitpur | 135 | 00:00 | 132 | 08:00 | Mirzapur | 137 | 04:00 | 130 | 17:00
Bakulia | 135 | 19:00 | 130 | 12:00 | Mithapukur | 135 | 05:00 | 124 | 08:00
Banani | 137 | 01:00 | 128 | 12:00 | MI_Cement | 138.7 | 04:00 | 132 | 11:00
Bangabhaban | 138 | 04:00 | 129 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 02:00 | 129 | 08:00 | Mogbazar | 138 | 04:00 | 129 | 12:00
Barguna | 141 | 17:00 | 135 | 00:00 | Mongla | 135 | 00:00 | 125 | 12:00
Barishal | 135 | 03:00 | 129 | 12:00 | Motijheel | 138 | 04:00 | 129 | 12:00
Barishal-230 | 136 | 02:00 | 129 | 13:00 | Muktagacha | 130 | 23:00 | 120 | 09:00
Baroaulia | 136 | 19:00 | 131 | 12:00 | Munshiganj | 137 | 01:00 | 131 | 12:00
Baroirhat | 134 | 19:30 | 130 | 12:00 | Mymensingh | 130 | 23:00 | 119 | 09:00
Bashundhara | 139 | 03:00 | 128 | 13:00 | Naogaon | 135 | 04:00 | 125 | 09:00
BashundharaCement | 137 | 03:00 | 130 | 12:00 | Narail | 139 | 01:00 | 127 | 13:00
Beanibazar | 138 | 01:00 | 132 | 12:00 | Narinda | 136 | 03:00 | 128 | 12:00
Benapole | 139 | 03:00 | 122 | 12:00 | Narshingdi | 135 | 01:00 | 120 | 18:30
Bhaluka | 130 | 04:00 | 120 | 12:00 | Natore | 137 | 01:00 | 129 | 12:00
Bhandaria | 133 | 05:00 | 125 | 14:00 | Nawabganj | 139 | 01:00 | 130 | 12:00
Bhangura | 139 | 15:00 | 130 | 12:00 | Netrakona | 125 | 21:00 | 116 | 10:00
Bheramara | 139 | 03:00 | 128 | 12:00 | New | 139 | 06:00 | 128 | 12:00
Bheramara(GK) | 138 | 03:00 | 128 | 12:00 | Niamatpur | 140 | 01:00 | 134 | 08:00
Bhulta | 132 | 00:00 | 126 | 12:00 | Noapara | 140 | 04:00 | 126 | 12:00
Bog-Sherpur | 137 | 02:00 | 129 | 12:00 | Pabna | 137 | 02:00 | 126 | 12:00
Bogura | 137 | 01:00 | 131 | 08:00 | Palashbari | 133 | 05:00 | 125 | 11:00
Bogura-230 | 138 | 02:00 | 131 | 12:00 | Panchagarh | 139 | 19:30 | 122 | 08:00
Brahmanbaria | 134 | 02:00 | 127 | 18:30 | Patuakhali | 140 | 17:00 | 133 | 07:00
Cantonment | 138 | 02:00 | 130 | 12:00 | Payra | 138 | 04:00 | 134 | 10:00
Chandpur | 140 | 19:00 | 129 | 01:00 | PHP | 133 | 20:00 | 129 | 09:00
Chandraghona | 136 | 19:00 | 132 | 12:00 | Postogola | 140 | 01:00 | 133 | 12:00
Chapai | 138 | 00:00 | 132 | 08:00 | Purbachal | 138 | 02:00 | 129 | 11:00
Charsaidpur | 138 | 02:00 | 131 | 12:00 | Purbasadipur | 133 | 19:00 | 119 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 04:00 | 131 | 00:00 | Rahanpur | 141 | 00:00 | 136 | 07:00
Chhatak | 136 | 01:00 | 128 | 18:00 | Rahanpur-400 | 142 | 02:00 | 136 | 09:00
Chowmuhani | 134 | 09:00 | 127 | 00:00 | Rahim | 137 | 03:00 | 130 | 12:00
Chuadanga | 139 | 05:00 | 123 | 13:00 | Rajbari | 136 | 03:00 | 127 | 12:00
Coxsbazar | 123 | 03:00 | 119 | 18:00 | Rajendrapur | 137 | 05:00 | 129 | 12:00
Cumilla(N) | 137 | 01:00 | 133 | 12:00 | Rajshahi | 139 | 02:00 | 129 | 13:00
Cumilla(S) | 136 | 08:00 | 128 | 09:00 | Rajshahi-230 | 140 | 03:00 | 127 | 12:00
Daudkandi | 135 | 02:00 | 130 | 11:00 | Ramganj | 136 | 18:00 | 127 | 01:00
Dhaka | 138 | 04:00 | 129 | 12:00 | Rampur | 136 | 04:00 | 129 | 12:00
Dhamrai | 136 | 03:00 | 128 | 10:00 | Rampura | 138 | 04:00 | 128 | 12:00
Dhanmondi | 137.5 | 05:00 | 130.5 | 12:00 | Rangamati | 136 | 05:00 | 131 | 12:00
Dohazari | 132 | 04:00 | 126 | 22:00 | Rangpur | 132 | 04:00 | 120 | 08:00
Faridpur | 135 | 02:00 | 129 | 12:00 | Ruppur | 139 | 05:00 | 132 | 12:00
Fatullah | 140 | 04:00 | 132 | 12:00 | Saidpur | 133 | 03:00 | 120 | 08:00
Fenchuganj | 141 | 06:00 | 136 | 18:30 | Satkhira | 139 | 05:00 | 126 | 12:00
Feni | 134 | 22:00 | 129 | 03:00 | Satmasjid | 139 | 05:00 | 129 | 13:00
Ghatail | 130 | 22:00 | 121 | 07:00 | Savar | 136 | 03:00 | 130 | 12:00
Ghorashal | 140 | 00:00 | 135 | 08:00 | SevenRings | 142 | 03:00 | 136 | 12:00
Goalpara | 139 | 02:00 | 127 | 13:00 | ShahCement | 138 | 02:00 | 131 | 12:00
Gollamari | 141 | 04:00 | 129 | 12:00 | Shahjadpur | 142 | 03:00 | 133 | 12:00
Gopalganj | 139 | 05:00 | 128 | 12:00 | Shahjibazar | 137 | 00:00 | 131 | 18:30
Gopalganj-400 | 138 | 03:00 | 130 | 12:00 | Shahmirpur | 136 | 02:00 | 131 | 11:00
Gulshan | 136 | 04:00 | 128 | 12:00 | Shariatpur | 138 | 03:00 | 128 | 13:00
Halishahar | 136 | 05:00 | 130 | 12:00 | Sherpur | 124 | 00:00 | 114 | 07:00
Haripur | 137 | 02:00 | 130 | 12:00 | Shikalbaha | 125 | 19:30 | 119 | 12:00
HaripurSBU | 137 | 02:00 | 131 | 11:00 | Shikalbaha-230 | 136 | 04:00 | 122 | 13:00
Hasnabad | 139 | 01:00 | 133 | 10:00 | Shitalakhya | 138.7 | 04:00 | 132 | 11:00
Hathazari | 137 | 18:00 | 133 | 23:00 | Sholosohor | 136 | 05:00 | 131 | 12:00
Ishurdi | 141 | 02:00 | 131 | 12:00 | Shyampur | 140 | 04:00 | 133 | 12:00
Jaldhaka | 132 | 20:00 | 120 | 08:00 | Shyampur-230 | 139 | 02:00 | 130 | 12:00
Jamalpur | 127 | 22:00 | 116 | 09:00 | Siddhirganj | 137 | 01:00 | 130 | 12:00
Jashore | 138 | 03:00 | 123 | 12:00 | Sirajganj | 140 | 04:00 | 129 | 12:00
Jhenaidah | 138 | 04:00 | 127 | 12:00 | Sonargaon | 136 | 01:00 | 129 | 11:00
Jhenaidah-230 | 141 | 02:00 | 126 | 12:00 | Sreemongol | 138 | 00:00 | 133 | 18:30
Joydebpur | 139 | 19:30 | 131 | 11:00 | Sreepur | 130 | 05:00 | 122 | 12:00
Joypurhat | 134 | 01:00 | 126 | 18:30 | Srinagar | 140 | 04:00 | 132 | 12:00
Juldah | 136 | 18:30 | 131 | 00:00 | SSM | 140 | 19:30 | 132 | 13:00
Kabirpur | 139 | 01:00 | 126 | 13:00 | Sunamganj | 135 | 00:00 | 130 | 12:00
Kachua | 137 | 19:00 | 130 | 00:00 | Sylhet | 138 | 03:00 | 132 | 18:30
Kaliakoir | 141 | 06:00 | 128 | 12:00 | Sylhet-132 | 139 | 02:00 | 132 | 12:00
Kallyanpur | 136 | 02:00 | 127 | 11:00 | Tangail | 132 | 04:00 | 126 | 08:00
Kalurghat | 135 | 03:00 | 130 | 10:00 | Thakurgaon | 138 | 19:00 | 119 | 08:00
Kamrangirchar | 140 | 03:00 | 125 | 12:00 | TK | 136 | 19:30 | 132 | 12:00
Kaptai | 137 | 10:00 | 135 | 13:00 | Tongi | 141 | 04:00 | 131 | 12:00
Kazla | 137 | 03:00 | 128 | 13:00 | Ullahpara | 138 | 00:00 | 130 | 12:00
Keranigonj | 139 | 04:00 | 131 | 12:00 | Ullon | 137 | 06:00 | 128 | 12:00
Khagrachori | 135 | 04:00 | 130 | 12:00 | Uttara | 136 | 01:00 | 128 | 13:00
Khulna | 137 | 00:00 | 126 | 13:00 | UttaraNew | 139 | 03:00 | 127 | 12:00
Khulna(S) | 141 | 02:00 | 129 | 12:00 | Zigatola | 141 | 05:00 | 132 | 12:00
Khulshi | 134 | 19:00 | 128 | 12:00
Kishoreganj | 132 | 03:00 | 126 | 09:00
Kodda | 138 | 05:00 | 129 | 11:00
KSRM | 137 | 19:30 | 132 | 02:00
Kulaura | 140 | 00:00 | 136 | 12:00
Kurigram | 133 | 19:30 | 121 | 18:00
Kushtia | 139 | 02:00 | 128 | 11:00
Lalbag | 140 | 04:00 | 131 | 12:00
Lalmonirhat | 132 | 20:00 | 121 | 08:00
Madanganj | 137 | 03:00 | 130 | 12:00
Madaripur | 136 | 04:00 | 130 | 12:00
Madartek | 137 | 04:00 | 128 | 12:00
Madunaghat | 136 | 04:00 | 132 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division