## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-02-2025 | [28 empty] | Date: | 02-02-2025 | [28 empty] | Date: | 02-02-2025 | [28 empty] | Date: | 02-02-2025 | [28 empty] | Date: | 02-02-2025 | [19 empty] | Date: | 02-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [19 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 64 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 17 | 0 | 400 | 281 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 220 | 0 | 0 | 19 | 0 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 50 | 50 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 295 | 0 | 288 | 36 | 42 | 0 | 5 | 113 | 0 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 16 | 68 | 0 | 0 | 0 | 5007 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 315 | 0 | 0 | 2.5 | 176 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 100 | 4207.5 | 9214.5 | 91.67
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 269 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 39 | 217 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 280 | 0 | 291 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 4711 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 319 | 0 | 0 | 2.5 | 173 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 132 | 220 | 0 | 0 | 1050 | 0 | 3977.5 | 8688.5 | 91.66
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 293 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 219 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 189 | 27 | 0 | 70 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 290 | 0 | 291 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 4660 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 140 | 0 | 325 | 0 | 0 | 2.5 | 169 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 132 | 220 | 0 | 0 | 1050 | 0 | 3688.5 | 8348.5 | 91.66
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 290 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 218 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 840 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 188 | 27 | 0 | 70 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 300 | 0 | 291 | 33 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 4503 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 126 | 0 | 320 | 0 | 0 | 2.5 | 169 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 132 | 220 | 0 | 0 | 1050 | 0 | 3588.5 | 8091.5 | 91.65
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 291 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 217 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 190 | 24 | 0 | 70 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 300 | 0 | 293 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 4362 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 120 | 0 | 325 | 0 | 0 | 2.5 | 167 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 132 | 220 | 0 | 0 | 1050 | 0 | 3487.5 | 7849.5 | 91.65
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 290 | 0 | 0 | 0 | 33 | 290 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 218 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 188 | 24 | 0 | 80 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 305 | 0 | 287 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 4235 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 111 | 0 | 320 | 0 | 0 | 2.5 | 167 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 1050 | 0 | 3417.5 | 7652.5 | 91.64
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 311 | 0 | 0 | 0 | 33 | 280 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 216 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 197 | 24 | 0 | 80 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 340 | 33 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0 | 0 | 4354 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 110 | 0 | 414 | 0 | 0 | 2.5 | 161 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 132 | 220 | 0 | 0 | 1045 | 0 | 3635.5 | 7989.5 | 91.64
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 314 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 324 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 217 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1074 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 216 | 24 | 0 | 80 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 290 | 0 | 380 | 33 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 72 | 0 | 0.2 | 3 | 4831.2 | 811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 109 | 0 | 414 | 0 | 0 | 2.5 | 160 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 132 | 220 | 0 | 0 | 1120 | 0 | 4039.5 | 8870.7 | 91.63
08:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 64 | 304 | 0 | 0 | 15 | 0 | 0 | 60 | 32 | 0 | 1 | 19 | 90 | 0 | 0 | 450 | 306 | 0 | 0 | 30 | 16.5 | 335 | 0 | 0 | 2 | 0 | 19 | 22 | 0 | 0 | 18 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 6 | 1 | 1 | 40 | 10 | 8 | 217 | 17 | 0 | 8 | 0 | 12 | 30 | 0 | 0 | 0 | 1224 | 2 | 51 | 10 | 195 | 0 | 0 | 0 | 29 | 189 | 20 | 19 | 70 | 100 | 10 | 17 | 0 | 52 | 0 | 3 | 0 | 320 | 0 | 342 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 15 | 9 | 56 | 69 | 0 | 1.73 | 6 | 5373.23 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.25 | 0 | 0 | 750.51 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.78 | 131 | 0 | 0 | 0 | 109 | 0 | 395 | 0 | 0.24 | 2.5 | 161 | 66 | 35 | 2 | 35 | 0 | 0 | 0.4 | 8 | 0.02 | 0 | 307 | 6 | 132 | 220 | 0 | 0 | 1120 | 115 | 4267.7 | 9640.93 | 91.63
09:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 64 | 295 | 0 | 0 | 54 | 0 | 0 | 85 | 32 | 0 | 15 | 55 | 162 | 8 | 0 | 450 | 314 | 0 | 0 | 35 | 33 | 335 | 0 | 0 | 4 | 0 | 21 | 22 | 0 | 0 | 35 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2 | 40 | 34 | 2 | 218 | 17 | 0 | 32 | 0 | 50 | 30 | 0 | 0 | 0 | 1224 | 9 | 43 | 30 | 197 | 0 | 0 | 0 | 29 | 204 | 26 | 82 | 50 | 100 | 42 | 8 | 0 | 54 | 0 | 11 | 0 | 325 | 0 | 370 | 33 | 42 | 0 | 5 | 90 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 32 | 0 | 4.13 | 6 | 5823.13 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 755.15 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 4.07 | 122 | 0 | 0 | 0 | 108 | 0 | 414 | 0 | 0.44 | 2.5 | 158 | 66 | 35 | 4 | 35 | 0 | 0 | 1.2 | 25 | 0.06 | 0 | 307 | 4 | 132 | 220 | 0 | 0 | 1120 | 150 | 4354.42 | 10177.55 | 91.62
10:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 70 | 290 | 0 | 0 | 54 | 0 | 0 | 85 | 32 | 0 | 15 | 55 | 162 | 17 | 0 | 450 | 286 | 0 | 0 | 35 | 16.5 | 335 | 0 | 0 | 7 | 0 | 21 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3 | 40 | 34 | 2 | 215 | 17 | 0 | 32 | 0 | 68 | 36 | 0 | 0 | 0 | 1224 | 14 | 43 | 30 | 185 | 0 | 0 | 0 | 29 | 182 | 30 | 95 | 50 | 100 | 65 | 17 | 0 | 52 | 0 | 12 | 0 | 310 | 0 | 370 | 33 | 42 | 0 | 5 | 80 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 33 | 0 | 7.53 | 6 | 5818.03 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1 | 0 | 0 | 661.46 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 26 | 0 | 10.52 | 122 | 0 | 0 | 0 | 108 | 0 | 313 | 0 | 1.24 | 2.5 | 156 | 65 | 35 | 6 | 6 | 0 | 0 | 1.4 | 43 | 0.07 | 0 | 250 | 4 | 100 | 220 | 0 | 0 | 1120 | 116 | 4350.29 | 10168.32 | 91.62
11:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 71 | 292 | 0 | 0 | 54 | 0 | 0 | 85 | 32 | 0 | 15 | 55 | 162 | 17 | 0 | 450 | 290 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 8 | 0 | 21 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3 | 40 | 34 | 2 | 216 | 17 | 0 | 32 | 0 | 68 | 44 | 0 | 0 | 0 | 1224 | 17 | 43 | 33 | 185 | 0 | 0 | 0 | 29 | 188 | 28 | 96 | 50 | 100 | 67 | 17 | 0 | 62 | 0 | 19 | 0 | 300 | 0 | 370 | 33 | 41 | 0 | 5 | 80 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 31 | 1 | 18.37 | 6 | 5829.87 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.47 | 0 | 0 | 660.63 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 64 | 0 | 25.3 | 124 | 0 | 0 | 0 | 108 | 0 | 321 | 0 | 2.68 | 2.5 | 162 | 65 | 35 | 13 | 6 | 0 | 0 | 2.7 | 60 | 0.06 | 0 | 300 | 4 | 100 | 200 | 0 | 0 | 1120 | 116 | 4502.34 | 10332.21 | 91.62
12:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 69 | 315 | 0 | 0 | 54 | 0 | 0 | 85 | 32 | 0 | 15 | 55 | 155 | 25 | 0 | 450 | 290 | 0 | 0 | 35 | 32 | 300 | 0 | 0 | 16 | 0 | 20.5 | 0 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 4 | 40 | 34 | 2 | 217 | 17 | 0 | 32 | 0 | 68 | 73 | 0 | 0 | 0 | 1224 | 10 | 43 | 55 | 195 | 0 | 0 | 0 | 29 | 183 | 30 | 95 | 70 | 136 | 64 | 17 | 0 | 68 | 0 | 22 | 0 | 300 | 0 | 335 | 33 | 41 | 0 | 5 | 80 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 58 | 30 | 1 | 27.14 | 6 | 5957.64 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.46 | 0 | 0 | 753.92 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 80 | 8 | 14.89 | 129 | 0 | 0 | 0 | 115 | 0 | 393 | 0 | 0.79 | 2.5 | 162 | 65 | 60 | 20 | 6 | 0 | 0 | 3.8 | 89 | 0.47 | 0 | 307 | 4 | 100 | 210 | 0 | 0 | 1120 | 116 | 4775.83 | 10733.47 | 91.61
13:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 69 | 402 | 0 | 0 | 54 | 0 | 0 | 89 | 16 | 0 | 15 | 55 | 144 | 25 | 0 | 450 | 286 | 0 | 0 | 35 | 8 | 330 | 0 | 0 | 24 | 0 | 20.5 | 0 | 0 | 0 | 35 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3 | 40 | 34 | 9 | 216 | 10 | 0 | 32 | 0 | 68 | 106 | 0 | 0 | 0 | 1224 | 7 | 43 | 100 | 195 | 0 | 0 | 0 | 29 | 190 | 30 | 95 | 50 | 132 | 50 | 17 | 0 | 68 | 0 | 45 | 0 | 300 | 0 | 370 | 36 | 41 | 0 | 5 | 80 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 58 | 28 | 1 | 31.15 | 6 | 6121.65 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.23 | 0 | 0 | 753.07 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 84 | 14 | 16.53 | 134 | 0 | 0 | 0 | 170 | 0 | 360 | 0 | 1.07 | 2.5 | 163 | 66 | 69 | 18 | 5 | 0 | 0 | 3.6 | 139 | 0.37 | 0 | 302 | 4 | 100 | 220 | 0 | 0 | 1120 | 116 | 4870.37 | 10992.02 | 91.61
14:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 69 | 405 | 0 | 0 | 54 | 0 | 0 | 98 | 16 | 0 | 0 | 55 | 144 | 25 | 0 | 400 | 240 | 0 | 0 | 35 | 32 | 310 | 0 | 0 | 20 | 0 | 20.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 3 | 216 | 0 | 0 | 32 | 0 | 68 | 195 | 0 | 0 | 0 | 1136 | 14 | 43 | 100 | 195 | 0 | 0 | 0 | 29 | 182 | 30 | 95 | 50 | 100 | 29 | 17 | 0 | 64 | 0 | 40 | 0 | 305 | 0 | 370 | 30 | 41 | 0 | 5 | 113 | 17 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 58 | 28 | 1 | 13.82 | 6 | 5907.32 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 0 | 0 | 753.33 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 71 | 14 | 32.53 | 143 | 0 | 0 | 0 | 208 | 0 | 313 | 0 | 3.2 | 2.5 | 165 | 66 | 70 | 15 | 0 | 0 | 0 | 2.8 | 127 | 0.23 | 0 | 241 | 3 | 134 | 220 | 0 | 0 | 1120 | 116 | 4822.23 | 10729.55 | 91.61
15:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 65 | 353 | 0 | 0 | 54 | 0 | 0 | 96 | 16 | 0 | 0 | 55 | 144 | 17 | 0 | 400 | 248 | 0 | 0 | 35 | 32 | 270 | 0 | 0 | 14 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 216 | 0 | 0 | 32 | 0 | 25 | 185 | 0 | 0 | 0 | 1100 | 11 | 43 | 100 | 195 | 0 | 0 | 0 | 29 | 183 | 30 | 50 | 50 | 51 | 28 | 17 | 0 | 64 | 0 | 33 | 0 | 300 | 0 | 371 | 33 | 40 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 58 | 31 | 1 | 15.64 | 6 | 5616.64 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.49 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 56 | 14 | 24.28 | 160 | 0 | 0 | 0 | 220 | 0 | 313 | 0 | 2.22 | 2.5 | 171 | 66 | 35 | 10 | 0 | 0 | 0 | 2.2 | 92 | 0.23 | 0 | 307 | 3 | 134 | 220 | 0 | 0 | 1132 | 54 | 4748.92 | 10365.56 | 91.6
16:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 67 | 400 | 0 | 0 | 17 | 0 | 0 | 59 | 16 | 0 | 0 | 55 | 54 | 17 | 0 | 400 | 270 | 0 | 0 | 17 | 32 | 270 | 0 | 0 | 8 | 0 | 14 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 156 | 0 | 0 | 32 | 0 | 17 | 186 | 0 | 0 | 0 | 1105 | 6 | 43 | 100 | 195 | 0 | 0 | 0 | 29 | 183 | 29 | 16 | 50 | 17 | 9 | 17 | 0 | 64 | 0 | 17 | 0 | 290 | 0 | 371 | 33 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 58 | 32 | 1 | 10.52 | 6 | 5310.52 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.24 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 32 | 14 | 14.15 | 160 | 0 | 0 | 0 | 220 | 0 | 314 | 0 | 1.31 | 2.5 | 174 | 68 | 35 | 6 | 0 | 0 | 0 | 1.2 | 40 | 0.13 | 0 | 307 | 3 | 134 | 220 | 0 | 0 | 1120 | 17 | 4608.53 | 9919.05 | 91.6
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 69 | 409 | 0 | 0 | 17 | 0 | 0 | 64 | 16 | 0 | 0 | 55 | 54 | 17 | 0 | 400 | 267 | 0 | 0 | 17 | 32 | 270 | 0 | 0 | 2 | 0 | 20.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 156 | 0 | 0 | 32 | 0 | 17 | 187 | 0 | 0 | 0 | 1119 | 1 | 51 | 100 | 195 | 0 | 0 | 0 | 30 | 183 | 26 | 16 | 50 | 17 | 9 | 17 | 0 | 62 | 0 | 5 | 0 | 300 | 0 | 370 | 33 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 58 | 33 | 0 | 3.12 | 6 | 5327.62 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.93 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | 0 | 8 | 14 | 3.78 | 160 | 0 | 0 | 0 | 220 | 0 | 315 | 0 | 0.31 | 2.5 | 175 | 66 | 35 | 2 | 0 | 0 | 0 | 0.4 | 11 | 0.04 | 0 | 307 | 4 | 134 | 220 | 0 | 0 | 1110 | 17 | 4527.96 | 9855.58 | 91.6
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 65 | 350 | 0 | 0 | 31 | 0 | 0 | 88 | 64 | 0 | 15 | 55 | 162 | 25 | 0 | 350 | 275 | 0 | 0 | 30 | 30 | 270 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 18 | 24 | 0 | 40 | 11 | 4 | 155 | 17 | 0 | 32 | 0 | 30 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 195 | 0 | 0 | 0 | 29 | 183 | 30 | 34 | 50 | 54 | 29 | 17 | 0 | 64 | 0 | 0 | 23 | 280 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 11 | 67 | 33 | 0 | 0 | 6 | 5805 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 25 | 0 | 0 | 4 | 98 | 0 | 7 | 0 | 0 | 30 | 0 | 160 | 0 | 0 | 0 | 220 | 0 | 313 | 0 | 0 | 2.5 | 175 | 66 | 77 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 180 | 0 | 0 | 1110 | 116 | 4730.5 | 10535.5 | 91.6
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 65 | 429 | 0 | 0 | 54 | 0 | 0 | 141 | 64 | 0 | 45 | 17 | 162 | 25 | 0 | 400 | 262 | 0 | 0 | 35 | 17 | 333 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 68 | 50 | 0 | 36 | 50 | 0 | 40 | 53 | 4 | 156 | 90 | 0 | 32 | 0 | 68 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 195 | 0 | 0 | 0 | 29 | 182 | 30 | 115 | 50 | 123 | 68 | 17 | 0 | 66 | 0 | 0 | 36 | 300 | 0 | 369 | 36 | 41 | 0 | 5 | 113 | 25 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 77 | 33 | 0 | 0 | 6 | 6532 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 40 | 0 | 0 | 5 | 98 | 0 | 35 | 0 | 0 | 30 | 0 | 198 | 0 | 0 | 0 | 220 | 0 | 394 | 0 | 0 | 2.5 | 177 | 66 | 95 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 180 | 0 | 0 | 1120 | 150 | 4697.5 | 11229.5 | 91.59
19:30 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 65 | 409 | 0 | 0 | 54 | 0 | 0 | 80 | 64 | 0 | 15 | 17 | 162 | 25 | 0 | 400 | 295 | 0 | 0 | 35 | 28 | 328 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 68 | 50 | 0 | 12 | 18 | 0 | 40 | 34 | 27 | 157 | 90 | 0 | 32 | 0 | 68 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 195 | 0 | 0 | 0 | 29 | 202 | 30 | 115 | 50 | 85 | 68 | 17 | 0 | 64 | 0 | 0 | 0 | 320 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 25 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 77 | 33 | 0 | 0 | 6 | 6286 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 5 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 414 | 0 | 0 | 2.5 | 172 | 66 | 95 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 1120 | 100 | 4592.5 | 10878.5 | 91.59
20:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 63 | 406 | 0 | 0 | 54 | 0 | 0 | 100 | 64 | 0 | 15 | 17 | 162 | 25 | 0 | 400 | 285 | 0 | 0 | 35 | 32 | 333 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 68 | 50 | 0 | 12 | 12 | 0 | 40 | 34 | 33 | 157 | 90 | 0 | 32 | 0 | 68 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 195 | 0 | 0 | 0 | 29 | 187 | 30 | 115 | 50 | 85 | 68 | 17 | 0 | 62 | 0 | 0 | 0 | 300 | 0 | 370 | 36 | 42 | 0 | 5 | 113 | 25 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 78 | 33 | 0 | 0 | 6 | 6271 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 5 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 394 | 0 | 0 | 2.5 | 170 | 66 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 1130 | 100 | 4573.5 | 10844.5 | 91.59
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 75 | 405 | 0 | 0 | 54 | 0 | 0 | 78 | 32 | 0 | 0 | 17 | 108 | 25 | 0 | 400 | 306 | 0 | 0 | 35 | 31 | 330 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 157 | 0 | 0 | 32 | 0 | 34 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 195 | 0 | 0 | 0 | 29 | 203 | 30 | 50 | 50 | 34 | 34 | 17 | 0 | 64 | 0 | 0 | 0 | 310 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 0 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 79 | 33 | 0 | 0 | 6 | 5737 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.58 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 414 | 0 | 0 | 2.5 | 165 | 66 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 134 | 220 | 0 | 0 | 1140 | 100 | 4747.08 | 10484.08 | 91.59
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 79 | 403 | 0 | 0 | 54 | 0 | 0 | 56 | 16 | 0 | 0 | 0 | 54 | 22 | 0 | 400 | 295 | 0 | 0 | 17 | 31 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 158 | 0 | 0 | 32 | 0 | 34 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 195 | 0 | 0 | 0 | 29 | 194 | 30 | 50 | 50 | 34 | 34 | 17 | 0 | 60 | 0 | 0 | 0 | 315 | 0 | 370 | 33 | 41 | 0 | 5 | 113 | 0 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 9 | 55 | 33 | 0 | 0 | 6 | 5432 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 408 | 0 | 0 | 2.5 | 170 | 67 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 134 | 220 | 0 | 0 | 1140 | 54 | 4706.5 | 10138.5 | 91.59
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 71 | 402 | 0 | 0 | 54 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 54 | 22 | 0 | 400 | 275 | 0 | 0 | 17 | 31 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 156 | 0 | 0 | 32 | 0 | 34 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 30 | 50 | 50 | 34 | 34 | 17 | 0 | 58 | 0 | 0 | 0 | 300 | 0 | 370 | 30 | 41 | 0 | 5 | 113 | 16 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 9 | 55 | 34 | 0 | 0 | 6 | 5356 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 309 | 0 | 0 | 2.5 | 165 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 100 | 180 | 0 | 0 | 1140 | 0 | 4420.98 | 9776.98 | 91.58
Total KWH | 0 | 766080 | 334080 | 0 | 0 | 0 | 0 | 1612090.92 | 8985600 | 0 | 0 | 766440 | 0 | 0 | 1402704 | 483840 | 0 | 188515 | 664706 | 2062080 | 462600 | 0 | 9839000 | 6898327 | 0 | 0 | 510543 | 630500 | 7619276 | 0 | 0 | 106868 | 0 | 471600 | 477720 | 0 | 0 | 575836 | 80291 | 58560 | 0 | 19680 | 187521 | 130032 | 0 | 146880 | 150720 | 20762 | 980000 | 347090 | 483360 | 4632727.27 | 265964 | 0 | 517440 | 0 | 852255 | 3081443 | 0 | 0 | 0 | 26705452 | 99900 | 1145304 | 1167563 | 4683636 | 0 | 0 | 0 | 696960 | 4668000 | 671832 | 1230720 | 1363730 | 1248480 | 708960 | 400850 | 0 | 1406400 | 0 | 202400 | 48976 | 7369000 | 0 | 8713000 | 798336 | 974000 | 0 | 116784 | 2504700 | 501648 | 0 | 2053440 | 715584 | 0 | 221000 | 0 | 515880 | 177600 | 1096800 | 1034880 | 5200 | 133660 | 108480 | 130302286.19 | 19882077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315360 | 0 | 0 | 16652062 | 0 | 0 | 55439 | 0 | 69408 | 14392 | 858656 | 0 | 25202 | 0 | 433330 | 132016 | 159000 | 3456273 | 0 | 0 | 0 | 4180364 | 0 | 8653018 | 0 | 14340 | 67158 | 4084000 | 1565673 | 849080 | 88633 | 235920 | 0 | 0 | 20870.04 | 628560 | 1804.5 | 0 | 6393000 | 135304 | 2991000 | 4985760 | 0 | 0 | 26930909.09 | 1498800 | 105377408.63 | 235679694.82

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-02-2025 | during | 03-02-2025 | during | 03-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 69 | 65 | 97.3 | 97.3 | 77 | 77 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 315 | 429 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 290 | 262 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 45 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20.5 | 21 | 22.5 | 22.5 | 22.5 | 22.5 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 0 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 32 | 17 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 26 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 85 | 141 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 155 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 17 | 17 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.654 | 2026.5 | 2169 | 4569.49 | 4551.49 | 2795.71 | 2777.71
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 73 | 186 | 225 | 225 | 151 | 151 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 68 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 50 | 75 | 75 | 75 | 75 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 68 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 4 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.58 | 0 | 3.58 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 53 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 90 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 2 | 5 | 12 | 5 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 217 | 156 | 150 | 150 | 220 | 220 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1807 | 2094 | 3055.3 | 3059.72 | 2970.3 | 2974.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 356.56 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 30 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 55 | 55 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 55 | 125 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 50 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 123 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 66 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 64 | 68 | 113 | 113 | 34 | 34 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 95 | 115 | 115 | 115 | 95 | 95 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 22 | 0 | 53 | 0 | 53 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1007 | 1087 | 2113.53 | 2060.53 | 1528.03 | 1475.03
2025-02-03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 2025-02-03 | during | 2025-02-03 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 33 | 210 | 210 | 80 | 80 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 77 | 200 | 200 | 58 | 58 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 27.14 | 0 | 31 | 0 | 31 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 166.14 | 160 | 634.2 | 601.5 | 256.2 | 223.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 41 | 41 | 41 | 42 | 41 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 113 | 163 | 163 | 113 | 113 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 36 | 44 | 44 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 335 | 369 | 380 | 380 | 252 | 252 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 100 | 250 | 0.01 | 0.01 | Only Gas turbine is available
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 951 | 1022 | 1205 | 1356 | 919.01 | 920.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 622 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 57.46 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 964.46 | 622 | 2829 | 2759 | 1155.01 | 1085.01
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 134 | 136 | 136 | 140 | 140 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 210 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 116 | 150 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1857.47 | 1898 | 2178.12 | 2177.12 | 2139 | 2138
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 40 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 129 | 198 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 115 | 220 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 393 | 394 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 8 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 51 | 98 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 0.79 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 753.92 | 752 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 14.89 | 0 | 28 | 0 | 28 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 80 | 0 | 70 | 0 | 70 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1548.1 | 1774.5 | 2578.59 | 2476.04 | 2123.81 | 2021.26
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 65 | 66 | 69 | 69 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 162 | 177 | 160 | 160 | 160 | 160 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 65 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 4.1 | 0 | 4.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 60 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 89 | 0 | 120 | 0 | 120 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 405.8 | 403 | 635.1 | 491 | 602.12 | 458.02
System Total |  |  |  |  | 27884.66 | 27066.632 | 10733.47 | 11229.5 | 19798.33 | 19532.4 | 14489.19 | 14073.26
Forecast Scenario (03-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9100 |  | 0 |  | 9100
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8160 |  | 0 |  | 8160
|  |  |  | 3:00 | 7910 |  | 0 |  | 7910
|  |  |  | 4:00 | 7630 |  | 0 |  | 7630
|  |  |  | 5:00 | 7600 |  | 0 |  | 7600
|  |  |  | 6:00 | 8020 |  | 0 |  | 8020
|  |  |  | 7:00 | 8880 |  | 0 |  | 8880
|  |  |  | 8:00 | 9880 |  | 0 |  | 9880
|  |  |  | 9:00 | 10300 |  | 0 |  | 10300
|  |  |  | 10:00 | 10100 |  | 0 |  | 10100
|  |  |  | 11:00 | 10250 |  | 0 |  | 10250
|  |  |  | 12:00 | 10600 |  | 0 |  | 10600
|  |  |  | 13:00 | 11000 |  | 0 |  | 11000
|  |  |  | 14:00 | 10560 |  | 0 |  | 10560
|  |  |  | 15:00 | 10100 |  | 0 |  | 10100
|  |  |  | 16:00 | 9700 |  | 0 |  | 9700
|  |  |  | 17:00 | 9950 |  | 0 |  | 9950
|  |  |  | 18:00 | 10700 |  | 0 |  | 10700
|  |  |  | 18:30 | 10950 |  | 0 |  | 10950
|  |  |  | 19:00 | 11200 |  | 0 |  | 11200
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10850 |  | 0 |  | 10850
|  |  |  | 21:00 | 10660 |  | 0 |  | 10660
|  |  |  | 22:00 | 10150 |  | 0 |  | 10150
|  |  |  | 23:00 | 9680 |  | 0 |  | 9680
Probable Maximum Temperature: |  |  | 27.10°C
Probable Maximum Demand at Day Peak: |  |  | 10600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 11200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 231.48 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 09:58 hrs on 03-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10733.47 | MW | 12:00 Hr. | Energy Generated |  |  | 235.6797 |  | MKWHr.
| Day Peak Demand |  |  | 10733.47 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.073 |  | MKWHr.
| Evening Peak Generation |  |  | 11229.5 | MW | 19:00 Hr. | Energy Demand |  |  | 235.7527 |  | MKWHr.
| Evening Peak Demand |  |  | 11229.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.7 |  | °C
| Minimum Generation of the Day |  |  | 7652.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 792.43 |  | MMCFD
| Maximum Generation of the Day |  |  | 11229.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.2772 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.9967 | 0 | 7.179 | 0 | 0 | 0.10687 | 0 | 0 | 44.2826 | Gas | 103.6631 | Gas | 375097517.032
| Chattogram Zone |  |  | 3.5648 | 31.3382 | 3.3126 | 0 | 0.98 | 0.12066 | 0 | 0.01968 | 39.3359 | Coal | 70.3118 | Coal | 496345303.9993
| Cumilla Zone |  |  | 13.6303 | 0 | 4.4047 | 0 | 0 | 0.2024 | 1.4064 | 0 | 19.6438 | HFO | 20.5339 | HFO | 372720084.8
| Mymensingh Zone |  |  | 1.0349 | 0 | 1.8988 | 0 | 0 | 0.13886 | 0 | 0 | 3.0725 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.9675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9675 | Hydro | 0.98 | Hydro | 98000
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.31536 | 19.8821 | 0 | 20.1974 | Solar | 2.2307 | Solar | 35000521.309
| Barishal Zone |  |  | 8.1121 | 33.3239 | 1.4988 | 0 | 0 | 0.0018045 | 0 | 0 | 42.9366 | Import | 37.9405 | Import | 199850670.68
| Rajshahi Zone |  |  | 16.3568 | 0 | 1.1551 | 0 | 0 | 0.60667 | 16.6521 | 0 | 34.7707 | Wind | 0.01968 | Wind | 307008
| Rangpur Zone |  |  | 0 | 5.6497 | 1.085 | 0 | 0 | 0.73806 | 0 | 0 | 7.4727
| Total |  |  | 103.6631 | 70.3118 | 20.5339 | 0 | 0.98 | 2.2307 | 37.9405 | 0.01968 | 235.6797
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 375097517.032 |  | Hydro | 98000
|  |  |  | Coal | 496345303.9993 |  | Solar | 35000521.309
|  |  |  | HFO | 372720084.8 |  | Import | 199850670.68
|  |  |  | HSD | 0 |  | Wind | 307008
[5 empty] | Total: | 147,94,19,105 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.8821 | Peak Hr Flow | 622.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6100381 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.6521 | Peak Hr Flow | 752.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 408 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4064 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 760 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.9405 | Peak Hr Flow | 1440.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3857
|  |  |  | Chattogram |  | 0 |  | 1238
|  |  |  | Cumilla |  | 0 |  | 929
|  |  |  | Mymensingh |  | 0 |  | 982
|  |  |  | Sylhet |  | 0 |  | 385
|  |  |  | Khulna |  | 0 |  | 1206
|  |  |  | Barishal |  | 0 |  | 300
|  |  |  | Rajshahi |  | 0 |  | 1097
|  |  |  | Rangpur |  | 0 |  | 805
|  |  |  | Total |  | 0 |  | 10799
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1122 |  |  |  | Total | 720.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1842.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 13:06 | Chandpur 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
| 08:21 | 17:00 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Annual
maintenance.
| 08:40 | 21:46 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D Due to CT Replace
| 08:45 | 19:33 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to Deed line
checking of Sylhet-Chhatak Ckt-1
| 08:51 | 15:03 | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Nawabganj 132/33kV end Due to
Deadline checking and from Keranigonj 230/132/33kV end Due to Dead line cheking and
yearly maintenance.
| 09:14 | 12:56 | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Mogbazar 132/33kV end. and from Rampura
230/132kV end Due to Work@ Mogbazar End for Annual Maintenance.
| 09:22 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to dead line
checking
| 09:50 | 10:24 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Tripped showing Diff. Relay relays Due to
Diff. pickup
| 09:50 | 10:25 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Tripped showing Diff. relay relays Due to
Diff. Pickup
| 09:50 | 10:26 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Tripped showing SIPROTEC 7SA611 relays
Due to Z1 trip at 34.9 km.
| 09:56 | 14:33 | GPH 230/33kV S/S ABUL KHAIR Forced S/D Due to Maintenance work in B phase Isolator.
| 10:59 | 17:36 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end.
| 11:03 | 13:20 | Sonargaon 132/33kV S/S Bashundhara Line Scheduled S/D Due to multi-meter change purpose.
| 11:10 | 17:37 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Thakurgaon 132/33kV end Due
to Tower painting for LILo ckt
| 11:26 |  | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to Anuual Maintenance on 132 KV, Relay test
by spmd PGCB.
| 11:28 | 12:29 | Mirpur 132/33kV S/S T1 HT Scheduled S/D Due to Anuual Maintenance on 132 KV, Relay test
by spmd PGCB.
| 12:00 |  | Day Peak generation = 10,734MW
| 12:45 | 17:12 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Faridpur 132/33kV end Due to Relay
test by SPMD, Khulna. and from Gopalganj 400/132kVend.
| 12:48 | 21:50 | Kabirpur -Tongi 132kV Ckt-1 Project Work S/D from Tongi 230/132/33kV end Due to Bay
Extension Work.
| 12:57 | 15:33 | Moghbazar-Rampura 132kV Ckt-1 Forced S/D from Mogbazar 132/33kV end Due to Line Isolator
Redhot and from Rampura 230/132kV end Due to Maintetance. Mogbazar 1 End.
|  | 13:10 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT is restored.
|  | 13:10 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT is restored.
| 13:55 | 15:15 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Relay tripping test
by SPMD
| 13:55 | 15:13 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Relay tripping test
by SPMD
|  | 14:29 | Jashore 132/33kV S/S T-3 LT is restored.
| 14:53 | 19:53 | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to S/D For Chhatak-1 and 90 MW
PS Looping Purpose.
|  | 15:40 | Khulshi-Madunaghat 132kV Ckt-1 is restored.
|  | 17:00 | Savar 132/33kV S/S Main Bus is restored.
|  | 18:49 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 is restored.
| 20:48 |  | Faridpur 132/33kV S/S Transformer-3 HT Forced S/D Due to Underground cable problem
| 02:41 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 04:02 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 06:33 |  | Rohanpur---Monakosha 400 KV ckt--1 S/D
| 06:45 | 07:07 | Kaliakoir-Tangail 132kV Ckt-1 Tripped from Kaliakoir 400/230/132kV end showing Dir.Over | [7 empty] | 147.0MW load
|  |  | Current relay relays Due to Dir.Over Current | [7 empty] | interrup. Kaliakoir
400/230/132kV end
| 06:45 | 07:06 | Kaliakoir-Tangail 132kV Ckt-2 Tripped from Kaliakoir 400/230/132kV end showing Distance | [7 empty] | 141.0MW load
|  |  | relay relays Due to Zone -01 Trip | [7 empty] | interrup. Kaliakoir
400/230/132kV end
| 07:10 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to CB=152, B Phase Bus loop joint
redhot maintenance.
| 07:10 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to CB=152, B Phase Bus loop joint
redhot maintenance.
| 07:44 |  | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 65 | 1612090.92 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 429 | 8985600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9839000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 262 | 6898327 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 45 | 188515 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7619276 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 766440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 483840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 664706 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 510543 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 471600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 477720 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 462600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 630500 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 334080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 141 | 1402704 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 766080 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2062080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 106868 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.654 | 2169 | 44282569.92
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 99900 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 517440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 980000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 186 | 3081443 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 852255 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 50 | 130032 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 68 | 187521 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 146880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 4 | 483360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 58560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 80291 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 53 | 347090 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 150720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 575836 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 90 | 265964 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26705452 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 2 | 19680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 156 | 4632727.27 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2094 | 39335913.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4668000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 671832 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 696960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4683636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1145304 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1167563 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 36 | 48976 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1363730 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 123 | 1248480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1406400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 400850 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 68 | 708960 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1230720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 202400 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1087 | 19643811
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 1034880 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1096800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 177600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 133660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 108480 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 515880 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 160 | 3072500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 974000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2504700 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 798336 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116784 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 715584 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2053440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 221000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 501648 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7369000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 369 | 8713000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2368.568 | 1022 | 23967492
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 622 | 19882077 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 315360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 622 | 20197437
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 135304 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 134 | 2991000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 26930909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 180 | 4985760 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1498800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6393000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1804.5 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1898 | 42936577.59
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 40 | 55439 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 14392 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 25202 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 198 | 3456273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 220 | 4180364 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 394 | 8653018 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 132016 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 67158 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 858656 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 69408 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 14340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 752 | 16652062 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 159000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 433330 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1774.5 | 34770658
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 66 | 1565673 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 177 | 4084000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 65 | 235920 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20870.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 849080 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 88633 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 628560 | -
Rangpur Area Total |  |  |  |  | 950 | 403 | 7472736.04
Eastern Grid Total |  |  |  |  | 16772.132 | 6532 | 130302286.19
Western Grid Total |  |  |  |  | 10294.5 | 4697.5 | 105377408.63
National Grid Total |  |  |  |  | 27066.632 | 11229.5 | 235679694.82
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7391.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3408.3 | MW
i) Dhaka area |  |  | 3857.2 |  | MW | i) Khulna area |  |  |  | 1205.6 | MW
ii) Chattogram area |  |  | 1238.5 |  | MW | ii) Barishal area |  |  |  | 300.5 | MW
iii) Cumilla area |  |  | 929 |  | MW | iii) Rajshahi area |  |  |  | 1097.2 | MW
iv) Mymensingh area |  |  | 982 |  | MW | iv) Rangpur area |  |  |  | 805 | MW
v) Sylhet area |  |  | 385 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10800 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 59 | 08:00 | 133 | Purbachal | 13 | 13:00
2 | AKSML | 123 | 08:00 | 68 | Jamalpur | 103 | 07:00 | 134 | Purbasadipur | 116 | 13:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jashore | 110 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 83 | 12:00 | 70 | Jhenaidah | 94 | 18:30 | 136 | Rahim | 25 | 18:00
5 | Agrabad | 68 | 18:30 | 71 | Joydebpur | 130 | 15:00 | 137 | Rajbari | 52 | 19:00
6 | Amnura | 47 | 08:00 | 72 | Joypurhat | 60 | 13:00 | 138 | Rajendrapur | 108 | 15:00
7 | Ashuganj | 63 | 13:00 | 73 | Juldah | 11 | 12:00 | 139 | Rajshahi | 89 | 20:00
8 | BSRM | 196 | 19:00 | 74 | KSRM | 28 | 12:00 | 140 | Rajshahi-230 | 58 | 13:00
9 | Bagerhat | 64 | 18:30 | 75 | Kabirpur | 196 | 11:00 | 141 | Ramganj | 88 | 18:30
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 19:30 | 142 | Rampur | 27 | 18:00
11 | Bakulia | 70 | 18:00 | 77 | Kallyanpur | 75 | 12:00 | 143 | Rangamati | 13 | 18:30
12 | Banani | 36 | 13:00 | 78 | Kalurghat | 32 | 12:00 | 144 | Rangpur | 99 | 14:00
13 | Bangabhaban | 9 | 13:00 | 79 | Kamrangirchar | 54 | 13:00 | 145 | Ruppur | 5 | 16:00
14 | Barapukuria | 66 | 12:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 0 | 00:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 76 | 00:00 | 147 | Saidpur | 106 | 11:00
16 | Barishal | 70 | 13:00 | 82 | Keranigonj | 60 | 14:00 | 148 | Satkhira | 86 | 18:30
17 | Barishal-230 | 76 | 18:30 | 83 | Khagrachori | 26 | 18:00 | 149 | Satmasjid | 85 | 13:00
18 | Baroaulia | 42 | 12:00 | 84 | Khulna | 73 | 13:00 | 150 | Savar | 147 | 12:00
19 | Baroirhat | 54 | 13:00 | 85 | Khulshi | 148 | 13:00 | 151 | SevenRings | 17.22 | 23:00
20 | Bashundhara | 136 | 13:00 | 86 | Kishoreganj | 124 | 18:30 | 152 | ShahCement | 24 | 19:30
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 207 | 19:00 | 153 | Shahjadpur | 60 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 18:00 | 154 | Shahjibazar | 95 | 18:00
23 | Benapole | 54 | 08:00 | 89 | Kurigram | 59 | 18:30 | 155 | Shahmirpur | 43 | 00:00
24 | Bhaluka | 118 | 12:00 | 90 | Kushtia | 101 | 18:00 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 34 | 22:00 | 91 | Lalbag | 48 | 13:00 | 157 | Sherpur | 132 | 18:30
26 | Bhangura | 28 | 18:30 | 92 | Lalmonirhat | 50 | 08:00 | 158 | Shikalbaha | 20 | 11:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | MI_Cement | 11.1 | 15:00 | 159 | Shitalakhya | 67 | 12:00
28 | Bhulta | 223 | 00:00 | 94 | Madanganj | 19 | 18:00 | 160 | Sholosohor | 33 | 15:00
29 | Bog-Sherpur | 66 | 08:00 | 95 | Madaripur | 71 | 21:00 | 161 | Shyampur | 148 | 10:00
30 | Bogura | 115 | 13:00 | 96 | Madartek | 51.4 | 13:00 | 162 | Siddhirganj | 95 | 12:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madunaghat | 39 | 12:00 | 163 | Sirajganj | 86 | 19:00
32 | Brahmanbaria | 106 | 18:30 | 98 | Magura | 45 | 18:30 | 164 | Sonargaon | 95 | 00:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 56 | 08:00 | 165 | Sreemongol | 46 | 19:30
34 | Chandpur | 44 | 18:30 | 100 | Manikganj | 112 | 18:30 | 166 | Sreepur | 85 | 12:00
35 | Chandraghona | 26 | 17:00 | 101 | Maniknagar | 50 | 13:00 | 167 | Srinagar | 31.09 | 13:00
36 | Chapai | 61 | 11:00 | 102 | Matarbari | 38 | 18:30 | 168 | Sunamganj | 40 | 20:00
37 | Charsaidpur | 45 | 15:00 | 103 | Matuail | 50 | 00:00 | 169 | Sylhet | 26 | 14:00
38 | Chauddagram | 44 | 14:00 | 104 | Millgate | 55 | 00:00 | 170 | Sylhet-132 | 80 | 18:00
39 | Chhatak | 23 | 18:30 | 105 | Mirpur | 87 | 14:00 | 171 | TK | 22.4 | 18:30
40 | Chowmuhani | 142 | 19:30 | 106 | Mirsorai | 9 | 19:00 | 172 | Tangail | 168 | 07:00
41 | Chuadanga | 75 | 18:30 | 107 | Mirzapur | 36 | 08:00 | 173 | Thakurgaon | 80 | 19:00
42 | Coxsbazar | 114 | 18:00 | 108 | Mithapukur | 73 | 08:00 | 174 | Tongi | 61 | 00:00
43 | Cumilla(N) | 110 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 27 | 19:00
44 | Cumilla(S) | 131 | 12:00 | 110 | Mogbazar | 108.2 | 15:00 | 176 | Ullon | 38 | 13:00
45 | Daudkandi | 108 | 21:00 | 111 | Mongla | 27 | 12:00 | 177 | Uttara | 60 | 13:00
46 | Dhaka | 32 | 12:00 | 112 | Motijheel | 27 | 13:00 | 178 | UttaraNew | 32 | 13:00
47 | Dhamrai | 106 | 12:00 | 113 | Muktagacha | 29 | 13:00 | 179 | Zigatola | 56 | 14:00
48 | Dhanmondi | 101 | 13:00 | 114 | Munshiganj | 70 | 14:00
49 | Dohazari | 72 | 18:30 | 115 | Mymensingh | 170 | 18:00
50 | Faridpur | 110 | 18:30 | 116 | Naogaon | 111 | 13:00
51 | Fatullah | 84 | 12:00 | 117 | Narail | 42 | 18:30
52 | Fenchuganj | 24 | 18:30 | 118 | Narinda | 57 | 13:00
53 | Feni | 67 | 18:30 | 119 | Narshingdi | 155 | 19:00
54 | GPH | 91 | 08:00 | 120 | Natore | 101 | 08:00
55 | Ghatail | 36 | 07:00 | 121 | Nawabganj | 31.6 | 13:00
56 | Ghorashal | 13 | 00:00 | 122 | Netrakona | 133 | 18:00
57 | Ghorashal-230 | 49 | 09:00 | 123 | New | 50 | 00:00
58 | Goalpara | 26 | 18:30 | 124 | Niamatpur | 80 | 11:00
59 | Gollamari | 44 | 13:00 | 125 | Noapara | 35 | 18:30
60 | Gopalganj | 79 | 18:30 | 126 | PHP | 9 | 14:00
61 | Gulshan | 76 | 13:00 | 127 | Pabna | 65 | 18:30
62 | Halishahar | 52 | 12:00 | 128 | Palashbari | 98 | 08:00
63 | HaripurSBU | 175 | 15:00 | 129 | Panchagarh | 45 | 18:30
64 | Hasnabad | 68 | 13:00 | 130 | Patuakhali | 56 | 21:00
65 | Hathazari | 54 | 18:00 | 131 | Payra | 14 | 00:00
66 | Ishurdi | 60 | 18:30 | 132 | Postogola | 41 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9214.5 | 0 |  | 9214.5
1:00 | 8688.5 | 0 |  | 8688.5
2:00 | 8348.5 | 0 |  | 8348.5
3:00 | 8091.5 | 0 |  | 8091.5
4:00 | 7849.5 | 0 |  | 7849.5
5:00 | 7652.5 | 0 |  | 7652.5
6:00 | 7989.5 | 0 |  | 7989.5
7:00 | 8870.7 | 0 |  | 8870.7
8:00 | 9640.93 | 32 |  | 9673.93
9:00 | 10177.55 | 23 |  | 10201.55
10:00 | 10168.32 | 18 |  | 10187.32
11:00 | 10332.21 | 0 |  | 10332.21
12:00 | 10733.47 | 0 |  | 10733.47
13:00 | 10992.02 | 0 |  | 10992.02
14:00 | 10729.55 | 0 |  | 10729.55
15:00 | 10365.56 | 0 |  | 10365.56
16:00 | 9919.05 | 0 |  | 9919.05
17:00 | 9855.58 | 0 |  | 9855.58
18:00 | 10535.5 | 0 |  | 10535.5
19:00 | 11229.5 | 0 |  | 11229.5
19:30 | 10878.5 | 0 |  | 10878.5
20:00 | 10844.5 | 0 |  | 10844.5
21:00 | 10484.08 | 0 |  | 10484.08
22:00 | 10138.5 | 0 |  | 10138.5
23:00 | 9776.98 | 0 |  | 9776.98
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5007 | 4207.5 | 9214.5 | DAILY GENERATION CURVE
00:30 | 4859 | 4092.5 | 8951.5
01:00 | 4711 | 3977.5 | 8688.5 | 02-02-2025
01:30 | 4685.5 | 3833 | 8518.5
02:00 | 4660 | 3688.5 | 8348.5
02:30 | 4581.5 | 3638.5 | 8220
03:00 | 4503 | 3588.5 | 8091.5
03:30 | 4432.5 | 3538 | 7970.5
04:00 | 4362 | 3487.5 | 7849.5
04:30 | 4298.5 | 3452.5 | 7751
05:00 | 4235 | 3417.5 | 7652.5
05:30 | 4294.5 | 3526.5 | 7821
06:00 | 4354 | 3635.5 | 7989.5
06:30 | 4592.6 | 3837.5 | 8430.1
07:00 | 4831.2 | 4039.5 | 8870.7
07:30 | 5102.215 | 4153.6 | 9255.815
08:00 | 5373.23 | 4267.7 | 9640.93
08:30 | 5598.18 | 4311.06 | 9909.24
09:00 | 5823.13 | 4354.42 | 10177.55
09:30 | 5820.58 | 4352.355 | 10172.935
10:00 | 5818.03 | 4350.29 | 10168.32
10:30 | 5823.95 | 4426.315 | 10250.265
11:00 | 5829.87 | 4502.34 | 10332.21
11:30 | 5893.755 | 4639.085 | 10532.84
12:00 | 5957.64 | 4775.83 | 10733.47
12:30 | 6039.645 | 4823.1 | 10862.745
13:00 | 6121.65 | 4870.37 | 10992.02
13:30 | 6014.485 | 4846.3 | 10860.785
14:00 | 5907.32 | 4822.23 | 10729.55
14:30 | 5761.98 | 4785.575 | 10547.555
15:00 | 5616.64 | 4748.92 | 10365.56
15:30 | 5463.58 | 4678.725 | 10142.305
16:00 | 5310.52 | 4608.53 | 9919.05
16:30 | 5319.07 | 4568.245 | 9887.315
17:00 | 5327.62 | 4527.96 | 9855.58
17:30 | 5566.31 | 4629.23 | 10195.54
18:00 | 5805 | 4730.5 | 10535.5
18:30 | 6168.5 | 4714 | 10882.5
19:00 | 6532 | 4697.5 | 11229.5
19:30 | 6286 | 4592.5 | 10878.5
20:00 | 6271 | 4573.5 | 10844.5
20:30 | 6004 | 4660.29 | 10664.29 |  | Executive Engineer
21:00 | 5737 | 4747.08 | 10484.08 |  | Network Operation Division
21:30 | 5584.5 | 4726.79 | 10311.29
22:00 | 5432 | 4706.5 | 10138.5
22:30 | 5394 | 4563.74 | 9957.74
23:00 | 5356 | 4420.98 | 9776.98

## En-Curve
QF-LDC-12
Date | 02-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2136 | 1929.5 | 907 | 0 | 62 | 732 | 40 | 3125 | 0 | 17 | 266 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2144 | 1932.5 | 906.5 | 0 | 60 | 729 | 40 | 2992 | 0 | 8.5 | 139 | 0 | 0 | 0 | 0 | 02-02-2025
01:00 | 2152 | 1935.5 | 906 | 0 | 58 | 726 | 40 | 2859 | 0 | 0 | 12 | 0 | 0 | 0 | 0
01:30 | 2189.5 | 1954 | 833 | 0 | 55 | 657.5 | 40 | 2783.5 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | Energy Generated | 235.6797 |  | MKWHr
02:00 | 2227 | 1972.5 | 760 | 0 | 52 | 589 | 40 | 2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0.073 |  | MKWHr
02:30 | 2236 | 1974.5 | 738.5 | 0 | 51 | 552.5 | 40 | 2627.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 235.7527 |  | MKWHr
03:00 | 2245 | 1976.5 | 717 | 0 | 50 | 516 | 40 | 2547 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2265 | 1974 | 717.5 | 0 | 52 | 471.5 | 40 | 2450.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2285 | 1971.5 | 718 | 0 | 54 | 427 | 40 | 2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2236 | 1929.5 | 718 | 0 | 54 | 419.5 | 40 | 2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2187 | 1887.5 | 718 | 0 | 54 | 412 | 40 | 2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2201 | 1918 | 718 | 0 | 51 | 444 | 40 | 2447.5 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0
06:00 | 2215 | 1948.5 | 718 | 0 | 48 | 476 | 40 | 2541 | 0 | 0 | 3 | 0 | 0 | 0 | 0
06:30 | 2267 | 1990.5 | 764.5 | 0 | 51 | 541.5 | 40 | 2714.5 | 0.1 | 12.5 | 48.5 | 0 | 0 | 0 | 0
07:00 | 2319 | 2032.5 | 811 | 0 | 54 | 607 | 40 | 2888 | 0.2 | 25 | 94 | 0 | 0 | 0 | 0
07:30 | 2258.5 | 2010.25 | 730.5 | 0 | 53 | 678.755 | 40 | 2991.5 | 16.81 | 67.5 | 407.5 | 0 | 0 | 1.5 | 16
08:00 | 2198 | 1988 | 650 | 0 | 52 | 750.51 | 40 | 3095 | 33.42 | 110 | 721 | 0 | 0 | 3 | 32
08:30 | 2194 | 1983.25 | 636 | 0 | 53 | 752.83 | 40 | 3094 | 66.16 | 110 | 978.5 | 0 | 0 | 1.5 | 27.5
09:00 | 2190 | 1978.5 | 622 | 0 | 54 | 755.15 | 40 | 3093 | 98.9 | 110 | 1236 | 0 | 0 | 0 | 23
09:30 | 2115.5 | 1949.75 | 764 | 0 | 53 | 708.305 | 40 | 3061.5 | 133.88 | 130 | 1217 | 0 | 0 | 0 | 20.5
10:00 | 2041 | 1921 | 906 | 0 | 52 | 661.46 | 40 | 3030 | 168.86 | 150 | 1198 | 0 | 0 | 0 | 18
10:30 | 2034 | 1909 | 906.5 | 0 | 57 | 661.045 | 40 | 3058.5 | 227.72 | 155.5 | 1201 | 0 | 0 | 0 | 9
11:00 | 2027 | 1897 | 907 | 0 | 62 | 660.63 | 40 | 3087 | 286.58 | 161 | 1204 | 0 | 0 | 0 | 0
11:30 | 2094.5 | 1906.5 | 907 | 0 | 65 | 707.275 | 40 | 3091 | 316.565 | 165 | 1240 | 0 | 0 | 0 | 0
12:00 | 2162 | 1916 | 907 | 0 | 68 | 753.92 | 40 | 3095 | 346.55 | 169 | 1276 | 0 | 0 | 0 | 0
12:30 | 2260.5 | 1912 | 907 | 0 | 68 | 753.495 | 40 | 3093 | 385.75 | 164 | 1279 | 0 | 0 | 0 | 0
13:00 | 2359 | 1908 | 907 | 0 | 68 | 753.07 | 40 | 3091 | 424.95 | 159 | 1282 | 0 | 0 | 0 | 0
13:30 | 2408 | 1892 | 907 | 0 | 66 | 753.2 | 40 | 3017.5 | 406.085 | 159 | 1210.5 | 0 | 0 | 1.5 | 0
14:00 | 2457 | 1876 | 907 | 0 | 64 | 753.33 | 40 | 2944 | 387.22 | 159 | 1139 | 0 | 0 | 3 | 0
14:30 | 2422.5 | 1875.75 | 907 | 0 | 64 | 754.165 | 40 | 2968 | 339.14 | 154 | 1020.5 | 0 | 0 | 2.5 | 0
15:00 | 2388 | 1875.5 | 907 | 0 | 64 | 755 | 40 | 2992 | 291.06 | 149 | 902 | 0 | 0 | 2 | 0
15:30 | 2413 | 1879.5 | 907 | 0 | 64 | 756.5 | 40 | 2961 | 224.305 | 149 | 745 | 0 | 0 | 3 | 0
16:00 | 2438 | 1883.5 | 907 | 0 | 64 | 758 | 40 | 2930 | 157.55 | 149 | 588 | 0 | 0 | 4 | 0
16:30 | 2442 | 1897.75 | 907 | 0 | 63 | 756.5 | 40 | 2931.5 | 100.065 | 155.5 | 590.5 | 0 | 0 | 3.5 | 0
17:00 | 2446 | 1912 | 907 | 0 | 62 | 755 | 40 | 2933 | 42.58 | 162 | 593 | 0 | 0 | 3 | 0
17:30 | 2417 | 1864.25 | 907 | 0 | 63 | 756 | 40 | 2985 | 21.29 | 282 | 858.5 | 0 | 0 | 1.5 | 0
18:00 | 2388 | 1816.5 | 907 | 0 | 64 | 757 | 40 | 3037 | 0 | 402 | 1124 | 0 | 0 | 0 | 0
18:30 | 2517.5 | 1839 | 764.5 | 0 | 65 | 754.5 | 40 | 3043.5 | 0 | 452.5 | 1405 | 0 | 0 | 1 | 0
19:00 | 2647 | 1861.5 | 622 | 0 | 66 | 752 | 40 | 3050 | 0 | 503 | 1686 | 0 | 0 | 2 | 0
19:30 | 2679 | 1981.5 | 621 | 0 | 64 | 756 | 40 | 3046 | 0 | 327 | 1363 | 0 | 0 | 1 | 0
20:00 | 2647 | 1965.5 | 621 | 0 | 62 | 755 | 40 | 3054 | 0 | 327 | 1372 | 0 | 0 | 1 | 0
20:30 | 2662.5 | 1975.5 | 734.5 | 0 | 63 | 755.29 | 40 | 3056.5 | 0 | 258 | 1118.5 | 0 | 0 | 0.5 | 0
21:00 | 2678 | 1985.5 | 848 | 0 | 64 | 755.58 | 40 | 3059 | 0 | 189 | 865 | 0 | 0 | 0 | 0
21:30 | 2672 | 1981.5 | 877 | 0 | 62 | 754.79 | 40 | 3062.5 | 0 | 136 | 725.5 | 0 | 0 | 0 | 0
22:00 | 2666 | 1977.5 | 906 | 0 | 60 | 754 | 40 | 3066 | 0 | 83 | 586 | 0 | 0 | 0 | 0
22:30 | 2593.5 | 1942.5 | 905.5 | 0 | 59 | 753.74 | 40 | 3062.5 | 0 | 75 | 525.5 | 0 | 0 | 0.5 | 0
23:00 | 2521 | 1907.5 | 905 | 0 | 58 | 753.48 | 40 | 3059 | 0 | 67 | 465 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 410 | 05:00 | 394 | 12:00 | Payra | 415 | 05:00 | 407 | 12:00
Ashuganj | 413 | 4:00 | 386 | 11:00 | Rahanpur | 418 | 05:00 | 402 | 12:00
Bhulta | 410 | 05:00 | 393 | 12:00 | Rampal | 411 | 04:00 | 388 | 12:00
Bibiana | 405 | 05:00 | 393 | 18:00
BIPTC | 408 | 02:00 | 392 | 10:00
Bogura | 416 | 04:00 | 398 | 12:00
Gopalganj | 412 | 05:00 | 396 | 12:00
Kaliakoir | 396 | 03:00 | 383 | 12:00
Madunaghat | 409 | 06:00 | 400 | 16:00
Meghnaghat | 402 | 08:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 227 | 16:00 | Keranigonj | 236 | 05:00 | 226 | 12:00
AKSML | 235 | 03:00 | 227 | 13:00 | Khulna(S) | 240 | 04:00 | 225 | 12:00
Aminbazar | 234 | 03:00 | 227 | 12:00 | Madunaghat | 233 | 04:00 | 228 | 13:00
Ashuganj | 240 | 03:00 | 232 | 12:00 | Madunaghat-400 | 234 | 04:00 | 228 | 17:00
Ashuganj-400 | 240 | 03:00 | 232 | 12:00 | Maniknagar | 236 | 03:00 | 228 | 12:00
Baghabari | 241 | 05:00 | 227 | 12:00 | Meghnaghat | 240 | 02:00 | 234 | 20:00
Barapukuria | 227 | 02:00 | 218 | 08:00 | Meghnaghat-400 | 239 | 05:00 | 230 | 12:00
Barapukuria-230 | 227 | 02:00 | 218 | 08:00 | Mirsorai | 236 | 19:00 | 225 | 17:00
Barishal | 245 | 05:00 | 236 | 12:00 | Rajshahi | 242 | 05:00 | 223 | 12:00
Bheramara | 239 | 04:00 | 222 | 12:00 | Rampal | 238 | 04:00 | 221 | 13:00
Bhulta | 239 | 05:00 | 228 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 233 | 05:00 | 224 | 17:00 | Rampura | 238 | 05:00 | 228 | 12:00
BIPTC | 241 | 04:00 | 223 | 12:00 | Shikalbaha | 233 | 05:00 | 226 | 15:00
Bogura | 241 | 04:00 | 230 | 12:00 | Shyampur | 236 | 03:00 | 227 | 12:00
Bogura-400 | 240 | 04:00 | 229 | 10:00 | Siddhirganj | 238 | 01:00 | 230 | 12:00
Borhanuddin | 247 | 04:00 | 241 | 13:00 | Sirajgonj | 246 | 04:00 | 238 | 10:00
BSRM | 234 | 05:00 | 228 | 16:00 | Sreepur | 241 | 05:00 | 231 | 12:00
Cumilla(N) | 234 | 06:00 | 227 | 17:00 | Tongi | 235 | 05:00 | 228 | 15:00
Faridpur | 245 | 05:00 | 233 | 13:00
Fenchuganj | 237 | 04:00 | 229 | 16:00
Ghorashal | 240 | 01:00 | 235 | 12:00
Ghorashal-230 | 238 | 05:00 | 228 | 12:00
Gopalganj | 244 | 05:00 | 234 | 13:00
GPH | 234 | 05:00 | 228 | 13:00
Haripur | 237 | 04:00 | 228 | 12:00
Hasnabad | 237 | 05:00 | 227 | 16:00
Hathazari | 235 | 19:00 | 230 | 22:00
Ishurdi | 242 | 05:00 | 225 | 12:00
Jhenaidah | 239 | 04:00 | 221 | 12:00
Kaliakoir | 235 | 03:00 | 226 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 129 | 12:00 | Magura | 141 | 04:00 | 126 | 12:00
Agargaon | 138 | 05:00 | 131 | 12:00 | Mahasthangarh | 136 | 03:00 | 127 | 08:00
Agrabad | 134 | 19:00 | 129 | 15:00 | Manikganj | 137 | 06:00 | 134 | 00:00
AKS | 132 | 03:00 | 128 | 15:00 | Maniknagar | 136 | 04:00 | 129 | 12:00
Aminbazar | 135 | 02:00 | 126 | 12:00 | Matarbari | 126 | 05:00 | 117 | 18:30
Amnura | 140 | 06:00 | 130 | 13:00 | Matuail | 137 | 05:00 | 131 | 12:00
Ashuganj | 142 | 06:00 | 138 | 11:00 | Millgate | 138 | 02:00 | 132 | 12:00
Bagerhat | 138 | 04:00 | 127 | 13:00 | Mirpur | 135 | 08:00 | 130 | 12:00
Bajitpur | 135 | 01:00 | 131 | 12:00 | Mirzapur | 137 | 04:00 | 131 | 07:00
Bakulia | 135 | 19:00 | 130 | 13:00 | Mithapukur | 134 | 05:00 | 124 | 09:00
Banani | 136 | 03:00 | 127 | 13:00 | MI_Cement | 138 | 05:00 | 131 | 12:00
Bangabhaban | 135 | 08:00 | 129 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 02:00 | 128 | 08:00 | Mogbazar | 138 | 06:00 | 130 | 11:00
Barguna | 142 | 09:00 | 130 | 21:00 | Mongla | 136 | 04:00 | 126 | 13:00
Barishal | 135 | 03:00 | 129 | 12:00 | Motijheel | 135 | 08:00 | 129 | 12:00
Barishal-230 | 136 | 04:00 | 130 | 12:00 | Muktagacha | 131 | 03:00 | 123 | 13:00
Baroaulia | 134 | 08:00 | 130 | 12:00 | Munshiganj | 136 | 06:00 | 130 | 16:00
Baroirhat | 134 | 09:00 | 127 | 15:00 | Mymensingh | 131 | 06:00 | 120 | 12:00
Bashundhara | 137 | 01:00 | 128 | 11:00 | Naogaon | 136 | 05:00 | 124 | 13:00
BashundharaCement | 136 | 04:00 | 130 | 12:00 | Narail | 139 | 03:00 | 124 | 13:00
Beanibazar | 138 | 03:00 | 131 | 15:00 | Narinda | 135 | 8:00 | 129 | 12:00
Benapole | 136 | 06:00 | 122 | 12:00 | Narshingdi | 132 | 03:00 | 126 | 12:00
Bhaluka | 129 | 05:00 | 121 | 13:00 | Natore | 136 | 01:00 | 128 | 12:00
Bhandaria | 132 | 03:00 | 126 | 13:00 | Nawabganj | 138 | 04:00 | 131 | 12:00
Bhangura | 139 | 04:00 | 129 | 12:00 | Netrakona | 125 | 04:00 | 117 | 13:00
Bheramara | 138 | 03:00 | 128 | 12:00 | New | 138 | 05:00 | 133 | 12:00
Bheramara(GK) | 140 | 04:00 | 128 | 12:00 | Niamatpur | 140 | 02:00 | 133 | 12:00
Bhulta | 131 | 08:00 | 125 | 12:00 | Noapara | 139 | 03:00 | 127 | 12:00
Bog-Sherpur | 137 | 03:00 | 128 | 12:00 | Pabna | 137 | 04:00 | 125 | 13:00
Bogura | 138 | 03:00 | 129 | 12:00 | Palashbari | 133 | 04:00 | 122 | 08:00
Bogura-230 | 138 | 04:00 | 130 | 10:00 | Panchagarh | 137 | 19:00 | 124 | 00:00
Brahmanbaria | 136 | 06:00 | 130 | 13:00 | Patuakhali | 140 | 08:00 | 133 | 23:00
Cantonment | 138 | 05:00 | 131 | 12:00 | Payra | 138 | 22:00 | 134 | 17:00
Chandpur | 139 | 09:00 | 129 | 01:00 | PHP | 133 | 09:00 | 127 | 16:00
Chandraghona | 135 | 03:00 | 132 | 07:00 | Postogola | 137 | 00:00 | 134 | 12:00
Chapai | 137 | 01:00 | 131 | 12:00 | Purbachal | 137 | 03:00 | 129 | 13:00
Charsaidpur | 137 | 04:00 | 131 | 15:00 | Purbasadipur | 131 | 19:00 | 118 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 08:00 | 129 | 16:00 | Rahanpur | 140 | 00:00 | 135 | 12:00
Chhatak | 138 | 05:00 | 126 | 18:00 | Rahanpur-400 | 142 | 04:00 | 136 | 09:00
Chowmuhani | 135 | 09:00 | 125 | 16:00 | Rahim | 135 | 04:00 | 129 | 16:00
Chuadanga | 139 | 03:00 | 125 | 13:00 | Rajbari | 135 | 04:00 | 128 | 12:00
Coxsbazar | 124 | 04:00 | 119 | 21:00 | Rajendrapur | 135 | 08:00 | 130 | 13:00
Cumilla(N) | 137 | 02:00 | 132 | 16:00 | Rajshahi | 139 | 03:00 | 130 | 12:00
Cumilla(S) | 136 | 08:00 | 129 | 00:00 | Rajshahi-230 | 140 | 04:00 | 126 | 12:00
Daudkandi | 134 | 04:00 | 128 | 15:00 | Ramganj | 135 | 09:00 | 125 | 07:00
Dhaka | 136 | 04:00 | 129 | 12:00 | Rampur | 134 | 19:00 | 129 | 16:00
Dhamrai | 135 | 03:00 | 128 | 12:00 | Rampura | 137 | 05:00 | 129 | 12:00
Dhanmondi | 137 | 01:00 | 131 | 12:00 | Rangamati | 134 | 03:00 | 131 | 13:00
Dohazari | 131 | 19:00 | 127 | 03:00 | Rangpur | 130 | 04:00 | 120 | 07:00
Faridpur | 135 | 04:00 | 130 | 12:00 | Ruppur | 141 | 05:00 | 130 | 12:00
Fatullah | 138 | 05:00 | 132 | 12:00 | Saidpur | 132 | 05:00 | 122 | 08:00
Fenchuganj | 141 | 04:00 | 137 | 13:00 | Satkhira | 139 | 05:00 | 127 | 18:30
Feni | 134 | 10:00 | 127 | 17:00 | Satmasjid | 137 | 05:00 | 131 | 12:00
Ghatail | 132 | 04:00 | 124 | 12:00 | Savar | 136 | 08:00 | 132 | 05:00
Ghorashal | 140 | 01:00 | 138 | 15:00 | SevenRings | 143 | 05:00 | 137 | 12:00
Goalpara | 141 | 05:00 | 127 | 13:00 | ShahCement | 137 | 04:00 | 131 | 15:00
Gollamari | 140 | 05:00 | 129 | 12:00 | Shahjadpur | 140 | 06:00 | 132 | 13:00
Gopalganj | 137 | 04:00 | 129 | 12:00 | Shahjibazar | 138 | 08:00 | 133 | 13:00
Gopalganj-400 | 137 | 04:00 | 131 | 12:00 | Shahmirpur | 134 | 19:00 | 130 | 14:00
Gulshan | 136 | 05:00 | 129 | 12:00 | Shariatpur | 135 | 02:00 | 129 | 13:00
Halishahar | 134 | 19:00 | 131 | 13:00 | Sherpur | 126 | 23:00 | 116 | 12:00
Haripur | 136 | 06:00 | 130 | 16:00 | Shikalbaha | 123 | 03:00 | 118 | 15:00
HaripurSBU | 136 | 06:00 | 123 | 09:00 | Shikalbaha-230 | 135 | 19:00 | 130 | 15:00
Hasnabad | 139 | 01:00 | 134 | 11:00 | Shitalakhya | 138 | 05:00 | 131 | 12:00
Hathazari | 136 | 09:00 | 133 | 16:00 | Sholosohor | 134 | 03:00 | 130 | 16:00
Ishurdi | 141 | 05:00 | 131 | 12:00 | Shyampur | 136 | 00:00 | 132 | 12:00
Jaldhaka | 129 | 19:00 | 117 | 07:00 | Shyampur-230 | 138 | 05:00 | 132 | 12:00
Jamalpur | 129 | 21:00 | 121 | 12:00 | Siddhirganj | 136 | 04:00 | 131 | 12:00
Jashore | 138 | 04:00 | 124 | 12:00 | Sirajganj | 138 | 04:00 | 127 | 12:00
Jhenaidah | 140 | 05:00 | 127 | 12:00 | Sonargaon | 135 | 01:00 | 129 | 13:00
Jhenaidah-230 | 140 | 04:00 | 128 | 12:00 | Sreemongol | 139 | 02:00 | 134 | 12:00
Joydebpur | 140 | 18:00 | 132 | 00:00 | Sreepur | 130 | 02:00 | 125 | 12:00
Joypurhat | 135 | 03:00 | 122 | 13:00 | Srinagar | 138 | 06:00 | 132 | 13:00
Juldah | 133 | 04:00 | 130 | 14:00 | SSM | 139 | 18:30 | 132 | 14:00
Kabirpur | 140 | 04:00 | 131 | 15:00 | Sunamganj | 137 | 03:00 | 125 | 18:00
Kachua | 137 | 08:00 | 130 | 01:00 | Sylhet | 140 | 05:00 | 131 | 18:30
Kaliakoir | 142 | 03:00 | 130 | 12:00 | Sylhet-132 | 138 | 02:00 | 130 | 18:00
Kallyanpur | 134 | 05:00 | 127 | 12:00 | Tangail | 132 | 00:00 | 126 | 07:00
Kalurghat | 135 | 19:00 | 131 | 16:00 | Thakurgaon | 136 | 19:00 | 122 | 07:00
Kamrangirchar | 137 | 08:00 | 126 | 12:00 | TK | 135 | 03:00 | 131 | 17:00
Kaptai | 137 | 9:00 | 135 | 1:00 | Tongi | 138 | 18:30 | 134 | 11:00
Kazla | 136 | 05:00 | 128 | 13:00 | Ullahpara | 139 | 03:00 | 129 | 12:00
Keranigonj | 138 | 05:00 | 13 | 19:00 | Ullon | 135 | 01:00 | 130 | 12:00
Khagrachori | 134 | 05:00 | 130 | 13:00 | Uttara | 135 | 03:00 | 130 | 13:00
Khulna | 139 | 05:00 | 127 | 12:00 | UttaraNew | 138 | 02:00 | 133 | 12:00
Khulna(S) | 140 | 04:00 | 130 | 12:00 | Zigatola | 139 | 05:00 | 133 | 12:00
Khulshi | 134 | 19:00 | 128 | 14:00
Kishoreganj | 131 | 01:00 | 127 | 12:00
Kodda | 138 | 05:00 | 130 | 12:00
KSRM | 136 | 18:30 | 131 | 16:00
Kulaura | 140 | 03:00 | 136 | 13:00
Kurigram | 130 | 03:00 | 120 | 08:00
Kushtia | 139 | 06:00 | 127 | 13:00
Lalbag | 138 | 03:00 | 132 | 12:00
Lalmonirhat | 132 | 19:00 | 119 | 09:00
Madanganj | 136 | 04:00 | 130 | 12:00
Madaripur | 136 | 05:00 | 130 | 12:00
Madartek | 136 | 03:00 | 128 | 12:00
Madunaghat | 135 | 10:00 | 130 | 17:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division