## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-02-2025 | [28 empty] | Date: | 03-02-2025 | [28 empty] | Date: | 03-02-2025 | [28 empty] | Date: | 03-02-2025 | [28 empty] | Date: | 03-02-2025 | [19 empty] | Date: | 03-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [19 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 293 | 0 | 0 | 0 | 31 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 153 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 197 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 300 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 25 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 9 | 24 | 34 | 0 | 0 | 0 | 4977 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 324 | 0 | 0 | 2.5 | 159 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 100 | 180 | 0 | 0 | 1140 | 0 | 4373.56 | 9350.56 | 91.58
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 298 | 0 | 0 | 0 | 31 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 38 | 152 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1025 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 195 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 295 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 9 | 8 | 34 | 0 | 0 | 0 | 4761 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 216 | 0 | 393 | 0 | 0 | 2.5 | 159 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 0 | 1100 | 0 | 4143.34 | 8904.34 | 91.58
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 289 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 38 | 157 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 187 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 305 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 4619 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 183 | 0 | 393 | 0 | 0 | 2.5 | 159 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 7 | 100 | 180 | 0 | 0 | 980 | 0 | 3729.8 | 8348.8 | 91.58
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 298 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 38 | 157 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 840 | 0 | 51 | 0 | 195 | 0 | 0 | 40 | 29 | 195 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 300 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 4641 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 135 | 0 | 414 | 0 | 0 | 2.5 | 161 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 0 | 840 | 0 | 3348.18 | 7989.18 | 91.57
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 272 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 38 | 156 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 195 | 0 | 0 | 3 | 29 | 183 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 305 | 0 | 370 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 4520 | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 109 | 0 | 392 | 0 | 0 | 2.5 | 164 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 0 | 800 | 0 | 3242.83 | 7762.83 | 91.57
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 279 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 38 | 157 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 705 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 0 | 369 | 36 | 41 | 0 | 5 | 113 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 4341.5 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 109 | 0 | 392 | 0 | 0 | 2.5 | 158 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 800 | 0 | 3224.91 | 7566.41 | 91.57
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 327 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 400 | 285 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 185 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 367 | 33 | 41 | 0 | 5 | 113 | 23 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 5 | 65 | 0 | 0 | 1 | 4421.5 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 106 | 0 | 414 | 0 | 0 | 2.5 | 159 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 820 | 0 | 3322.16 | 7743.66 | 91.57
07:00 | 0 | 2 | 8 | 0 | 0 | 0 | 0 | 65 | 308 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 400 | 279 | 0 | 0 | 5 | 33 | 335 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 32 | 156 | 0 | 0 | 0 | 0 | 1 | 186 | 0 | 0 | 0 | 960 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 25 | 191 | 27 | 1 | 50 | 17 | 0 | 17 | 0 | 48 | 0 | 1 | 0 | 310 | 0 | 285 | 36 | 41 | 0 | 5 | 113 | 23 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4475.5 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 509.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 125 | 0 | 0 | 0 | 105 | 0 | 394 | 0 | 0.02 | 2.5 | 160 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 6 | 100 | 180 | 0 | 0 | 970 | 10 | 3609.29 | 8084.79 | 91.57
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 65 | 301 | 0 | 0 | 17 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 400 | 300 | 0 | 0 | 30 | 30 | 335 | 0 | 0 | 5 | 0 | 14.5 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 159 | 0 | 0 | 12 | 0 | 17 | 186 | 0 | 0 | 0 | 1120 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 26 | 191 | 27 | 31 | 50 | 20 | 14 | 17 | 0 | 54 | 0 | 5 | 0 | 305 | 0 | 367 | 33 | 42 | 0 | 5 | 113 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 19 | 22 | 0 | 4.68 | 0 | 4895.18 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.81 | 0 | 0 | 593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 5.53 | 125 | 0 | 0 | 0 | 107 | 0 | 414 | 0 | 0.44 | 2.5 | 160 | 66 | 0 | 2 | 0 | 0 | 0 | 0.4 | 9 | 0.03 | 0 | 307 | 5 | 100 | 180 | 0 | 0 | 1120 | 35 | 4160.71 | 9055.89 | 91.56
09:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 65 | 291 | 0 | 0 | 47 | 0 | 0 | 29 | 48 | 0 | 20 | 14 | 162 | 17 | 0 | 400 | 278 | 0 | 0 | 35 | 29 | 335 | 0 | 0 | 14 | 0 | 14.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 40 | 25 | 2 | 156 | 24 | 0 | 20 | 0 | 48 | 186 | 0 | 0 | 0 | 1224 | 5 | 51 | 30 | 195 | 0 | 0 | 0 | 29 | 190 | 30 | 85 | 50 | 100 | 24 | 17 | 0 | 56 | 0 | 9 | 0 | 310 | 0 | 369 | 36 | 42 | 0 | 5 | 113 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 19 | 9 | 56 | 23 | 0 | 18.95 | 6 | 5763.45 | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.39 | 0 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17.35 | 125 | 0 | 0 | 0 | 109 | 0 | 386 | 0 | 1.08 | 2.5 | 166 | 67 | 70 | 4 | 22 | 0 | 0 | 1.2 | 20 | 0.1 | 0 | 307 | 4 | 136 | 220 | 0 | 0 | 1120 | 134 | 4366.62 | 10130.07 | 91.56
10:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 60 | 280 | 0 | 0 | 54 | 0 | 0 | 51 | 48 | 0 | 55 | 53 | 54 | 20 | 0 | 350 | 300 | 0 | 0 | 17 | 29 | 300 | 0 | 0 | 23 | 0 | 14.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 50 | 2 | 40 | 34 | 2 | 155 | 17 | 0 | 37 | 0 | 34 | 187 | 0 | 0 | 0 | 1226 | 15 | 51 | 30 | 195 | 0 | 0 | 0 | 27 | 201 | 31 | 50 | 50 | 51 | 28 | 17 | 0 | 50 | 0 | 32 | 0 | 285 | 0 | 370 | 30 | 42 | 0 | 5 | 113 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 22 | 1 | 31.85 | 6 | 5627.35 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.72 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 41.65 | 126 | 0 | 0 | 0 | 108 | 0 | 330 | 0 | 2.07 | 2.5 | 157 | 67 | 35 | 4 | 40 | 0 | 0 | 2.6 | 52 | 0.27 | 0 | 307 | 4 | 136 | 220 | 0 | 0 | 1110 | 35 | 4576.81 | 10204.16 | 91.56
11:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 63 | 275 | 0 | 0 | 17 | 0 | 0 | 52 | 64 | 0 | 55 | 17 | 54 | 25 | 0 | 320 | 301 | 0 | 0 | 17 | 29 | 300 | 0 | 0 | 28 | 0 | 14.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 50 | 4 | 40 | 34 | 2 | 156 | 17 | 0 | 50 | 0 | 34 | 187 | 0 | 0 | 0 | 1224 | 17 | 51 | 30 | 187 | 0 | 0 | 0 | 28 | 209 | 31 | 50 | 50 | 51 | 38 | 17 | 0 | 64 | 0 | 59 | 0 | 300 | 0 | 370 | 27 | 42 | 0 | 0 | 20 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 20 | 0 | 39.24 | 6 | 5547.74 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.93 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 53.87 | 133 | 0 | 0 | 0 | 110 | 0 | 348 | 0 | 4.54 | 2.5 | 156 | 68 | 35 | 4 | 40 | 0 | 0 | 3.5 | 121 | 0.38 | 0 | 307 | 3 | 136 | 220 | 0 | 0 | 1110 | 35 | 4712.72 | 10260.46 | 91.55
12:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 66 | 286 | 0 | 0 | 39 | 0 | 0 | 78 | 82 | 0 | 55 | 17 | 108 | 0 | 0 | 400 | 298 | 0 | 0 | 35 | 29 | 335 | 0 | 0 | 30 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 36 | 50 | 4 | 40 | 34 | 4 | 155 | 17 | 0 | 50 | 0 | 57 | 187 | 0 | 0 | 0 | 1224 | 19 | 51 | 30 | 197 | 0 | 0 | 0 | 29 | 193 | 31 | 96 | 50 | 100 | 38 | 17 | 0 | 68 | 0 | 62 | 0 | 310 | 0 | 370 | 30 | 41 | 0 | 5 | 15 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 18 | 2 | 44.68 | 6 | 5932.68 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.16 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 48.83 | 148 | 0 | 0 | 0 | 133 | 0 | 332 | 0 | 4.52 | 2.5 | 157 | 66 | 70 | 9 | 48 | 0 | 0 | 3.6 | 150 | 0.46 | 0 | 307 | 4 | 100 | 180 | 0 | 0 | 1110 | 72 | 4798.07 | 10730.75 | 91.55
13:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 65 | 409 | 0 | 0 | 54 | 0 | 0 | 115 | 82 | 0 | 55 | 27 | 108 | 25 | 0 | 420 | 311 | 0 | 0 | 35 | 23 | 331 | 0 | 0 | 28 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 36 | 50 | 4 | 40 | 34 | 9 | 157 | 35 | 0 | 50 | 0 | 85 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 45 | 197 | 0 | 0 | 0 | 29 | 192 | 31 | 115 | 50 | 100 | 29 | 17 | 0 | 72 | 0 | 57 | 0 | 315 | 0 | 372 | 30 | 40 | 0 | 5 | 18 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 17 | 2 | 43.1 | 6 | 6234.1 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.16 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 54.76 | 205 | 0 | 0 | 0 | 201 | 0 | 401 | 0 | 4.58 | 2.5 | 155 | 67 | 70 | 12 | 49 | 0 | 0 | 3.8 | 141 | 0.42 | 0 | 307 | 5 | 132 | 110 | 0 | 0 | 1130 | 72 | 4976.22 | 11210.32 | 91.55
14:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 69 | 409 | 0 | 0 | 54 | 0 | 0 | 102 | 16 | 0 | 55 | 35 | 108 | 25 | 0 | 350 | 270 | 0 | 0 | 35 | 30 | 325 | 0 | 0 | 25 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 36 | 38 | 3 | 40 | 34 | 4 | 157 | 21 | 0 | 50 | 0 | 85 | 188 | 0 | 0 | 0 | 1224 | 17 | 51 | 60 | 195 | 0 | 0 | 0 | 29 | 183 | 31 | 115 | 50 | 100 | 29 | 17 | 0 | 69 | 0 | 50 | 0 | 295 | 0 | 347 | 27 | 42 | 0 | 5 | 15 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 19 | 59 | 17 | 2 | 43.02 | 6 | 5998.02 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 0 | 757.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 50.6 | 214 | 0 | 0 | 0 | 208 | 0 | 348 | 0 | 4.58 | 2.5 | 161 | 67 | 70 | 13 | 49 | 0 | 0 | 3.6 | 125 | 0.2 | 0 | 307 | 5 | 132 | 110 | 0 | 0 | 1130 | 72 | 4899.22 | 10897.24 | 91.55
15:00 | 0 | 51 | 26 | 0 | 0 | 0 | 0 | 69 | 409 | 0 | 0 | 54 | 0 | 0 | 75 | 16 | 0 | 55 | 35 | 108 | 25 | 0 | 350 | 255 | 0 | 0 | 35 | 29 | 329 | 0 | 0 | 17 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 2 | 40 | 34 | 2 | 155 | 0 | 0 | 50 | 0 | 85 | 187 | 0 | 0 | 0 | 1224 | 13 | 51 | 60 | 192 | 0 | 0 | 0 | 29 | 182 | 27 | 115 | 50 | 100 | 28 | 17 | 0 | 68 | 0 | 39 | 0 | 285 | 0 | 347 | 32 | 41 | 0 | 5 | 18 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 17 | 1 | 34.78 | 6 | 5827.78 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.67 | 0 | 0 | 663.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 38.17 | 214 | 0 | 0 | 0 | 213 | 0 | 315 | 0 | 3.57 | 2.5 | 164 | 66 | 35 | 11 | 26 | 0 | 0 | 2.4 | 99 | 0.32 | 0 | 307 | 4 | 132 | 110 | 0 | 0 | 1130 | 72 | 4648.11 | 10475.89 | 91.54
16:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 69 | 372 | 0 | 0 | 35 | 0 | 0 | 105 | 16 | 0 | 55 | 35 | 108 | 25 | 0 | 350 | 295 | 0 | 0 | 17 | 29 | 327 | 0 | 0 | 10 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 12 | 1 | 40 | 17 | 2 | 158 | 0 | 0 | 50 | 0 | 51 | 187 | 0 | 0 | 0 | 1110 | 8 | 51 | 60 | 195 | 0 | 0 | 0 | 29 | 192 | 30 | 68 | 50 | 51 | 28 | 17 | 0 | 56 | 0 | 21 | 0 | 300 | 0 | 357 | 32 | 40 | 0 | 5 | 18 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 67 | 19 | 1 | 15.79 | 6 | 5566.79 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.52 | 0 | 0 | 665.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 21.07 | 160 | 0 | 0 | 0 | 212 | 0 | 322 | 0 | 1.96 | 2.5 | 170 | 66 | 35 | 5 | 21 | 0 | 0 | 1.4 | 53 | 0.19 | 0 | 250 | 4 | 132 | 110 | 0 | 0 | 1120 | 72 | 4412.31 | 9979.1 | 91.54
17:00 | 0 | 54 | 25 | 0 | 0 | 0 | 0 | 69 | 381 | 0 | 0 | 35 | 0 | 0 | 105 | 38 | 0 | 55 | 35 | 108 | 25 | 0 | 350 | 300 | 0 | 0 | 17 | 29 | 329 | 0 | 0 | 2 | 0 | 20 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 26 | 7 | 0 | 0 | 14 | 18 | 0 | 40 | 17 | 5 | 155 | 17 | 0 | 50 | 0 | 51 | 188 | 0 | 0 | 0 | 1100 | 2 | 51 | 65 | 184 | 0 | 0 | 0 | 29 | 186 | 30 | 68 | 50 | 51 | 28 | 17 | 0 | 64 | 0 | 5 | 0 | 310 | 0 | 357 | 32 | 39 | 0 | 5 | 50 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 67 | 20 | 0 | 3.47 | 6 | 5639.47 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.59 | 0 | 0 | 662.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 5.13 | 160 | 0 | 0 | 0 | 211 | 0 | 398 | 0 | 0.4 | 2.5 | 167 | 66 | 35 | 2 | 20 | 0 | 0 | 0.4 | 13 | 0.05 | 0 | 250 | 4 | 132 | 110 | 0 | 0 | 1110 | 78 | 4366.26 | 10005.73 | 91.54
18:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 65 | 401 | 0 | 0 | 42 | 0 | 0 | 135 | 48 | 0 | 55 | 35 | 162 | 25 | 0 | 420 | 305 | 0 | 0 | 17 | 17 | 301 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 15 | 10 | 0 | 32 | 51 | 0 | 0 | 36 | 36 | 0 | 40 | 48 | 3 | 156 | 17 | 0 | 50 | 4 | 66 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 81 | 195 | 0 | 0 | 0 | 29 | 199 | 30 | 73 | 50 | 60 | 62 | 17 | 0 | 64 | 24 | 0 | 12 | 280 | 0 | 370 | 34 | 41 | 0 | 5 | 70 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 57 | 22 | 0 | 0 | 6 | 6208 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.64 | 0 | 0 | 35 | 0 | 10 | 0 | 50 | 0 | 12 | 0 | 0 | 30 | 0 | 164 | 0 | 0 | 0 | 180 | 0 | 327 | 0 | 0 | 2.5 | 163 | 66 | 57 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 7 | 132 | 110 | 0 | 0 | 1110 | 100 | 4538.14 | 10746.14 | 91.54
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 65 | 401 | 0 | 0 | 54 | 0 | 0 | 149 | 48 | 0 | 55 | 35 | 162 | 25 | 0 | 420 | 280 | 0 | 0 | 35 | 29 | 331 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 30 | 7 | 0 | 33 | 51 | 0 | 0 | 45 | 60 | 0 | 40 | 62 | 15 | 156 | 53 | 0 | 50 | 8 | 98 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 108 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 115 | 50 | 100 | 75 | 16 | 0 | 62 | 24 | 0 | 49 | 300 | 0 | 370 | 35 | 42 | 0 | 5 | 110 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 23 | 0 | 0 | 6 | 6619 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.04 | 0 | 0 | 41 | 0 | 44 | 0 | 97 | 0 | 34 | 0 | 0 | 30 | 0 | 211 | 0 | 0 | 0 | 220 | 0 | 395 | 0 | 0 | 2.5 | 165 | 66 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1120 | 100 | 4729.54 | 11348.54 | 91.53
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 65 | 402 | 0 | 0 | 54 | 0 | 0 | 149 | 32 | 0 | 55 | 35 | 162 | 25 | 0 | 420 | 290 | 0 | 0 | 35 | 29 | 330 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 37 | 51 | 0 | 0 | 12 | 24 | 0 | 40 | 80 | 23 | 157 | 17 | 0 | 32 | 0 | 85 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 116 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 115 | 50 | 68 | 75 | 17 | 0 | 62 | 0 | 0 | 48 | 300 | 0 | 370 | 35 | 42 | 0 | 5 | 112 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 23 | 0 | 0 | 6 | 6398 | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.94 | 0 | 0 | 41 | 0 | 0 | 0 | 98 | 0 | 34 | 0 | 0 | 30 | 0 | 210 | 0 | 0 | 0 | 218 | 0 | 393 | 0 | 0 | 2.5 | 163 | 66 | 74 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1130 | 100 | 4570.44 | 10968.44
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 72 | 401 | 0 | 0 | 54 | 0 | 0 | 149 | 32 | 0 | 55 | 35 | 162 | 25 | 0 | 420 | 281 | 0 | 0 | 35 | 29 | 330 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 36 | 51 | 0 | 0 | 12 | 24 | 0 | 40 | 76 | 30 | 157 | 17 | 0 | 32 | 0 | 85 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 115 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 115 | 50 | 68 | 77 | 17 | 0 | 56 | 0 | 0 | 40 | 290 | 0 | 370 | 36 | 42 | 0 | 5 | 163 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 23 | 0 | 0 | 6 | 6419.5 | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.25 | 0 | 0 | 41 | 0 | 0 | 0 | 98 | 0 | 35 | 0 | 0 | 30 | 0 | 210 | 0 | 0 | 0 | 218 | 0 | 394 | 0 | 0 | 2.5 | 164 | 66 | 74 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1130 | 100 | 4541.75 | 10961.25 | 91.53
21:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 72 | 401 | 0 | 0 | 54 | 0 | 0 | 132 | 32 | 0 | 32 | 35 | 162 | 25 | 0 | 420 | 280 | 0 | 0 | 35 | 29 | 333 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 41 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 35 | 214 | 0 | 0 | 24 | 0 | 85 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 115 | 50 | 68 | 53 | 17 | 0 | 60 | 0 | 0 | 0 | 300 | 0 | 370 | 33 | 42 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 23 | 0 | 0 | 6 | 6134 | 866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 393 | 0 | 0 | 2.5 | 163 | 66 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1130 | 100 | 4541.5 | 10675.5 | 91.53
22:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 54 | 0 | 0 | 96 | 32 | 0 | 0 | 0 | 108 | 25 | 0 | 420 | 263 | 0 | 0 | 35 | 29 | 335 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 213 | 0 | 0 | 19 | 0 | 34 | 187 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 68 | 50 | 34 | 53 | 17 | 0 | 56 | 0 | 0 | 0 | 300 | 60 | 375 | 32 | 42 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 23 | 0 | 0 | 6 | 5774 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 393 | 0 | 0 | 2.5 | 161 | 66 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 110 | 0 | 0 | 1130 | 54 | 4547.5 | 10321.5 | 91.53
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 70 | 401 | 0 | 0 | 17 | 0 | 0 | 78 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 350 | 273 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 156 | 0 | 0 | 19 | 0 | 0 | 186 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 80 | 29 | 183 | 30 | 34 | 45 | 0 | 9 | 17 | 0 | 64 | 0 | 0 | 0 | 280 | 102 | 376 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 23 | 0 | 0 | 6 | 5301 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 393 | 0 | 0 | 2.5 | 161 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 110 | 0 | 0 | 1130 | 17 | 4440.5 | 9741.5 | 91.52
Total KWH | 0 | 920640 | 369600 | 0 | 0 | 0 | 0 | 1588045.46 | 8899200 | 0 | 0 | 721080 | 0 | 0 | 1585152 | 575040 | 0 | 696942 | 447927 | 1815840 | 466920 | 0 | 9299000 | 6868218 | 0 | 0 | 476955 | 713000 | 7940649 | 0 | 0 | 182140 | 0 | 420000 | 495000 | 0 | 0 | 559527 | 60218 | 19200 | 0 | 330240 | 155753 | 0 | 0 | 386880 | 445440 | 20797 | 948000 | 606360 | 454080 | 3847272.73 | 237527 | 0 | 626880 | 13815 | 1040436 | 4270593 | 0 | 0 | 0 | 26301815 | 94365 | 1204006 | 966836 | 4683636 | 0 | 0 | 322000 | 687840 | 4610000 | 717408 | 1439040 | 1175850 | 1115520 | 670320 | 405600 | 0 | 1350720 | 44779 | 343327 | 114240 | 7313500 | 203400 | 9084000 | 779904 | 697000 | 0 | 104064 | 2199845 | 516048 | 0 | 2045760 | 718368 | 0 | 144000 | 0 | 466200 | 188400 | 1008000 | 677760 | 8800 | 270380 | 103920 | 131281018.19 | 20603880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438480 | 0 | 0 | 15306620 | 0 | 0 | 69088 | 0 | 71808 | 0 | 300898 | 0 | 60233 | 0 | 632120 | 79718 | 339000 | 4171364 | 0 | 0 | 0 | 4306082 | 0 | 9056145 | 0 | 28200 | 64260 | 3934000 | 1535563 | 826018 | 65482 | 478377 | 0 | 0 | 20851.44 | 789840 | 2496 | 0 | 6327000 | 143836 | 2875000 | 3557540 | 0 | 0 | 25924363.64 | 1213200 | 103221463.08 | 234502481.27

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-02-2025 | during | 04-02-2025 | during | 04-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 66 | 65 | 97.3 | 97.3 | 77 | 77 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 286 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 280 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 39 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 82 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 17 | 20 | 22.5 | 22.5 | 22.5 | 22.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 29 | 29 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 26 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 78 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 17 | 17 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.654 | 1974 | 2244 | 4580.87 | 4551.87 | 2827.09 | 2798.09
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 187 | 187 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 57 | 98 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 70 | 70 | 70 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 45 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 15 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 7 | 108 | 108 | 32 | 32 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.51 | 0 | 3.51 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 62 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 60 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 1 | 33 | 14 | 3 | 14 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 155 | 156 | 150 | 150 | 156 | 156 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1913 | 2154 | 3015.23 | 3000.72 | 2864.23 | 2849.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 193 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 356.56 | 356.56 | 150 | 320 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 30 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 40 | 51 | 40 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 30 | 108 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 49 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 100 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 62 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 24 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 16 | 14.08 | 20.83 | 14.08 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 75 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 96 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 962 | 1089 | 2067.78 | 2035.53 | 1726.28 | 1864.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-02-2025 | during | 04-02-2025 | during | 04-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 18 | 23 | 210 | 210 | 20 | 20 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 58 | 200 | 200 | 70 | 70 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.68 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 173.68 | 131 | 645.2 | 601.5 | 203.2 | 159.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 41 | 42 | 40 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 15 | 110 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 30 | 35 | 44 | 44 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | Tripped
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 370 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 130 | 130 | 130 | 130 | Only Gas turbine is available
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 910 | 1001 | 1234 | 1236 | 1200 | 1200
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 922 | 730 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74.16 | 0 | 57 | 0 | 57 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 996.16 | 730 | 3152 | 3095 | 1142.02 | 1085.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 132 | 136 | 136 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1110 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 110 | 220 | 110 | 220 | 110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 72 | 100 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.46 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1773.46 | 1776 | 2178.12 | 2067.12 | 2142.12 | 2031.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 41 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 34 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 148 | 211 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 133 | 220 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 332 | 395 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 44 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.52 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 756 | 753.04 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.83 | 0 | 45 | 0 | 45 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1524.85 | 1827.54 | 2501.79 | 2357.24 | 2165.81 | 2021.26
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 66 | 66 | 65 | 65 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 165 | 160 | 160 | 160 | 160 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 48 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 4.1 | 0 | 4.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 150 | 0 | 139.5 | 0 | 143.12 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 503.6 | 396 | 636.6 | 473 | 625.23 | 458.01
System Total |  |  |  |  | 27884.66 | 27066.632 | 10730.75 | 11348.54 | 20011.59 | 19417.98 | 14895.98 | 14466.75
Forecast Scenario (04-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9350 |  | 0 |  | 9350
|  |  |  | 1:00 | 8900 |  | 0 |  | 8900
|  |  |  | 2:00 | 8340 |  | 0 |  | 8340
|  |  |  | 3:00 | 7980 |  | 0 |  | 7980
|  |  |  | 4:00 | 7760 |  | 0 |  | 7760
|  |  |  | 5:00 | 7560 |  | 0 |  | 7560
|  |  |  | 6:00 | 7740 |  | 0 |  | 7740
|  |  |  | 7:00 | 8500 |  | 0 |  | 8500
|  |  |  | 8:00 | 9300 |  | 0 |  | 9300
|  |  |  | 9:00 | 10130 |  | 0 |  | 10130
|  |  |  | 10:00 | 10200 |  | 0 |  | 10200
|  |  |  | 11:00 | 10260 |  | 0 |  | 10260
|  |  |  | 12:00 | 10770 |  | 0 |  | 10770
|  |  |  | 13:00 | 11240 |  | 0 |  | 11240
|  |  |  | 14:00 | 10930 |  | 0 |  | 10930
|  |  |  | 15:00 | 10360 |  | 0 |  | 10360
|  |  |  | 16:00 | 9920 |  | 0 |  | 9920
|  |  |  | 17:00 | 9860 |  | 0 |  | 9860
|  |  |  | 18:00 | 10550 |  | 0 |  | 10550
|  |  |  | 18:30 | 10400 |  | 0 |  | 10400
|  |  |  | 19:00 | 11300 |  | 0 |  | 11300
|  |  |  | 19:30 | 10880 |  | 0 |  | 10880
|  |  |  | 20:00 | 10850 |  | 0 |  | 10850
|  |  |  | 21:00 | 10490 |  | 0 |  | 10490
|  |  |  | 22:00 | 10150 |  | 0 |  | 10150
|  |  |  | 23:00 | 9780 |  | 0 |  | 9780
Probable Maximum Temperature: |  |  | 26.30°C
Probable Maximum Demand at Day Peak: |  |  | 10770.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 232.22 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:42 hrs on 04-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10730.75 | MW | 12:00 Hr. | Energy Generated |  |  | 234.5025 |  | MKWHr.
| Day Peak Demand |  |  | 10773.75 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.236 |  | MKWHr.
| Evening Peak Generation |  |  | 11348.54 | MW | 19:00 Hr. | Energy Demand |  |  | 234.7385 |  | MKWHr.
| Evening Peak Demand |  |  | 11380.54 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.8 |  | °C
| Minimum Generation of the Day |  |  | 7566.41 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 796.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 11348.54 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.3224 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.69 | 0 | 7.6092 | 0 | 0 | 0.18214 | 0 | 0 | 44.4813 | Gas | 103.8789 | Gas | 374622351.171
| Chattogram Zone |  |  | 4.7247 | 30.1491 | 4.152 | 0 | 0.948 | 0.11516 | 0 | 0.33024 | 40.4192 | Coal | 67.87 | Coal | 479340561.2336
| Cumilla Zone |  |  | 13.8063 | 0 | 4.3507 | 0 | 0 | 0.34333 | 1.3507 | 0 | 19.8511 | HFO | 20.9778 | HFO | 383005277.65
| Mymensingh Zone |  |  | 0.67776 | 0 | 1.7665 | 0 | 0 | 0.27918 | 0 | 0 | 2.7235 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8059 | Hydro | 0.948 | Hydro | 94800
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.43848 | 20.6039 | 0 | 21.0424 | Solar | 3.2363 | Solar | 49953988.974
| Barishal Zone |  |  | 6.5764 | 32.2514 | 1.2132 | 0 | 0 | 0.002496 | 0 | 0 | 40.0434 | Import | 37.2612 | Import | 190442261.8
| Rajshahi Zone |  |  | 17.5979 | 0 | 0.58174 | 0 | 0 | 0.99932 | 15.3066 | 0 | 34.4855 | Wind | 0.33024 | Wind | 5151744
| Rangpur Zone |  |  | 0 | 5.4696 | 1.3044 | 0 | 0 | 0.87617 | 0 | 0 | 7.6501
| Total |  |  | 103.8789 | 67.87 | 20.9778 | 0 | 0.948 | 3.2363 | 37.2612 | 0.33024 | 234.5025
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 374622351.171 |  | Hydro | 94800
|  |  |  | Coal | 479340561.2336 |  | Solar | 49953988.974
|  |  |  | HFO | 383005277.65 |  | Import | 190442261.8
|  |  |  | HSD | 0 |  | Wind | 5151744
[5 empty] | Total: | 148,26,10,984 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6039 | Peak Hr Flow | 730.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7981090.969 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.3066 | Peak Hr Flow | 753.04 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 398 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3507 | Peak Hr Flow | 62.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 754 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.2612 | Peak Hr Flow | 1545.04 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3991
|  |  |  | Chattogram |  | 0 |  | 1218
|  |  |  | Cumilla |  | 0 |  | 914
|  |  |  | Mymensingh |  | 31 |  | 989
|  |  |  | Sylhet |  | 0 |  | 366
|  |  |  | Khulna |  | 0 |  | 1224
|  |  |  | Barishal |  | 0 |  | 300
|  |  |  | Rajshahi |  | 0 |  | 1101
|  |  |  | Rangpur |  | 0 |  | 805
|  |  |  | Total |  | 31 |  | 10908
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1122 |  |  |  | Total | 742.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1864.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:02 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) is restored.
|  | 08:02 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) is restored.
| 08:26 | 19:53 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Line
bypass by the contractor
| 08:31 | 18:08 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Shutdown due to Deep Cleaning.
| 08:42 |  | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to 132 Bus Section 3-4 Shutdown
|  | 08:43 | Mirzapur 132/33kV S/S Mirzapur-Kaliakoir ckt-2B(E-09) is restored.
|  | 08:43 | Mirzapur 132/33kV S/S Mirzapur-Kaliakair-ckt-2A(E08) is restored.
| 08:44 |  | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to 132 Bus Section 3-4 Shutdown
| 08:45 | 12:49 | Madanganj-Munsiganj 132 kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end Due to As per
request of Backup NLDC. and from Munshiganj 132/33kV end Due to Deadline Checking
| 08:50 | 16:08 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance works
| 08:56 | 22:21 | Sylhet 132/33kV S/S 20 MW PP Project Work S/D Due to 132 KV Bus Section-3 Shutdown
Purpose.
| 08:57 | 09:37 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to 132 Bus Section
3-4 Shutdown
|  | 08:58 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
| 09:06 | 10:19 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Relay
Testing work by SMPD2
|  | 09:07 | Mirzapur 132/33kV S/S Transformer-01(E05) HT is restored.
|  | 09:17 | Mirzapur 132/33kV S/S Transformer-01(E05) LT is restored.
| 09:18 | 09:40 | Sylhet 132/33kV S/S 150MW GT PS Scheduled S/D Due to 132 Bus Section 3-4 Shutdown
| 09:21 | 10:01 | Sylhet 132/33kV S/S 75 MW ST PS Scheduled S/D Due to 132 Bus Section 3-4 Shutdown
| 09:25 | 17:40 | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to 33KV Bus Maintenance
| 09:32 |  | Matarbari - SS Power 400 kv L-1 was shut down due to A/M
|  | 09:48 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
| 10:18 | 20:18 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from Baharampur end
| 10:48 | 11:21 | Mirpur 132/33kV S/S T2 HT Scheduled S/D Due to Annual Maintenance Relay test
| 11:44 | 16:39 | BIPTC S/S 20DF22 Tripped showing Differential 87.1 relays Due to Tripeed by capacitor
unbalance 60/61 instant L2
| 11:44 | 16:39 | BIPTC S/S 20DF22 Scheduled S/D Due to Trip by C1 unbalance 60/61 instant L2
| 12:00 |  | Day Peak Gen. 10730 MW
| 12:25 | 16:11 | Hathazari 230/132/33kV S/S MT-01 HT Scheduled S/D
| 12:25 | 16:11 | Hathazari 230/132/33kV S/S MT-01 LT Scheduled S/D
| 12:27 |  | Bhola Nutan Biddut BD LTD GT-2 Tripped with remarks:- High exhust Temperature
| 12:41 |  | Bhola Nutan Biddyut CCPP GT-2 tripped at 12:41 hours.
| 12:49 | 17:14 | Madanganj-Munsiganj 132 kV Ckt-2 Scheduled S/D from Munshiganj 132/33kV end Due to Dead
Line Check and from Madanganj 132/33kV end Due to As per order of Backup NLDC.
| 13:19 |  | Rajbari 132/33KV T-3 S/D Withdraw.
| 13:47 |  | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to H-Pole
Installation work and from Shikalbaha 230/132kVend.
|  | 14:14 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
| 15:12 | 16:50 | Jamalpur 132/33kV S/S T-1 LT Scheduled S/D Due to Project work
| 15:12 | 16:50 | Jamalpur 132/33kV S/S T-1 HT Scheduled S/D Due to Project work
|  | 16:10 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 is restored.
|  | 16:56 | Jamalpur 132/33kV S/S Bus-B is restored.
| 17:03 | 21:23 | Jamalpur 132/33kV S/S Bus-A Scheduled S/D Due to Project work
| 19:00 |  | Evening Peak Generation = 11349MW
| 19:35 |  | Sylhet 132/33kV S/S 75 MW ST PS Scheduled S/D Due to 132 kV bus section 3&4 close
| 19:35 | 20:00 | Sylhet 132/33kV S/S 150MW GT PS Scheduled S/D Due to 132 kV bus section 3&4 close
| 19:37 | 19:58 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to 132 kV bus
section 3&4 close
|  | 21:20 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 is restored.
| 21:40 |  | Bibiyana South 400 MW Synchronized with remarks:- gt
| 22:22 |  | Ashuganj South 360 MW GT was sync.
| 22:22 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 01:42 |  | Daudkandi 132/33kV S/S Transformer-3 HT Forced S/D Due to 132/33 KV Transformer-3
shutdown of under ground cable change( Y-Phase)for over temperature
| 01:42 |  | Daudkandi 132/33kV S/S Transformer-3 LT Forced S/D Due to shutdown of under ground cable
change( Y-Phase)for over temperature
| 05:00 |  | Minimum generation 7713 MW
| 07:23 |  | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to Shutdown
Taken by Ghorasal power station for Maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 65 | 1588045.46 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 8899200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9299000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 6868218 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 696942 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7940649 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 721080 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 575040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 447927 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 476955 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 420000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 495000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 466920 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 29 | 713000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 369600 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1585152 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 920640 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1815840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 182140 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.654 | 2244 | 44481348.46
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 13815 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 94365 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 626880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 948000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 187 | 4270593 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 98 | 1040436 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 155753 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 45 | 386880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 454080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 7 | 19200 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20797 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 60218 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 62 | 606360 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 445440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 559527 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 237527 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26301815 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 33 | 330240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 156 | 3847272.73 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2154 | 40419198.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4610000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 322000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 717408 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 687840 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4683636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1204006 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 108 | 966836 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 49 | 114240 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1175850 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1115520 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1350720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 24 | 44779 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 405600 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 670320 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1439040 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 343327 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1089 | 19851122
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 23 | 677760 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1008000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 188400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 270380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 103920 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 466200 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 131 | 2723460
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 697000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2199845 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 779904 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 104064 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718368 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2045760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 144000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 516048 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7313500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 9084000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 203400 | Only Gas turbine is available
Sylhet Area Total |  |  |  |  | 2368.568 | 1001 | 23805889
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 730 | 20603880 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 438480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 730 | 21042360
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 143836 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 2875000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 25924363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 3557540 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1213200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6327000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2496 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1776 | 40043435.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 41 | 69088 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 34 | 60233 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 211 | 4171364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 220 | 4306082 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 395 | 9056145 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 79718 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 64260 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 300898 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 44 | 71808 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 753.04 | 15306620 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 339000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 632120 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1827.54 | 34485536
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 66 | 1535563 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 3934000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 478377 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20851.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 826018 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 65482 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 789840 | -
Rangpur Area Total |  |  |  |  | 950 | 396 | 7650131.44
Eastern Grid Total |  |  |  |  | 16772.132 | 6619 | 131281018.19
Western Grid Total |  |  |  |  | 10294.5 | 4729.54 | 103221463.08
National Grid Total |  |  |  |  | 27066.632 | 11348.54 | 234502481.27
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7446.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3430.7 | MW
i) Dhaka area |  |  | 3990.53 |  | MW | i) Khulna area |  |  |  | 1224.2 | MW
ii) Chattogram area |  |  | 1217.5 |  | MW | ii) Barishal area |  |  |  | 300.5 | MW
iii) Cumilla area |  |  | 914 |  | MW | iii) Rajshahi area |  |  |  | 1101 | MW
iv) Mymensingh area |  |  | 958 |  | MW | iv) Rangpur area |  |  |  | 805 | MW
v) Sylhet area |  |  | 366 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10876.73 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 18:30 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 105 | 05:00 | 68 | Jamalpur | 105 | 09:00 | 134 | Purbasadipur | 123 | 13:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jashore | 107 | 09:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 80 | 13:00 | 70 | Jhenaidah | 96 | 18:30 | 136 | Rahim | 22 | 06:00
5 | Agrabad | 68 | 18:30 | 71 | Joydebpur | 145 | 18:30 | 137 | Rajbari | 52 | 19:00
6 | Amnura | 48 | 13:00 | 72 | Joypurhat | 51 | 18:30 | 138 | Rajendrapur | 102 | 10:00
7 | Ashuganj | 65 | 13:00 | 73 | Juldah | 11 | 13:00 | 139 | Rajshahi | 112 | 13:00
8 | BSRM | 200 | 18:00 | 74 | KSRM | 16 | 00:00 | 140 | Rajshahi-230 | 40 | 21:00
9 | Bagerhat | 61 | 18:30 | 75 | Kabirpur | 175 | 20:00 | 141 | Ramganj | 86 | 14:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 52 | 18:30 | 142 | Rampur | 27 | 13:00
11 | Bakulia | 73 | 18:30 | 77 | Kallyanpur | 75 | 18:30 | 143 | Rangamati | 13 | 18:30
12 | Banani | 36 | 12:00 | 78 | Kalurghat | 32 | 15:00 | 144 | Rangpur | 102 | 13:00
13 | Bangabhaban | 9 | 13:00 | 79 | Kamrangirchar | 53.3 | 18:30 | 145 | Ruppur | 9 | 16:00
14 | Barapukuria | 66 | 12:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 0 | 00:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 100 | 13:00 | 147 | Saidpur | 101 | 11:00
16 | Barishal | 72 | 12:00 | 82 | Keranigonj | 60 | 12:00 | 148 | Satkhira | 88 | 18:30
17 | Barishal-230 | 74 | 18:30 | 83 | Khagrachori | 24 | 18:30 | 149 | Satmasjid | 88 | 13:00
18 | Baroaulia | 48 | 13:00 | 84 | Khulna | 74 | 13:00 | 150 | Savar | 184 | 10:00
19 | Baroirhat | 55 | 18:00 | 85 | Khulshi | 149 | 11:00 | 151 | SevenRings | 20.03 | 12:00
20 | Bashundhara | 139 | 12:00 | 86 | Kishoreganj | 126 | 19:00 | 152 | ShahCement | 23 | 01:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 274 | 15:00 | 153 | Shahjadpur | 67 | 19:00
22 | Beanibazar | 44 | 18:30 | 88 | Kulaura | 27 | 18:00 | 154 | Shahjibazar | 85 | 18:00
23 | Benapole | 46 | 11:00 | 89 | Kurigram | 62 | 08:00 | 155 | Shahmirpur | 47 | 18:00
24 | Bhaluka | 112 | 11:00 | 90 | Kushtia | 106 | 18:30 | 156 | Shariatpur | 53 | 21:00
25 | Bhandaria | 34.5 | 21:00 | 91 | Lalbag | 54 | 14:00 | 157 | Sherpur | 118 | 21:00
26 | Bhangura | 28 | 13:00 | 92 | Lalmonirhat | 48 | 08:00 | 158 | Shikalbaha | 18 | 12:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 11.2 | 19:00 | 159 | Shitalakhya | 64.7 | 13:00
28 | Bhulta | 251 | 11:00 | 94 | Madanganj | 18 | 07:00 | 160 | Sholosohor | 34 | 12:00
29 | Bog-Sherpur | 66 | 13:00 | 95 | Madaripur | 69 | 21:00 | 161 | Shyampur | 134 | 01:00
30 | Bogura | 118 | 19:30 | 96 | Madartek | 51.27 | 13:00 | 162 | Siddhirganj | 102 | 11:00
31 | Borhanuddin | 54 | 22:00 | 97 | Madunaghat | 34 | 13:00 | 163 | Sirajganj | 86 | 19:00
32 | Brahmanbaria | 104 | 18:00 | 98 | Magura | 46 | 18:30 | 164 | Sonargaon | 84 | 10:00
33 | Cantonment | 82 | 13:00 | 99 | Mahasthangarh | 56 | 08:00 | 165 | Sreemongol | 46 | 18:00
34 | Chandpur | 45 | 20:00 | 100 | Manikganj | 105 | 19:00 | 166 | Sreepur | 77 | 10:00
35 | Chandraghona | 26 | 18:30 | 101 | Maniknagar | 54 | 13:00 | 167 | Srinagar | 29.6 | 21:00
36 | Chapai | 72 | 09:00 | 102 | Matarbari | 37 | 18:30 | 168 | Sunamganj | 38 | 22:00
37 | Charsaidpur | 41 | 12:00 | 103 | Matuail | 52 | 11:00 | 169 | Sylhet | 24 | 10:00
38 | Chauddagram | 48 | 13:00 | 104 | Millgate | 66 | 12:00 | 170 | Sylhet-132 | 80 | 13:00
39 | Chhatak | 21 | 21:00 | 105 | Mirpur | 92 | 13:00 | 171 | TK | 21.5 | 18:30
40 | Chowmuhani | 144 | 18:00 | 106 | Mirsorai | 8 | 18:00 | 172 | Tangail | 156 | 12:00
41 | Chuadanga | 78 | 13:00 | 107 | Mirzapur | 40 | 18:00 | 173 | Thakurgaon | 78 | 18:30
42 | Coxsbazar | 115 | 18:00 | 108 | Mithapukur | 74 | 18:30 | 174 | Tongi | 85 | 11:00
43 | Cumilla(N) | 114 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 24 | 18:30
44 | Cumilla(S) | 135 | 14:00 | 110 | Mogbazar | 105 | 14:00 | 176 | Ullon | 37 | 13:00
45 | Daudkandi | 107 | 18:00 | 111 | Mongla | 23 | 19:30 | 177 | Uttara | 65 | 13:00
46 | Dhaka | 34 | 13:00 | 112 | Motijheel | 28 | 13:00 | 178 | UttaraNew | 34 | 13:00
47 | Dhamrai | 104 | 15:00 | 113 | Muktagacha | 28 | 13:00 | 179 | Zigatola | 56 | 13:00
48 | Dhanmondi | 101 | 13:00 | 114 | Munshiganj | 70 | 13:00
49 | Dohazari | 58 | 12:00 | 115 | Mymensingh | 175 | 14:00
50 | Faridpur | 108 | 18:30 | 116 | Naogaon | 113 | 13:00
51 | Fatullah | 84 | 12:00 | 117 | Narail | 42 | 18:30
52 | Fenchuganj | 24 | 18:00 | 118 | Narinda | 59 | 13:00
53 | Feni | 67 | 18:30 | 119 | Narshingdi | 155 | 19:30
54 | GPH | 88 | 00:00 | 120 | Natore | 102 | 18:30
55 | Ghatail | 38 | 13:00 | 121 | Nawabganj | 31.6 | 13:00
56 | Ghorashal | 14 | 10:00 | 122 | Netrakona | 138 | 09:00
57 | Ghorashal-230 | 57 | 19:00 | 123 | New | 69 | 11:00
58 | Goalpara | 30 | 13:00 | 124 | Niamatpur | 84 | 13:00
59 | Gollamari | 48 | 18:30 | 125 | Noapara | 36 | 18:30
60 | Gopalganj | 79 | 18:30 | 126 | PHP | 7 | 08:00
61 | Gulshan | 80 | 13:00 | 127 | Pabna | 65 | 18:30
62 | Halishahar | 51 | 15:00 | 128 | Palashbari | 94 | 08:00
63 | HaripurSBU | 171 | 12:00 | 129 | Panchagarh | 44 | 18:30
64 | Hasnabad | 71 | 10:00 | 130 | Patuakhali | 55.5 | 20:00
65 | Hathazari | 55 | 18:00 | 131 | Payra | 14 | 18:30
66 | Ishurdi | 61 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9350.56 | 0 |  | 9350.56
1:00 | 8904.34 | 0 |  | 8904.34
2:00 | 8348.8 | 0 |  | 8348.8
3:00 | 7989.18 | 0 |  | 7989.18
4:00 | 7762.83 | 0 |  | 7762.83
5:00 | 7566.41 | 0 |  | 7566.41
6:00 | 7743.66 | 0 |  | 7743.66
7:00 | 8084.79 | 0 |  | 8084.79
8:00 | 9055.89 | 0 |  | 9055.89
9:00 | 10130.07 | 0 |  | 10130.07
10:00 | 10204.16 | 0 |  | 10204.16
11:00 | 10260.46 | 0 |  | 10260.46
12:00 | 10730.75 | 41 |  | 10773.75
13:00 | 11210.32 | 30 |  | 11241.32
14:00 | 10897.24 | 35 |  | 10934.24
15:00 | 10475.89 | 27 |  | 10503.89
16:00 | 9979.1 | 0 |  | 9979.1
17:00 | 10005.73 | 0 |  | 10005.73
18:00 | 10746.14 | 72 |  | 10821.38
19:00 | 11348.54 | 31 |  | 11380.54
19:30 | 10968.44 | 22 |  | 10991.44
20:00 | 10961.25 | 0 |  | 10961.25
21:00 | 10675.5 | 0 |  | 10675.5
22:00 | 10321.5 | 0 |  | 10321.5
23:00 | 9741.5 | 0 |  | 9741.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4977 | 4373.56 | 9350.56 | DAILY GENERATION CURVE
00:30 | 4869 | 4258.45 | 9127.45
01:00 | 4761 | 4143.34 | 8904.34 | 03-02-2025
01:30 | 4690 | 3936.57 | 8626.57
02:00 | 4619 | 3729.8 | 8348.8
02:30 | 4630 | 3538.99 | 8168.99
03:00 | 4641 | 3348.18 | 7989.18
03:30 | 4580.5 | 3295.505 | 7876.005
04:00 | 4520 | 3242.83 | 7762.83
04:30 | 4430.75 | 3233.87 | 7664.62
05:00 | 4341.5 | 3224.91 | 7566.41
05:30 | 4381.5 | 3273.535 | 7655.035
06:00 | 4421.5 | 3322.16 | 7743.66
06:30 | 4448.5 | 3465.725 | 7914.225
07:00 | 4475.5 | 3609.29 | 8084.79
07:30 | 4685.34 | 3885 | 8570.34
08:00 | 4895.18 | 4160.71 | 9055.89
08:30 | 5329.315 | 4263.665 | 9592.98
09:00 | 5763.45 | 4366.62 | 10130.07
09:30 | 5695.4 | 4471.715 | 10167.115
10:00 | 5627.35 | 4576.81 | 10204.16
10:30 | 5587.545 | 4644.765 | 10232.31
11:00 | 5547.74 | 4712.72 | 10260.46
11:30 | 5740.21 | 4755.395 | 10495.605
12:00 | 5932.68 | 4798.07 | 10730.75
12:30 | 6083.39 | 4887.145 | 10970.535
13:00 | 6234.1 | 4976.22 | 11210.32
13:30 | 6116.06 | 4937.72 | 11053.78
14:00 | 5998.02 | 4899.22 | 10897.24
14:30 | 5912.9 | 4773.665 | 10686.565
15:00 | 5827.78 | 4648.11 | 10475.89
15:30 | 5697.285 | 4530.21 | 10227.495
16:00 | 5566.79 | 4412.31 | 9979.1
16:30 | 5603.13 | 4389.285 | 9992.415
17:00 | 5639.47 | 4366.26 | 10005.73
17:30 | 5923.735 | 4452.2 | 10375.935
18:00 | 6208 | 4538.14 | 10746.14
18:30 | 6413.5 | 4633.84 | 11047.34
19:00 | 6619 | 4729.54 | 11348.54
19:30 | 6398 | 4570.44 | 10968.44
20:00 | 6419.5 | 4541.75 | 10961.25
20:30 | 6276.75 | 4541.625 | 10818.375 |  | Executive Engineer
21:00 | 6134 | 4541.5 | 10675.5 |  | Network Operation Division
21:30 | 5954 | 4544.5 | 10498.5
22:00 | 5774 | 4547.5 | 10321.5
22:30 | 5537.5 | 4494 | 10031.5
23:00 | 5301 | 4440.5 | 9741.5

## En-Curve
QF-LDC-12
Date | 03-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2551 | 1937.5 | 906 | 0 | 54 | 746.06 | 40 | 3050 | 0 | 0 | 63 | 0 | 0 | 3 | 0 | DAILY ENERGY CURVE
00:30 | 2582.5 | 1934.5 | 905.5 | 0 | 52 | 672.95 | 60 | 2876.5 | 0 | 0 | 40 | 0 | 0 | 3.5 | 0 | 03-02-2025
01:00 | 2614 | 1931.5 | 905 | 0 | 50 | 599.84 | 80 | 2703 | 0 | 0 | 17 | 0 | 0 | 4 | 0
01:30 | 2574 | 1933 | 905.5 | 0 | 49 | 512.07 | 80 | 2560.5 | 0 | 0 | 8.5 | 0 | 0 | 4 | 0 | Energy Generated | 234.5025 |  | MKWHr
02:00 | 2534 | 1934.5 | 906 | 0 | 48 | 424.3 | 80 | 2418 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | Energy not Served | 0.236 |  | MKWHr
02:30 | 2553.5 | 1935 | 814 | 0 | 47 | 419.99 | 80 | 2315.5 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | Total Energy Requirement | 234.7385 |  | MKWHr
03:00 | 2573 | 1935.5 | 722 | 0 | 46 | 415.68 | 80 | 2213 | 0 | 0 | 0 | 0 | 0 | 4 | 0
03:30 | 2508.5 | 1925 | 720.5 | 0 | 46 | 416.005 | 80 | 2174 | 0 | 0 | 0 | 0 | 0 | 6 | 0
04:00 | 2444 | 1914.5 | 719 | 0 | 46 | 416.33 | 80 | 2135 | 0 | 0 | 0 | 0 | 0 | 8 | 0
04:30 | 2414 | 1899.75 | 718.5 | 0 | 46 | 415.87 | 80 | 2085 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0
05:00 | 2384 | 1885 | 718 | 0 | 46 | 415.41 | 80 | 2035 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 2381 | 1880.5 | 718 | 0 | 47 | 420.035 | 80 | 2118.5 | 0 | 0 | 8 | 0 | 0 | 2 | 0
06:00 | 2378 | 1876 | 718 | 0 | 48 | 424.66 | 80 | 2202 | 0 | 0 | 16 | 0 | 0 | 1 | 0
06:30 | 2286.5 | 1881 | 717.5 | 0 | 48 | 467.04 | 80 | 2388.5 | 1.185 | 5 | 38.5 | 0 | 0 | 1 | 0
07:00 | 2195 | 1886 | 717 | 0 | 48 | 509.42 | 80 | 2575 | 2.37 | 10 | 61 | 0 | 0 | 1 | 0
07:30 | 2246 | 1876.5 | 812 | 0 | 51 | 551.21 | 60 | 2753.5 | 28.13 | 17.5 | 174 | 0 | 0 | 0.5 | 0
08:00 | 2297 | 1867 | 907 | 0 | 54 | 593 | 40 | 2932 | 53.89 | 25 | 287 | 0 | 0 | 0 | 0
08:30 | 2299.5 | 1887.5 | 766 | 0 | 55 | 678 | 40 | 2986 | 105.48 | 75 | 700.5 | 0 | 0 | 0 | 0
09:00 | 2302 | 1908 | 625 | 0 | 56 | 763 | 40 | 3040 | 157.07 | 125 | 1114 | 0 | 0 | 0 | 0
09:30 | 2257.5 | 1878 | 768.5 | 0 | 53 | 758 | 40 | 3031 | 248.115 | 125 | 1008 | 0 | 0 | 0 | 0
10:00 | 2213 | 1848 | 912 | 0 | 50 | 753 | 40 | 3022 | 339.16 | 125 | 902 | 0 | 0 | 0 | 0
10:30 | 2227 | 1794.5 | 912 | 0 | 57 | 753.5 | 40 | 3021.5 | 414.81 | 133 | 879 | 0 | 0 | 0 | 0
11:00 | 2241 | 1741 | 912 | 0 | 64 | 754 | 40 | 3021 | 490.46 | 141 | 856 | 0 | 0 | 0 | 0
11:30 | 2247.5 | 1763.25 | 917 | 0 | 66 | 755 | 40 | 3020 | 521.355 | 150 | 1015 | 0 | 0 | 0.5 | 20.5
12:00 | 2254 | 1785.5 | 922 | 0 | 68 | 756 | 40 | 3019 | 552.25 | 159 | 1174 | 0 | 0 | 1 | 41
12:30 | 2426 | 1783.5 | 922 | 0 | 70 | 757 | 40 | 3029.5 | 538.035 | 159 | 1241 | 0 | 0 | 4.5 | 35.5
13:00 | 2598 | 1781.5 | 922 | 0 | 72 | 758 | 40 | 3040 | 523.82 | 159 | 1308 | 0 | 0 | 8 | 30
13:30 | 2561 | 1716.5 | 922 | 0 | 70.5 | 757.88 | 40 | 3043 | 503.9 | 121 | 1305 | 0 | 0 | 13 | 32.5
14:00 | 2524 | 1651.5 | 922 | 0 | 69 | 757.76 | 40 | 3046 | 483.98 | 83 | 1302 | 0 | 0 | 18 | 35
14:30 | 2508.5 | 1639.5 | 922 | 0 | 68.5 | 710.62 | 40 | 3046 | 431.445 | 88 | 1218.5 | 0 | 0 | 13.5 | 31
15:00 | 2493 | 1627.5 | 922 | 0 | 68 | 663.48 | 40 | 3046 | 378.91 | 93 | 1135 | 0 | 0 | 9 | 27
15:30 | 2461.5 | 1656.5 | 921.5 | 0 | 62 | 664.575 | 40 | 2960 | 292.42 | 92.5 | 1059.5 | 0 | 0 | 17 | 13.5
16:00 | 2430 | 1685.5 | 921 | 0 | 56 | 665.67 | 40 | 2874 | 205.93 | 92 | 984 | 0 | 0 | 25 | 0
16:30 | 2470.5 | 1704.5 | 921 | 0 | 60 | 663.93 | 40 | 2861 | 128.985 | 108 | 1009 | 0 | 0 | 25.5 | 0
17:00 | 2511 | 1723.5 | 921 | 0 | 64 | 662.19 | 40 | 2848 | 52.04 | 124 | 1034 | 0 | 0 | 26 | 0
17:30 | 2472.5 | 1755 | 921.5 | 0 | 64 | 708.915 | 40 | 2915 | 26.02 | 237.5 | 1206.5 | 0 | 0 | 29 | 36
18:00 | 2434 | 1786.5 | 922 | 0 | 64 | 755.64 | 40 | 2982 | 0 | 351 | 1379 | 0 | 0 | 32 | 72
18:30 | 2519.5 | 1817 | 826 | 0 | 63 | 754.34 | 40 | 3010 | 0 | 407 | 1578 | 0 | 0 | 32.5 | 51.5
19:00 | 2605 | 1847.5 | 730 | 0 | 62 | 753.04 | 40 | 3038 | 0 | 463 | 1777 | 0 | 0 | 33 | 31
19:30 | 2599 | 1868.5 | 636 | 0 | 62 | 748.94 | 40 | 3047 | 0 | 429 | 1501 | 0 | 0 | 37 | 22
20:00 | 2599 | 1909 | 635 | 0 | 56 | 753.25 | 40 | 3048 | 0 | 422 | 1463 | 0 | 0 | 36 | 0
20:30 | 2603 | 1893.25 | 750.5 | 0 | 58 | 754.125 | 40 | 3076 | 0 | 293.5 | 1311.5 | 0 | 0 | 38.5 | 0
21:00 | 2607 | 1877.5 | 866 | 0 | 60 | 755 | 40 | 3104 | 0 | 165 | 1160 | 0 | 0 | 41 | 0
21:30 | 2641 | 1869 | 893.5 | 0 | 58 | 754 | 40 | 3102.5 | 0 | 156.5 | 944 | 0 | 0 | 40 | 0
22:00 | 2675 | 1860.5 | 921 | 0 | 56 | 753 | 40 | 3101 | 0 | 148 | 728 | 0 | 0 | 39 | 0
22:30 | 2733.5 | 1824 | 921 | 0 | 60 | 756.5 | 40 | 3072 | 0 | 99 | 496 | 0 | 0 | 29.5 | 0
23:00 | 2792 | 1787.5 | 921 | 0 | 64 | 760 | 40 | 3043 | 0 | 50 | 264 | 0 | 0 | 20 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 413 | 05:00 | 390 | 12:00 | Payra | 417 | 04:00 | 407 | 11:00
Ashuganj | 414 | 5:00 | 387 | 12:00 | Rahanpur | 419 | 04:00 | 394 | 08:00
Bhulta | 411 | 03:00 | 389 | 12:00 | Rampal | 413 | 04:00 | 383 | 12:00
Bibiana | 409 | 04:00 | 394 | 10:00
BIPTC | 408 | 03:00 | 387 | 10:00
Bogura | 420 | 04:00 | 392 | 08:00
Gopalganj | 415 | 04:00 | 392 | 12:00
Kaliakoir | 401 | 07:00 | 379 | 11:00
Madunaghat | 409 | 05:00 | 401 | 13:00
Meghnaghat | 410 | 05:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 05:00 | 225 | 11:00 | Keranigonj | 237 | 04:00 | 224 | 12:00
AKSML | 233 | 05:00 | 229 | 00:00 | Khulna(S) | 242 | 04:00 | 222 | 12:00
Aminbazar | 238 | 05:00 | 225 | 12:00 | Madunaghat | 235 | 19:00 | 230 | 00:00
Ashuganj | 242 | 03:00 | 230 | 11:00 | Madunaghat-400 | 234 | 05:00 | 230 | 01:00
Ashuganj-400 | 242 | 03:00 | 230 | 11:00 | Maniknagar | 237 | 04:00 | 226 | 12:00
Baghabari | 242 | 04:00 | 228 | 12:00 | Meghnaghat | 244 | 06:00 | 234 | 12:00
Barapukuria | 227 | 05:00 | 216 | 08:00 | Meghnaghat-400 | 240 | 04:00 | 229 | 12:00
Barapukuria-230 | 227 | 05:00 | 216 | 08:00 | Mirsorai | 235 | 05:00 | 227 | 00:00
Barishal | 245 | 03:00 | 236 | 11:00 | Rajshahi | 241 | 04:00 | 222 | 11:00
Bheramara | 240 | 04:00 | 222 | 12:00 | Rampal | 240 | 04:00 | 218 | 12:00
Bhulta | 240 | 05:00 | 226 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 235 | 04:00 | 224 | 12:00 | Rampura | 240 | 05:00 | 226 | 12:00
BIPTC | 242 | 04:00 | 223 | 11:00 | Shikalbaha | 236 | 19:00 | 227 | 00:00
Bogura | 241 | 03:00 | 228 | 08:00 | Shyampur | 239 | 05:00 | 225 | 12:00
Bogura-400 | 241 | 04:00 | 226 | 08:00 | Siddhirganj | 235 | 02:00 | 225 | 11:00
Borhanuddin | 247 | 06:00 | 242 | 13:00 | Sirajgonj | 246 | 04:00 | 237 | 12:00
BSRM | 235 | 05:00 | 227 | 00:00 | Sreepur | 242 | 05:00 | 229 | 12:00
Cumilla(N) | 236 | 06:00 | 228 | 12:00 | Tongi | 237 | 04:00 | 223 | 11:00
Faridpur | 246 | 04:00 | 232 | 11:00
Fenchuganj | 238 | 03:00 | 227 | 12:00
Ghorashal | 238 | 09:00 | 224 | 21:00
Ghorashal-230 | 240 | 05:00 | 223 | 13:00
Gopalganj | 246 | 05:00 | 233 | 11:00
GPH | 235 | 05:00 | 227 | 00:00
Haripur | 240 | 05:00 | 227 | 12:00
Hasnabad | 236 | 03:00 | 225 | 11:00
Hathazari | 236 | 09:00 | 229 | 00:00
Ishurdi | 243 | 04:00 | 225 | 12:00
Jhenaidah | 240 | 05:00 | 221 | 08:00
Kaliakoir | 237 | 04:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 127 | 12:00 | Magura | 140 | 04:00 | 126 | 11:00
Agargaon | 139 | 05:00 | 129 | 12:00 | Mahasthangarh | 136 | 05:00 | 125 | 08:00
Agrabad | 135 | 19:00 | 130 | 00:00 | Manikganj | 140 | 07:00 | 132 | 11:00
AKS | 133 | 19:00 | 130 | 00:00 | Maniknagar | 136 | 04:00 | 127 | 12:00
Aminbazar | 137 | 05:00 | 129 | 11:00 | Matarbari | 125 | 04:00 | 120 | 13:00
Amnura | 141 | 19:00 | 128 | 11:00 | Matuail | 136.5 | 04:00 | 129 | 12:00
Ashuganj | 143 | 05:00 | 137 | 11:00 | Millgate | 140 | 03:00 | 129 | 12:00
Bagerhat | 136 | 05:00 | 125 | 12:00 | Mirpur | 136 | 03:00 | 128 | 11:00
Bajitpur | 134 | 15:00 | 130 | 10:00 | Mirzapur | 140 | 06:00 | 129 | 11:00
Bakulia | 138 | 07:00 | 130 | 00:00 | Mithapukur | 134 | 04:00 | 120 | 08:00
Banani | 137 | 03:00 | 127 | 12:00 | MI_Cement | 138 | 05:00 | 131.3 | 12:00
Bangabhaban | 136 | 03:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 135 | 02:00 | 127 | 08:00 | Mogbazar | 138 | 04:00 | 128 | 13:00
Barguna | 140 | 09:00 | 134 | 00:00 | Mongla | 137 | 06:00 | 124 | 12:00
Barishal | 135 | 03:00 | 129 | 12:00 | Motijheel | 136 | 03:00 | 127 | 12:00
Barishal-230 | 137 | 03:00 | 130 | 11:00 | Muktagacha | 132 | 04:00 | 116 | 11:00
Baroaulia | 135 | 09:00 | 131 | 15:00 | Munshiganj | 136 | 04:00 | 131 | 11:00
Baroirhat | 134 | 18:30 | 129 | 00:00 | Mymensingh | 131 | 05:00 | 115 | 11:00
Bashundhara | 140 | 04:00 | 127 | 12:00 | Naogaon | 136 | 02:00 | 124 | 08:00
BashundharaCement | 136 | 05:00 | 130 | 12:00 | Narail | 140 | 04:00 | 124 | 12:00
Beanibazar | 138 | 04:00 | 130 | 12:00 | Narinda | 136 | 04:00 | 127 | 12:00
Benapole | 138 | 03:00 | 121 | 12:00 | Narshingdi | 132 | 01:00 | 125 | 12:00
Bhaluka | 130 | 03:00 | 120 | 12:00 | Natore | 138 | 04:00 | 128 | 08:00
Bhandaria | 132 | 05:00 | 126 | 13:00 | Nawabganj | 140 | 05:00 | 130 | 12:00
Bhangura | 138 | 04:00 | 129 | 11:00 | Netrakona | 125 | 23:00 | 114 | 12:00
Bheramara | 139 | 05:00 | 128 | 11:00 | New | 140 | 02:00 | 130 | 11:00
Bheramara(GK) | 139 | 04:00 | 128 | 11:00 | Niamatpur | 141 | 03:00 | 132 | 09:00
Bhulta | 131 | 06:00 | 124 | 12:00 | Noapara | 139 | 04:00 | 125 | 12:00
Bog-Sherpur | 138 | 05:00 | 127 | 12:00 | Pabna | 137 | 04:00 | 125 | 12:00
Bogura | 138 | 06:00 | 129 | 10:00 | Palashbari | 131 | 01:00 | 120 | 08:00
Bogura-230 | 138 | 03:00 | 128 | 08:00 | Panchagarh | 141 | 19:30 | 121 | 08:00
Brahmanbaria | 138 | 06:00 | 129 | 12:00 | Patuakhali | 140 | 09:00 | 133 | 00:00
Cantonment | 138 | 04:00 | 129 | 12:00 | Payra | 138 | 19:00 | 134 | 00:00
Chandpur | 140 | 18:30 | 127 | 00:00 | PHP | 134 | 18:00 | 128 | 00:00
Chandraghona | 136 | 19:00 | 132 | 00:00 | Postogola | 140 | 05:00 | 133 | 11:00
Chapai | 140 | 05:00 | 130 | 10:00 | Purbachal | 138 | 04:00 | 127 | 12:00
Charsaidpur | 137 | 05:00 | 131 | 12:00 | Purbasadipur | 132 | 03:00 | 122 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 19:00 | 130 | 00:00 | Rahanpur | 140 | 00:00 | 133 | 08:00
Chhatak | 138 | 06:00 | 129 | 12:00 | Rahanpur-400 | 142 | 03:00 | 133 | 08:00
Chowmuhani | 135 | 19:00 | 125 | 00:00 | Rahim | 135 | 05:00 | 129 | 11:00
Chuadanga | 139 | 05:00 | 122 | 12:00 | Rajbari | 136 | 04:00 | 127 | 12:00
Coxsbazar | 127 | 04:00 | 120 | 12:00 | Rajendrapur | 137 | 04:00 | 126 | 13:00
Cumilla(N) | 138 | 05:00 | 133 | 12:00 | Rajshahi | 138 | 06:00 | 129 | 11:00
Cumilla(S) | 138 | 19:00 | 128 | 09:00 | Rajshahi-230 | 140 | 04:00 | 126 | 13:00
Daudkandi | 134 | 05:00 | 128 | 12:00 | Ramganj | 136 | 09:00 | 126 | 00:00
Dhaka | 136 | 05:00 | 128 | 12:00 | Rampur | 134 | 04:00 | 130 | 12:00
Dhamrai | 135 | 04:00 | 127 | 19:30 | Rampura | 137 | 04:00 | 128 | 12:00
Dhanmondi | 137 | 06:00 | 130 | 12:00 | Rangamati | 134 | 04:00 | 132 | 00:00
Dohazari | 131 | 05:00 | 124 | 01:00 | Rangpur | 132 | 06:00 | 121 | 09:00
Faridpur | 136 | 04:00 | 130 | 10:00 | Ruppur | 140 | 06:00 | 131 | 10:00
Fatullah | 139 | 05:00 | 132 | 12:00 | Saidpur | 134 | 02:00 | 119 | 08:00
Fenchuganj | 142 | 04:00 | 135 | 13:00 | Satkhira | 137 | 05:00 | 126 | 11:00
Feni | 134 | 18:00 | 127 | 00:00 | Satmasjid | 138 | 04:00 | 129 | 12:00
Ghatail | 132 | 03:00 | 119 | 11:00 | Savar | 137 | 20:00 | 129 | 11:00
Ghorashal | 140 | 00:00 | 135 | 12:00 | SevenRings | 143 | 04:00 | 134 | 12:00
Goalpara | 139 | 04:00 | 127 | 12:00 | ShahCement | 137 | 05:00 | 131 | 11:00
Gollamari | 139 | 02:00 | 129 | 11:00 | Shahjadpur | 140 | 00:00 | 133 | 11:00
Gopalganj | 138 | 04:00 | 129 | 11:00 | Shahjibazar | 140 | 05:00 | 132 | 12:00
Gopalganj-400 | 138 | 04:00 | 130 | 12:00 | Shahmirpur | 136 | 18:30 | 130 | 00:00
Gulshan | 136 | 05:00 | 127 | 12:00 | Shariatpur | 136 | 04:00 | 128 | 11:00
Halishahar | 136 | 19:00 | 132 | 16:00 | Sherpur | 126 | 06:00 | 110 | 11:00
Haripur | 136 | 04:00 | 129 | 12:00 | Shikalbaha | 125 | 19:00 | 119 | 00:00
HaripurSBU | 136 | 03:00 | 129 | 12:00 | Shikalbaha-230 | 137 | 19:00 | 131 | 00:00
Hasnabad | 138 | 19:00 | 133 | 11:00 | Shitalakhya | 138 | 05:00 | 131.3 | 12:00
Hathazari | 136 | 08:00 | 133 | 12:00 | Sholosohor | 135 | 19:00 | 131 | 00:00
Ishurdi | 141 | 04:00 | 130 | 12:00 | Shyampur | 136 | 01:00 | 131 | 12:00
Jaldhaka | 131 | 03:00 | 118 | 08:00 | Shyampur-230 | 139 | 05:00 | 132 | 11:00
Jamalpur | 128 | 06:00 | 112 | 13:00 | Siddhirganj | 137 | 04:00 | 130 | 12:00
Jashore | 136 | 06:00 | 123 | 12:00 | Sirajganj | 138 | 03:00 | 127 | 08:00
Jhenaidah | 140 | 04:00 | 127 | 12:00 | Sonargaon | 135 | 03:00 | 127 | 12:00
Jhenaidah-230 | 141 | 04:00 | 127 | 12:00 | Sreemongol | 140 | 03:00 | 132 | 12:00
Joydebpur | 140 | 19:00 | 133 | 12:00 | Sreepur | 132 | 05:00 | 124 | 10:00
Joypurhat | 135 | 03:00 | 122 | 11:00 | Srinagar | 139 | 06:00 | 131 | 12:00
Juldah | 135 | 09:00 | 130 | 00:00 | SSM | 139 | 09:00 | 136 | 01:00
Kabirpur | 141 | 06:00 | 125 | 12:00 | Sunamganj | 138 | 05:00 | 127 | 12:00
Kachua | 139 | 19:00 | 128 | 00:00 | Sylhet | 140 | 04:00 | 130 | 13:00
Kaliakoir | 148 | 07:00 | 129 | 11:00 | Sylhet-132 | 139 | 03:00 | 130 | 11:00
Kallyanpur | 136 | 04:00 | 127 | 11:00 | Tangail | 134 | 05:00 | 123 | 08:00
Kalurghat | 135 | 04:00 | 131 | 00:00 | Thakurgaon | 140 | 19:30 | 118 | 08:00
Kamrangirchar | 139 | 03:00 | 126 | 11:00 | TK | 135 | 09:00 | 132 | 03:00
Kaptai | 137 | 1:00 | 125 | 12:00 | Tongi | 141 | 04:00 | 131 | 11:00
Kazla | 136 | 04:00 | 127 | 12:00 | Ullahpara | 139 | 02:00 | 129 | 12:00
Keranigonj | 138 | 04:00 | 130 | 11:00 | Ullon | 136 | 03:00 | 127 | 12:00
Khagrachori | 134 | 04:00 | 131 | 11:00 | Uttara | 136 | 04:00 | 128 | 11:00
Khulna | 139 | 03:00 | 127 | 12:00 | UttaraNew | 139 | 03:00 | 129 | 12:00
Khulna(S) | 141 | 04:00 | 128 | 12:00 | Zigatola | 140 | 04:00 | 130 | 13:00
Khulshi | 133 | 03:00 | 130 | 00:00
Kishoreganj | 132 | 01:00 | 126 | 12:00
Kodda | 140 | 06:00 | 127 | 12:00
KSRM | 136 | 19:00 | 132 | 00:00
Kulaura | 142 | 05:00 | 135 | 11:00
Kurigram | 131 | 01:00 | 113 | 08:00
Kushtia | 139 | 03:00 | 127 | 12:00
Lalbag | 140 | 05:00 | 131 | 11:00
Lalmonirhat | 131 | 01:00 | 120 | 08:00
Madanganj | 136 | 05:00 | 130 | 12:00
Madaripur | 137 | 05:00 | 130 | 12:00
Madartek | 137 | 04:00 | 128 | 12:00
Madunaghat | 135 | 05:00 | 132 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division