## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-02-2025 | during | 05-02-2025 | during | 05-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 72 | 73 | 97.3 | 97.3 | 77 | 77 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 405 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 261 | 256 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 133 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 18 | 13 | 22.5 | 22.5 | 22.5 | 22.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 21 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 28 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 26 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 122 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 36 | 17 | 17 | 35 | 35 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.654 | 1894 | 2208 | 4581.87 | 4551.87 | 2889.78 | 2859.78
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 37 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 188 | 227 | 185 | 185 | 185 | 185 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 85 | 68 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 84 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 22 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 51 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.82 | 0 | 3.82 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 49 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 75 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 126 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 15 | 15 | 4 | 2 | 4 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 154 | 157 | 150 | 150 | 150 | 150 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1841 | 2312 | 2940.54 | 2934.72 | 2940.54 | 2934.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 90 | 58 | 356.56 | 356.56 | 150 | 150 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 29 | 31 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 19 | 14 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 40 | 51 | 40 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 70 | 93 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 32 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 105 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 76 | 55 | 55 | 55 | 55 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 978 | 1070 | 2021.53 | 1977.53 | 1680.03 | 1636.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-02-2025 | during | 05-02-2025 | during | 05-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 210 | 210 | 70 | 70 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.42 | 0 | 43.26 | 0 | 43.26 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 160.42 | 138.5 | 646.46 | 601.5 | 506.46 | 461.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 29 | 40 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 30 | 36 | 44 | 44 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 0 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 50 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 359 | 370 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 102 | 255 | 40 | 70 | 130 | 130 | Preparation for ST startup
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1086 | 1276 | 1144 | 1176 | 1200 | 1200
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 921 | 638 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 75.2 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 996.2 | 638 | 3170 | 3095 | 1726 | 1651
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 136 | 136 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1110 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 150 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1821.57 | 1681 | 2068.12 | 2067.12 | 2032.12 | 2031.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 42 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 6 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 38 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 179 | 165 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 150 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 369 | 394 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 51 | 97 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.82 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 760.83 | 752 | 748 | 748 | 748 | 748 | Under Maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.95 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 97 | 0 | 97 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1638.1 | 1719.5 | 2510.79 | 2359.24 | 2174.81 | 2023.26
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 67 | 67 | 68 | 68 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 158 | 160 | 160 | 160 | 160 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 4.1 | 0 | 4.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 74 | 75 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 144 | 0 | 161.04 | 0 | 161.04 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 458 | 400 | 675.14 | 490 | 677.14 | 492
System Total |  |  |  |  | 27884.66 | 27066.632 | 10873.29 | 11443 | 19758.45 | 19252.98 | 15826.88 | 15289.41
Forecast Scenario (05-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9050 |  | 0 |  | 9050
|  |  |  | 1:00 | 8460 |  | 0 |  | 8460
|  |  |  | 2:00 | 8080 |  | 0 |  | 8080
|  |  |  | 3:00 | 7720 |  | 0 |  | 7720
|  |  |  | 4:00 | 7600 |  | 0 |  | 7600
|  |  |  | 5:00 | 7440 |  | 0 |  | 7440
|  |  |  | 6:00 | 7850 |  | 0 |  | 7850
|  |  |  | 7:00 | 8750 |  | 0 |  | 8750
|  |  |  | 8:00 | 9780 |  | 0 |  | 9780
|  |  |  | 9:00 | 10290 |  | 0 |  | 10290
|  |  |  | 10:00 | 10060 |  | 0 |  | 10060
|  |  |  | 11:00 | 10090 |  | 0 |  | 10090
|  |  |  | 12:00 | 10590 |  | 0 |  | 10590
|  |  |  | 13:00 | 10790 |  | 0 |  | 10790
|  |  |  | 14:00 | 10270 |  | 0 |  | 10270
|  |  |  | 15:00 | 9920 |  | 0 |  | 9920
|  |  |  | 16:00 | 9460 |  | 0 |  | 9460
|  |  |  | 17:00 | 9440 |  | 0 |  | 9440
|  |  |  | 18:00 | 10740 |  | 0 |  | 10740
|  |  |  | 18:30 | 10850 |  | 0 |  | 10850
|  |  |  | 19:00 | 10960 |  | 0 |  | 10960
|  |  |  | 19:30 | 10910 |  | 0 |  | 10910
|  |  |  | 20:00 | 10820 |  | 0 |  | 10820
|  |  |  | 21:00 | 10600 |  | 0 |  | 10600
|  |  |  | 22:00 | 10040 |  | 0 |  | 10040
|  |  |  | 23:00 | 9525 |  | 0 |  | 9525
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 10590.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10960.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10960.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 228.325 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:06 hrs on 05-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-02-2025 | [28 empty] | Date: | 04-02-2025 | [28 empty] | Date: | 04-02-2025 | [28 empty] | Date: | 04-02-2025 | [28 empty] | Date: | 04-02-2025 | [19 empty] | Date: | 04-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [19 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 279 | 0 | 0 | 0 | 31 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 154 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1010 | 0 | 51 | 0 | 197 | 0 | 0 | 264 | 29 | 183 | 30 | 0 | 45 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 290 | 102 | 376 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 23 | 0 | 0 | 6 | 5156 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 192 | 0 | 394 | 0 | 0 | 2.5 | 163 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 7 | 132 | 220 | 0 | 0 | 1040 | 0 | 4203.5 | 9359.5 | 91.52
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 290 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 156 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 197 | 0 | 0 | 265 | 29 | 183 | 30 | 0 | 45 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 300 | 102 | 375 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 12 | 0 | 0 | 6 | 4990 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 151 | 0 | 393 | 0 | 0 | 2.5 | 164 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 132 | 110 | 0 | 0 | 860 | 0 | 3756.5 | 8746.5 | 91.52
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 293 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 157 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 842 | 0 | 43 | 0 | 148 | 0 | 0 | 265 | 29 | 185 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 290 | 102 | 375 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 4779 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 147 | 0 | 313 | 0 | 0 | 2.5 | 154 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 7 | 132 | 110 | 0 | 0 | 800 | 0 | 3480.5 | 8259.5 | 91.52
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 309 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 156 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 808 | 0 | 43 | 0 | 108 | 0 | 0 | 195 | 29 | 202 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 295 | 102 | 375 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4668 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 136 | 0 | 340 | 0 | 0 | 2.5 | 163 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 132 | 110 | 0 | 0 | 800 | 0 | 3280.5 | 7948.5 | 91.51
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 300 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 156 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 800 | 0 | 43 | 0 | 108 | 0 | 0 | 100 | 29 | 194 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 310 | 102 | 375 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 4529.5 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 147 | 0 | 318 | 0 | 0 | 2.5 | 158 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 110 | 0 | 0 | 800 | 0 | 3265.5 | 7795 | 91.51
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 273 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 155 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 800 | 0 | 43 | 0 | 108 | 0 | 0 | 40 | 29 | 183 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 300 | 102 | 375 | 36 | 42 | 0 | 5 | 120 | 17 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 4431.5 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 171 | 0 | 308 | 0 | 0 | 2.5 | 160 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 110 | 0 | 0 | 800 | 0 | 3282.5 | 7714 | 91.51
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 300 | 0 | 0 | 0 | 32 | 280 | 0 | 0 | 0 | 0 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 156 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 192 | 0 | 0 | 36 | 29 | 193 | 30 | 0 | 50 | 0 | 0 | 11 | 0 | 50 | 0 | 0 | 0 | 305 | 102 | 375 | 36 | 42 | 0 | 5 | 163 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 4677.5 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 182 | 0 | 393 | 0 | 0 | 2.5 | 156 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 110 | 0 | 0 | 840 | 0 | 3419.5 | 8097 | 91.51
07:00 | 0 | 10 | 8 | 0 | 0 | 0 | 0 | 68 | 401 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 300 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 1 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 159 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 1077 | 1 | 51 | 0 | 195 | 0 | 0 | 33 | 29 | 201 | 27 | 0 | 50 | 0 | 0 | 11 | 0 | 50 | 0 | 3 | 0 | 305 | 102 | 375 | 36 | 42 | 0 | 5 | 163 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 32 | 42 | 0 | 0.85 | 2 | 5058.85 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.05 | 0 | 0 | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.85 | 205 | 0 | 0 | 0 | 183 | 0 | 414 | 0 | 0.08 | 2.5 | 156 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.02 | 0 | 220 | 6 | 136 | 110 | 0 | 0 | 930 | 0 | 3959.5 | 9018.35 | 91.5
08:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 68 | 401 | 0 | 0 | 13 | 0 | 0 | 65 | 32 | 0 | 0 | 3 | 108 | 17 | 0 | 400 | 283 | 0 | 0 | 35 | 31 | 335 | 0 | 0 | 7 | 0 | 20 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 10 | 158 | 0 | 0 | 13 | 0 | 10 | 186 | 0 | 0 | 0 | 1224 | 7 | 51 | 16 | 195 | 0 | 0 | 35 | 30 | 184 | 27 | 29 | 50 | 34 | 13 | 11 | 0 | 52 | 0 | 20 | 0 | 310 | 102 | 375 | 36 | 42 | 0 | 5 | 163 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 7 | 9 | 56 | 28 | 0 | 8.1 | 6 | 5618.1 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 760.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8.47 | 205 | 0 | 0 | 0 | 181 | 0 | 381 | 0 | 0.73 | 2.5 | 156 | 67 | 35 | 4 | 0 | 0 | 0 | 0.9 | 28 | 0.12 | 0 | 307 | 5 | 136 | 110 | 0 | 0 | 1080 | 90 | 4232.13 | 9850.23 | 91.5
09:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 68 | 401 | 0 | 0 | 54 | 0 | 0 | 90 | 32 | 0 | 0 | 20 | 162 | 17 | 0 | 400 | 269 | 0 | 0 | 35 | 29 | 335 | 0 | 0 | 15 | 0 | 20 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 10 | 4 | 2 | 40 | 1 | 2 | 157 | 0 | 0 | 32 | 0 | 69 | 187 | 0 | 0 | 0 | 1224 | 13 | 51 | 58 | 197 | 0 | 0 | 70 | 29 | 182 | 30 | 68 | 0 | 100 | 27 | 11 | 0 | 50 | 0 | 37 | 0 | 305 | 102 | 375 | 36 | 42 | 0 | 5 | 163 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 23 | 9 | 56 | 26 | 0 | 18.87 | 6 | 6034.87 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.33 | 0 | 0 | 758.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 20.51 | 210 | 0 | 0 | 0 | 183 | 0 | 326 | 0 | 1.76 | 2.5 | 125 | 69 | 70 | 11 | 0 | 0 | 0 | 2.2 | 69 | 0.26 | 0 | 307 | 4 | 136 | 110 | 0 | 0 | 1120 | 116 | 4362.87 | 10397.74 | 91.5
10:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 68 | 401 | 0 | 0 | 35 | 0 | 0 | 119 | 16 | 0 | 4 | 54 | 108 | 17 | 0 | 350 | 251 | 0 | 0 | 35 | 29 | 280 | 0 | 0 | 21 | 0 | 8 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 12 | 3 | 40 | 17 | 2 | 157 | 0 | 0 | 32 | 0 | 85 | 187 | 0 | 0 | 0 | 1100 | 17 | 43 | 70 | 197 | 0 | 0 | 95 | 26 | 183 | 30 | 64 | 0 | 100 | 28 | 11 | 0 | 54 | 0 | 53 | 0 | 285 | 102 | 310 | 36 | 30 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 10 | 1 | 29.2 | 6 | 5717.2 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5 | 0 | 0 | 668.75 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 63 | 0 | 33.53 | 153 | 0 | 0 | 0 | 165 | 0 | 325 | 0 | 2.96 | 2.5 | 120 | 68 | 72 | 19 | 0 | 0 | 0 | 3.6 | 108 | 0.41 | 0 | 250 | 5 | 100 | 110 | 0 | 0 | 1050 | 116 | 4405.25 | 10122.45 | 91.49
11:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 71 | 363 | 0 | 0 | 35 | 0 | 0 | 122 | 16 | 0 | 15 | 55 | 108 | 25 | 0 | 300 | 255 | 0 | 0 | 35 | 25 | 250 | 0 | 0 | 25 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 4 | 40 | 17 | 2 | 158 | 0 | 0 | 32 | 0 | 85 | 203 | 0 | 0 | 0 | 1100 | 20 | 43 | 70 | 187 | 0 | 0 | 99 | 23 | 182 | 30 | 70 | 0 | 100 | 28 | 11 | 0 | 58 | 0 | 62 | 0 | 275 | 102 | 310 | 30 | 30 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 10 | 1 | 37.11 | 6 | 5674.11 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.27 | 0 | 0 | 663.64 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 79 | 0 | 38.88 | 150 | 0 | 0 | 0 | 142 | 0 | 313 | 0 | 3.39 | 2.5 | 160 | 67 | 74 | 25 | 0 | 0 | 0 | 4.6 | 131 | 0.51 | 0 | 250 | 4 | 100 | 110 | 0 | 0 | 1060 | 116 | 4512.79 | 10186.9 | 91.49
12:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 72 | 405 | 0 | 0 | 35 | 0 | 0 | 122 | 16 | 0 | 15 | 55 | 108 | 25 | 0 | 300 | 261 | 0 | 0 | 35 | 24 | 280 | 0 | 0 | 26 | 0 | 18 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 4 | 40 | 17 | 3 | 154 | 0 | 0 | 32 | 0 | 85 | 188 | 0 | 0 | 0 | 1224 | 20 | 51 | 70 | 197 | 0 | 0 | 90 | 19 | 182 | 29 | 72 | 0 | 100 | 29 | 11 | 0 | 62 | 0 | 66 | 0 | 290 | 102 | 359 | 30 | 30 | 0 | 5 | 120 | 17 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 9 | 59 | 10 | 2 | 39.42 | 6 | 5959.42 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2 | 0 | 0 | 760.83 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 85 | 0 | 43.95 | 179 | 0 | 0 | 0 | 143 | 0 | 369 | 0 | 3.82 | 2.5 | 156 | 67 | 74 | 12 | 0 | 0 | 0 | 5 | 144 | 0.57 | 0 | 307 | 4 | 130 | 110 | 0 | 0 | 1120 | 150 | 4913.87 | 10873.29 | 91.49
13:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 74 | 402 | 0 | 0 | 35 | 0 | 0 | 106 | 16 | 0 | 0 | 55 | 108 | 25 | 0 | 420 | 284 | 0 | 0 | 17 | 30 | 328 | 0 | 0 | 24 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 12 | 6 | 157 | 0 | 0 | 32 | 0 | 17 | 188 | 0 | 0 | 0 | 1224 | 19 | 51 | 70 | 195 | 0 | 0 | 80 | 14 | 182 | 29 | 78 | 0 | 68 | 28 | 11 | 0 | 66 | 0 | 61 | 0 | 280 | 102 | 370 | 33 | 30 | 0 | 5 | 163 | 17 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 19 | 58 | 8 | 2 | 39.61 | 6 | 6022.61 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 759.88 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 88 | 26 | 44.51 | 168 | 0 | 0 | 0 | 178 | 0 | 381 | 0 | 3.61 | 2.5 | 160 | 67 | 35 | 26 | 0 | 0 | 0 | 5.1 | 140 | 0 | 0 | 307 | 4 | 134 | 110 | 0 | 0 | 1130 | 150 | 4970.6 | 10993.21 | 91.49
14:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 74 | 405 | 0 | 0 | 35 | 0 | 0 | 88 | 16 | 0 | 0 | 55 | 72 | 25 | 0 | 400 | 295 | 0 | 0 | 17 | 30 | 328 | 0 | 0 | 20 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 3 | 157 | 0 | 0 | 32 | 0 | 17 | 188 | 0 | 0 | 0 | 1168 | 17 | 48 | 10 | 195 | 0 | 0 | 80 | 29 | 182 | 26 | 75 | 0 | 17 | 29 | 11 | 0 | 68 | 0 | 50 | 0 | 300 | 102 | 371 | 33 | 30 | 0 | 5 | 120 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 9 | 58 | 8 | 1 | 36.76 | 6 | 5733.76 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 74 | 30 | 37.89 | 158 | 0 | 0 | 0 | 156 | 0 | 319 | 0 | 3.36 | 2.5 | 157 | 67 | 35 | 22 | 0 | 0 | 0 | 4.6 | 118 | 0.45 | 0 | 250 | 5 | 134 | 110 | 0 | 0 | 1130 | 150 | 4761.9 | 10495.66 | 91.49
15:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 35 | 0 | 0 | 70 | 16 | 0 | 0 | 17 | 72 | 25 | 0 | 400 | 306 | 0 | 0 | 17 | 30 | 326 | 0 | 0 | 15 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 157 | 0 | 0 | 32 | 0 | 17 | 188 | 0 | 0 | 0 | 1150 | 13 | 51 | 7 | 195 | 0 | 0 | 58 | 29 | 184 | 27 | 73 | 0 | 17 | 29 | 13 | 0 | 64 | 0 | 43 | 0 | 305 | 180 | 371 | 32 | 30 | 0 | 5 | 120 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 8 | 1 | 26.55 | 6 | 5672.55 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 61 | 30 | 26.49 | 160 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 2.39 | 2.5 | 157 | 65 | 0 | 16 | 0 | 0 | 0 | 3.6 | 84 | 0.35 | 0 | 250 | 5 | 134 | 110 | 0 | 0 | 1120 | 72 | 4553.33 | 10225.88 | 91.48
16:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 17 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 35 | 25 | 0 | 400 | 306 | 0 | 0 | 0 | 29 | 325 | 0 | 0 | 8 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 157 | 0 | 0 | 17 | 0 | 0 | 188 | 0 | 0 | 0 | 1150 | 7 | 51 | 0 | 195 | 0 | 0 | 58 | 29 | 193 | 30 | 34 | 0 | 0 | 28 | 17 | 0 | 56 | 0 | 25 | 0 | 315 | 253 | 371 | 33 | 29 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 57 | 8 | 0 | 12.14 | 6 | 5561.14 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.49 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 30 | 30 | 13.97 | 161 | 0 | 0 | 0 | 157 | 0 | 407 | 0 | 1.34 | 2.5 | 157 | 63 | 0 | 9 | 0 | 0 | 0 | 1.6 | 44 | 0.21 | 0 | 250 | 4 | 132 | 110 | 0 | 0 | 1120 | 35 | 4484.11 | 10045.25 | 91.48
17:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 35 | 25 | 0 | 400 | 297 | 0 | 0 | 17 | 29 | 325 | 0 | 0 | 2 | 0 | 17 | 22 | 0 | 0 | 35 | 30 | 0 | 0 | 7 | 0 | 0 | 0 | 5 | 5 | 0 | 40 | 0 | 5 | 157 | 0 | 0 | 12 | 0 | 1 | 205 | 0 | 0 | 0 | 1185 | 2 | 51 | 0 | 195 | 0 | 0 | 60 | 29 | 183 | 30 | 34 | 0 | 1 | 29 | 5 | 0 | 60 | 0.5 | 6 | 0 | 300 | 253 | 371 | 33 | 29 | 0 | 5 | 120 | 25 | 0 | 85 | 30 | 0 | 18 | 0 | 1 | 9 | 58 | 11 | 0 | 2.88 | 6 | 5562.38 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2 | 0 | 0 | 755 | 0 | 0 | 25 | 0 | 0 | 5 | 50 | 0 | 0 | 0 | 8 | 30 | 3.51 | 156 | 0 | 0 | 0 | 156 | 0 | 326 | 0 | 0.34 | 2.5 | 160 | 66 | 0 | 2 | 2 | 0 | 0 | 0.4 | 13 | 0.6 | 0 | 307 | 4 | 136 | 110 | 0 | 0 | 1120 | 39 | 4408.55 | 9970.93 | 91.48
18:00 | 0 | 80 | 34 | 0 | 0 | 0 | 0 | 71 | 300 | 0 | 0 | 44 | 20 | 0 | 0 | 133 | 0 | 30 | 28 | 144 | 25 | 0 | 320 | 316 | 0 | 0 | 35 | 28 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 32 | 21 | 0 | 10 | 78 | 0 | 0 | 48 | 60 | 0 | 40 | 14 | 10 | 158 | 53 | 0 | 26 | 0 | 25 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 195 | 0 | 0 | 58 | 18 | 206 | 30 | 56 | 0 | 48 | 69 | 5 | 0 | 52 | 52 | 0 | 35 | 300 | 253 | 330 | 36 | 29 | 0 | 5 | 120 | 25 | 0 | 85 | 30 | 0 | 18 | 0 | 25 | 9 | 58 | 11 | 0 | 0 | 6 | 6203 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 26 | 0 | 0 | 5 | 96 | 0 | 20 | 8 | 0 | 30 | 0 | 147 | 0 | 0 | 0 | 145 | 0 | 345 | 0 | 0 | 2.5 | 158 | 66 | 41 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 130 | 110 | 0 | 0 | 1110 | 17 | 4480.5 | 10683.5 | 91.48
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 73 | 401 | 0 | 0 | 54 | 36 | 0 | 0 | 133 | 0 | 55 | 55 | 162 | 25 | 0 | 400 | 256 | 0 | 0 | 35 | 28 | 330 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 35 | 32 | 51 | 0 | 15 | 84 | 0 | 0 | 70 | 75 | 0 | 40 | 49 | 22 | 157 | 126 | 0 | 37 | 0 | 68 | 227 | 0 | 0 | 0 | 1224 | 0 | 51 | 93 | 197 | 0 | 0 | 58 | 14 | 183 | 31 | 115 | 0 | 105 | 76 | 17 | 0 | 46 | 52 | 0 | 32 | 300 | 255 | 370 | 36 | 29 | 0 | 0 | 163 | 25 | 0 | 50 | 30 | 0 | 18 | 0 | 54.5 | 9 | 58 | 11 | 0 | 0 | 6 | 7004.5 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 42 | 0 | 0 | 6 | 97 | 0 | 38 | 43 | 0 | 30 | 0 | 165 | 0 | 0 | 0 | 150 | 0 | 394 | 0 | 0 | 2.5 | 158 | 67 | 75 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 110 | 0 | 0 | 1110 | 17 | 4438.5 | 11443 | 91.47
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 73 | 405 | 0 | 0 | 54 | 36 | 0 | 0 | 133 | 0 | 55 | 55 | 162 | 25 | 0 | 400 | 305 | 0 | 0 | 35 | 28 | 330 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 32 | 0 | 0 | 14 | 84 | 0 | 0 | 12 | 24 | 0 | 40 | 51 | 29 | 157 | 17 | 0 | 32 | 0 | 68 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 197 | 0 | 0 | 77 | 14 | 196 | 31 | 115 | 0 | 136 | 76 | 17 | 0 | 46 | 52 | 0 | 32 | 305 | 260 | 375 | 36 | 29 | 0 | 0 | 120 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 9 | 58 | 11 | 0 | 0 | 6 | 6845 | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 42 | 0 | 0 | 0 | 98 | 0 | 37 | 43 | 0 | 30 | 0 | 139 | 0 | 0 | 0 | 145 | 0 | 327 | 0 | 0 | 2.5 | 153 | 67 | 75 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 110 | 0 | 0 | 1120 | 17 | 4313.5 | 11158.5
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 73 | 401 | 0 | 0 | 54 | 36 | 0 | 2 | 133 | 0 | 15 | 55 | 162 | 25 | 0 | 400 | 303 | 0 | 0 | 35 | 28 | 331 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 50 | 0 | 0 | 9 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 51 | 30 | 157 | 0 | 0 | 32 | 0 | 85 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 197 | 0 | 0 | 99 | 22 | 186 | 31 | 115 | 0 | 136 | 79 | 17 | 0 | 42 | 52 | 0 | 0 | 290 | 260 | 375 | 36 | 30 | 0 | 2 | 120 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 9 | 58 | 17 | 0 | 0 | 6 | 6691 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 8 | 43 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 145 | 0 | 318 | 0 | 0 | 2.5 | 157 | 67 | 75 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 110 | 0 | 0 | 1120 | 17 | 4226.5 | 10917.5 | 91.47
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 73 | 401 | 0 | 0 | 17 | 17 | 0 | 81 | 64 | 0 | 0 | 0 | 90 | 25 | 0 | 420 | 316 | 0 | 0 | 17 | 31 | 328 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 50 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 157 | 0 | 0 | 32 | 0 | 34 | 227 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 197 | 0 | 0 | 125 | 21 | 202 | 31 | 115 | 0 | 51 | 27 | 17 | 0 | 50 | 52 | 0 | 0 | 295 | 260 | 375 | 36 | 30 | 0 | 2 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 18 | 0 | 0 | 6 | 6246 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.31 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 2.5 | 160 | 67 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 110 | 0 | 0 | 1120 | 17 | 4460.81 | 10706.81 | 91.47
22:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 73 | 400 | 0 | 0 | 17 | 17 | 0 | 138 | 32 | 0 | 0 | 0 | 90 | 25 | 0 | 420 | 273 | 0 | 0 | 17 | 31 | 330 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 156 | 0 | 0 | 32 | 0 | 34 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 197 | 0 | 0 | 18 | 22 | 183 | 31 | 115 | 0 | 51 | 27 | 17 | 0 | 52 | 0 | 0 | 0 | 290 | 260 | 375 | 36 | 30 | 0 | 2 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 16 | 0 | 0 | 6 | 5974 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752.32 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 195 | 0 | 393 | 0 | 0 | 2.5 | 161 | 67 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 134 | 110 | 0 | 0 | 1130 | 17 | 4467.82 | 10441.82 | 91.47
23:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 73 | 400 | 0 | 0 | 0 | 0 | 0 | 104 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 285 | 0 | 0 | 0 | 31 | 333 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 155 | 0 | 0 | 32 | 0 | 0 | 227 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 30 | 22 | 183 | 31 | 50 | 70 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 275 | 260 | 375 | 36 | 30 | 0 | 2 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 16 | 0 | 0 | 6 | 5576 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 195 | 0 | 386 | 0 | 0 | 2.5 | 160 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 136 | 110 | 0 | 0 | 1130 | 17 | 4379.38 | 9955.38 | 91.46
Total KWH | 0 | 1059840 | 422880 | 0 | 0 | 0 | 0 | 1674818.19 | 9604800 | 0 | 0 | 572040 | 141120 | 0 | 1472976 | 798720 | 0 | 206756 | 510385 | 1640160 | 506880 | 0 | 9069500 | 7024785 | 0 | 0 | 411764 | 728700 | 7700194 | 0 | 0 | 164127 | 0 | 399000 | 491400 | 0 | 0 | 554509 | 188182 | 79680 | 0 | 469440 | 199378 | 0 | 0 | 192960 | 203520 | 24121 | 968000 | 228330 | 507360 | 3730909.09 | 122109 | 0 | 471360 | 0 | 788690 | 4896146 | 0 | 0 | 0 | 26192725 | 135405 | 1128750 | 824430 | 4349091 | 0 | 0 | 2286000 | 601920 | 4624000 | 711216 | 1210560 | 561280 | 1027200 | 598080 | 326860 | 0 | 1284480 | 229781 | 429264 | 69632 | 7257500 | 3801600 | 9121000 | 815328 | 828000 | 0 | 100944 | 3573573 | 480432 | 0 | 1783680 | 709248 | 0 | 225000 | 0 | 331920 | 192000 | 1056000 | 398400 | 7700 | 251720 | 117360 | 135867618.28 | 20053090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514800 | 0 | 0 | 15978969 | 0 | 0 | 102963 | 0 | 0 | 13209 | 685152 | 0 | 63710 | 107376 | 560410 | 213475 | 272248 | 4240364 | 0 | 0 | 0 | 4177391 | 0 | 8681455 | 0 | 23700 | 67176 | 3832000 | 1585745 | 713019 | 162119 | 213542 | 0 | 0 | 31003.68 | 882720 | 3505 | 0 | 6088000 | 142985 | 3105000 | 2586130 | 0 | 0 | 25101090.91 | 1171200 | 101373547.59 | 237241165.87

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10873.29 | MW | 12:00 Hr. | Energy Generated |  |  | 237.2412 |  | MKWHr.
| Day Peak Demand |  |  | 10936.29 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.784 |  | MKWHr.
| Evening Peak Generation |  |  | 11443 | MW | 19:00 Hr. | Energy Demand |  |  | 238.0252 |  | MKWHr.
| Evening Peak Demand |  |  | 11481 | MW | 19:00 Hr. | Maximum Temperature |  |  | 26 |  | °C
| Minimum Generation of the Day |  |  | 7714 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 849.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 11443 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.1947 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.2001 | 0 | 7.2366 | 0 | 0 | 0.16413 | 0 | 0 | 44.6008 | Gas | 109.2879 | Gas | 392648593.9365
| Chattogram Zone |  |  | 5.4035 | 29.9236 | 3.0287 | 0 | 0.968 | 0.15953 | 0 | 0.46944 | 39.9528 | Coal | 66.5305 | Coal | 470324386.0455
| Cumilla Zone |  |  | 14.5891 | 0 | 3.9597 | 0 | 0 | 0.42926 | 1.2845 | 0 | 20.2625 | HFO | 19.206 | HFO | 351459744.29
| Mymensingh Zone |  |  | 0.3984 | 0 | 1.6973 | 0 | 0 | 0.25942 | 0 | 0 | 2.3551 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6963 | Hydro | 0.968 | Hydro | 96800
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.5148 | 20.0531 | 0 | 20.5679 | Solar | 3.4628 | Solar | 54037318.208
| Barishal Zone |  |  | 5.8341 | 31.1891 | 1.1712 | 0 | 0 | 0.003505 | 0 | 0 | 38.1979 | Import | 37.3165 | Import | 193752142.07
| Rajshahi Zone |  |  | 17.1664 | 0 | 1.1859 | 0 | 0 | 0.85636 | 15.979 | 0 | 35.1876 | Wind | 0.46944 | Wind | 7323264
| Rangpur Zone |  |  | 0 | 5.4177 | 0.92656 | 0 | 0 | 1.0758 | 0 | 0 | 7.4201
| Total |  |  | 109.2879 | 66.5305 | 19.206 | 0 | 0.968 | 3.4628 | 37.3165 | 0.46944 | 237.2412
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 392648593.9365 |  | Hydro | 96800
|  |  |  | Coal | 470324386.0455 |  | Solar | 54037318.208
|  |  |  | HFO | 351459744.29 |  | Import | 193752142.07
|  |  |  | HSD | 0 |  | Wind | 7323264
[5 empty] | Total: | 146,96,42,248 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.0531 | Peak Hr Flow | 638.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 5802313000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.979 | Peak Hr Flow | 752.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 264 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2845 | Peak Hr Flow | 46.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 746 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.3165 | Peak Hr Flow | 1436.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4138
|  |  |  | Chattogram |  | 0 |  | 1140
|  |  |  | Cumilla |  | 0 |  | 960
|  |  |  | Mymensingh |  | 36 |  | 972
|  |  |  | Sylhet |  | 0 |  | 312
|  |  |  | Khulna |  | 0 |  | 1228
|  |  |  | Barishal |  | 0 |  | 292
|  |  |  | Rajshahi |  | 0 |  | 1105
|  |  |  | Rangpur |  | 0 |  | 803
|  |  |  | Total |  | 36 |  | 10950
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1122 |  |  |  | Total | 742.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1864.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 | 10:37 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance ( Deep Cleaning of Insulator Disc)
| 08:28 | 15:09 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 08:50 | 14:01 | Bogura-Sirajganj 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end. and from Sirajgonj
230 end Due to Annual Maintenance
| 08:53 |  | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual maintenance.
| 09:24 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:- At 08:50 AM
| 09:35 |  | Aminbazar-Airport(Old) 230kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing Pick | [7 empty] | and 184.0MW load
|  |  | up L1,L2,L3 DIFF TRIP PH A FAULT PH B FAULT PH C FAULT Z 1 OPTD Z COM OPTD relays | [7 empty] | interrup. Agargaon
|  |  | Due to Tower Disk Insulator broken Y phase and from Agargaon 230/132kV end showing | [7 empty] | 230/132kV end
Differential relay, distance relay relays Due to Disc failure.
| 09:45 | 16:25 | Hathazari 230/132/33kV S/S MT-04 HT Scheduled S/D
| 09:45 | 16:15 | Hathazari 230/132/33kV S/S MT-04 LT Scheduled S/D
| 10:10 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end. and from
Kishoreganj 132/33kVend.
| 10:44 | 19:57 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from Baharampur end
| 11:24 | 14:16 | Ghatail 132/33kV S/S T-2 HT Forced S/D Due to Pbs work in 33 kv Bus-2
| 11:32 | 14:18 | Ghatail 132/33kV S/S T-2 LT Forced S/D Due to Pbs work in 33 kv Bus-2
| 11:46 | 13:44 | Sholosohor 132/33kV S/S TRAFO-02 LT Forced S/D Due to Shutdown needed to clear out crow
nests from 33KV gantry and to clean 132KV bushing.
| 11:47 | 13:42 | Sholosohor 132/33kV S/S TRAFO-02 HT Forced S/D Due to Shutdown needed to clear out crow
nests from 33KV gantry and to clean 132KV bushing.
| 12:00 |  | Day Peak Generation: 10869 MW.
| 12:37 |  | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to T-2,33 KV CB Trip coil maintenance.
|  | 14:26 | Daudkandi 132/33kV S/S Transformer-3 HT is restored.
|  | 14:28 | Daudkandi 132/33kV S/S Transformer-3 LT is restored.
|  | 18:26 | Sylhet 132/33kV S/S T4 HT is restored.
| 18:33 | 18:55 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing O/C & E/F: A & B-phase fault relays Due
to 33kv PDB Auxilary Transformer bushing loop burn
| 18:33 | 20:58 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing N/A relays Due to 33kv PDB Auxilary
Transformer bushing loop burn
| 18:33 | 18:55 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing O/C & E/F: Inst fault relays Due to
33kv PDB Auxilary Transformer bushing loop burn
| 19:00 |  | Evening Peak Gen. 11443 MW
| 05:00 |  | Minimum Generation = 7,783MW
| 06:34 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:-
| 07:00 |  | Baroaulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Annual
Deadline checking by Khulsi ss
| 07:15 |  | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Dead line
checking and from Bhulta 400/230kV end Due to Annual Maintenance work by Rampura Grid
Substation.
| 07:16 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For BPDB maintenance work.
| 07:16 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For BPDB Maintenance Work.
| 07:35 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to oil leakage Maintenance.
| 07:36 |  | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 07:37 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to oil Leakage Maintenance.
| 07:56 |  | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to due to
relay Changing work by SPMD-2
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 73 | 1674818.19 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9604800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9069500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 256 | 7024785 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 206756 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7700194 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 572040 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 133 | 798720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 510385 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 411764 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 399000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 491400 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 506880 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 728700 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 422880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 1472976 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1059840 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1640160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 164127 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 141120 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.654 | 2208 | 44600845.19
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 135405 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 471360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 968000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 4896146 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 788690 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 84 | 199378 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 192960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 507360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 79680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 188182 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 228330 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 75 | 203520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 554509 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 126 | 122109 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26192725 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 15 | 469440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 157 | 3730909.09 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2312 | 39952824.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4624000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 58 | 2286000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 31 | 711216 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 14 | 601920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4349091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1128750 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 93 | 824430 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 32 | 69632 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 561280 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 105 | 1027200 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1284480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52 | 229781 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 326860 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 598080 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1210560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 429264 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1070 | 20262544
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 398400 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1056000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 192000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 117360 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 331920 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 138.5 | 2355100
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 29 | 828000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3573573 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 815328 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 100944 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 709248 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 1783680 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | Tripped
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 225000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 480432 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7257500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 9121000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 255 | 3801600 | Only Gas turbine is available
Sylhet Area Total |  |  |  |  | 2368.568 | 1276 | 28696305
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 638 | 20053090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 514800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 638 | 20567890
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 142985 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 3105000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 25101090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2586130 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 1171200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6088000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3505 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1681 | 38197910.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 42 | 102963 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 6 | 13209 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 38 | 63710 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 165 | 4240364 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 150 | 4177391 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 394 | 8681455 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 213475 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 67176 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 107376 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 685152 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 752 | 15978969 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 272248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 560410 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1719.5 | 35187598
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 67 | 1585745 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3832000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 213542 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31003.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 75 | 713019 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 162119 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 882720 | -
Rangpur Area Total |  |  |  |  | 950 | 400 | 7420148.68
Eastern Grid Total |  |  |  |  | 16772.132 | 7004.5 | 135867618.28
Western Grid Total |  |  |  |  | 10294.5 | 4438.5 | 101373547.59
National Grid Total |  |  |  |  | 27066.632 | 11443 | 237241165.87
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7486 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3427.6 | MW
i) Dhaka area |  |  | 4138 |  | MW | i) Khulna area |  |  |  | 1227.5 | MW
ii) Chattogram area |  |  | 1139.5 |  | MW | ii) Barishal area |  |  |  | 291.9 | MW
iii) Cumilla area |  |  | 960.5 |  | MW | iii) Rajshahi area |  |  |  | 1105.2 | MW
iv) Mymensingh area |  |  | 936 |  | MW | iv) Rangpur area |  |  |  | 803 | MW
v) Sylhet area |  |  | 312 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10913.6 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 19 | 23:00 | 67 | Jaldhaka | 64 | 18:30 | 133 | Purbachal | 13 | 13:00
2 | AKSML | 69 | 00:00 | 68 | Jamalpur | 98 | 07:00 | 134 | Purbasadipur | 117 | 08:00
3 | Aftabnagar | 26 | 11:00 | 69 | Jashore | 108 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 80 | 13:00 | 70 | Jhenaidah | 98 | 08:00 | 136 | Rahim | 24 | 17:00
5 | Agrabad | 66 | 18:00 | 71 | Joydebpur | 142 | 09:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 48 | 09:00 | 72 | Joypurhat | 52 | 08:00 | 138 | Rajendrapur | 96 | 15:00
7 | Ashuganj | 96.5 | 19:00 | 73 | Juldah | 11 | 16:00 | 139 | Rajshahi | 102 | 19:00
8 | BSRM | 198 | 02:00 | 74 | KSRM | 35 | 11:00 | 140 | Rajshahi-230 | 45 | 13:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 214 | 19:00 | 141 | Ramganj | 84 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 18:00 | 142 | Rampur | 27 | 18:00
11 | Bakulia | 70 | 18:30 | 77 | Kallyanpur | 63 | 12:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 51 | 13:00 | 78 | Kalurghat | 32 | 10:00 | 144 | Rangpur | 102 | 18:30
13 | Bangabhaban | 8 | 10:00 | 79 | Kamrangirchar | 66 | 12:00 | 145 | Ruppur | 4.8 | 15:00
14 | Barapukuria | 62 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 0 | 00:00
15 | Barguna | 14 | 21:00 | 81 | Kazla | 93 | 16:00 | 147 | Saidpur | 103 | 09:00
16 | Barishal | 67 | 12:00 | 82 | Keranigonj | 60 | 19:00 | 148 | Satkhira | 90 | 19:00
17 | Barishal-230 | 74 | 18:30 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 69 | 14:00
18 | Baroaulia | 45 | 18:00 | 84 | Khulna | 68 | 13:00 | 150 | Savar | 195 | 12:00
19 | Baroirhat | 55 | 18:30 | 85 | Khulshi | 132 | 22:00 | 151 | SevenRings | 16.2 | 20:00
20 | Bashundhara | 134 | 14:00 | 86 | Kishoreganj | 124 | 18:30 | 152 | ShahCement | 24 | 21:00
21 | BashundharaCement | 12 | 10:00 | 87 | Kodda | 287 | 18:00 | 153 | Shahjadpur | 64 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 20:00 | 154 | Shahjibazar | 83 | 18:00
23 | Benapole | 54 | 08:00 | 89 | Kurigram | 64 | 08:00 | 155 | Shahmirpur | 45 | 03:00
24 | Bhaluka | 114 | 09:00 | 90 | Kushtia | 108 | 18:30 | 156 | Shariatpur | 51 | 20:00
25 | Bhandaria | 34 | 22:00 | 91 | Lalbag | 58 | 12:00 | 157 | Sherpur | 118 | 22:00
26 | Bhangura | 27 | 18:00 | 92 | Lalmonirhat | 51 | 08:00 | 158 | Shikalbaha | 22 | 18:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | MI_Cement | 17.7 | 20:00 | 159 | Shitalakhya | 64.7 | 12:00
28 | Bhulta | 239 | 16:00 | 94 | Madanganj | 20 | 12:00 | 160 | Sholosohor | 34 | 12:00
29 | Bog-Sherpur | 66 | 10:00 | 95 | Madaripur | 66 | 20:00 | 161 | Shyampur | 156 | 10:00
30 | Bogura | 119 | 13:00 | 96 | Madartek | 49.49 | 13:00 | 162 | Siddhirganj | 96 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 36 | 18:00 | 163 | Sirajganj | 90 | 19:00
32 | Brahmanbaria | 102 | 18:00 | 98 | Magura | 48 | 18:30 | 164 | Sonargaon | 82 | 10:00
33 | Cantonment | 62 | 18:30 | 99 | Mahasthangarh | 56 | 08:00 | 165 | Sreemongol | 47 | 20:00
34 | Chandpur | 44 | 18:30 | 100 | Manikganj | 115 | 19:00 | 166 | Sreepur | 79 | 15:00
35 | Chandraghona | 26 | 18:30 | 101 | Maniknagar | 52 | 13:00 | 167 | Srinagar | 29.68 | 21:00
36 | Chapai | 63 | 11:00 | 102 | Matarbari | 38 | 18:30 | 168 | Sunamganj | 40 | 18:00
37 | Charsaidpur | 41 | 23:00 | 103 | Matuail | 51 | 12:00 | 169 | Sylhet | 30 | 18:00
38 | Chauddagram | 44 | 13:00 | 104 | Millgate | 69 | 11:00 | 170 | Sylhet-132 | 81 | 21:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 101 | 10:00 | 171 | TK | 22.5 | 19:00
40 | Chowmuhani | 142 | 18:00 | 106 | Mirsorai | 8 | 13:00 | 172 | Tangail | 160 | 07:00
41 | Chuadanga | 76 | 18:30 | 107 | Mirzapur | 37 | 07:00 | 173 | Thakurgaon | 80 | 19:00
42 | Coxsbazar | 109 | 18:00 | 108 | Mithapukur | 70 | 18:00 | 174 | Tongi | 90 | 12:00
43 | Cumilla(N) | 123 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 25 | 08:00
44 | Cumilla(S) | 128 | 14:00 | 110 | Mogbazar | 95.7 | 13:00 | 176 | Ullon | 38 | 14:00
45 | Daudkandi | 112 | 18:00 | 111 | Mongla | 28 | 06:00 | 177 | Uttara | 65 | 13:00
46 | Dhaka | 34 | 13:00 | 112 | Motijheel | 27 | 13:00 | 178 | UttaraNew | 33 | 13:00
47 | Dhamrai | 108 | 10:00 | 113 | Muktagacha | 30 | 07:00 | 179 | Zigatola | 54 | 13:00
48 | Dhanmondi | 85 | 13:00 | 114 | Munshiganj | 64 | 20:00
49 | Dohazari | 66 | 18:00 | 115 | Mymensingh | 171 | 13:00
50 | Faridpur | 108 | 18:30 | 116 | Naogaon | 105 | 09:00
51 | Fatullah | 82 | 12:00 | 117 | Narail | 42 | 18:30
52 | Fenchuganj | 24 | 18:00 | 118 | Narinda | 58.5 | 13:00
53 | Feni | 67 | 18:30 | 119 | Narshingdi | 157 | 20:00
54 | GPH | 84 | 04:00 | 120 | Natore | 98 | 19:30
55 | Ghatail | 42 | 19:30 | 121 | Nawabganj | 29.8 | 13:00
56 | Ghorashal | 12 | 00:00 | 122 | Netrakona | 134 | 08:00
57 | Ghorashal-230 | 56 | 13:00 | 123 | New | 68.8 | 12:00
58 | Goalpara | 24 | 13:00 | 124 | Niamatpur | 78 | 18:00
59 | Gollamari | 88 | 03:00 | 125 | Noapara | 36 | 19:00
60 | Gopalganj | 81 | 18:30 | 126 | PHP | 6 | 01:00
61 | Gulshan | 76 | 13:00 | 127 | Pabna | 65 | 18:30
62 | Halishahar | 48 | 16:00 | 128 | Palashbari | 100 | 08:00
63 | HaripurSBU | 177 | 12:00 | 129 | Panchagarh | 47 | 18:30
64 | Hasnabad | 69 | 12:00 | 130 | Patuakhali | 54.9 | 21:00
65 | Hathazari | 54 | 19:30 | 131 | Payra | 14 | 18:30
66 | Ishurdi | 66 | 11:00 | 132 | Postogola | 42 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9359.5 | 0 |  | 9359.5
1:00 | 8746.5 | 0 |  | 8746.5
2:00 | 8259.5 | 0 |  | 8259.5
3:00 | 7948.5 | 0 |  | 7948.5
4:00 | 7795 | 0 |  | 7795
5:00 | 7714 | 0 |  | 7714
6:00 | 8097 | 0 |  | 8097
7:00 | 9018.35 | 0 |  | 9018.35
8:00 | 9850.23 | 65 |  | 9918.23
9:00 | 10397.74 | 27 |  | 10425.74
10:00 | 10122.45 | 220 |  | 10352.45
11:00 | 10186.9 | 55 |  | 10243.9
12:00 | 10873.29 | 60 |  | 10936.29
13:00 | 10993.21 | 80 |  | 11077.21
14:00 | 10495.66 | 65 |  | 10563.66
15:00 | 10225.88 | 31 |  | 10257.88
16:00 | 10045.25 | 30 |  | 10076.25
17:00 | 9970.93 | 45 |  | 10017.93
18:00 | 10683.5 | 70 |  | 10756.5
19:00 | 11443 | 36 |  | 11481
19:30 | 11158.5 | 0 |  | 11158.5
20:00 | 10917.5 | 0 |  | 10917.5
21:00 | 10706.81 | 0 |  | 10706.81
22:00 | 10441.82 | 0 |  | 10441.82
23:00 | 9955.38 | 0 |  | 9955.38
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5156 | 4203.5 | 9359.5 | DAILY GENERATION CURVE
00:30 | 5073 | 3980 | 9053
01:00 | 4990 | 3756.5 | 8746.5 | 04-02-2025
01:30 | 4884.5 | 3618.5 | 8503
02:00 | 4779 | 3480.5 | 8259.5
02:30 | 4723.5 | 3380.5 | 8104
03:00 | 4668 | 3280.5 | 7948.5
03:30 | 4598.75 | 3273 | 7871.75
04:00 | 4529.5 | 3265.5 | 7795
04:30 | 4480.5 | 3274 | 7754.5
05:00 | 4431.5 | 3282.5 | 7714
05:30 | 4554.5 | 3351 | 7905.5
06:00 | 4677.5 | 3419.5 | 8097
06:30 | 4868.175 | 3689.5 | 8557.675
07:00 | 5058.85 | 3959.5 | 9018.35
07:30 | 5338.475 | 4095.815 | 9434.29
08:00 | 5618.1 | 4232.13 | 9850.23
08:30 | 5826.485 | 4297.5 | 10123.985
09:00 | 6034.87 | 4362.87 | 10397.74
09:30 | 5876.035 | 4384.06 | 10260.095
10:00 | 5717.2 | 4405.25 | 10122.45
10:30 | 5695.655 | 4459.02 | 10154.675
11:00 | 5674.11 | 4512.79 | 10186.9
11:30 | 5816.765 | 4713.33 | 10530.095
12:00 | 5959.42 | 4913.87 | 10873.29
12:30 | 5991.015 | 4942.235 | 10933.25
13:00 | 6022.61 | 4970.6 | 10993.21
13:30 | 5878.185 | 4866.25 | 10744.435
14:00 | 5733.76 | 4761.9 | 10495.66
14:30 | 5703.155 | 4657.615 | 10360.77
15:00 | 5672.55 | 4553.33 | 10225.88
15:30 | 5616.845 | 4518.72 | 10135.565
16:00 | 5561.14 | 4484.11 | 10045.25
16:30 | 5561.76 | 4446.33 | 10008.09
17:00 | 5562.38 | 4408.55 | 9970.93
17:30 | 5882.69 | 4444.525 | 10327.215
18:00 | 6203 | 4480.5 | 10683.5
18:30 | 6603.75 | 4459.5 | 11063.25
19:00 | 7004.5 | 4438.5 | 11443
19:30 | 6845 | 4313.5 | 11158.5
20:00 | 6691 | 4226.5 | 10917.5
20:30 | 6468.5 | 4343.655 | 10812.155 |  | Executive Engineer
21:00 | 6246 | 4460.81 | 10706.81 |  | Network Operation Division
21:30 | 6110 | 4464.315 | 10574.315
22:00 | 5974 | 4467.82 | 10441.82
22:30 | 5775 | 4423.6 | 10198.6
23:00 | 5576 | 4379.38 | 9955.38

## En-Curve
QF-LDC-12
Date | 04-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2950 | 1906.5 | 923 | 0 | 58 | 621 | 40 | 2662 | 0 | 17 | 151 | 0 | 0 | 31 | 0 | DAILY ENERGY CURVE
00:30 | 2923.5 | 1856 | 922.5 | 0 | 53 | 578 | 40 | 2504 | 0 | 17 | 117 | 0 | 0 | 42 | 0 | 04-02-2025
01:00 | 2897 | 1805.5 | 922 | 0 | 48 | 535 | 40 | 2346 | 0 | 17 | 83 | 0 | 0 | 53 | 0
01:30 | 2844.5 | 1755.5 | 922.5 | 0 | 48 | 503 | 40 | 2270 | 0 | 8.5 | 59 | 0 | 0 | 52 | 0 | Energy Generated | 237.2412 |  | MKWHr
02:00 | 2792 | 1705.5 | 923 | 0 | 48 | 471 | 40 | 2194 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | Energy not Served | 0.784 |  | MKWHr
02:30 | 2776 | 1695.5 | 829 | 0 | 51 | 465 | 40 | 2168.5 | 0 | 0 | 26 | 0 | 0 | 53 | 0 | Total Energy Requirement | 238.0252 |  | MKWHr
03:00 | 2760 | 1685.5 | 735 | 0 | 54 | 459 | 40 | 2143 | 0 | 0 | 17 | 0 | 0 | 55 | 0
03:30 | 2708.5 | 1688.75 | 733.5 | 0 | 51 | 459.5 | 40 | 2136.5 | 0 | 0 | 8.5 | 0 | 0 | 45.5 | 0
04:00 | 2657 | 1692 | 732 | 0 | 48 | 460 | 40 | 2130 | 0 | 0 | 0 | 0 | 0 | 36 | 0
04:30 | 2637 | 1673.5 | 732 | 0 | 46 | 460.5 | 40 | 2130.5 | 0 | 0 | 0 | 0 | 0 | 35 | 0
05:00 | 2617 | 1655 | 732 | 0 | 44 | 461 | 40 | 2131 | 0 | 0 | 0 | 0 | 0 | 34 | 0
05:30 | 2640 | 1751 | 732 | 0 | 47 | 462.5 | 40 | 2199.5 | 0 | 0 | 0 | 0 | 0 | 33.5 | 0
06:00 | 2663 | 1847 | 732 | 0 | 50 | 464 | 40 | 2268 | 0 | 0 | 0 | 0 | 0 | 33 | 0
06:30 | 2712.5 | 1873.25 | 827 | 0 | 50 | 533 | 40 | 2438 | 6.425 | 17 | 29.5 | 0 | 0 | 31 | 0
07:00 | 2762 | 1899.5 | 922 | 0 | 50 | 602 | 40 | 2608 | 12.85 | 34 | 59 | 0 | 0 | 29 | 0
07:30 | 2730 | 1882 | 780 | 0 | 51 | 681.205 | 40 | 2800 | 67.085 | 71 | 309 | 0 | 0 | 23 | 32.5
08:00 | 2698 | 1864.5 | 638 | 0 | 52 | 760.41 | 40 | 2992 | 121.32 | 108 | 559 | 0 | 0 | 17 | 65
08:30 | 2666.5 | 1850 | 638 | 0 | 51 | 759.36 | 40 | 2997 | 197.625 | 108 | 802 | 0 | 0 | 14.5 | 46
09:00 | 2635 | 1835.5 | 638 | 0 | 50 | 758.31 | 40 | 3002 | 273.93 | 108 | 1045 | 0 | 0 | 12 | 27
09:30 | 2518 | 1759 | 767.5 | 0 | 52 | 713.53 | 40 | 2873.5 | 344.565 | 106 | 1076 | 0 | 0 | 10 | 123.5
10:00 | 2401 | 1682.5 | 897 | 0 | 54 | 668.75 | 40 | 2745 | 415.2 | 104 | 1107 | 0 | 0 | 8 | 220
10:30 | 2357.5 | 1656.5 | 909.5 | 0 | 56 | 666.195 | 40 | 2770 | 459.48 | 110 | 1118.5 | 0 | 0 | 11 | 137.5
11:00 | 2314 | 1630.5 | 922 | 0 | 58 | 663.64 | 40 | 2795 | 503.76 | 116 | 1130 | 0 | 0 | 14 | 55
11:30 | 2429 | 1648 | 921.5 | 0 | 60 | 712.235 | 40 | 2911.5 | 515.36 | 129.5 | 1148.5 | 0 | 0 | 14.5 | 57.5
12:00 | 2544 | 1665.5 | 921 | 0 | 62 | 760.83 | 40 | 3028 | 526.96 | 143 | 1167 | 0 | 0 | 15 | 60
12:30 | 2586 | 1756 | 922 | 0 | 64 | 760.355 | 40 | 3036.5 | 530.895 | 155.5 | 1065.5 | 0 | 0 | 16.5 | 70
13:00 | 2628 | 1846.5 | 923 | 0 | 66 | 759.88 | 40 | 3045 | 534.83 | 168 | 964 | 0 | 0 | 18 | 80
13:30 | 2581.5 | 1839.5 | 922 | 0 | 67 | 758.44 | 40 | 2987 | 496.495 | 174 | 860.5 | 0 | 0 | 18 | 72.5
14:00 | 2535 | 1832.5 | 921 | 0 | 68 | 757 | 40 | 2929 | 458.16 | 180 | 757 | 0 | 0 | 18 | 65
14:30 | 2560 | 1840 | 921 | 0 | 66 | 759 | 40 | 2914 | 402.27 | 180 | 661.5 | 0 | 0 | 17 | 48
15:00 | 2585 | 1847.5 | 921 | 0 | 64 | 761 | 40 | 2899 | 346.38 | 180 | 566 | 0 | 0 | 16 | 31
15:30 | 2673 | 1875.5 | 921.5 | 0 | 60 | 757 | 40 | 2898 | 265.065 | 180 | 454.5 | 0 | 0 | 11 | 30.5
16:00 | 2761 | 1903.5 | 922 | 0 | 56 | 753 | 40 | 2897 | 183.75 | 180 | 343 | 0 | 0 | 6 | 30
16:30 | 2725.5 | 1867 | 922 | 0 | 58 | 754 | 40 | 2946 | 116.84 | 232.5 | 339.75 | 0 | 0 | 6.5 | 37.5
17:00 | 2690 | 1830.5 | 922 | 0 | 60 | 755 | 40 | 2995 | 49.93 | 285 | 336.5 | 0 | 0 | 7 | 45
17:30 | 2599 | 1799.5 | 921.5 | 0 | 56 | 755 | 40 | 3009 | 24.965 | 411 | 702.75 | 0 | 0 | 8.5 | 57.5
18:00 | 2508 | 1768.5 | 921 | 0 | 52 | 755 | 40 | 3023 | 0 | 537 | 1069 | 0 | 0 | 10 | 70
18:30 | 2645 | 1790 | 779.5 | 0 | 49 | 753.5 | 40 | 3023 | 0 | 564.5 | 1406.25 | 0 | 0 | 12.5 | 53
19:00 | 2782 | 1811.5 | 638 | 0 | 46 | 752 | 40 | 3023 | 0 | 592 | 1743.5 | 0 | 0 | 15 | 36
19:30 | 2699 | 1866.5 | 637 | 0 | 46 | 757 | 40 | 3028 | 0 | 569 | 1502 | 0 | 0 | 14 | 0
20:00 | 2741 | 1860.5 | 638 | 0 | 42 | 760 | 40 | 3032 | 0 | 368 | 1427 | 0 | 0 | 9 | 0
20:30 | 2847 | 1903.5 | 780 | 0 | 46 | 757.155 | 40 | 3033.5 | 0 | 285 | 1114 | 0 | 0 | 6 | 0
21:00 | 2953 | 1946.5 | 922 | 0 | 50 | 754.31 | 40 | 3035 | 0 | 202 | 801 | 0 | 0 | 3 | 0
21:30 | 2888 | 1924.5 | 921.5 | 0 | 51 | 753.315 | 40 | 3040 | 0 | 176 | 778.5 | 0 | 0 | 1.5 | 0
22:00 | 2823 | 1902.5 | 921 | 0 | 52 | 752.32 | 40 | 3045 | 0 | 150 | 756 | 0 | 0 | 0 | 0
22:30 | 2863 | 1901.5 | 921.5 | 0 | 50 | 754.1 | 40 | 3044 | 0 | 108.5 | 516 | 0 | 0 | 0 | 0
23:00 | 2903 | 1900.5 | 922 | 0 | 48 | 755.88 | 40 | 3043 | 0 | 67 | 276 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 04:00 | 392 | 12:00 | Payra | 417 | 01:00 | 407 | 12:00
Ashuganj | 415 | 4:00 | 391 | 12:00 | Rahanpur | 420 | 05:00 | 391 | 13:00
Bhulta | 410 | 01:00 | 391 | 16:00 | Rampal | 431 | 02:00 | 388 | 13:00
Bibiana | 405 | 04:00 | 397 | 15:00
BIPTC | 407 | 04:00 | 387 | 11:00
Bogura | 418 | 05:00 | 390 | 09:00
Gopalganj | 414 | 04:00 | 393 | 12:00
Kaliakoir | 394 | 05:00 | 378 | 16:00
Madunaghat | 409 | 03:00 | 400 | 13:00
Meghnaghat | 410 | 05:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 05:00 | 225 | 13:00 | Keranigonj | 237 | 05:00 | 224 | 13:00
AKSML | 236 | 19:00 | 226 | 13:00 | Khulna(S) | 242 | 04:00 | 222 | 13:00
Aminbazar | 236 | 05:00 | 225 | 15:00 | Madunaghat | 236 | 18:30 | 228 | 13:00
Ashuganj | 243 | 01:00 | 231 | 12:00 | Madunaghat-400 | 235 | 05:00 | 228 | 16:00
Ashuganj-400 | 243 | 4:00 | 230 | 15:00 | Maniknagar | 243 | 19:00 | 226 | 12:00
Baghabari | 239 | 00:00 | 226 | 12:00 | Meghnaghat | 242 | 04:00 | 233 | 12:00
Barapukuria | 226 | 06:00 | 217 | 08:00 | Meghnaghat-400 | 239 | 03:00 | 229 | 12:00
Barapukuria-230 | 224 | 5:00 | 215 | 7:00 | Mirsorai | 238 | 19:00 | 8 | 19:00
Barishal | 247 | 05:00 | 236 | 13:00 | Rajshahi | 241 | 05:00 | 223 | 11:00
Bheramara | 240 | 05:00 | 223 | 12:00 | Rampal | 239 | 03:00 | 220 | 13:00
Bhulta | 239 | 05:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 23:00 | 228 | 13:00 | Rampura | 239 | 05:00 | 226 | 12:00
BIPTC | 242 | 04:00 | 223 | 12:00 | Shikalbaha | 233 | 18:00 | 226 | 13:00
Bogura | 241 | 05:00 | 225 | 13:00 | Shyampur | 237 | 04:00 | 226 | 12:00
Bogura-400 | 241 | 03:00 | 225 | 09:00 | Siddhirganj | 236 | 20:00 | 227 | 12:00
Borhanuddin | 248 | 02:00 | 240 | 12:00 | Sirajgonj | 245 | 01:00 | 238 | 12:00
BSRM | 238 | 19:00 | 225 | 16:00 | Sreepur | 239 | 02:00 | 230 | 12:00
Cumilla(N) | 236 | 06:00 | 226 | 13:00 | Tongi | 236 | 04:00 | 223 | 12:00
Faridpur | 246 | 04:00 | 233 | 12:00
Fenchuganj | 237 | 01:00 | 232 | 07:00
Ghorashal | 238 | 08:00 | 230 | 00:00
Ghorashal-230 | 237 | 01:00 | 225 | 12:00
Gopalganj | 246 | 04:00 | 233 | 12:00
GPH | 237 | 19:00 | 226 | 16:00
Haripur | 239 | 05:00 | 227 | 12:00
Hasnabad | 234 | 00:00 | 225 | 12:00
Hathazari | 238 | 17:00 | 229 | 16:00
Ishurdi | 242 | 04:00 | 226 | 12:00
Jhenaidah | 239 | 03:00 | 220 | 13:00
Kaliakoir | 235 | 04:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 127 | 11:00 | Magura | 138 | 03:00 | 126 | 12:00
Agargaon | 138 | 04:00 | 130 | 12:00 | Mahasthangarh | 137 | 05:00 | 125 | 13:00
Agrabad | 136 | 18:30 | 129 | 15:00 | Manikganj | 136 | 00:00 | 129 | 16:00
AKS | 134 | 18:30 | 128 | 13:00 | Maniknagar | 135 | 04:00 | 127 | 16:00
Aminbazar | 138 | 22:00 | 127 | 11:00 | Matarbari | 127 | 02:00 | 120 | 16:00
Amnura | 141 | 18:30 | 127 | 12:00 | Matuail | 136 | 03:00 | 130 | 12:00
Ashuganj | 142 | 05:00 | 137 | 13:00 | Millgate | 138 | 01:00 | 130 | 12:00
Bagerhat | 134 | 04:00 | 125 | 12:00 | Mirpur | 137 | 03:00 | 128 | 15:00
Bajitpur | 136 | 01:00 | 132 | 09:00 | Mirzapur | 135 | 02:00 | 128 | 16:00
Bakulia | 137 | 19:00 | 129 | 13:00 | Mithapukur | 135 | 04:00 | 122 | 08:00
Banani | 137 | 04:00 | 128 | 13:00 | MI_Cement | 137 | 06:00 | 130 | 12:00
Bangabhaban | 136 | 05:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 05:00 | 127 | 08:00 | Mogbazar | 137 | 05:00 | 130 | 12:00
Barguna | 141 | 09:00 | 134 | 21:00 | Mongla | 138 | 04:00 | 125 | 12:00
Barishal | 136 | 01:00 | 129 | 12:00 | Motijheel | 136 | 05:00 | 127 | 12:00
Barishal-230 | 138 | 05:00 | 129 | 13:00 | Muktagacha | 127 | 00:00 | 117 | 16:00
Baroaulia | 137 | 19:00 | 130 | 16:00 | Munshiganj | 135 | 05:00 | 129 | 16:00
Baroirhat | 136 | 19:00 | 127 | 16:00 | Mymensingh | 129 | 08:00 | 113 | 12:00
Bashundhara | 138 | 02:00 | 128 | 13:00 | Naogaon | 135 | 01:00 | 122 | 13:00
BashundharaCement | 135 | 05:00 | 129 | 12:00 | Narail | 140 | 03:00 | 125 | 12:00
Beanibazar | 138 | 02:00 | 133 | 13:00 | Narinda | 135 | 4:00 | 127 | 16:00
Benapole | 138 | 04:00 | 123 | 13:00 | Narshingdi | 137 | 06:00 | 124 | 12:00
Bhaluka | 130 | 02:00 | 118 | 12:00 | Natore | 138 | 02:00 | 128 | 12:00
Bhandaria | 135 | 06:00 | 127 | 12:00 | Nawabganj | 138 | 01:00 | 131 | 12:00
Bhangura | 136 | 00:00 | 129 | 12:00 | Netrakona | 126 | 01:00 | 111 | 12:00
Bheramara | 139 | 04:00 | 128 | 12:00 | New | 138 | 03:00 | 130 | 12:00
Bheramara(GK) | 139 | 03:00 | 128 | 12:00 | Niamatpur | 140 | 01:00 | 130 | 13:00
Bhulta | 131 | 18:00 | 124 | 12:00 | Noapara | 139 | 03:00 | 125 | 13:00
Bog-Sherpur | 138 | 05:00 | 126 | 13:00 | Pabna | 138 | 05:00 | 126 | 12:00
Bogura | 138 | 05:00 | 128 | 08:00 | Palashbari | 133 | 04:00 | 118 | 08:00
Bogura-230 | 139 | 05:00 | 127 | 13:00 | Panchagarh | 139 | 05:00 | 128 | 08:00
Brahmanbaria | 137 | 01:00 | 131 | 13:00 | Patuakhali | 139 | 08:00 | 133 | 18:00
Cantonment | 144 | 10:00 | 130 | 12:00 | Payra | 137 | 01:00 | 132 | 08:00
Chandpur | 142 | 18:30 | 126 | 15:00 | PHP | 135 | 18:30 | 125 | 13:00
Chandraghona | 136 | 18:30 | 131 | 13:00 | Postogola | 139 | 03:00 | 132 | 16:00
Chapai | 140 | 03:00 | 130 | 08:00 | Purbachal | 137 | 02:00 | 127 | 12:00
Charsaidpur | 137 | 03:00 | 130 | 12:00 | Purbasadipur | 132 | 03:00 | 122 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 137 | 19:30 | 127 | 16:00 | Rahanpur | 142 | 03:00 | 132 | 12:00
Chhatak | 137 | 06:00 | 132 | 12:00 | Rahanpur-400 | 142 | 01:00 | 132 | 13:00
Chowmuhani | 135 | 18:30 | 124 | 16:00 | Rahim | 135 | 02:00 | 129 | 12:00
Chuadanga | 139 | 05:00 | 123 | 13:00 | Rajbari | 136 | 01:00 | 130 | 06:00
Coxsbazar | 125 | 02:00 | 120 | 13:00 | Rajendrapur | 136 | 02:00 | 128 | 13:00
Cumilla(N) | 139 | 19:00 | 131 | 16:00 | Rajshahi | 138 | 04:00 | 129 | 12:00
Cumilla(S) | 138 | 18:30 | 127 | 11:00 | Rajshahi-230 | 139 | 04:00 | 125 | 13:00
Daudkandi | 134 | 02:00 | 127 | 16:00 | Ramganj | 138 | 18:30 | 123 | 15:00
Dhaka | 137 | 02:00 | 129 | 12:00 | Rampur | 136 | 18:30 | 128 | 13:00
Dhamrai | 135 | 03:00 | 127 | 16:00 | Rampura | 137 | 05:00 | 128 | 12:00
Dhanmondi | 137 | 03:00 | 130 | 12:00 | Rangamati | 136 | 18:30 | 130 | 13:00
Dohazari | 135 | 19:00 | 127 | 13:00 | Rangpur | 135 | 06:00 | 117 | 08:00
Faridpur | 136 | 04:00 | 130 | 12:00 | Ruppur | 140 | 04:00 | 130 | 12:00
Fatullah | 138 | 03:00 | 131 | 12:00 | Saidpur | 135 | 05:00 | 124 | 08:00
Fenchuganj | 142 | 04:00 | 138 | 12:00 | Satkhira | 138 | 04:00 | 125 | 13:00
Feni | 135 | 19:00 | 124 | 16:00 | Satmasjid | 137 | 02:00 | 129 | 12:00
Ghatail | 131 | 08:00 | 121 | 16:00 | Savar | 136 | 19:00 | 127 | 15:00
Ghorashal | 141 | 20:00 | 134 | 11:00 | SevenRings | 142 | 02:00 | 135 | 12:00
Goalpara | 139 | 03:00 | 128 | 12:00 | ShahCement | 137 | 03:00 | 130 | 12:00
Gollamari | 139 | 04:00 | 129 | 12:00 | Shahjadpur | 140 | 23:00 | 133 | 12:00
Gopalganj | 138 | 04:00 | 128 | 13:00 | Shahjibazar | 140 | 06:00 | 134 | 12:00
Gopalganj-400 | 138 | 03:00 | 130 | 12:00 | Shahmirpur | 136 | 19:00 | 129 | 16:00
Gulshan | 136 | 02:00 | 128 | 12:00 | Shariatpur | 138 | 04:00 | 128 | 12:00
Halishahar | 135 | 05:00 | 130 | 15:00 | Sherpur | 124 | 08:00 | 112 | 01:00
Haripur | 136 | 05:00 | 129 | 12:00 | Shikalbaha | 126 | 19:00 | 118 | 13:00
HaripurSBU | 136 | 05:00 | 129 | 12:00 | Shikalbaha-230 | 138 | 18:30 | 130 | 13:00
Hasnabad | 138 | 00:00 | 132 | 12:00 | Shitalakhya | 137 | 06:00 | 130 | 12:00
Hathazari | 136 | 17:00 | 132 | 12:00 | Sholosohor | 136 | 19:00 | 131 | 12:00
Ishurdi | 141 | 04:00 | 131 | 12:00 | Shyampur | 137 | 01:00 | 130 | 12:00
Jaldhaka | 133 | 05:00 | 118 | 08:00 | Shyampur-230 | 139 | 04:00 | 131 | 12:00
Jamalpur | 132 | 08:00 | 115 | 03:00 | Siddhirganj | 136 | 04:00 | 129 | 12:00
Jashore | 139 | 03:00 | 123 | 13:00 | Sirajganj | 138 | 03:00 | 127 | 12:00
Jhenaidah | 139 | 02:00 | 130 | 21:00 | Sonargaon | 134 | 20:00 | 128 | 16:00
Jhenaidah-230 | 141 | 05:00 | 128 | 12:00 | Sreemongol | 139 | 01:00 | 134 | 12:00
Joydebpur | 140 | 14:00 | 130 | 12:00 | Sreepur | 131 | 03:00 | 124 | 12:00
Joypurhat | 137 | 04:00 | 121 | 13:00 | Srinagar | 139 | 04:00 | 131 | 12:00
Juldah | 138 | 18:30 | 129 | 16:00 | SSM | 140 | 04:00 | 132 | 13:00
Kabirpur | 140 | 00:00 | 129 | 16:00 | Sunamganj | 137 | 06:00 | 131 | 13:00
Kachua | 140 | 18:30 | 127 | 16:00 | Sylhet | 139 | 05:00 | 134 | 12:00
Kaliakoir | 141 | 05:00 | 129 | 12:00 | Sylhet-132 | 138 | 01:00 | 134 | 12:00
Kallyanpur | 135 | 02:00 | 127 | 12:00 | Tangail | 130 | 00:00 | 122 | 16:00
Kalurghat | 136 | 18:30 | 130 | 12:00 | Thakurgaon | 137 | 05:00 | 125 | 08:00
Kamrangirchar | 137 | 00:00 | 125 | 12:00 | TK | 135 | 05:00 | 130 | 16:00
Kaptai | N/A | N/A | N/A | N/A | Tongi | 140 | 04:00 | 132 | 11:00
Kazla | 135 | 03:00 | 127 | 13:00 | Ullahpara | 139 | 01:00 | 129 | 12:00
Keranigonj | 138 | 04:00 | 130 | 12:00 | Ullon | 136 | 03:00 | 127 | 12:00
Khagrachori | 135 | 05:00 | 130 | 13:00 | Uttara | 137 | 05:00 | 128 | 17:00
Khulna | 138 | 02:00 | 126 | 12:00 | UttaraNew | 139 | 01:00 | 130 | 12:00
Khulna(S) | 140 | 04:00 | 128 | 13:00 | Zigatola | 139 | 03:00 | 131 | 13:00
Khulshi | 136 | 19:00 | 128 | 15:00
Kishoreganj | 132 | 03:00 | 124 | 13:00
Kodda | 137 | 08:00 | 128 | 12:00
KSRM | 138 | 19:00 | 131 | 14:00
Kulaura | 141 | 01:00 | 137 | 13:00
Kurigram | 132 | 06:00 | 116 | 08:00
Kushtia | 140 | 04:00 | 127 | 12:00
Lalbag | 139 | 04:00 | 131 | 12:00
Lalmonirhat | 133 | 04:00 | 120 | 08:00
Madanganj | 135 | 04:00 | 129 | 12:00
Madaripur | 136 | 03:00 | 130 | 12:00
Madartek | 137 | 05:00 | 129 | 12:00
Madunaghat | 137 | 18:30 | 130 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division