## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9417.04 | 0 |  | 9417.04
1:00 | 8959.77 | 0 |  | 8959.77
2:00 | 8439.59 | 0 |  | 8439.59
3:00 | 8088.97 | 0 |  | 8088.97
4:00 | 7874.52 | 0 |  | 7874.52
5:00 | 7782.43 | 0 |  | 7782.43
6:00 | 8066.4 | 0 |  | 8066.4
7:00 | 9059.68 | 21 |  | 9081.68
8:00 | 9532.52 | 50 |  | 9584.52
9:00 | 10358.82 | 33 |  | 10392.82
10:00 | 10422.17 | 41 |  | 10465.17
11:00 | 10557.76 | 36 |  | 10595.76
12:00 | 10978.35 | 35 |  | 11015.35
13:00 | 11324.63 | 28 |  | 11353.63
14:00 | 10793.45 | 29 |  | 10823.45
15:00 | 10513.47 | 0 |  | 10513.47
16:00 | 9997.71 | 0 |  | 9997.71
17:00 | 10096.97 | 40 |  | 10138.97
18:00 | 11002.2 | 95 |  | 11101.48
19:00 | 11541.74 | 90 |  | 11635.74
19:30 | 11405.89 | 80 |  | 11489.89
20:00 | 11269.39 | 70 |  | 11342.39
21:00 | 10875 | 65 |  | 10942.93
22:00 | 10457 | 42 |  | 10501
23:00 | 9827.5 | 36 |  | 9865.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 05-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2962 | 1948.5 | 922 | 0 | 40 | 657.54 | 40 | 2645 | 0 | 51 | 151 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2998 | 1916 | 922.5 | 0 | 39 | 612.405 | 40 | 2499.5 | 0 | 34 | 127 | 0 | 0 | 0 | 0 | 05-02-2025
01:00 | 3034 | 1883.5 | 923 | 0 | 38 | 567.27 | 40 | 2354 | 0 | 17 | 103 | 0 | 0 | 0 | 0
01:30 | 2997 | 1890 | 922 | 0 | 38 | 494.68 | 40 | 2209.5 | 0 | 24.5 | 84 | 0 | 0 | 0 | 0 | Energy Generated | 239.8572 |  | MKWHr
02:00 | 2960 | 1896.5 | 921 | 0 | 38 | 422.09 | 40 | 2065 | 0 | 32 | 65 | 0 | 0 | 0 | 0 | Energy not Served | 0.711 |  | MKWHr
02:30 | 2949.5 | 1882.5 | 829 | 0 | 37 | 418.28 | 40 | 2050.5 | 0 | 16 | 41 | 0 | 0 | 0.5 | 0 | Total Energy Requirement | 240.5682 |  | MKWHr
03:00 | 2939 | 1868.5 | 737 | 0 | 36 | 414.47 | 40 | 2036 | 0 | 0 | 17 | 0 | 0 | 1 | 0
03:30 | 2860 | 1850.5 | 734.5 | 0 | 37 | 415.745 | 40 | 2034.5 | 0 | 0 | 8.5 | 0 | 0 | 1 | 0
04:00 | 2781 | 1832.5 | 732 | 0 | 38 | 417.02 | 40 | 2033 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:30 | 2747.5 | 1817 | 732 | 0 | 38 | 418.975 | 40 | 2033.5 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
05:00 | 2714 | 1801.5 | 732 | 0 | 38 | 420.93 | 40 | 2034 | 0 | 0 | 0 | 0 | 0 | 2 | 0
05:30 | 2759 | 1823.5 | 731.5 | 0 | 39 | 418.915 | 40 | 2108 | 0 | 0 | 2.5 | 0 | 0 | 2 | 0
06:00 | 2804 | 1845.5 | 731 | 0 | 40 | 416.9 | 40 | 2182 | 0 | 0 | 5 | 0 | 0 | 2 | 0
06:30 | 2868 | 1856.5 | 820.5 | 0 | 37 | 486.1 | 40 | 2376.5 | 4.94 | 19 | 53.5 | 0 | 0 | 1 | 10.5
07:00 | 2932 | 1867.5 | 910 | 0 | 34 | 555.3 | 40 | 2571 | 9.88 | 38 | 102 | 0 | 0 | 0 | 21
07:30 | 2885 | 1852 | 850 | 0 | 37 | 619.55 | 40 | 2475 | 55.05 | 81.5 | 401 | 0 | 0 | 0 | 35.5
08:00 | 2838 | 1836.5 | 790 | 0 | 40 | 683.8 | 40 | 2379 | 100.22 | 125 | 700 | 0 | 0 | 0 | 50
08:30 | 2818 | 1787.75 | 710 | 0 | 42 | 720.95 | 40 | 2379.5 | 161.97 | 138 | 1147.5 | 0 | 0 | 0 | 41.5
09:00 | 2798 | 1739 | 630 | 0 | 44 | 758.1 | 40 | 2380 | 223.72 | 151 | 1595 | 0 | 0 | 0 | 33
09:30 | 2716 | 1717.5 | 744 | 0 | 43 | 757.89 | 40 | 2343.5 | 296.505 | 150 | 1582.1 | 0 | 0 | 0 | 37
10:00 | 2634 | 1696 | 858 | 0 | 42 | 757.68 | 40 | 2307 | 369.29 | 149 | 1569.2 | 0 | 0 | 0 | 41
10:30 | 2650.5 | 1690 | 885.5 | 0 | 43 | 756.365 | 40 | 2297 | 423.9 | 164 | 1539.7 | 0 | 0 | 0 | 38.5
11:00 | 2667 | 1684 | 913 | 0 | 44 | 755.05 | 40 | 2287 | 478.51 | 179 | 1510.2 | 0 | 0 | 0 | 36
11:30 | 2744.5 | 1662.5 | 913.5 | 0 | 46 | 754.985 | 40 | 2323 | 499.37 | 211 | 1568.2 | 0 | 0 | 5 | 35.5
12:00 | 2822 | 1641 | 914 | 0 | 48 | 754.92 | 40 | 2359 | 520.23 | 243 | 1626.2 | 0 | 0 | 10 | 35
12:30 | 2831 | 1622.25 | 914 | 0 | 51 | 758.855 | 40 | 2347 | 511.185 | 266.5 | 1798.7 | 0 | 0 | 11 | 31.5
13:00 | 2840 | 1603.5 | 914 | 0 | 54 | 762.79 | 40 | 2335 | 502.14 | 290 | 1971.2 | 0 | 0 | 12 | 28
13:30 | 2747.5 | 1599.25 | 914 | 0 | 54 | 749.83 | 40 | 2330.5 | 471.76 | 298 | 1842.2 | 0 | 0 | 12 | 28.5
14:00 | 2655 | 1595 | 914 | 0 | 54 | 736.87 | 40 | 2326 | 441.38 | 306 | 1713.2 | 0 | 0 | 12 | 29
14:30 | 2714 | 1588.5 | 913.5 | 0 | 54 | 750.3 | 40 | 2363.5 | 380.46 | 302.5 | 1533.7 | 0 | 0 | 13 | 14.5
15:00 | 2773 | 1582 | 913 | 0 | 54 | 763.73 | 40 | 2401 | 319.54 | 299 | 1354.2 | 0 | 0 | 14 | 0
15:30 | 2790 | 1609.25 | 913.5 | 0 | 51 | 762.41 | 40 | 2395.5 | 244.23 | 299.5 | 1136.7 | 0 | 0 | 13.5 | 0
16:00 | 2807 | 1636.5 | 914 | 0 | 48 | 761.09 | 40 | 2390 | 168.92 | 300 | 919.2 | 0 | 0 | 13 | 0
16:30 | 2785 | 1635.5 | 914 | 0 | 48 | 761.265 | 40 | 2397 | 108.875 | 332.5 | 1014.2 | 0 | 0 | 11 | 20
17:00 | 2763 | 1634.5 | 914 | 0 | 48 | 761.44 | 40 | 2404 | 48.83 | 365 | 1109.2 | 0 | 0 | 9 | 40
17:30 | 2614.5 | 1620.75 | 914 | 0 | 47 | 760.22 | 40 | 2452.5 | 24.415 | 489.5 | 1576.7 | 0 | 0 | 10 | 67.5
18:00 | 2466 | 1607 | 914 | 0 | 46 | 759 | 40 | 2501 | 0 | 614 | 2044.2 | 0 | 0 | 11 | 95
18:30 | 2660 | 1654.75 | 776.5 | 0 | 47 | 758.52 | 40 | 2594 | 0 | 602 | 2130.2 | 0 | 0 | 9 | 92.5
19:00 | 2854 | 1702.5 | 639 | 0 | 48 | 758.04 | 40 | 2687 | 0 | 590 | 2216.2 | 0 | 0 | 7 | 90
19:30 | 2796 | 1723.5 | 630 | 0 | 44 | 755.39 | 40 | 2768 | 0 | 577 | 2069 | 0 | 0 | 3 | 80
20:00 | 2794 | 1703 | 630 | 0 | 46 | 757.39 | 40 | 2825 | 0 | 497 | 1977 | 0 | 0 | 0 | 70
20:30 | 2651.5 | 1697 | 771.5 | 0 | 46 | 755.695 | 40 | 2919.5 | 0 | 381 | 1810 | 0 | 0 | 0 | 67.5
21:00 | 2509 | 1691 | 913 | 0 | 46 | 754 | 40 | 3014 | 0 | 265 | 1643 | 0 | 0 | 0 | 65
21:30 | 2529 | 1687.5 | 913 | 0 | 46 | 754.5 | 40 | 3072.5 | 0 | 219 | 1404.5 | 0 | 0 | 0 | 53.5
22:00 | 2549 | 1684 | 913 | 0 | 46 | 755 | 40 | 3131 | 0 | 173 | 1166 | 0 | 0 | 0 | 42
22:30 | 2580.5 | 1679.25 | 913 | 0 | 47 | 709 | 40 | 3130.5 | 0 | 120 | 923 | 0 | 0 | 0 | 39
23:00 | 2612 | 1674.5 | 913 | 0 | 48 | 663 | 40 | 3130 | 0 | 67 | 680 | 0 | 0 | 0 | 36
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5321 | 4096.04 | 9417.04 | DAILY GENERATION CURVE
00:30 | 5262.5 | 3925.905 | 9188.405
01:00 | 5204 | 3755.77 | 8959.77 | 05-02-2025
01:30 | 5097.5 | 3602.18 | 8699.68
02:00 | 4991 | 3448.59 | 8439.59
02:30 | 4928.5 | 3335.78 | 8264.28
03:00 | 4866 | 3222.97 | 8088.97
03:30 | 4799 | 3182.745 | 7981.745
04:00 | 4732 | 3142.52 | 7874.52
04:30 | 4676.5 | 3151.975 | 7828.475
05:00 | 4621 | 3161.43 | 7782.43
05:30 | 4734 | 3190.415 | 7924.415
06:00 | 4847 | 3219.4 | 8066.4
06:30 | 5037.1 | 3525.94 | 8563.04
07:00 | 5227.2 | 3832.48 | 9059.68
07:30 | 5261.675 | 4034.425 | 9296.1
08:00 | 5296.15 | 4236.37 | 9532.52
08:30 | 5650.245 | 4295.425 | 9945.67
09:00 | 6004.34 | 4354.48 | 10358.82
09:30 | 5976.51 | 4413.985 | 10390.495
10:00 | 5948.68 | 4473.49 | 10422.17
10:30 | 5944.18 | 4545.785 | 10489.965
11:00 | 5939.68 | 4618.08 | 10557.76
11:30 | 5958.945 | 4809.11 | 10768.055
12:00 | 5978.21 | 5000.14 | 10978.35
12:30 | 6126.765 | 5024.725 | 11151.49
13:00 | 6275.32 | 5049.31 | 11324.63
13:30 | 6123.465 | 4935.575 | 11059.04
14:00 | 5971.61 | 4821.84 | 10793.45
14:30 | 5838.04 | 4815.42 | 10653.46
15:00 | 5704.47 | 4809 | 10513.47
15:30 | 5518.545 | 4737.045 | 10255.59
16:00 | 5332.62 | 4665.09 | 9997.71
16:30 | 5436 | 4611.34 | 10047.34
17:00 | 5539.38 | 4557.59 | 10096.97
17:30 | 5840.54 | 4709.045 | 10549.585
18:00 | 6141.7 | 4860.5 | 11002.2
18:30 | 6386.45 | 4885.52 | 11271.97
19:00 | 6631.2 | 4910.54 | 11541.74
19:30 | 6467 | 4938.89 | 11405.89
20:00 | 6323.5 | 4945.89 | 11269.39
20:30 | 6130 | 4942.195 | 11072.195 |  | Executive Engineer
21:00 | 5936.5 | 4938.5 | 10875 |  | Network Operation Division
21:30 | 5746.5 | 4919.5 | 10666
22:00 | 5556.5 | 4900.5 | 10457
22:30 | 5399.75 | 4742.5 | 10142.25
23:00 | 5243 | 4584.5 | 9827.5

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10978.35 | MW | 12:00 Hr. | Energy Generated |  |  | 239.8572 |  | MKWHr.
| Day Peak Demand |  |  | 11015.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.711 |  | MKWHr.
| Evening Peak Generation |  |  | 11541.74 | MW | 19:00 Hr. | Energy Demand |  |  | 240.5682 |  | MKWHr.
| Evening Peak Demand |  |  | 11635.74 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.7 |  | °C
| Minimum Generation of the Day |  |  | 7782.43 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 807.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 11541.74 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.7431 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 35.776 | 0 | 9.7375 | 0 | 0 | 0.16305 | 0 | 0 | 45.6766 | Gas | 108.9003 | Gas | 390680213.218
| Chattogram Zone |  |  | 5.7705 | 20.8418 | 7.8003 | 0 | 0.964 | 0.14012 | 0 | 0.08928 | 35.6059 | Coal | 59.3917 | Coal | 423793798.7565
| Cumilla Zone |  |  | 17.319 | 0 | 5.828 | 0 | 0 | 0.35232 | 1.0426 | 0 | 24.5419 | HFO | 30.4598 | HFO | 563530237.61
| Mymensingh Zone |  |  | 0.24864 | 0 | 1.9165 | 0 | 0 | 0.22509 | 0 | 0 | 2.3902 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2209 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 0 | 2.4 | 0.11942 | 0 | 0 | 0.47232 | 20.2938 | 0 | 23.2856 | Solar | 3.1768 | Solar | 49317288.416
| Barishal Zone |  |  | 5.9126 | 30.7353 | 0.39653 | 0 | 0 | 0.003225 | 0 | 0 | 37.0476 | Import | 36.8753 | Import | 188579910.35
| Rajshahi Zone |  |  | 16.6527 | 0 | 2.6635 | 0 | 0 | 0.8827 | 15.5389 | 0 | 35.7379 | Wind | 0.08928 | Wind | 1392768
| Rangpur Zone |  |  | 0 | 5.4146 | 1.9981 | 0 | 0 | 0.93797 | 0 | 0 | 8.3507
| Total |  |  | 108.9003 | 59.3917 | 30.4598 | 0 | 0.964 | 3.1768 | 36.8753 | 0.08928 | 239.8572
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 390680213.218 |  | Hydro | 96400
|  |  |  | Coal | 423793798.7565 |  | Solar | 49317288.416
|  |  |  | HFO | 563530237.61 |  | Import | 188579910.35
|  |  |  | HSD | 0 |  | Wind | 1392768
[5 empty] | Total: | 161,73,90,616 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.2938 | Peak Hr Flow | 639.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8788363.706 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.5389 | Peak Hr Flow | 758.04 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 436 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0426 | Peak Hr Flow | 48.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 890 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.8753 | Peak Hr Flow | 1445.04 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4193
|  |  |  | Chattogram |  | 0 |  | 1235
|  |  |  | Cumilla |  | 0 |  | 884
|  |  |  | Mymensingh |  | 90 |  | 994
|  |  |  | Sylhet |  | 0 |  | 397
|  |  |  | Khulna |  | 0 |  | 1225
|  |  |  | Barishal |  | 0 |  | 304
|  |  |  | Rajshahi |  | 0 |  | 1110
|  |  |  | Rangpur |  | 0 |  | 792
|  |  |  | Total |  | 90 |  | 11134
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 742.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1534.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:20 | Sylhet 132/33kV S/S T4 LT is restored.
| 08:22 | 08:30 | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to Load Shift to T4 X-former Informed to NLDC | [7 empty] | 10.0MW load
|  |  | 299724 | [7 empty] | interrup.
| 08:23 | 08:27 | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to Load Shift to T4 X-former Informed to NLDC | [7 empty] | 10.0MW load
|  |  | 299724 | [7 empty] | interrup.
| 08:24 | 20:13 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Shutdown due to Annual Maintenance( Deep Cleaning).
| 08:26 |  | Maniknagar-Siddhirganj 230kV Ckt-1 Scheduled S/D from Maniknagar 230/132kV end Due to
Aircraft obstruction Light installation between Tower no 30 and 31. and from Siddhirganj
230/132kV end Due to Internal work of Maniknagar end
| 08:30 | 13:09 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Scheduled S/D Due to Annual maintenance
dead line checking
| 08:31 | 08:31 | Baroaulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Annual
Deadline checking by Khulsi ss
| 08:31 |  | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual maintenance.
|  | 08:34 | Feni 132/33kV S/S T-1(405T) HT is restored.
|  | 08:34 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 09:01 | 17:29 | Keraniganj-Nawabganj 132kV Ckt-2 Scheduled S/D from Nawabganj 132/33kV end Due to Dead
line Checking and from Keranigonj 230/132/33kV end Due to Dead line checking
| 09:25 |  | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to Annual maintenance
| 09:25 |  | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D Due to Annual maintenance
| 09:36 |  | Madartek 132/33kV S/S GT-02 HT Scheduled S/D Due to Annual Maintenance
| 09:59 | 12:45 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 09:59 | 12:45 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 10:05 | 19:55 | Gopalganj 400/132kV S/S ATR-04 LT Project Work S/D
| 10:06 | 19:54 | Gopalganj 400/132kV S/S ATR-04 HT Project Work S/D
| 10:17 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Scheduled S/D Due to 230/132KV TR-2 B-PH
Oil Senrifusing
| 10:18 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT Scheduled S/D Due to 230/132KV TR-2 B-PH
Oil Senrifusing
| 11:34 | 14:56 | Madanganj-Munsiganj 132 kV Ckt-2 Forced S/D from Madanganj 132/33kV end. and from
Munshiganj 132/33kV end Due to SF6 Gas pressure return valve leakage maintenance on R-
Phase
| 12:00 |  | Day peak generation 10973MW
|  | 12:09 | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) HT is restored.
|  | 12:54 | Faridpur 132/33kV S/S Transformer-3 HT is restored.
| 13:01 | 13:51 | Keranigonj 230/132/33kV S/S TR-2 LT Scheduled S/D Due to 33KV Kalatiya feeder problem
| 13:01 | 13:40 | Keranigonj 230/132/33kV S/S TR-2 HT Scheduled S/D Due to 33KV Kalatiya feeder problem
|  | 13:04 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 13:04 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
| 13:37 | 15:14 | AKSML-Khulshi 132kV Ckt-1 Forced S/D from AKS 132/33kV end Due to Emergency shutdown from
Khulshi to AKSPL 132 kv line Circuit-1 because a balloon shown in tower no. 28 & remove
it from tower. and from Khulshi 132/33kV end Due to Baloon Removing from tower no-28
| 15:27 | 16:16 | Sirajganj 132/33kV S/S Solar Park 1 Forced S/D Due to BCRECL has taken Shutdown due to CB
mechanical problem at 68MW Sirajgonj Solar park End.
| 16:10 | 16:21 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Forced S/D Due to RTU এনালগ ডাটার ডিরেকশন
পরিবর্তন।
| 16:11 | 16:22 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Forced S/D Due to RTU এনালগ ডাটার ডিরেকশন পরিবর্তন
| 17:16 | 19:15 | Chandpur 132/33kV S/S 422T LT Forced S/D Due to Pbs ReD hotaintainence | [7 empty] | 19.0MW load
interrup.
| 17:17 |  | Madartek 132/33kV S/S GT-02 LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 8.0MW load
interrup.
|  | 17:20 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 is restored.
| 17:30 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
|  | 18:00 | Bhulta-Rampura 230 kV Ckt-2 is restored.
| 18:14 |  | Bibiyana South 400 MW Synchronized with remarks:- st
|  | 18:37 | Aminbazar-Kallyanpur 132kV Ckt-2 is restored.
| 19:00 |  | Evening peak Generation is 11541 MW
| 19:03 |  | Bibiyana South 400 MW Tripped with remarks:- GT,ST
| 19:05 |  | Bibiyana South 400 MW Tripped with remarks:- plant
| 20:10 |  | SS Power Synchronized with remarks:- Unit2
| 20:10 |  | SS Power Unit-2 Synchronized with remarks:- None
| 20:10 |  | Bibiyana South 400 MW Synchronized with remarks:- gt
| 22:27 |  | Bibiyana South 400 MW ST was sync.
| 22:27 |  | Bibiyana South 400 MW Synchronized with remarks:- st
| 00:00 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- Due to Maintenance
| 00:39 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- Due to Maintenance
| 02:35 |  | SS Power Unit-2 was forced shutdown due to high water conductivity.
| 05:00 |  | Min. Gen. 7825 MW
| 05:06 | 05:31 | Patuakhali 132/33kV S/S 415T (T-2) LT Tripped showing Earth & Over current relays Due to | [7 empty] | 10.0MW load
|  |  | Amtoli 33 kV Feeder fault ( PBS) | [7 empty] | interrup.
| 05:06 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Tripped showing E/F & Over current relays Due to | [7 empty] | 10.0MW load
|  |  | Amtoli 33kV fault | [7 empty] | interrup.
| 05:55 |  | Bibiyana-3 400MW was shutdown.
| 07:19 |  | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Station Aux-1 transformer fuse set | [7 empty] | 12.0MW load
|  |  | replace and jumper wire connection | [7 empty] | interrup.
| 07:20 |  | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Station Aux-1 transformer fuse set | [7 empty] | 12.0MW load
|  |  | replace and jumper wire connection | [7 empty] | interrup.
| 07:24 |  | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to Red Hot Works to 33kv bus ds | [7 empty] | 20.0MW load
interrup.
| 07:24 |  | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Red Hot Works to 33kv bus ds | [7 empty] | 20.0MW load
interrup.
| 07:47 |  | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 07:50 |  | Rampal 1320 MW (BIFPCL) unit-2 was forced shutdown due to boiler problem.
| 07:50 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 1224227.28 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9514800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8529000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 253 | 6983971 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 610218 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7560940 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 737640 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 459840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 626015 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 534579 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 343800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 437400 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 600600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 581300 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 26 | 405120 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 39142 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2351952 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 966720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 13 | 29760 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2340000 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 163052 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 636480 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.654 | 2195 | 45676556.28
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 34176.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119475 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 595200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5287091 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 91 | 1385854 | -
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 23 | 147225 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 84 | 629295 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 84 | 798720 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 4 | 483360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 347520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 65 | 617236 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 32974 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 102 | 1085600 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 857280 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 568309 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 108 | 700873 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 17089089 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 7 | 89280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 156 | 3752727.27 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1838 | 35605925.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4615000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 255 | 5340000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 28 | 723456 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 28 | 596640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 143 | 3445818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 40 | 1104706 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1615854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 40 | 349232 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1081470 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 163 | 1261440 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1042560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 522163 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 411930 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 27360 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 742560 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1309440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 352318 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1378.2 | 24541947
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 5 | 248640 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 59 | 1075200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 199200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 216190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 108240 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 533880 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 114 | 2390250
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 714000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3759873 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 816120 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116688 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 717792 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1920960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 219000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 544944 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7231000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 9135000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 80 | 2045500 | Preparation for ST startup
Sylhet Area Total |  |  |  |  | 2368.568 | 1106 | 27220877
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 639 | 20293818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 30 | 57600 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 30 | 61824 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 472320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 290 | 2400000 | Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 989 | 23285562
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 13728 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 141413 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 3206000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 24583272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2565160 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 36 | 382800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6152000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3225 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1698 | 37047598.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 33 | 107926 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 21 | 83406 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 38 | 226114 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 4142091 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 172 | 3749909 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 391 | 8686473 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 291819 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 74250 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 514382 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 902080 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 409824 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 127968 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 758.04 | 15538909 | Under Maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 291000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 566740 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1788.54 | 35737851
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 67 | 1555636 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 3859000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 895171 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29456.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1102881 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 136673 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 771840 | -
Rangpur Area Total |  |  |  |  | 950 | 435 | 8350657.16
Eastern Grid Total |  |  |  |  | 16772.132 | 6631.2 | 135435556.15
Western Grid Total |  |  |  |  | 10294.5 | 4910.54 | 104421668.89
National Grid Total |  |  |  |  | 27066.632 | 11541.74 | 239857225.04
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-02-2025 | during | 06-02-2025 | during | 06-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 61 | 0 | 97.3 | 97.3 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 404 | 400.75 | 400.75 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 283 | 253 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 26 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 16.5 | 12 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 17 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 28 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 26 | 26 | 52.19 | 52.19 | 26 | 26 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 90 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 13 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 36 | 36.09 | 36.09 | 36.09 | 36.09 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.654 | 2068.5 | 2195 | 4598.96 | 4570.96 | 2797.94 | 2769.94
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 227 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 91 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 23 | 0 | 40 | 0 | 40 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 34 | 84 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 84 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 4 | 2 | 22 | 2 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 25 | 60 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 32 | 65 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 56 | 102 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 108 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 590 | 612 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 10 | 7 | 3 | 5 | 3 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 157 | 156 | 270 | 270 | 300 | 300 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1552 | 1838 | 3097.72 | 3139.72 | 2515.72 | 2557.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 185 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 250 | 255 | 260 | 260 | 260 | 260 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 28 | 46.94 | 46.94 | 30 | 30 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 22 | 28 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 115 | 143 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 40 | 40 | 40 | 51 | 40 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 113 | 125 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 32 | 40 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 163 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 48 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 75 | 113 | 113 | 34 | 34 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 37 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1110.2 | 1378.2 | 1982.97 | 1938.97 | 1754.2 | 1710.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-02-2025 | during | 06-02-2025 | during | 06-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 5 | 210 | 210 | 25 | 25 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 59 | 200 | 200 | 59 | 59 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.51 | 0 | 39.17 | 0 | 39.17 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 150.51 | 114 | 642.37 | 601.5 | 194.37 | 153.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 36 | 40 | 40 | 36 | 36 | machine problem
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 0 | 30 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 370 | 380 | 380 | 0 | 0 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 55 | 80 | 320 | 320 | 290 | 290 | Authority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1097 | 1106 | 1440 | 1410 | 972 | 942
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 914 | 639 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 30 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 30 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78.33 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 290 | 1234 | 1234 | 0 | 0 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 992.33 | 989 | 3170 | 3095 | 1726 | 1651
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 3 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 132 | 132 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1080 | 1090 | 1244 | 1244 | 900 | 900 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 36 | 150 | 150 | 17 | 17 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1649.53 | 1698 | 2068.12 | 2067.12 | 1588 | 1587
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 33 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 4 | 21 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 10 | 38 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 162 | 168 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 168 | 172 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 397 | 391 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 20 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 34 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 49 | 97 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.36 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 754.92 | 758.04 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.8 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1810.58 | 1788.54 | 2584.79 | 2430.24 | 2178.01 | 2023.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 68 | 67 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 165 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 87 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 4.1 | 0 | 4.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 75 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 132 | 0 | 157.28 | 0 | 157.28 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 547.7 | 435 | 649.38 | 468 | 649.38 | 468
System Total |  |  |  |  | 27884.66 | 27066.632 | 10978.35 | 11541.74 | 20234.31 | 19721.51 | 14375.62 | 13862.82
Forecast Scenario (06-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9360 |  | 0 |  | 9360
|  |  |  | 1:00 | 8780 |  | 0 |  | 8780
|  |  |  | 2:00 | 8300 |  | 0 |  | 8300
|  |  |  | 3:00 | 8000 |  | 0 |  | 8000
|  |  |  | 4:00 | 7800 |  | 0 |  | 7800
|  |  |  | 5:00 | 7750 |  | 0 |  | 7750
|  |  |  | 6:00 | 8090 |  | 0 |  | 8090
|  |  |  | 7:00 | 9030 |  | 0 |  | 9030
|  |  |  | 8:00 | 9800 |  | 0 |  | 9800
|  |  |  | 9:00 | 10350 |  | 0 |  | 10350
|  |  |  | 10:00 | 10400 |  | 0 |  | 10400
|  |  |  | 11:00 | 10450 |  | 0 |  | 10450
|  |  |  | 12:00 | 11000 |  | 0 |  | 11000
|  |  |  | 13:00 | 11200 |  | 0 |  | 11200
|  |  |  | 14:00 | 10600 |  | 0 |  | 10600
|  |  |  | 15:00 | 10250 |  | 0 |  | 10250
|  |  |  | 16:00 | 10070 |  | 0 |  | 10070
|  |  |  | 17:00 | 10010 |  | 0 |  | 10010
|  |  |  | 18:00 | 10800 |  | 0 |  | 10800
|  |  |  | 18:30 | 10200 |  | 0 |  | 10200
|  |  |  | 19:00 | 11500 |  | 0 |  | 11500
|  |  |  | 19:30 | 11200 |  | 0 |  | 11200
|  |  |  | 20:00 | 10950 |  | 0 |  | 10950
|  |  |  | 21:00 | 10750 |  | 0 |  | 10750
|  |  |  | 22:00 | 10450 |  | 0 |  | 10450
|  |  |  | 23:00 | 9950 |  | 0 |  | 9950
Probable Maximum Temperature: |  |  | 29.20°C
Probable Maximum Demand at Day Peak: |  |  | 11000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 235.64 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:22 hrs on 06-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7612.89 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3431.1 | MW
i) Dhaka area |  |  | 4192.89 |  | MW | i) Khulna area |  |  |  | 1225 | MW
ii) Chattogram area |  |  | 1235 |  | MW | ii) Barishal area |  |  |  | 304.5 | MW
iii) Cumilla area |  |  | 884 |  | MW | iii) Rajshahi area |  |  |  | 1109.6 | MW
iv) Mymensingh area |  |  | 904 |  | MW | iv) Rangpur area |  |  |  | 792 | MW
v) Sylhet area |  |  | 397 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11043.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 09:00 | 67 | Jaldhaka | 63 | 18:30 | 133 | Purbachal | 13 | 13:00
2 | AKSML | 33 | 19:00 | 68 | Jamalpur | 83 | 07:00 | 134 | Purbasadipur | 122 | 12:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 107 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 77 | 13:00 | 70 | Jhenaidah | 96 | 18:30 | 136 | Rahim | 26 | 23:00
5 | Agrabad | 68 | 18:00 | 71 | Joydebpur | 138 | 18:30 | 137 | Rajbari | 58 | 18:30
6 | Amnura | 49 | 08:00 | 72 | Joypurhat | 53 | 08:00 | 138 | Rajendrapur | 96 | 18:30
7 | Ashuganj | 65 | 15:00 | 73 | Juldah | 12 | 13:00 | 139 | Rajshahi | 91 | 13:00
8 | BSRM | 195 | 23:00 | 74 | KSRM | 32 | 04:00 | 140 | Rajshahi-230 | 43 | 13:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 229 | 12:00 | 141 | Ramganj | 86 | 18:30
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 18:30 | 142 | Rampur | 28 | 18:00
11 | Bakulia | 72 | 13:00 | 77 | Kallyanpur | 57 | 13:00 | 143 | Rangamati | 13 | 18:30
12 | Banani | 38.6 | 09:00 | 78 | Kalurghat | 30 | 10:00 | 144 | Rangpur | 96 | 18:30
13 | Bangabhaban | 9 | 11:00 | 79 | Kamrangirchar | 57.2 | 11:00 | 145 | Ruppur | 5.2 | 15:00
14 | Barapukuria | 63 | 08:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 0 | 00:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 103 | 13:00 | 147 | Saidpur | 103 | 09:00
16 | Barishal | 72 | 13:00 | 82 | Keranigonj | 63 | 13:00 | 148 | Satkhira | 94 | 18:30
17 | Barishal-230 | 74 | 19:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 78 | 14:00
18 | Baroaulia | 54 | 13:00 | 84 | Khulna | 69 | 13:00 | 150 | Savar | 193 | 12:00
19 | Baroirhat | 53 | 18:00 | 85 | Khulshi | 133 | 18:00 | 151 | SevenRings | 15.37 | 00:00
20 | Bashundhara | 135 | 13:00 | 86 | Kishoreganj | 126 | 18:30 | 152 | ShahCement | 36 | 22:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 280 | 18:00 | 153 | Shahjadpur | 64 | 18:30
22 | Beanibazar | 44 | 18:30 | 88 | Kulaura | 27 | 19:00 | 154 | Shahjibazar | 88 | 18:30
23 | Benapole | 53 | 08:00 | 89 | Kurigram | 62 | 08:00 | 155 | Shahmirpur | 42 | 00:00
24 | Bhaluka | 120 | 09:00 | 90 | Kushtia | 96 | 18:30 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 34 | 18:30 | 91 | Lalbag | 59 | 13:00 | 157 | Sherpur | 112 | 00:00
26 | Bhangura | 28 | 18:30 | 92 | Lalmonirhat | 50 | 08:00 | 158 | Shikalbaha | 21 | 13:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 18.3 | 15:00 | 159 | Shitalakhya | 64.9 | 12:00
28 | Bhulta | 248 | 12:00 | 94 | Madanganj | 18 | 13:00 | 160 | Sholosohor | 38 | 12:00
29 | Bog-Sherpur | 68 | 13:00 | 95 | Madaripur | 69 | 13:00 | 161 | Shyampur | 144 | 13:00
30 | Bogura | 122 | 18:30 | 96 | Madartek | 49.39 | 21:00 | 162 | Siddhirganj | 101 | 12:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madunaghat | 37 | 18:30 | 163 | Sirajganj | 92 | 19:30
32 | Brahmanbaria | 109 | 19:30 | 98 | Magura | 44 | 13:00 | 164 | Sonargaon | 83 | 10:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 60 | 08:00 | 165 | Sreemongol | 49 | 18:30
34 | Chandpur | 48 | 20:00 | 100 | Manikganj | 109 | 18:30 | 166 | Sreepur | 82 | 09:00
35 | Chandraghona | 25 | 19:00 | 101 | Maniknagar | 54 | 13:00 | 167 | Srinagar | 30.24 | 21:00
36 | Chapai | 70 | 13:00 | 102 | Matarbari | 37 | 18:00 | 168 | Sunamganj | 41 | 18:30
37 | Charsaidpur | 41 | 06:00 | 103 | Matuail | 52 | 12:00 | 169 | Sylhet | 30 | 18:00
38 | Chauddagram | 46 | 13:00 | 104 | Millgate | 68 | 11:00 | 170 | Sylhet-132 | 80 | 18:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 102 | 18:30 | 171 | TK | 23 | 20:00
40 | Chowmuhani | 146 | 18:30 | 106 | Mirsorai | 9 | 18:30 | 172 | Tangail | 156 | 07:00
41 | Chuadanga | 75 | 18:30 | 107 | Mirzapur | 38 | 14:00 | 173 | Thakurgaon | 77 | 18:30
42 | Coxsbazar | 112 | 18:00 | 108 | Mithapukur | 74 | 18:30 | 174 | Tongi | 80 | 18:30
43 | Cumilla(N) | 126 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 25 | 08:00
44 | Cumilla(S) | 119 | 14:00 | 110 | Mogbazar | 106.6 | 15:00 | 176 | Ullon | 37 | 13:00
45 | Daudkandi | 109 | 19:00 | 111 | Mongla | 38 | 16:00 | 177 | Uttara | 63 | 13:00
46 | Dhaka | 34 | 12:00 | 112 | Motijheel | 27 | 13:00 | 178 | UttaraNew | 33 | 13:00
47 | Dhamrai | 104 | 09:00 | 113 | Muktagacha | 26 | 07:00 | 179 | Zigatola | 54 | 13:00
48 | Dhanmondi | 102 | 13:00 | 114 | Munshiganj | 70 | 13:00
49 | Dohazari | 70 | 19:00 | 115 | Mymensingh | 167 | 12:00
50 | Faridpur | 110 | 18:30 | 116 | Naogaon | 110 | 09:00
51 | Fatullah | 79 | 12:00 | 117 | Narail | 43 | 18:30
52 | Fenchuganj | 25 | 18:00 | 118 | Narinda | 58 | 13:00
53 | Feni | 66 | 18:00 | 119 | Narshingdi | 161 | 20:00
54 | GPH | 85 | 08:00 | 120 | Natore | 110 | 18:30
55 | Ghatail | 50 | 07:00 | 121 | Nawabganj | 30.6 | 13:00
56 | Ghorashal | 15 | 19:30 | 122 | Netrakona | 133 | 08:00
57 | Ghorashal-230 | 58 | 18:00 | 123 | New | 69 | 12:00
58 | Goalpara | 24 | 19:00 | 124 | Niamatpur | 87 | 10:00
59 | Gollamari | 50 | 13:00 | 125 | Noapara | 36 | 18:30
60 | Gopalganj | 79.6 | 18:30 | 126 | PHP | 5 | 17:00
61 | Gulshan | 80 | 13:00 | 127 | Pabna | 67 | 18:30
62 | Halishahar | 52 | 18:00 | 128 | Palashbari | 95 | 09:00
63 | HaripurSBU | 158 | 01:00 | 129 | Panchagarh | 43 | 18:00
64 | Hasnabad | 72 | 11:00 | 130 | Patuakhali | 56 | 21:00
65 | Hathazari | 55 | 18:00 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 61 | 19:30 | 132 | Postogola | 44 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 04:00 | 394 | 12:00 | Payra | 417 | 03:00 | 409 | 12:00
Ashuganj | 415 | 4:00 | 393 | 12:00 | Rahanpur | 419 | 04:00 | 396 | 08:00
Bhulta | 413 | 04:00 | 393 | 12:00 | Rampal | 412 | 04:00 | 389 | 12:00
Bibiana | 405 | 02:00 | 398 | 12:00
BIPTC | 407 | 03:00 | 391 | 12:00
Bogura | 417 | 02:00 | 391 | 08:00
Gopalganj | 414 | 04:00 | 396 | 12:00
Kaliakoir | 394 | 02:00 | 381 | 12:00
Madunaghat | 411 | 19:00 | 403 | 17:00
Meghnaghat | 410 | 04:00 | 395 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 04:00 | 227 | 12:00 | Keranigonj | 237 | 04:00 | 226 | 12:00
AKSML | 240 | 18:30 | 230 | 01:00 | Khulna(S) | 240 | 03:00 | 223 | 13:00
Aminbazar | 237 | 02:00 | 227 | 12:00 | Madunaghat | 238 | 18:30 | 230 | 00:00
Ashuganj | 243 | 02:00 | 234 | 12:00 | Madunaghat-400 | 238 | 19:00 | 231 | 00:00
Ashuganj-400 | 243 | 02:00 | 234 | 12:00 | Maniknagar | 237 | 06:00 | 227 | 12:00
Baghabari | 239 | 01:00 | 229 | 11:00 | Meghnaghat | 244 | 21:00 | 235 | 12:00
Barapukuria | 227 | 02:00 | 219 | 07:00 | Meghnaghat-400 | 240 | 04:00 | 230 | 12:00
Barapukuria-230 | 227 | 02:00 | 219 | 07:00 | Mirsorai | 242 | 18:30 | 223 | 11:00
Barishal | 245 | 04:00 | 237 | 12:00 | Rajshahi | 240 | 05:00 | 223 | 12:00
Bheramara | 239 | 03:00 | 223 | 12:00 | Rampal | 237 | 02:00 | 221 | 12:00
Bhulta | 239 | 03:00 | 228 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 235 | 01:00 | 223 | 01:00 | Rampura | 240 | 04:00 | 227 | 12:00
BIPTC | 241 | 04:00 | 224 | 12:00 | Shikalbaha | 237 | 18:00 | 223 | 12:00
Bogura | 242 | 04:00 | 229 | 08:00 | Shyampur | 238 | 02:00 | 227 | 12:00
Bogura-400 | 240 | 02:00 | 226 | 08:00 | Siddhirganj | 237 | 08:00 | 232 | 14:00
Borhanuddin | 247 | 02:00 | 243 | 01:00 | Sirajgonj | 247 | 04:00 | 239 | 12:00
BSRM | 239 | 18:00 | 229 | 23:00 | Sreepur | 240 | 03:00 | 230 | 12:00
Cumilla(N) | 236 | 19:00 | 229 | 16:00 | Tongi | 234 | 03:00 | 224 | 12:00
Faridpur | 246 | 04:00 | 234 | 12:00
Fenchuganj | 237 | 00:00 | 232 | 18:00
Ghorashal | 240 | 08:00 | 230 | 00:00
Ghorashal-230 | 238 | 04:00 | 226 | 12:00
Gopalganj | 245 | 02:00 | 232 | 11:00
GPH | 238 | 19:00 | 229 | 23:00
Haripur | 239 | 04:00 | 228 | 12:00
Hasnabad | 235 | 18:30 | 228 | 15:00
Hathazari | 238 | 13:00 | 230 | 02:00
Ishurdi | 242 | 04:00 | 226 | 12:00
Jhenaidah | 239 | 04:00 | 219 | 12:00
Kaliakoir | 235 | 04:00 | 225 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 128 | 12:00 | Magura | 138 | 04:00 | 126 | 12:00
Agargaon | 139 | 04:00 | 131 | 12:00 | Mahasthangarh | 136 | 03:00 | 128 | 07:00
Agrabad | 137 | 18:30 | 131 | 00:00 | Manikganj | 136 | 01:00 | 132 | 16:00
AKS | 135 | 18:30 | 128 | 04:00 | Maniknagar | 136 | 05:00 | 127 | 12:00
Aminbazar | 136 | 00:00 | 130 | 13:00 | Matarbari | 129 | 13:00 | 121 | 04:00
Amnura | 142 | 20:00 | 130 | 08:00 | Matuail | 136 | 02:00 | 130.8 | 12:00
Ashuganj | 143 | 05:00 | 139 | 12:00 | Millgate | 138 | 01:00 | 129 | 12:00
Bagerhat | 137 | 04:00 | 125 | 12:00 | Mirpur | 137 | 03:00 | 129 | 16:00
Bajitpur | 135 | 04:00 | 130 | 12:00 | Mirzapur | 135 | 02:00 | 129 | 07:00
Bakulia | 137 | 13:00 | 130 | 23:00 | Mithapukur | 134 | 19:30 | 119 | 08:00
Banani | 138 | 04:00 | 128 | 12:00 | MI_Cement | 138 | 04:00 | 131 | 12:00
Bangabhaban | 136 | 03:00 | 127 | 13:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 02:00 | 129 | 07:00 | Mogbazar | 138 | 02:00 | 130 | 12:00
Barguna | 137 | 19:00 | 134 | 14:00 | Mongla | 134 | 04:00 | 123 | 12:00
Barishal | 136 | 04:00 | 130 | 12:00 | Motijheel | 136 | 03:00 | 127 | 13:00
Barishal-230 | 136 | 02:00 | 130 | 12:00 | Muktagacha | 127 | 00:00 | 118 | 12:00
Baroaulia | 136 | 19:00 | 132 | 01:00 | Munshiganj | 137 | 03:00 | 130 | 12:00
Baroirhat | 135 | 18:00 | 129 | 00:00 | Mymensingh | 125 | 00:00 | 116 | 06:00
Bashundhara | 137 | 01:00 | 129 | 12:00 | Naogaon | 135 | 01:00 | 127 | 07:00
BashundharaCement | 135 | 18:00 | 131 | 12:00 | Narail | 139 | 03:00 | 126 | 12:00
Beanibazar | 148 | 06:00 | 134 | 12:00 | Narinda | 136 | 05:00 | 127 | 12:00
Benapole | 138 | 02:00 | 122 | 12:00 | Narshingdi | 135 | 03:00 | 126 | 12:00
Bhaluka | 132 | 13:00 | 120 | 12:00 | Natore | 137 | 01:00 | 129 | 08:00
Bhandaria | 134 | 02:00 | 127 | 12:00 | Nawabganj | 139 | 03:00 | 131 | 12:00
Bhangura | 136 | 00:00 | 130 | 11:00 | Netrakona | 125 | 04:00 | 115 | 12:00
Bheramara | 138 | 03:00 | 129 | 12:00 | New | 137 | 00:00 | 130 | 19:00
Bheramara(GK) | 137 | 04:00 | 129 | 12:00 | Niamatpur | 139 | 01:00 | 132 | 07:00
Bhulta | 131 | 06:00 | 125 | 12:00 | Noapara | 139 | 04:00 | 125 | 12:00
Bog-Sherpur | 138 | 04:00 | 130 | 07:00 | Pabna | 137 | 02:00 | 126 | 12:00
Bogura | 138 | 03:00 | 131 | 07:00 | Palashbari | 133 | 20:00 | 124 | 07:00
Bogura-230 | 138 | 02:00 | 130 | 08:00 | Panchagarh | 141 | 14:00 | 129 | 07:00
Brahmanbaria | 136 | 08:00 | 132 | 12:00 | Patuakhali | 136 | 01:00 | 134 | 07:00
Cantonment | 138 | 02:00 | 131 | 12:00 | Payra | 137 | 02:00 | 134 | 11:00
Chandpur | 141 | 08:00 | 127 | 00:00 | PHP | 134 | 08:00 | 128 | 00:00
Chandraghona | 138 | 19:00 | 133 | 00:00 | Postogola | 140 | 01:00 | 133 | 12:00
Chapai | 140 | 02:00 | 131 | 11:00 | Purbachal | 138 | 03:00 | 129 | 12:00
Charsaidpur | 137 | 01:00 | 131 | 12:00 | Purbasadipur | 134 | 14:00 | 123 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 08:00 | 131 | 00:00 | Rahanpur | 140 | 00:00 | 134 | 07:00
Chhatak | 138 | 03:00 | 132 | 12:00 | Rahanpur-400 | 142 | 02:00 | 134 | 08:00
Chowmuhani | 133 | 08:00 | 125 | 00:00 | Rahim | 136 | 04:00 | 130 | 12:00
Chuadanga | 140 | 22:00 | 126 | 12:00 | Rajbari | 136 | 02:00 | 129 | 12:00
Coxsbazar | 127 | 14:00 | 122 | 00:00 | Rajendrapur | 136 | 20:00 | 128 | 12:00
Cumilla(N) | 138 | 09:00 | 134 | 00:00 | Rajshahi | 138 | 19:00 | 129 | 07:00
Cumilla(S) | 136 | 03:00 | 129 | 10:00 | Rajshahi-230 | 140 | 04:00 | 127 | 12:00
Daudkandi | 135 | 20:00 | 130 | 12:00 | Ramganj | 136 | 18:30 | 124 | 00:00
Dhaka | 136 | 03:00 | 129 | 12:00 | Rampur | 137 | 18:30 | 130 | 07:00
Dhamrai | 134 | 03:00 | 129 | 15:00 | Rampura | 137 | 02:00 | 129 | 12:00
Dhanmondi | 138 | 05:00 | 131 | 12:00 | Rangamati | 137 | 19:00 | 132 | 00:00
Dohazari | 136 | 18:30 | 128 | 00:00 | Rangpur | 133 | 14:00 | 119 | 08:00
Faridpur | 136 | 04:00 | 130 | 12:00 | Ruppur | 140 | 04:00 | 131 | 12:00
Fatullah | 139 | 04:00 | 132 | 12:00 | Saidpur | 134 | 20:00 | 121 | 08:00
Fenchuganj | 144 | 01:00 | 138 | 11:00 | Satkhira | 137 | 05:00 | 125 | 07:00
Feni | 135 | 19:00 | 128 | 12:00 | Satmasjid | 138 | 02:00 | 130 | 12:00
Ghatail | 128 | 00:00 | 119 | 07:00 | Savar | 136 | 20:00 | 128 | 16:00
Ghorashal | 140 | 17:00 | 136 | 12:00 | SevenRings | 142 | 02:00 | 136 | 12:00
Goalpara | 137 | 02:00 | 128 | 12:00 | ShahCement | 137 | 01:00 | 131 | 12:00
Gollamari | 139 | 04:00 | 128 | 12:00 | Shahjadpur | 142 | 03:00 | 135 | 10:00
Gopalganj | 138 | 05:00 | 128 | 12:00 | Shahjibazar | 141 | 06:00 | 135 | 12:00
Gopalganj-400 | 138 | 04:00 | 131 | 12:00 | Shahmirpur | 139 | 18:30 | 130 | 13:00
Gulshan | 136 | 04:00 | 128 | 12:00 | Shariatpur | 138 | 04:00 | 130 | 12:00
Halishahar | 137 | 19:00 | 131 | 00:00 | Sherpur | 124 | 19:00 | 111 | 06:00
Haripur | 136 | 04:00 | 130 | 12:00 | Shikalbaha | 127 | 19:00 | 120 | 00:00
HaripurSBU | 136 | 03:00 | 130 | 12:00 | Shikalbaha-230 | 139 | 19:00 | 131 | 23:00
Hasnabad | 138 | 19:00 | 133 | 11:00 | Shitalakhya | 138 | 04:00 | 131 | 12:00
Hathazari | 139 | 18:00 | 133 | 15:00 | Sholosohor | 137 | 19:00 | 132 | 16:00
Ishurdi | 141 | 04:00 | 132 | 12:00 | Shyampur | 138 | 04:00 | 133 | 11:00
Jaldhaka | 133 | 20:00 | 121 | 07:00 | Shyampur-230 | 138 | 04:00 | 132 | 12:00
Jamalpur | 126 | 00:00 | 112 | 06:00 | Siddhirganj | 136 | 01:00 | 131 | 12:00
Jashore | 136 | 03:00 | 124 | 08:00 | Sirajganj | 139 | 03:00 | 130 | 16:00
Jhenaidah | 139 | 03:00 | 124 | 12:00 | Sonargaon | 134 | 03:00 | 129 | 12:00
Jhenaidah-230 | 140 | 03:00 | 127 | 12:00 | Sreemongol | 141 | 04:00 | 135 | 12:00
Joydebpur | 140 | 18:30 | 130 | 12:00 | Sreepur | 130 | 03:00 | 123 | 12:00
Joypurhat | 135 | 01:00 | 124 | 11:00 | Srinagar | 140 | 04:00 | 132 | 12:00
Juldah | 139 | 18:30 | 130 | 23:00 | SSM | 140 | 18:30 | 134 | 22:00
Kabirpur | 139 | 18:00 | 128 | 12:00 | Sunamganj | 138 | 01:00 | 131 | 18:00
Kachua | 138 | 18:30 | 129 | 00:00 | Sylhet | 140 | 02:00 | 134 | 12:00
Kaliakoir | 140 | 00:00 | 130 | 12:00 | Sylhet-132 | 140 | 02:00 | 134 | 12:00
Kallyanpur | 134 | 04:00 | 128 | 12:00 | Tangail | 129 | 00:00 | 123 | 12:00
Kalurghat | 137 | 18:00 | 132 | 00:00 | Thakurgaon | 140 | 14:00 | 126 | 07:00
Kamrangirchar | 139 | 01:00 | 126 | 12:00 | TK | 138 | 18:00 | 133 | 00:00
Kaptai | 139 | 19:00 | 135 | 1:00 | Tongi | 138 | 03:00 | 131 | 12:00
Kazla | 136 | 04:00 | 127 | 13:00 | Ullahpara | 139 | 03:00 | 131 | 11:00
Keranigonj | 138 | 01:00 | 131 | 12:00 | Ullon | 137 | 06:00 | 128 | 12:00
Khagrachori | 135 | 18:00 | 132 | 00:00 | Uttara | 137 | 04:00 | 129 | 15:00
Khulna | 138 | 04:00 | 125 | 13:00 | UttaraNew | 139 | 03:00 | 130 | 11:00
Khulna(S) | 139 | 03:00 | 128 | 12:00 | Zigatola | 140 | 05:00 | 132 | 13:00
Khulshi | 136 | 18:30 | 129 | 07:00
Kishoreganj | 131 | 03:00 | 125 | 09:00
Kodda | 138 | 17:00 | 131 | 06:00
KSRM | 138 | 19:30 | 132 | 00:00
Kulaura | 141 | 03:00 | 138 | 11:00
Kurigram | 133 | 04:00 | 117 | 08:00
Kushtia | 135 | 02:00 | 128 | 12:00
Lalbag | 137 | 07:00 | 132 | 11:00
Lalmonirhat | 130 | 20:00 | 120 | 07:00
Madanganj | 135 | 18:00 | 131 | 12:00
Madaripur | 136 | 05:00 | 130 | 12:00
Madartek | 137 | 04:00 | 128 | 12:00
Madunaghat | 136 | 14:00 | 132 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-02-2025 | [28 empty] | Date: | 05-02-2025 | [28 empty] | Date: | 05-02-2025 | [28 empty] | Date: | 05-02-2025 | [28 empty] | Date: | 05-02-2025 | [19 empty] | Date: | 05-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [19 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 78 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 317 | 0 | 0 | 0 | 31 | 332 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 197 | 0 | 0 | 110 | 22 | 201 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 295 | 230 | 375 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 18 | 0 | 0 | 6 | 5321 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 179 | 0 | 414 | 0 | 0 | 2.5 | 160 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 136 | 110 | 0 | 0 | 1060 | 0 | 4096.04 | 9417.04 | 91.46
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 270 | 0 | 0 | 0 | 31 | 331 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 902 | 0 | 51 | 0 | 197 | 0 | 0 | 260 | 22 | 183 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 280 | 230 | 375 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 18 | 18 | 0 | 0 | 6 | 5204 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 152 | 0 | 386 | 0 | 0 | 2.5 | 158 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 136 | 110 | 0 | 0 | 920 | 0 | 3755.77 | 8959.77 | 91.46
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 273 | 0 | 0 | 0 | 31 | 333 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 197 | 0 | 0 | 265 | 22 | 183 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 32 | 285 | 170 | 375 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 0 | 20 | 0 | 0 | 6 | 4991 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 125 | 0 | 392 | 0 | 0 | 2.5 | 160 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 136 | 110 | 0 | 0 | 780 | 0 | 3448.59 | 8439.59 | 91.46
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 301 | 0 | 0 | 0 | 32 | 330 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 158 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 197 | 0 | 0 | 265 | 22 | 187 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 295 | 150 | 375 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4866 | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 117 | 0 | 396 | 0 | 0 | 2.5 | 160 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 136 | 110 | 0 | 0 | 750 | 0 | 3222.97 | 8088.97 | 91.46
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 300 | 0 | 0 | 0 | 32 | 260 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 158 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 197 | 0 | 0 | 265 | 22 | 183 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 305 | 150 | 375 | 36 | 30 | 0 | 5 | 120 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4732 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 119 | 0 | 321 | 0 | 0 | 2.5 | 157 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 110 | 0 | 0 | 750 | 0 | 3142.52 | 7874.52 | 91.46
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 310 | 0 | 0 | 0 | 32 | 260 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 158 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 753 | 0 | 51 | 0 | 197 | 0 | 0 | 265 | 23 | 183 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 300 | 150 | 333 | 36 | 30 | 0 | 5 | 120 | 23 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4621 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 119 | 0 | 340 | 0 | 0 | 2.5 | 155 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 110 | 0 | 0 | 750 | 0 | 3161.43 | 7782.43 | 91.45
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 365 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 370 | 312 | 0 | 0 | 0 | 32 | 328 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 158 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 851 | 0 | 51 | 0 | 148 | 0 | 0 | 265 | 22 | 177 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 300 | 150 | 333 | 36 | 30 | 0 | 5 | 163 | 23 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4847 | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 118 | 0 | 354 | 0 | 0 | 2.5 | 155 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 110 | 0 | 0 | 800 | 0 | 3219.4 | 8066.4 | 91.45
07:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 66 | 410 | 0 | 0 | 0 | 0 | 0 | 55 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 325 | 0 | 0 | 0 | 32 | 325 | 0 | 0 | 1 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1000 | 1 | 51 | 0 | 88 | 0 | 0 | 265 | 23 | 218 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 2 | 0 | 320 | 105 | 375 | 36 | 30 | 0 | 5 | 163 | 23 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 9 | 36 | 20 | 0 | 0.2 | 2 | 5227.2 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.55 | 0 | 0 | 555.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.11 | 169 | 0 | 0 | 0 | 110 | 0 | 414 | 0 | 0 | 2.5 | 155 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 0 | 270 | 6 | 136 | 110 | 0 | 0 | 920 | 0 | 3832.48 | 9059.68 | 91.45
08:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 65 | 401 | 0 | 0 | 20 | 20 | 0 | 88 | 32 | 0 | 0 | 8 | 135 | 22 | 0 | 420 | 323 | 0 | 0 | 35 | 32 | 319 | 0 | 0 | 4 | 0 | 19 | 22 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 1 | 40 | 3 | 10 | 157 | 36 | 0 | 21 | 0 | 14 | 226 | 0 | 0 | 0 | 584 | 6 | 51 | 43 | 88 | 0 | 0 | 260 | 22 | 224 | 31 | 38 | 50 | 25 | 10 | 17 | 0 | 40 | 0 | 14 | 0 | 325 | 54 | 370 | 33 | 30 | 0 | 5 | 163 | 23 | 0 | 79 | 30 | 0 | 18 | 0 | 12 | 9 | 56 | 10 | 0 | 7.15 | 0 | 5296.15 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.73 | 0 | 0 | 683.8 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 16 | 0 | 5.77 | 156 | 0 | 0 | 0 | 109 | 0 | 414 | 0 | 0.54 | 2.5 | 152 | 69 | 65 | 4 | 17 | 0 | 0 | 0.9 | 22 | 0.13 | 0 | 307 | 5 | 136 | 110 | 0 | 0 | 1110 | 17 | 4236.37 | 9532.52 | 91.44
09:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 62 | 401 | 0 | 0 | 35 | 34 | 0 | 114 | 48 | 0 | 28 | 45 | 162 | 25 | 0 | 420 | 303 | 0 | 0 | 35 | 17 | 316 | 0 | 0 | 9 | 0 | 16.5 | 6 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 2 | 40 | 41 | 2 | 157 | 72 | 0 | 36 | 0 | 86 | 226 | 0 | 0 | 0 | 585 | 11 | 40 | 100 | 88 | 0 | 0 | 260 | 23 | 222 | 28 | 115 | 50 | 113 | 28 | 17 | 0 | 44 | 25 | 30 | 0 | 300 | 55 | 370 | 33 | 30 | 0 | 5 | 163 | 23 | 0 | 79 | 30 | 0 | 18 | 0 | 35 | 9 | 56 | 5 | 1 | 16.84 | 0 | 6004.34 | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.47 | 0 | 0 | 758.1 | 0 | 0 | 0 | 0 | 32 | 0 | 25 | 0 | 0 | 30 | 40 | 0 | 20.62 | 150 | 0 | 0 | 0 | 109 | 0 | 392 | 0 | 1.44 | 2.5 | 153 | 68 | 73 | 9 | 94 | 0 | 0 | 2.1 | 55 | 0.25 | 0 | 307 | 4 | 136 | 110 | 0 | 0 | 1110 | 17 | 4354.48 | 10358.82 | 91.43
10:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 63 | 401 | 0 | 0 | 35 | 36 | 0 | 130 | 16 | 0 | 55 | 17 | 162 | 25 | 0 | 420 | 284 | 0 | 0 | 35 | 17 | 333 | 0 | 0 | 20 | 0 | 16.5 | 15 | 0 | 0 | 35 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 2 | 40 | 51 | 2 | 158 | 17 | 0 | 45 | 0 | 105 | 226 | 0 | 0 | 0 | 593 | 15 | 40 | 100 | 88 | 0 | 0 | 260 | 23 | 183 | 28 | 115 | 50 | 120 | 28 | 17 | 0 | 42 | 52.2 | 44 | 30 | 305 | 15 | 370 | 33 | 30 | 0 | 5 | 120 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 5 | 1 | 26.98 | 2 | 5948.68 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.49 | 0 | 0 | 757.68 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 0 | 0 | 35 | 63 | 0 | 35.77 | 149 | 0 | 0 | 0 | 110 | 0 | 308 | 0 | 3.06 | 2.5 | 167 | 69 | 75 | 15 | 35 | 0 | 0 | 3.6 | 92 | 0.39 | 0 | 250 | 4 | 136 | 110 | 0 | 0 | 1070 | 17 | 4473.49 | 10422.17 | 91.43
11:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 63 | 401 | 0 | 0 | 43 | 36 | 0 | 146 | 16 | 0 | 55 | 17 | 162 | 25 | 0 | 420 | 287 | 0 | 0 | 35 | 17 | 331 | 0 | 0 | 25 | 0 | 16.5 | 15 | 0 | 0 | 35 | 15 | 25 | 0 | 0 | 4 | 0 | 0 | 50 | 50 | 3 | 40 | 51 | 2 | 158 | 17 | 0 | 47 | 0 | 105 | 226 | 0 | 0 | 0 | 595 | 17 | 40 | 100 | 88 | 0 | 0 | 260 | 23 | 182 | 28 | 70 | 50 | 68 | 29 | 17 | 0 | 44 | 52.2 | 54 | 32 | 290 | 46 | 368 | 33 | 30 | 0 | 5 | 120 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 5 | 1 | 33.98 | 6 | 5939.68 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.88 | 0 | 0 | 755.05 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 34 | 80 | 0 | 43.84 | 148 | 0 | 0 | 0 | 117 | 0 | 309 | 0 | 3.84 | 2.5 | 156 | 68 | 75 | 20 | 35 | 0 | 0 | 4.5 | 119 | 0.47 | 0 | 250 | 4 | 136 | 110 | 0 | 0 | 1060 | 17 | 4618.08 | 10557.76 | 91.43
12:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 61 | 401 | 0 | 0 | 54 | 36 | 0 | 149 | 16 | 0 | 55 | 26 | 162 | 25 | 0 | 300 | 283 | 0 | 0 | 17 | 17 | 331 | 0 | 0 | 26 | 0 | 16.5 | 15 | 0 | 0 | 35 | 32 | 25 | 0 | 10 | 34 | 0 | 0 | 62 | 90 | 3 | 40 | 56 | 2 | 157 | 17 | 0 | 50 | 1 | 105 | 226 | 0 | 0 | 0 | 590 | 17 | 40 | 113 | 115 | 0 | 0 | 250 | 22 | 185 | 30 | 37 | 50 | 34 | 29 | 17 | 0 | 48 | 52.2 | 56 | 32 | 305 | 55 | 370 | 33 | 30 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 5 | 2 | 37.51 | 6 | 5978.21 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.33 | 0 | 0 | 754.92 | 0 | 0 | 0 | 0 | 35 | 4 | 49 | 35 | 10 | 34 | 85 | 20 | 49.8 | 162 | 0 | 0 | 0 | 168 | 0 | 397 | 0 | 4.36 | 2.5 | 157 | 68 | 75 | 24 | 87 | 0 | 0 | 4.7 | 132 | 0.53 | 0 | 307 | 3 | 132 | 110 | 0 | 0 | 1080 | 17 | 5000.14 | 10978.35 | 91.42
13:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 61 | 402 | 0 | 0 | 54 | 36 | 0 | 139 | 16 | 15 | 55 | 53 | 162 | 25 | 0 | 300 | 259 | 0 | 0 | 35 | 17 | 328 | 0 | 0 | 26 | 0 | 0 | 15 | 0 | 0 | 35 | 100 | 46 | 0 | 12 | 68 | 0 | 0 | 100 | 90 | 3 | 40 | 96 | 7 | 155 | 90 | 0 | 50 | 8 | 105 | 226 | 0 | 0 | 0 | 592 | 17 | 40 | 120 | 115 | 0 | 0 | 255 | 22 | 184 | 31 | 34 | 45 | 34 | 28 | 17 | 0 | 54 | 52.2 | 54 | 28 | 300 | 58 | 370 | 33 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 5 | 2 | 35.12 | 6 | 6275.32 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.29 | 0 | 0 | 762.79 | 0 | 0 | 0 | 0 | 60 | 6 | 49 | 35 | 15 | 43 | 90 | 30 | 47.31 | 174 | 0 | 0 | 0 | 177 | 0 | 395 | 0 | 4.15 | 2.5 | 154 | 67 | 75 | 20 | 96 | 0 | 0 | 4.8 | 124 | 0.47 | 0 | 307 | 5 | 130 | 110 | 0 | 0 | 1060 | 17 | 5049.31 | 11324.63 | 91.42
14:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 60 | 356 | 0 | 0 | 54 | 36 | 0 | 122 | 16 | 0 | 30 | 55 | 162 | 25 | 0 | 300 | 271 | 0 | 0 | 35 | 16.5 | 280 | 0 | 0 | 23 | 0 | 0 | 15 | 0 | 0 | 35 | 45 | 48 | 0 | 12 | 68 | 0 | 0 | 50 | 50 | 2 | 40 | 105 | 5 | 158 | 90 | 0 | 50 | 0 | 105 | 226 | 0 | 0 | 0 | 592 | 15 | 40 | 122 | 115 | 0 | 0 | 255 | 20 | 183 | 30 | 34 | 45 | 34 | 29 | 17 | 0 | 54 | 52.2 | 47 | 32 | 285 | 57 | 370 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 19 | 59 | 5 | 2 | 26.91 | 6 | 5971.61 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 736.87 | 0 | 0 | 0 | 0 | 35 | 6 | 48 | 0 | 30 | 34 | 79 | 30 | 41.43 | 178 | 0 | 0 | 0 | 170 | 0 | 310 | 0 | 3.68 | 2.5 | 152 | 67 | 75 | 20 | 90 | 0 | 0 | 4 | 111 | 0.36 | 0 | 307 | 4 | 130 | 110 | 0 | 0 | 1050 | 17 | 4821.84 | 10793.45 | 91.41
15:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 64 | 380 | 0 | 0 | 54 | 36 | 0 | 115 | 16 | 0 | 30 | 55 | 162 | 25 | 0 | 300 | 251 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 35 | 15 | 25 | 0 | 14 | 68 | 0 | 0 | 12 | 50 | 2 | 40 | 105 | 2 | 156 | 17 | 0 | 0 | 0 | 105 | 228 | 0 | 0 | 0 | 591 | 11 | 40 | 128 | 115 | 0 | 0 | 250 | 27 | 183 | 30 | 34 | 45 | 0 | 29 | 17 | 0 | 54 | 52.2 | 31 | 32 | 295 | 57 | 370 | 32 | 30 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 5 | 1 | 19.77 | 6 | 5704.47 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.6 | 0 | 0 | 763.73 | 0 | 0 | 0 | 0 | 0 | 6 | 41 | 0 | 30 | 25 | 60 | 30 | 29.17 | 178 | 0 | 0 | 0 | 169 | 0 | 388 | 0 | 2.59 | 2.5 | 160 | 67 | 75 | 15 | 35 | 0 | 0 | 3.1 | 77 | 0.31 | 0 | 307 | 4 | 130 | 110 | 0 | 0 | 1120 | 17 | 4809 | 10513.47 | 91.41
16:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 65 | 403 | 0 | 0 | 38 | 36 | 0 | 115 | 16 | 0 | 15 | 33 | 54 | 25 | 0 | 300 | 283 | 0 | 0 | 17 | 16.5 | 300 | 0 | 0 | 9 | 0 | 16.5 | 15 | 0 | 0 | 35 | 15 | 17 | 0 | 13 | 68 | 0 | 0 | 12 | 12 | 1 | 40 | 51 | 2 | 158 | 17 | 0 | 15 | 0 | 34 | 226 | 0 | 0 | 0 | 593 | 6 | 40 | 60 | 117 | 0 | 0 | 250 | 29 | 184 | 30 | 34 | 45 | 0 | 28 | 17 | 0 | 48 | 52.2 | 16 | 32 | 285 | 52 | 372 | 35 | 30 | 0 | 5 | 163 | 25 | 0 | 81 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 5 | 1 | 10.42 | 6 | 5332.62 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.51 | 0 | 0 | 761.09 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 30 | 34 | 31 | 30 | 14.75 | 179 | 0 | 0 | 0 | 176 | 0 | 395 | 0 | 1.27 | 2.5 | 165 | 67 | 35 | 8 | 35 | 0 | 0 | 1.8 | 43 | 0.17 | 0 | 307 | 4 | 130 | 110 | 0 | 0 | 1100 | 17 | 4665.09 | 9997.71 | 91.41
17:00 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 70 | 400 | 0 | 0 | 17 | 36 | 0 | 108 | 40 | 0 | 15 | 19 | 108 | 25 | 0 | 300 | 285 | 0 | 0 | 25 | 16.5 | 300 | 0 | 0 | 3 | 0 | 13.5 | 15 | 0 | 0 | 35 | 65 | 13 | 0 | 9 | 68 | 16 | 0 | 22 | 40 | 0 | 40 | 34 | 9 | 156 | 30 | 0 | 47 | 4 | 34 | 227 | 0 | 0 | 0 | 609 | 2 | 40 | 70 | 117 | 0 | 0 | 255 | 29 | 183 | 27 | 54 | 45 | 9 | 27 | 17 | 0 | 48 | 52.2 | 4 | 34 | 315 | 55 | 370 | 33 | 30 | 0 | 5 | 120 | 25 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 5 | 0 | 3.18 | 6 | 5539.38 | 914 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7.42 | 0 | 0 | 761.44 | 0 | 0 | 0 | 0 | 0 | 7 | 40 | 0 | 32 | 34 | 9 | 30 | 3.74 | 180 | 0 | 0 | 0 | 176 | 0 | 350 | 0 | 0.34 | 2.5 | 165 | 67 | 38 | 2 | 48 | 0 | 0 | 0.6 | 13 | 0.55 | 0 | 307 | 5 | 130 | 110 | 0 | 0 | 1100 | 17 | 4557.59 | 10096.97 | 91.4
18:00 | 0 | 90 | 26 | 0 | 0 | 0 | 0 | 70 | 321 | 0 | 0 | 51 | 36 | 0 | 131 | 82 | 3 | 50 | 54 | 146 | 25 | 5 | 280 | 295 | 0 | 0 | 35 | 28 | 260 | 0 | 0 | 0 | 0 | 16.5 | 15 | 0 | 0 | 35 | 115 | 42 | 0 | 11 | 84 | 16 | 14 | 50 | 85 | 0 | 40 | 51 | 12 | 157 | 108 | 0 | 50 | 8 | 85 | 199 | 0 | 0 | 0 | 612 | 0 | 51 | 102 | 105 | 0 | 0 | 225 | 29 | 182 | 29 | 115 | 45 | 110 | 69 | 17 | 0 | 46 | 52.2 | 0 | 47 | 275 | 52 | 355 | 36 | 29 | 0 | 5 | 163 | 25 | 0 | 41 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 5 | 0 | 0 | 6 | 6141.7 | 914 | 0 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 759 | 0 | 0 | 33 | 0 | 18 | 16 | 97 | 35 | 38 | 43 | 0 | 30 | 0 | 140 | 0 | 0 | 0 | 149 | 0 | 313 | 0 | 0 | 2.5 | 165 | 67 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 6 | 132 | 110 | 0 | 0 | 1080 | 36 | 4860.5 | 11002.2 | 91.4
19:00 | 0 | 90 | 26 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 36 | 0 | 132 | 48 | 0 | 55 | 55 | 162 | 25 | 13 | 420 | 253 | 0 | 0 | 35 | 28 | 330 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 0 | 35 | 65 | 60 | 0 | 7 | 84 | 23 | 0 | 84 | 100 | 0 | 40 | 102 | 4 | 156 | 108 | 0 | 32 | 8 | 91 | 227 | 0 | 0 | 0 | 612 | 0 | 40 | 125 | 143 | 0 | 0 | 255 | 28 | 182 | 28 | 115 | 50 | 163 | 75 | 17 | 17 | 48 | 52.2 | 0 | 40 | 285 | 80 | 370 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 5 | 0 | 0 | 6 | 6631.2 | 639 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 758.04 | 0 | 0 | 33 | 0 | 0 | 21 | 97 | 35 | 38 | 43 | 0 | 30 | 0 | 168 | 0 | 0 | 0 | 172 | 0 | 391 | 0 | 0 | 2.5 | 165 | 67 | 95 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 7 | 132 | 110 | 0 | 0 | 1090 | 36 | 4910.54 | 11541.74 | 91.4
19:30 | 0 | 90 | 26 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 36 | 0 | 132 | 32 | 0 | 55 | 55 | 162 | 25 | 14 | 370 | 290 | 0 | 0 | 35 | 24 | 328 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 35 | 65 | 25 | 0 | 3 | 84 | 32 | 0 | 100 | 100 | 0 | 40 | 105 | 11 | 157 | 108 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 129 | 143 | 0 | 0 | 255 | 28 | 182 | 31 | 115 | 50 | 155 | 75 | 17 | 0 | 44 | 0 | 0 | 40 | 300 | 0 | 370 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 8 | 0 | 0 | 6 | 6467 | 630 | 0 | 0 | 26 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 755.39 | 0 | 0 | 33 | 0 | 0 | 21 | 97 | 0 | 38 | 43 | 0 | 30 | 0 | 181 | 0 | 0 | 0 | 174 | 0 | 393 | 0 | 0 | 2.5 | 165 | 67 | 95 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1100 | 36 | 4938.89 | 11405.89 | 91.4
20:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 36 | 0 | 132 | 16 | 0 | 55 | 55 | 162 | 25 | 0 | 370 | 272 | 0 | 0 | 35 | 24 | 328 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 25 | 0 | 0 | 84 | 40 | 0 | 90 | 100 | 0 | 40 | 105 | 18 | 156 | 90 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 155 | 0 | 0 | 255 | 29 | 182 | 29 | 115 | 50 | 166 | 77 | 17 | 0 | 46 | 0 | 0 | 40 | 280 | 0 | 370 | 36 | 30 | 0 | 5 | 163 | 17 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 10 | 0 | 0 | 6 | 6323.5 | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 757.39 | 0 | 0 | 33 | 0 | 0 | 23 | 97 | 0 | 38 | 43 | 0 | 30 | 0 | 182 | 0 | 0 | 0 | 172 | 0 | 393 | 0 | 0 | 2.5 | 163 | 67 | 95 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1110 | 36 | 4945.89 | 11269.39 | 91.39
21:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 53 | 36 | 0 | 132 | 16 | 0 | 55 | 55 | 162 | 25 | 0 | 300 | 266 | 0 | 0 | 35 | 24 | 332 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 50 | 100 | 0 | 40 | 105 | 24 | 156 | 0 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 805 | 0 | 51 | 125 | 195 | 0 | 0 | 40 | 29 | 182 | 29 | 115 | 45 | 100 | 78 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 15 | 370 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 59 | 11 | 0 | 0 | 6 | 5936.5 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 43 | 0 | 30 | 0 | 183 | 0 | 0 | 0 | 168 | 0 | 314 | 0 | 0 | 2.5 | 164 | 67 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1100 | 36 | 4938.5 | 10875 | 91.39
22:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 51 | 36 | 0 | 132 | 16 | 0 | 0 | 0 | 162 | 25 | 0 | 300 | 260 | 0 | 0 | 35 | 24 | 333 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 34 | 28 | 156 | 0 | 0 | 19 | 0 | 105 | 226 | 0 | 0 | 0 | 870 | 0 | 51 | 60 | 195 | 0 | 0 | 30 | 29 | 182 | 29 | 115 | 40 | 100 | 78 | 17 | 0 | 46 | 0 | 0 | 0 | 285 | 55 | 370 | 36 | 30 | 0 | 5 | 163 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 9 | 58 | 9 | 0 | 0 | 6 | 5556.5 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 43 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 167 | 0 | 314 | 0 | 0 | 2.5 | 162 | 67 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 1110 | 36 | 4900.5 | 10457 | 91.39
23:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 46 | 55 | 0 | 132 | 16 | 0 | 0 | 0 | 108 | 25 | 0 | 300 | 295 | 0 | 0 | 17 | 24 | 330 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 156 | 0 | 0 | 18 | 0 | 17 | 226 | 0 | 0 | 0 | 920 | 0 | 51 | 0 | 195 | 0 | 0 | 18 | 29 | 195 | 31 | 100 | 35 | 17 | 45 | 17 | 0 | 48 | 0 | 0 | 0 | 280 | 103 | 370 | 33 | 29 | 0 | 5 | 120 | 25 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 9 | 0 | 0 | 6 | 5243 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 173 | 0 | 330 | 0 | 0 | 2.5 | 161 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 132 | 110 | 0 | 0 | 1110 | 17 | 4584.5 | 9827.5 | 91.38
Total KWH | 0 | 966720 | 405120 | 0 | 0 | 0 | 0 | 1224227.28 | 9514800 | 0 | 0 | 737640 | 636480 | 0 | 2351952 | 459840 | 39142 | 610218 | 626015 | 2340000 | 600600 | 29760 | 8529000 | 6983971 | 0 | 0 | 534579 | 581300 | 7560940 | 0 | 0 | 163052 | 0 | 343800 | 437400 | 0 | 0 | 568309 | 617236 | 347520 | 0 | 89280 | 629295 | 147225 | 32974 | 798720 | 857280 | 20641 | 964000 | 1085600 | 483360 | 3752727.27 | 700873 | 0 | 595200 | 34176.6 | 1385854 | 5287091 | 0 | 0 | 0 | 17089089 | 119475 | 1104706 | 1615854 | 3445818 | 0 | 0 | 5340000 | 596640 | 4615000 | 723456 | 1309440 | 1081470 | 1261440 | 742560 | 411930 | 27360 | 1042560 | 522163 | 352318 | 349232 | 7231000 | 2045500 | 9135000 | 816120 | 714000 | 0 | 116688 | 3759873 | 544944 | 0 | 1920960 | 717792 | 0 | 219000 | 0 | 533880 | 199200 | 1075200 | 248640 | 8900 | 216190 | 108240 | 135435556.15 | 20293818 | 0 | 0 | 57600 | 61824 | 0 | 0 | 0 | 0 | 0 | 0 | 472320 | 2400000 | 0 | 15538909 | 0 | 0 | 107926 | 0 | 409824 | 83406 | 902080 | 127968 | 226114 | 514382 | 566740 | 291819 | 291000 | 4142091 | 0 | 0 | 0 | 3749909 | 0 | 8686473 | 0 | 24960 | 74250 | 3859000 | 1555636 | 1102881 | 136673 | 895171 | 0 | 0 | 29456.16 | 771840 | 3225 | 13728 | 6152000 | 141413 | 3206000 | 2565160 | 0 | 0 | 24583272.73 | 382800 | 104421668.89 | 239857225.04

## Volt
e
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
| Date: | 03-02-2025
| Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
| 400 kV | KV |  | KV |  | 400 kV | KV |  | KV |  |  |  | `
| Aminbazar | 413 | 05:00 | 390 | 12:00 | Payra | 417 | 04:00 | 407 | 11:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 414 | 5:00 | 387 | 12:00 | Rahanpur | 419 | 04:00 | 394 | 08:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 411 | 03:00 | 389 | 12:00 | Rampal | 413 | 04:00 | 383 | 12:00
| Bibiana | 409 | 04:00 | 394 | 10:00
| BIPTC | 408 | 03:00 | 387 | 10:00
| Bogura | 420 | 04:00 | 392 | 08:00
| Gopalganj | 415 | 04:00 | 392 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| Kaliakoir | 401 | 07:00 | 379 | 11:00 | [5 empty] | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Madunaghat | 409 | 05:00 | 401 | 13:00 | [5 empty] | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| Meghnaghat | 410 | 05:00 | 391 | 12:00 | [5 empty] | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| 230 kV | KV |  | KV |  | 230 kV | KV |  | KV
| Agargaon | 238 | 05:00 | 225 | 11:00 | Keranigonj | 237 | 04:00 | 224 | 12:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| AKSML | 233 | 05:00 | 229 | 00:00 | Khulna(S) | 242 | 04:00 | 222 | 12:00
| Aminbazar | 238 | 05:00 | 225 | 12:00 | Madunaghat | 235 | 19:00 | 230 | 00:00 | 230 kV MAX | 247 |  | 247 | 216
| Ashuganj | 242 | 03:00 | 230 | 11:00 | Madunaghat-400 | 234 | 05:00 | 230 | 01:00 | 230 kV MIN | 216 |  | 246 | 218 |  |  |  | Substation | Total | Updated
| Ashuganj-400 | 242 | 03:00 | 230 | 11:00 | Maniknagar | 237 | 04:00 | 226 | 12:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Baghabari | 242 | 04:00 | 228 | 12:00 | Meghnaghat | 244 | 06:00 | 234 | 12:00 | 132 kV MAX | 148 |  | 148 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Barapukuria | 227 | 05:00 | 216 | 08:00 | Meghnaghat-400 | 240 | 04:00 | 229 | 12:00 | 132 kV MIN | 110 |  | 143 | 110 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Barapukuria-230 | 227 | 05:00 | 216 | 08:00 | Mirsorai | 235 | 05:00 | 227 | 00:00 | [35 empty] | 6:00
| Barishal | 245 | 03:00 | 236 | 11:00 | Rajshahi | 241 | 04:00 | 222 | 11:00 |  | 400 | [33 empty] | 392
| Bheramara | 240 | 04:00 | 222 | 12:00 | Rampal | 240 | 04:00 | 218 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bhulta | 240 | 05:00 | 226 | 12:00 | Rampur | N/A | N/A | N/A | N/A | ` |  |  |  | 230 | [30 empty] | 21:00
| Bibiana | 235 | 04:00 | 224 | 12:00 | Rampura | 240 | 05:00 | 226 | 12:00 |  | rampur-charged |  |  | B.P-499228
| BIPTC | 242 | 04:00 | 223 | 11:00 | Shikalbaha | 236 | 19:00 | 227 | 00:00 |  | 132 |  |  | Ash 400-299274
| Bogura | 241 | 03:00 | 228 | 08:00 | Shyampur | 239 | 05:00 | 225 | 12:00 |  | Megna
| Bogura-400 | 241 | 04:00 | 226 | 08:00 | Siddhirganj | 235 | 02:00 | 225 | 11:00 |  | Maniknagar=narinda | 132 kv
| Borhanuddin | 247 | 06:00 | 242 | 13:00 | Sirajgonj | 246 | 04:00 | 237 | 12:00 |  | kaptai by call 399528
| BSRM | 235 | 05:00 | 227 | 00:00 | Sreepur | 242 | 05:00 | 229 | 12:00
| Cumilla(N) | 236 | 06:00 | 228 | 12:00 | Tongi | 237 | 04:00 | 223 | 11:00
| Faridpur | 246 | 04:00 | 232 | 11:00
| Fenchuganj | 238 | 03:00 | 227 | 12:00
| Ghorashal | 238 | 09:00 | 224 | 21:00 | [6 empty] | Madu-399663
| Ghorashal-230 | 240 | 05:00 | 223 | 13:00 | [6 empty] | Meg-299636
| Gopalganj | 246 | 05:00 | 233 | 11:00 | [6 empty] | Gopalganj-230 | 599470
| GPH | 235 | 05:00 | 227 | 00:00
| Haripur | 240 | 05:00 | 227 | 12:00
| Hasnabad | 236 | 03:00 | 225 | 11:00
| Hathazari | 236 | 09:00 | 229 | 00:00
| Ishurdi | 243 | 04:00 | 225 | 12:00
| Jhenaidah | 240 | 05:00 | 221 | 08:00
| Kaliakoir | 237 | 04:00 | 224 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 03:00 | 127 | 12:00 | Magura | 140 | 04:00 | 126 | 11:00
| Agargaon | 139 | 05:00 | 129 | 12:00 | Mahasthangarh | 136 | 05:00 | 125 | 08:00
| Agrabad | 135 | 19:00 | 130 | 00:00 | Manikganj | 140 | 07:00 | 132 | 11:00
| AKS | 133 | 19:00 | 130 | 00:00 | Maniknagar | 136 | 04:00 | 127 | 12:00
| Aminbazar | 137 | 05:00 | 129 | 11:00 | Matarbari | 125 | 04:00 | 120 | 13:00
| Amnura | 141 | 19:00 | 128 | 11:00 | Matuail | 136.5 | 04:00 | 129 | 12:00
| Ashuganj | 143 | 05:00 | 137 | 11:00 | Millgate | 140 | 03:00 | 129 | 12:00
| Bagerhat | 136 | 05:00 | 125 | 12:00 | Mirpur | 136 | 03:00 | 128 | 11:00
| Bajitpur | 134 | 15:00 | 130 | 10:00 | Mirzapur | 140 | 06:00 | 129 | 11:00
| Bakulia | 138 | 07:00 | 130 | 00:00 | Mithapukur | 134 | 04:00 | 120 | 08:00
| Banani | 137 | 03:00 | 127 | 12:00 | MI_Cement | 138 | 05:00 | 131.3 | 12:00
| Bangabhaban | 136 | 03:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Barapukuria | 135 | 02:00 | 127 | 08:00 | Mogbazar | 138 | 04:00 | 128 | 13:00
| Barguna | 140 | 09:00 | 134 | 00:00 | Mongla | 137 | 06:00 | 124 | 12:00
| Barishal | 135 | 03:00 | 129 | 12:00 | Motijheel | 136 | 03:00 | 127 | 12:00
| Barishal-230 | 137 | 03:00 | 130 | 11:00 | Muktagacha | 132 | 04:00 | 116 | 11:00
| Baroaulia | 135 | 09:00 | 131 | 15:00 | Munshiganj | 136 | 04:00 | 131 | 11:00
| Baroirhat | 134 | 18:30 | 129 | 00:00 | Mymensingh | 131 | 05:00 | 115 | 11:00
| Bashundhara | 140 | 04:00 | 127 | 12:00 | Naogaon | 136 | 02:00 | 124 | 08:00
| BashundharaCement | 136 | 05:00 | 130 | 12:00 | Narail | 140 | 04:00 | 124 | 12:00
| Beanibazar | 138 | 04:00 | 130 | 12:00 | Narinda | 136 | 04:00 | 127 | 12:00
| Benapole | 138 | 03:00 | 121 | 12:00 | Narshingdi | 132 | 01:00 | 125 | 12:00
| Bhaluka | 130 | 03:00 | 120 | 12:00 | Natore | 138 | 04:00 | 128 | 08:00
| Bhandaria | 132 | 05:00 | 126 | 13:00 | Nawabganj | 140 | 05:00 | 130 | 12:00
| Bhangura | 138 | 04:00 | 129 | 11:00 | Netrakona | 125 | 23:00 | 114 | 12:00
| Bheramara | 139 | 05:00 | 128 | 11:00 | New | 140 | 02:00 | 130 | 11:00
| Bheramara(GK) | 139 | 04:00 | 128 | 11:00 | Niamatpur | 141 | 03:00 | 132 | 09:00
| Bhulta | 131 | 06:00 | 124 | 12:00 | Noapara | 139 | 04:00 | 125 | 12:00
| Bog-Sherpur | 138 | 05:00 | 127 | 12:00 | Pabna | 137 | 04:00 | 125 | 12:00
| Bogura | 138 | 06:00 | 129 | 10:00 | Palashbari | 131 | 01:00 | 120 | 08:00
| Bogura-230 | 138 | 03:00 | 128 | 08:00 | Panchagarh | 141 | 19:30 | 121 | 08:00
| Brahmanbaria | 138 | 06:00 | 129 | 12:00 | Patuakhali | 140 | 09:00 | 133 | 00:00
| Cantonment | 138 | 04:00 | 129 | 12:00 | Payra | 138 | 19:00 | 134 | 00:00
| Chandpur | 140 | 18:30 | 127 | 00:00 | PHP | 134 | 18:00 | 128 | 00:00
| Chandraghona | 136 | 19:00 | 132 | 00:00 | Postogola | 140 | 05:00 | 133 | 11:00
| Chapai | 140 | 05:00 | 130 | 10:00 | Purbachal | 138 | 04:00 | 127 | 12:00
| Charsaidpur | 137 | 05:00 | 131 | 12:00 | Purbasadipur | 132 | 03:00 | 122 | 08:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Chauddagram | 135 | 19:00 | 130 | 00:00 | Rahanpur | 140 | 00:00 | 133 | 08:00
| Chhatak | 138 | 06:00 | 129 | 12:00 | Rahanpur-400 | 142 | 03:00 | 133 | 08:00
| Chowmuhani | 135 | 19:00 | 125 | 00:00 | Rahim | 135 | 05:00 | 129 | 11:00
| Chuadanga | 139 | 05:00 | 122 | 12:00 | Rajbari | 136 | 04:00 | 127 | 12:00
| Coxsbazar | 127 | 04:00 | 120 | 12:00 | Rajendrapur | 137 | 04:00 | 126 | 13:00
| Cumilla(N) | 138 | 05:00 | 133 | 12:00 | Rajshahi | 138 | 06:00 | 129 | 11:00
| Cumilla(S) | 138 | 19:00 | 128 | 09:00 | Rajshahi-230 | 140 | 04:00 | 126 | 13:00
| Daudkandi | 134 | 05:00 | 128 | 12:00 | Ramganj | 136 | 09:00 | 126 | 00:00
| Dhaka | 136 | 05:00 | 128 | 12:00 | Rampur | 134 | 04:00 | 130 | 12:00
| Dhamrai | 135 | 04:00 | 127 | 19:30 | Rampura | 137 | 04:00 | 128 | 12:00
| Dhanmondi | 137 | 06:00 | 130 | 12:00 | Rangamati | 134 | 04:00 | 132 | 00:00
| Dohazari | 131 | 05:00 | 124 | 01:00 | Rangpur | 132 | 06:00 | 121 | 09:00
| Faridpur | 136 | 04:00 | 130 | 10:00 | Ruppur | 140 | 06:00 | 131 | 10:00
| Fatullah | 139 | 05:00 | 132 | 12:00 | Saidpur | 134 | 02:00 | 119 | 08:00
| Fenchuganj | 142 | 04:00 | 135 | 13:00 | Satkhira | 137 | 05:00 | 126 | 11:00
| Feni | 134 | 18:00 | 127 | 00:00 | Satmasjid | 138 | 04:00 | 129 | 12:00
| Ghatail | 132 | 03:00 | 119 | 11:00 | Savar | 137 | 20:00 | 129 | 11:00
| Ghorashal | 140 | 00:00 | 135 | 12:00 | SevenRings | 143 | 04:00 | 134 | 12:00
| Goalpara | 139 | 04:00 | 127 | 12:00 | ShahCement | 137 | 05:00 | 131 | 11:00
| Gollamari | 139 | 02:00 | 129 | 11:00 | Shahjadpur | 140 | 00:00 | 133 | 11:00
| Gopalganj | 138 | 04:00 | 129 | 11:00 | Shahjibazar | 140 | 05:00 | 132 | 12:00
| Gopalganj-400 | 138 | 04:00 | 130 | 12:00 | Shahmirpur | 136 | 18:30 | 130 | 00:00
| Gulshan | 136 | 05:00 | 127 | 12:00 | Shariatpur | 136 | 04:00 | 128 | 11:00
| Halishahar | 136 | 19:00 | 132 | 16:00 | Sherpur | 126 | 06:00 | 110 | 11:00
| Haripur | 136 | 04:00 | 129 | 12:00 | Shikalbaha | 125 | 19:00 | 119 | 00:00
| HaripurSBU | 136 | 03:00 | 129 | 12:00 | Shikalbaha-230 | 137 | 19:00 | 131 | 00:00
| Hasnabad | 138 | 19:00 | 133 | 11:00 | Shitalakhya | 138 | 05:00 | 131.3 | 12:00
| Hathazari | 136 | 08:00 | 133 | 12:00 | Sholosohor | 135 | 19:00 | 131 | 00:00
| Ishurdi | 141 | 04:00 | 130 | 12:00 | Shyampur | 136 | 01:00 | 131 | 12:00
| Jaldhaka | 131 | 03:00 | 118 | 08:00 | Shyampur-230 | 139 | 05:00 | 132 | 11:00
| Jamalpur | 128 | 06:00 | 112 | 13:00 | Siddhirganj | 137 | 04:00 | 130 | 12:00
| Jashore | 136 | 06:00 | 123 | 12:00 | Sirajganj | 138 | 03:00 | 127 | 08:00
| Jhenaidah | 140 | 04:00 | 127 | 12:00 | Sonargaon | 135 | 03:00 | 127 | 12:00
| Jhenaidah-230 | 141 | 04:00 | 127 | 12:00 | Sreemongol | 140 | 03:00 | 132 | 12:00
| Joydebpur | 140 | 19:00 | 133 | 12:00 | Sreepur | 132 | 05:00 | 124 | 10:00
| Joypurhat | 135 | 03:00 | 122 | 11:00 | Srinagar | 139 | 06:00 | 131 | 12:00
| Juldah | 135 | 09:00 | 130 | 00:00 | SSM | 139 | 09:00 | 136 | 01:00
| Kabirpur | 141 | 06:00 | 125 | 12:00 | Sunamganj | 138 | 05:00 | 127 | 12:00
| Kachua | 139 | 19:00 | 128 | 00:00 | Sylhet | 140 | 04:00 | 130 | 13:00
| Kaliakoir | 148 | 07:00 | 129 | 11:00 | Sylhet-132 | 139 | 03:00 | 130 | 11:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kallyanpur | 136 | 04:00 | 127 | 11:00 | Tangail | 134 | 05:00 | 123 | 08:00 |  |  | Nos | Nos | Nos
| Kalurghat | 135 | 04:00 | 131 | 00:00 | Thakurgaon | 140 | 19:30 | 118 | 08:00 |  |  | 173 | 39 | 9 | 221
| Kamrangirchar | 139 | 03:00 | 126 | 11:00 | TK | 135 | 09:00 | 132 | 03:00
| Kaptai | 137 | 1:00 | 125 | 12:00 | Tongi | 141 | 04:00 | 131 | 11:00
| Kazla | 136 | 04:00 | 127 | 12:00 | Ullahpara | 139 | 02:00 | 129 | 12:00
| Keranigonj | 138 | 04:00 | 130 | 11:00 | Ullon | 136 | 03:00 | 127 | 12:00
| Khagrachori | 134 | 04:00 | 131 | 11:00 | Uttara | 136 | 04:00 | 128 | 11:00
| Khulna | 139 | 03:00 | 127 | 12:00 | UttaraNew | 139 | 03:00 | 129 | 12:00
| Khulna(S) | 141 | 04:00 | 128 | 12:00 | Zigatola | 140 | 04:00 | 130 | 13:00
| Khulshi | 133 | 03:00 | 130 | 00:00
| Kishoreganj | 132 | 01:00 | 126 | 12:00
| Kodda | 140 | 06:00 | 127 | 12:00
| KSRM | 136 | 19:00 | 132 | 00:00
| Kulaura | 142 | 05:00 | 135 | 11:00
| Kurigram | 131 | 01:00 | 113 | 08:00
| Kushtia | 139 | 03:00 | 127 | 12:00 | [7 empty] | 360
| Lalbag | 140 | 05:00 | 131 | 11:00
| Lalmonirhat | 131 | 01:00 | 120 | 08:00
| Madanganj | 136 | 05:00 | 130 | 12:00
| Madaripur | 137 | 05:00 | 130 | 12:00
| Madartek | 137 | 04:00 | 128 | 12:00
| Madunaghat | 135 | 05:00 | 132 | 00:00
|  | Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division
.