## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-02-2025 | during | 08-02-2025 | during | 08-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 1 | 1 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 407 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 330 | 450 | 450 | 400 | 400 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 289 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 30 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 21 | 16 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 8 | 52.19 | 52.19 | 26 | 26 | machine problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 87 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 49 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 17 | 17 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 17 | 54 | 36.09 | 36.09 | 36.09 | 36.09 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.654 | 1463 | 1861 | 4600.96 | 4570.96 | 2789.67 | 2759.67
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 23 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 223 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 81 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 8 | 8 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 18 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 34 | 42 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 32 | 32 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 12 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 6 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 15 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 12 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 605 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 18 | 27 | 20 | 20 | 20 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 275 | 275 | 270 | 270 | 275 | 275 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1345 | 1429 | 2658.86 | 2672.86 | 2391.86 | 2405.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 48 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 360 | 360 | 356.56 | 356.56 | 356.56 | 356.56 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 29 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 195 | 184 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 40 | 51 | 40 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 40 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 40 | 163 | 163 | 30 | 30 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 21 | 84 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 75 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 36 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 899 | 1081 | 2079.53 | 2035.53 | 1930.53 | 1886.53
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-02-2025 | during | 08-02-2025 | during | 08-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 23 | 210 | 210 | 20 | 20 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 19 | 200 | 200 | 18 | 18 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 59 | 115 | 115 | 56 | 56 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.61 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 24 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 169.61 | 131 | 651.3 | 601.5 | 220.3 | 170.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 28 | 29 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 36 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1023 | 1012 | 1040 | 1040 | 1006 | 1006
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 914 | 633 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90.94 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 563 | 625 | 617.1 | 617.1 | 617 | 617 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1567.94 | 1258 | 2558.1 | 2483.1 | 1732 | 1657
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 134 | 132 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 580 | 622 | 622 | 622 | 622 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1194.65 | 1171 | 1445.12 | 1445.12 | 1445.12 | 1445.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 182 | 183 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 201 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 387 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 16 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 91 | 90 | 90 | 90 | 90 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.65 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 756 | 762 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.13 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1724.28 | 1660.5 | 2510.79 | 2351.24 | 2175 | 2015.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 161 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 26 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 4.1 | 0 | 4.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 81 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 174 | 0 | 175.42 | 0 | 175.42 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 425.7 | 276 | 615.52 | 412 | 581.52 | 378
System Total |  |  |  |  | 27884.66 | 27066.632 | 9812.18 | 9879.5 | 18160.18 | 17612.31 | 14272 | 13724.13
Forecast Scenario (08-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 0 |  | 0 |  | 0
|  |  |  | 1:00 | 8800 |  | 0 |  | 8800
|  |  |  | 2:00 | 8370 |  | 0 |  | 8370
|  |  |  | 3:00 | 8040 |  | 0 |  | 8040
|  |  |  | 4:00 | 7850 |  | 0 |  | 7850
|  |  |  | 5:00 | 7100 |  | 0 |  | 7100
|  |  |  | 6:00 | 7450 |  | 0 |  | 7450
|  |  |  | 7:00 | 8200 |  | 0 |  | 8200
|  |  |  | 8:00 | 9000 |  | 0 |  | 9000
|  |  |  | 9:00 | 9500 |  | 0 |  | 9500
|  |  |  | 10:00 | 9600 |  | 0 |  | 9600
|  |  |  | 11:00 | 9750 |  | 0 |  | 9750
|  |  |  | 12:00 | 10300 |  | 0 |  | 10300
|  |  |  | 13:00 | 10470 |  | 0 |  | 10470
|  |  |  | 14:00 | 10300 |  | 0 |  | 10300
|  |  |  | 15:00 | 10000 |  | 0 |  | 10000
|  |  |  | 16:00 | 9700 |  | 0 |  | 9700
|  |  |  | 17:00 | 9660 |  | 0 |  | 9660
|  |  |  | 18:00 | 10720 |  | 0 |  | 10720
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11400 |  | 0 |  | 11400
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10900 |  | 0 |  | 10900
|  |  |  | 21:00 | 10750 |  | 0 |  | 10750
|  |  |  | 22:00 | 10300 |  | 0 |  | 10300
|  |  |  | 23:00 | 9800 |  | 0 |  | 9800
Probable Maximum Temperature: |  |  | 26.20°C
Probable Maximum Demand at Day Peak: |  |  | 10300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 217.96 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:25 hrs on 08-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-02-2025 | [28 empty] | Date: | 07-02-2025 | [28 empty] | Date: | 07-02-2025 | [28 empty] | Date: | 07-02-2025 | [28 empty] | Date: | 07-02-2025 | [19 empty] | Date: | 07-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [19 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 54 | 0 | 115 | 16 | 0 | 0 | 0 | 17 | 16 | 0 | 320 | 243 | 0 | 0 | 0 | 28 | 305 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 65 | 0 | 0 | 0 | 0 | 40 | 109 | 38 | 274 | 0 | 0 | 22 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 115 | 195 | 0 | 0 | 240 | 29 | 182 | 32 | 0 | 40 | 100 | 74 | 17 | 0 | 40 | 0 | 0 | 0 | 275 | 306 | 0 | 36 | 30 | 0 | 5 | 120 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 11 | 0 | 0 | 6 | 5258 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 757.74 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 43 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 171 | 0 | 315 | 0 | 0 | 2.5 | 170 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 110 | 0 | 0 | 840 | 17 | 4267.24 | 9525.24 | 91.27
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 320 | 272 | 0 | 0 | 0 | 30 | 296 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 15 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 274 | 0 | 0 | 19 | 0 | 17 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 320 | 29 | 182 | 32 | 0 | 40 | 51 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 280 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 11 | 0 | 0 | 6 | 4695 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 168 | 0 | 315 | 0 | 0 | 2.5 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 110 | 0 | 0 | 840 | 17 | 4153.5 | 8848.5 | 91.27
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 320 | 298 | 0 | 0 | 0 | 30 | 294 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 274 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 197 | 0 | 0 | 285 | 29 | 200 | 32 | 0 | 40 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 22 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 18 | 0 | 0 | 6 | 4478 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 160 | 0 | 345 | 0 | 0 | 2.5 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 136 | 110 | 0 | 0 | 830 | 0 | 3977.5 | 8455.5 | 91.26
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 320 | 311 | 0 | 0 | 0 | 32 | 294 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 277 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 197 | 0 | 0 | 285 | 29 | 73 | 29 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 305 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 22 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 20 | 0 | 0 | 6 | 4395 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 160 | 0 | 367 | 0 | 0 | 2.5 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 136 | 110 | 0 | 0 | 590 | 0 | 3765.5 | 8160.5 | 91.26
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 320 | 279 | 0 | 0 | 0 | 33 | 293 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 197 | 0 | 0 | 285 | 29 | 0 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 22 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 21 | 0 | 0 | 6 | 4234 | 724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 154 | 0 | 393 | 0 | 0 | 2.5 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 136 | 110 | 0 | 0 | 600 | 0 | 3692.5 | 7926.5 | 91.25
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 320 | 293 | 0 | 0 | 0 | 33 | 292 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 197 | 0 | 0 | 285 | 29 | 0 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 32 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 21 | 0 | 0 | 6 | 4203 | 724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 147 | 0 | 309 | 0 | 0 | 2.5 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 136 | 110 | 0 | 0 | 622 | 0 | 3674.5 | 7877.5 | 91.25
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 14 | 16 | 0 | 450 | 272 | 0 | 0 | 0 | 33 | 43 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 545 | 0 | 51 | 0 | 197 | 0 | 0 | 285 | 29 | 0 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 32 | 0 | 0 | 0 | 295 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 22 | 0 | 0 | 6 | 4177 | 724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 142 | 0 | 394 | 0 | 0 | 2.5 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 6 | 136 | 110 | 0 | 0 | 622 | 0 | 3926.5 | 8103.5 | 91.24
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 48 | 0 | 78 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 450 | 287 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 1 | 0 | 15 | 22 | 0 | 0 | 20 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 12 | 0 | 23 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 15 | 197 | 0 | 0 | 285 | 29 | 0 | 29 | 0 | 0 | 40 | 2 | 17 | 0 | 32 | 0 | 3 | 0 | 275 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 57 | 9 | 22 | 0 | 1.74 | 6 | 4415.74 | 724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 556 | 0 | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.37 | 180 | 0 | 0 | 0 | 161 | 0 | 310 | 0 | 0.17 | 2.5 | 154 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 4 | 0.02 | 0 | 307 | 6 | 136 | 110 | 0 | 0 | 622 | 17 | 3997 | 8412.74 | 91.24
08:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 54 | 0 | 85 | 0 | 0 | 4 | 0 | 17 | 16 | 0 | 450 | 287 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 10 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 24 | 24 | 1 | 40 | 2 | 40 | 275 | 0 | 0 | 19 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 3 | 51 | 48 | 197 | 0 | 0 | 385 | 29 | 0 | 30 | 0 | 0 | 71 | 26 | 17 | 0 | 32 | 0 | 22 | 0 | 300 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 7 | 57 | 9 | 18 | 1 | 14.89 | 6 | 4830.89 | 629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.88 | 594 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 29 | 0 | 16.82 | 181 | 0 | 0 | 0 | 182 | 0 | 392 | 0 | 1.45 | 2.5 | 155 | 0 | 70 | 5 | 25 | 0 | 0 | 0.9 | 41 | 0.13 | 0 | 307 | 5 | 136 | 110 | 0 | 0 | 622 | 17 | 4312.68 | 9143.57 | 91.23
09:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 107 | 0 | 0 | 30 | 0 | 17 | 16 | 0 | 450 | 261 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 19 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 24 | 2 | 40 | 30 | 33 | 275 | 0 | 0 | 19 | 0 | 34 | 227 | 0 | 0 | 0 | 612 | 11 | 51 | 50 | 197 | 0 | 0 | 390 | 29 | 0 | 29 | 0 | 0 | 68 | 28 | 17 | 0 | 36 | 0 | 44 | 0 | 280 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 21 | 57 | 9 | 18 | 1 | 28.72 | 6 | 4884.72 | 629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.57 | 618 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 60 | 0 | 34.45 | 180 | 0 | 0 | 0 | 190 | 0 | 388 | 0 | 2.92 | 2.5 | 155 | 0 | 35 | 14 | 35 | 0 | 0 | 1.1 | 91 | 0.32 | 0 | 307 | 3 | 136 | 110 | 0 | 0 | 600 | 17 | 4447.86 | 9332.58 | 91.23
10:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 15 | 0 | 17 | 16 | 0 | 450 | 287 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 27 | 0 | 15 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 17 | 33 | 275 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 16 | 51 | 20 | 197 | 0 | 0 | 360 | 29 | 0 | 32 | 0 | 0 | 34 | 29 | 15 | 0 | 40 | 0 | 60 | 0 | 290 | 275 | 0 | 33 | 30 | 0 | 2 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 57 | 9 | 17 | 2 | 39.76 | 6 | 4676.76 | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.38 | 561 | 0 | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 86 | 0 | 50.37 | 180 | 0 | 0 | 0 | 196 | 0 | 392 | 0 | 4.24 | 2.5 | 174 | 0 | 35 | 22 | 0 | 0 | 0 | 1.6 | 128 | 0.5 | 0 | 250 | 4 | 136 | 110 | 0 | 0 | 600 | 17 | 4543.59 | 9220.35 | 91.22
11:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 15 | 0 | 17 | 16 | 0 | 450 | 309 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 31 | 0 | 18 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 275 | 0 | 0 | 19 | 0 | 0 | 222 | 0 | 0 | 0 | 585 | 19 | 51 | 20 | 197 | 0 | 0 | 360 | 29 | 0 | 32 | 0 | 0 | 17 | 29 | 14 | 0 | 48 | 0 | 69 | 0 | 310 | 320 | 0 | 33 | 28 | 0 | 2 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 68 | 9 | 10 | 2 | 48.2 | 6 | 4728.2 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.77 | 562 | 0 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 103 | 0 | 60.61 | 182 | 0 | 0 | 0 | 150 | 0 | 400 | 0 | 5.32 | 2.5 | 163 | 0 | 35 | 27 | 0 | 0 | 0 | 2.2 | 161 | 0.61 | 0 | 267 | 4 | 134 | 110 | 0 | 0 | 560 | 17 | 4625.01 | 9353.21 | 91.22
12:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 0 | 52 | 16 | 0 | 15 | 0 | 17 | 16 | 0 | 450 | 304 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 33 | 0 | 21 | 15 | 0 | 0 | 17 | 12 | 0 | 0 | 18 | 0 | 8 | 0 | 24 | 24 | 4 | 40 | 6 | 34 | 275 | 12 | 0 | 23 | 0 | 0 | 223 | 0 | 0 | 0 | 605 | 20 | 51 | 40 | 195 | 0 | 0 | 360 | 29 | 0 | 32 | 0 | 0 | 21 | 29 | 14 | 0 | 56 | 0 | 72 | 0 | 320 | 320 | 0 | 33 | 28 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 57 | 9 | 10 | 2 | 50.61 | 6 | 4899.61 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.94 | 563 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 113 | 0 | 64.13 | 182 | 0 | 0 | 0 | 171 | 0 | 414 | 0 | 5.65 | 2.5 | 157 | 0 | 35 | 29 | 26 | 0 | 0 | 4.7 | 174 | 0.65 | 0 | 307 | 4 | 134 | 110 | 0 | 0 | 622 | 17 | 4912.57 | 9812.18 | 91.21
13:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 48 | 0 | 61 | 16 | 0 | 25 | 0 | 17 | 16 | 0 | 450 | 285 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 32 | 0 | 21 | 7 | 0 | 0 | 30 | 65 | 0 | 0 | 11 | 0 | 8 | 0 | 50 | 50 | 0 | 40 | 44 | 34 | 275 | 36 | 0 | 32 | 0 | 35 | 223 | 0 | 0 | 0 | 609 | 19 | 51 | 88 | 195 | 0 | 0 | 360 | 29 | 0 | 31 | 0 | 0 | 101 | 28 | 14 | 0 | 56 | 0 | 68 | 0 | 315 | 320 | 0 | 36 | 28 | 0 | 5 | 120 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 57 | 9 | 11 | 2 | 48.36 | 6 | 5243.36 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.19 | 607 | 0 | 756 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 34 | 111 | 0 | 61.97 | 182 | 0 | 0 | 0 | 185 | 0 | 395 | 0 | 5.85 | 2.5 | 158 | 0 | 94 | 29 | 57 | 0 | 0 | 4.7 | 175 | 0.62 | 0 | 293 | 4 | 134 | 110 | 0 | 0 | 622 | 17 | 5073.83 | 10317.19 | 91.21
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 0 | 30 | 0 | 0 | 15 | 0 | 17 | 16 | 0 | 380 | 271 | 0 | 0 | 0 | 33 | 37 | 0 | 0 | 28 | 0 | 15 | 7 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 24 | 24 | 3 | 40 | 17 | 34 | 275 | 0 | 0 | 19 | 0 | 17 | 223 | 0 | 0 | 0 | 560 | 18 | 51 | 40 | 145 | 0 | 0 | 360 | 29 | 0 | 31 | 3 | 30 | 17 | 29 | 14 | 0 | 50 | 0 | 62 | 0 | 280 | 320 | 0 | 36 | 28 | 0 | 5 | 120 | 24 | 0 | 82 | 20 | 0 | 18 | 0 | 17 | 59 | 9 | 11 | 2 | 40.61 | 6 | 4501.61 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.16 | 514 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 0 | 58.77 | 182 | 0 | 0 | 0 | 140 | 0 | 315 | 0 | 5.29 | 2.5 | 161 | 0 | 54 | 25 | 35 | 0 | 0 | 3.9 | 152 | 0.54 | 0 | 200 | 3 | 134 | 110 | 0 | 0 | 500 | 17 | 4336.16 | 8837.77 | 91.2
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 380 | 302 | 0 | 0 | 0 | 33 | 28 | 0 | 0 | 24 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 8 | 0 | 0 | 0 | 2 | 40 | 0 | 29 | 275 | 0 | 0 | 19 | 0 | 0 | 223 | 0 | 0 | 0 | 500 | 14 | 51 | 12 | 145 | 0 | 0 | 365 | 29 | 0 | 29 | 17 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 48 | 0 | 300 | 320 | 0 | 30 | 28 | 0 | 5 | 120 | 16 | 0 | 82 | 20 | 0 | 18 | 0 | 17 | 59 | 9 | 20 | 2 | 32.63 | 6 | 4221.63 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.32 | 515 | 0 | 616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 48.9 | 182 | 0 | 0 | 0 | 140 | 0 | 324 | 0 | 4.35 | 2.5 | 161 | 0 | 0 | 19 | 0 | 0 | 0 | 2.9 | 117 | 0.41 | 0 | 200 | 3 | 132 | 110 | 0 | 0 | 490 | 17 | 4141.38 | 8363.01 | 91.2
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 312 | 0 | 0 | 0 | 33 | 180 | 0 | 0 | 15 | 0 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 0 | 1 | 40 | 0 | 29 | 277 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 500 | 9 | 51 | 0 | 145 | 0 | 0 | 360 | 29 | 0 | 29 | 0 | 70 | 0 | 0 | 17 | 0 | 46 | 0 | 27 | 0 | 310 | 320 | 0 | 33 | 28 | 0 | 5 | 120 | 14 | 0 | 82 | 20 | 0 | 18 | 0 | 17 | 59 | 9 | 22 | 1 | 17.85 | 6 | 4283.85 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.31 | 513 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 28.84 | 182 | 0 | 0 | 0 | 140 | 0 | 344 | 0 | 2.57 | 2.5 | 162 | 0 | 0 | 9 | 0 | 0 | 0 | 1.5 | 69 | 0.24 | 0 | 200 | 3 | 132 | 110 | 0 | 0 | 500 | 0 | 3845.96 | 8129.81 | 91.19
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 310 | 0 | 0 | 0 | 33 | 328 | 0 | 0 | 4 | 0 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 275 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 520 | 3 | 51 | 0 | 145 | 0 | 0 | 360 | 29 | 0 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 45 | 0 | 8 | 0 | 310 | 320 | 0 | 33 | 28 | 0 | 5 | 120 | 23 | 0 | 82 | 20 | 0 | 18 | 0 | 17 | 59 | 19 | 22 | 0 | 4.7 | 6 | 4349.7 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.69 | 513 | 0 | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 6.23 | 183 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0.45 | 2.5 | 160 | 0 | 0 | 3 | 0 | 0 | 0 | 0.3 | 18 | 0.07 | 0 | 200 | 3 | 130 | 110 | 0 | 0 | 500 | 0 | 3845.24 | 8194.94 | 91.19
18:00 | 0 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 11 | 42 | 0 | 72 | 48 | 0 | 12 | 11 | 50 | 20 | 0 | 330 | 306 | 0 | 0 | 17 | 33 | 270 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 10 | 42 | 275 | 0 | 0 | 1 | 0 | 25 | 224 | 0 | 0 | 0 | 609 | 0 | 51 | 58 | 145 | 0 | 0 | 300 | 29 | 26 | 29 | 6 | 0 | 30 | 19 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 28 | 0 | 5 | 120 | 23 | 0 | 82 | 20 | 0 | 18 | 0 | 17 | 59 | 19 | 22 | 0 | 0 | 6 | 4649 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 34 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 140 | 0 | 321 | 0 | 0 | 2.5 | 160 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 490 | 35 | 4136.5 | 8785.5 | 91.18
19:00 | 0 | 49 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 0 | 87 | 16 | 0 | 30 | 35 | 72 | 17 | 0 | 330 | 289 | 0 | 0 | 17 | 33 | 335 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 27 | 0 | 8 | 0 | 18 | 15 | 0 | 40 | 34 | 42 | 275 | 0 | 0 | 19 | 0 | 81 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 80 | 184 | 0 | 0 | 360 | 29 | 48 | 29 | 36 | 40 | 84 | 75 | 17 | 0 | 48 | 0 | 0 | 0 | 305 | 320 | 0 | 36 | 29 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 24 | 59 | 19 | 23 | 0 | 0 | 6 | 5514 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 34 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 201 | 0 | 387 | 0 | 0 | 2.5 | 161 | 0 | 81 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 580 | 35 | 4365.5 | 9879.5 | 91.18
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 17 | 0 | 87 | 16 | 0 | 0 | 0 | 72 | 25 | 0 | 330 | 320 | 0 | 0 | 17 | 33 | 332 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 14 | 0 | 8 | 0 | 24 | 24 | 0 | 40 | 34 | 42 | 275 | 0 | 0 | 19 | 0 | 70 | 224 | 0 | 0 | 0 | 612 | 0 | 51 | 30 | 185 | 0 | 0 | 360 | 29 | 47 | 29 | 71 | 40 | 68 | 47 | 17 | 0 | 46 | 0 | 0 | 0 | 325 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 23 | 0 | 0 | 6 | 5376.5 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 43 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 201 | 0 | 414 | 0 | 0 | 2.5 | 159 | 0 | 95 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 622 | 35 | 4450.5 | 9827
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 45 | 17 | 0 | 87 | 16 | 0 | 0 | 0 | 72 | 25 | 0 | 330 | 323 | 0 | 0 | 17 | 33 | 332 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 24 | 24 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 19 | 0 | 51 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 30 | 185 | 0 | 0 | 360 | 29 | 50 | 31 | 71 | 40 | 68 | 57 | 17 | 0 | 48 | 0 | 0 | 0 | 310 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 23 | 0 | 0 | 6 | 5325 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 43 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 201 | 0 | 414 | 0 | 0 | 2.5 | 157 | 0 | 95 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 110 | 0 | 0 | 622 | 35 | 4454.5 | 9779.5 | 91.17
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 17 | 0 | 87 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 330 | 307 | 0 | 0 | 17 | 33 | 270 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 19 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 19 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 30 | 185 | 0 | 0 | 360 | 29 | 68 | 31 | 69 | 40 | 17 | 45 | 17 | 0 | 50 | 0 | 0 | 0 | 325 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 23 | 0 | 0 | 6 | 5046 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 756.09 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 43 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 198 | 0 | 414 | 0 | 0 | 2.5 | 159 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 110 | 0 | 0 | 622 | 35 | 4659.59 | 9705.59 | 91.17
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 65 | 0 | 0 | 0 | 0 | 17 | 25 | 0 | 330 | 283 | 0 | 0 | 17 | 33 | 270 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 18 | 0 | 17 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 360 | 29 | 229 | 31 | 17 | 40 | 17 | 9 | 11 | 0 | 42 | 0 | 0 | 0 | 310 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 36 | 0 | 0 | 6 | 4936 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 758.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 198 | 0 | 380 | 0 | 0 | 2.5 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 110 | 0 | 0 | 622 | 35 | 4449.27 | 9385.27 | 91.16
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 330 | 299 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 570 | 0 | 51 | 0 | 195 | 0 | 0 | 365 | 29 | 228 | 29 | 0 | 40 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 0 | 285 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 23 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 32 | 0 | 0 | 0 | 4604 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568 | 0 | 680.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 195 | 0 | 410 | 0 | 0 | 2.5 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 7 | 140 | 110 | 0 | 0 | 622 | 0 | 4249.9 | 8853.9 | 91.16
Total KWH | 0 | 534720 | 196800 | 0 | 0 | 0 | 0 | 0 | 9475200 | 0 | 0 | 136080 | 543600 | 0 | 2357568 | 147360 | 0 | 187450 | 66579 | 393120 | 379800 | 0 | 9001000 | 6943156 | 0 | 0 | 132775 | 787900 | 4185584 | 0 | 0 | 225675 | 0 | 387000 | 402840 | 0 | 0 | 452891 | 70255 | 0 | 0 | 364800 | 0 | 114768 | 0 | 194880 | 212160 | 21820 | 962040 | 306110 | 911520 | 6589090.91 | 48509 | 0 | 307200 | 0 | 645672 | 5289421 | 0 | 0 | 0 | 13718180 | 132840 | 1201348 | 674109 | 4416000 | 0 | 0 | 8254000 | 685440 | 1268000 | 735192 | 278400 | 579880 | 885600 | 518280 | 382910 | 0 | 989760 | 0 | 490318 | 0 | 7293000 | 7669100 | 0 | 801144 | 701000 | 0 | 107712 | 3564163.63 | 480384 | 0 | 1959360 | 662880 | 0 | 270000 | 0 | 396360 | 1095600 | 304800 | 450240 | 14100 | 330690 | 138720 | 114424854.54 | 19922909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612720 | 12843640 | 0 | 16369091 | 0 | 0 | 0 | 0 | 48480 | 0 | 435024 | 0 | 0 | 321230 | 757940 | 0 | 432000 | 4580400 | 0 | 0 | 0 | 4300191 | 0 | 8860436 | 0 | 38100 | 66888 | 3906000 | 0 | 815217 | 179860 | 252672 | 0 | 0 | 25145.64 | 1143000 | 4000 | 0 | 6502000 | 131774 | 3228000 | 240868 | 0 | 0 | 14961454.55 | 351600 | 101330640.19 | 215755494.73

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9812.18 | MW | 12:00 Hr. | Energy Generated |  |  | 215.7555 |  | MKWHr.
| Day Peak Demand |  |  | 9864.18 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.857 |  | MKWHr.
| Evening Peak Generation |  |  | 9879.5 | MW | 19:00 Hr. | Energy Demand |  |  | 216.6125 |  | MKWHr.
| Evening Peak Demand |  |  | 9910.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27.7 |  | °C
| Minimum Generation of the Day |  |  | 7877.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 761.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 10317.19 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 6.0513 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.5625 | 0 | 4.6961 | 0 | 0 | 0.22567 | 0 | 0 | 36.4842 | Gas | 100.6537 | Gas | 363950720.0396
| Chattogram Zone |  |  | 6.2009 | 20.3073 | 2.3524 | 0 | 0.96204 | 0.15466 | 0 | 0.3648 | 30.3422 | Coal | 58.5204 | Coal | 421703725.6003
| Cumilla Zone |  |  | 17.5228 | 0 | 2.3564 | 0 | 0 | 0.49032 | 0.98976 | 0 | 21.3592 | HFO | 13.5646 | HFO | 251758331.85
| Mymensingh Zone |  |  | 0.45024 | 0 | 1.9355 | 0 | 0 | 0.34479 | 0 | 0 | 2.7305 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.5087 | Hydro | 0.96204 | Hydro | 96204
| Khulna Zone |  |  | 0 | 12.8436 | 0 | 0 | 0 | 0.61272 | 19.9229 | 0 | 33.3793 | Solar | 4.4082 | Solar | 68632736.264
| Barishal Zone |  |  | 3.6006 | 21.4635 | 0.3516 | 0 | 0 | 0.004 | 0 | 0 | 25.4197 | Import | 37.2818 | Import | 193762277.87
| Rajshahi Zone |  |  | 17.8079 | 0 | 0.80473 | 0 | 0 | 1.228 | 16.3691 | 0 | 36.2098 | Wind | 0.3648 | Wind | 5690880
| Rangpur Zone |  |  | 0 | 3.906 | 1.0679 | 0 | 0 | 1.348 | 0 | 0 | 6.3219
| Total |  |  | 100.6537 | 58.5204 | 13.5646 | 0 | 0.96204 | 4.4082 | 37.2818 | 0.3648 | 215.7555
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 363950720.0396 |  | Hydro | 96204
|  |  |  | Coal | 421703725.6003 |  | Solar | 68632736.264
|  |  |  | HFO | 251758331.85 |  | Import | 193762277.87
|  |  |  | HSD | 0 |  | Wind | 5690880
[5 empty] | Total: | 130,55,94,875 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.9229 | Peak Hr Flow | 633.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9584636.441 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.3691 | Peak Hr Flow | 762.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 330 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.98976 | Peak Hr Flow | 48.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 838 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.2818 | Peak Hr Flow | 1443.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3253
|  |  |  | Chattogram |  | 0 |  | 1004
|  |  |  | Cumilla |  | 0 |  | 847
|  |  |  | Mymensingh |  | 30 |  | 932
|  |  |  | Sylhet |  | 0 |  | 356
|  |  |  | Khulna |  | 0 |  | 1136
|  |  |  | Barishal |  | 0 |  | 285
|  |  |  | Rajshahi |  | 0 |  | 1028
|  |  |  | Rangpur |  | 0 |  | 756
|  |  |  | Total |  | 30 |  | 9597
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 742.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1534.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:28 | 18:02 | Jhenaidah-Khulna 230kV Ckt-1 Project Work S/D from Khulna(S) 230/132kV end Due to
Shutdown taken by Project and from Jhenaidah 230/132kV end Due to Kaligonj to mahespur
line strining
| 08:29 | 18:03 | Jhenaidah-Khulna 230kV Ckt-2 Project Work S/D from Khulna(S) 230/132kV end Due to
Shutdown taken by Project and from Jhenaidah 230/132kV end Due to Kaligonj to mahespur
line strining work
| 08:35 | 10:02 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to 33kV Bus-1 Maintenance work | [7 empty] | 15.0MW load
interrup.
| 08:35 | 10:02 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 33kV Bus-1 Maintenance work | [7 empty] | 15.0MW load
interrup.
| 08:47 |  | Tongi 230/132/33kV S/S T-01 HT Forced S/D Due to Oil down for maintenance work
| 08:47 |  | Tongi 230/132/33kV S/S T-01 LT Forced S/D Due to Oil Down FOR maintenance work
| 08:52 | 16:58 | Shikalbaha 230/132kV S/S ATR 02 LT Scheduled S/D
| 08:53 | 16:58 | Shikalbaha 230/132kV S/S ATR 02 HT Scheduled S/D
| 09:04 | 17:27 | Bogura 230/132kV S/S Bogura (W) CKT-1 Project Work S/D Due to Project Work
| 09:04 | 17:27 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Project Work S/D Due to Due to Project work
| 09:06 | 17:28 | Bogura 230/132kV S/S Bogura (W) CKT-2 Project Work S/D Due to Project Work
| 09:06 | 17:28 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Project Work S/D Due to Due to Project work
| 09:11 | 17:24 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Due to Project
work
| 09:12 | 17:25 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Due to Project
work
| 12:00 |  | Day Peak generation = 9,812MW
|  | 14:43 | Munshiganj 132/33kV S/S Transformer-2 HT is restored.
| 17:42 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 19:00 |  | Evening Peak Gen. 9879 MW
| 19:04 |  | Adani - Rohanpur 400 kv line-2 was switched on.
| 20:56 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 05:00 |  | Minimum Generation is 6901 MW
| 06:40 | 06:57 | Ashuganj-Shahjibazar 132kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing Distance
Relay relays Due to N/A
| 07:15 |  | Purbasadipur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to For bus
shutdown at Purbasadipur grid SS
| 07:15 |  | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to For bus
shutdown at Purbasadipur grid SS.
| 07:15 |  | Purbasadipur 132/33kV S/S Single Bus Scheduled S/D | [7 empty] | 180.0MW load
interrup.
| 07:30 |  | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Wzpdcl 33 kv loop connection work. | [7 empty] | 14.0MW load
interrup.
| 07:31 |  | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Wzpdcl 33 kv loop connection work. | [7 empty] | 14.0MW load
interrup.
| 07:58 |  | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9475200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 9001000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 289 | 6943156 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 187450 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 4185584 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 136080 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 147360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 66579 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 132775 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 387000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 402840 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 379800 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 33 | 787900 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 196800 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 2357568 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 49 | 534720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 393120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 225675 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 54 | 543600 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.654 | 1861 | 36484207
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132840 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 307200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 962040 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5289421 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 81 | 645672 | -
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 8 | 114768 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 18 | 194880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 911520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21820 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 70255 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 306110 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 15 | 212160 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 452891 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 48509 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13718180 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 27 | 364800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 275 | 6589090.91 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1429 | 30342156.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 48 | 1268000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 360 | 8254000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 29 | 735192 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 685440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 184 | 4416000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1201348 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 674109 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 579880 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 84 | 885600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 48 | 989760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 382910 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 518280 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 278400 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 490318 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1081 | 21359237
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 23 | 450240 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 304800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1095600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 330690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 138720 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 24 | 396360 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 131 | 2730510
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 29 | 701000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3564163.63 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 801144 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 107712 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 662880 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1959360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 270000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 480384 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7293000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Partial Shutdown due to maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7669100 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1012 | 23508743.63
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 633 | 19922909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 612720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 625 | 12843640 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1258 | 33379269
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 131774 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 3228000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 14961454.55 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 240868 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 351600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6502000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4000 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1171 | 25419696.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 183 | 4580400 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 201 | 4300191 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 387 | 8860436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 66888 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 34 | 321230 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 435024 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 48480 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 762 | 16369091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 432000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 757940 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1660.5 | 36209780
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3906000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 252672 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25145.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 81 | 815217 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 179860 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1143000 | -
Rangpur Area Total |  |  |  |  | 950 | 276 | 6321894.64
Eastern Grid Total |  |  |  |  | 16772.132 | 5514 | 114424854.54
Western Grid Total |  |  |  |  | 10294.5 | 4365.5 | 101330640.19
National Grid Total |  |  |  |  | 27066.632 | 9879.5 | 215755494.73
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6361.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3204.6 | MW
i) Dhaka area |  |  | 3253.05 |  | MW | i) Khulna area |  |  |  | 1136 | MW
ii) Chattogram area |  |  | 1003.7 |  | MW | ii) Barishal area |  |  |  | 285 | MW
iii) Cumilla area |  |  | 847 |  | MW | iii) Rajshahi area |  |  |  | 1027.6 | MW
iv) Mymensingh area |  |  | 902 |  | MW | iv) Rangpur area |  |  |  | 756 | MW
v) Sylhet area |  |  | 356 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9566.35 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 62 | 09:00 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 105.7 | 15:00 | 68 | Jamalpur | 93 | 18:30 | 134 | Purbasadipur | 130 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 102 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 73 | 13:00 | 70 | Jhenaidah | 95 | 18:30 | 136 | Rahim | 20 | 00:00
5 | Agrabad | 56 | 19:00 | 71 | Joydebpur | 111 | 12:00 | 137 | Rajbari | 52 | 18:30
6 | Amnura | 63 | 10:00 | 72 | Joypurhat | 54 | 09:00 | 138 | Rajendrapur | 88 | 13:00
7 | Ashuganj | 93 | 22:00 | 73 | Juldah | 10 | 00:00 | 139 | Rajshahi | 95 | 13:00
8 | BSRM | 195 | 20:00 | 74 | KSRM | 31 | 08:00 | 140 | Rajshahi-230 | 44 | 13:00
9 | Bagerhat | 58 | 19:00 | 75 | Kabirpur | 160 | 00:00 | 141 | Ramganj | 98 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 52 | 13:00 | 142 | Rampur | 25 | 00:00
11 | Bakulia | 61 | 13:00 | 77 | Kallyanpur | 81 | 12:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 26 | 13:00 | 78 | Kalurghat | 22 | 00:00 | 144 | Rangpur | 107 | 13:00
13 | Bangabhaban | 3 | 11:00 | 79 | Kamrangirchar | 49.5 | 00:00 | 145 | Ruppur | 4 | 11:00
14 | Barapukuria | 62 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 0 | 00:00
15 | Barguna | 14 | 21:00 | 81 | Kazla | 84 | 13:00 | 147 | Saidpur | 97 | 10:00
16 | Barishal | 75 | 13:00 | 82 | Keranigonj | 47 | 00:00 | 148 | Satkhira | 90 | 08:00
17 | Barishal-230 | 60 | 20:00 | 83 | Khagrachori | 24 | 18:30 | 149 | Satmasjid | 76 | 13:00
18 | Baroaulia | 42 | 15:00 | 84 | Khulna | 59 | 13:00 | 150 | Savar | 116 | 11:00
19 | Baroirhat | 50 | 13:00 | 85 | Khulshi | 139 | 12:00 | 151 | SevenRings | 15.97 | 00:00
20 | Bashundhara | 127 | 13:00 | 86 | Kishoreganj | 118 | 13:00 | 152 | ShahCement | 32 | 01:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 221 | 00:00 | 153 | Shahjadpur | 50 | 18:30
22 | Beanibazar | 44 | 13:00 | 88 | Kulaura | 26 | 12:00 | 154 | Shahjibazar | 74 | 21:00
23 | Benapole | 52 | 07:00 | 89 | Kurigram | 65 | 08:00 | 155 | Shahmirpur | 38 | 05:00
24 | Bhaluka | 98 | 09:00 | 90 | Kushtia | 98 | 18:30 | 156 | Shariatpur | 51 | 13:00
25 | Bhandaria | 35 | 14:00 | 91 | Lalbag | 53 | 00:00 | 157 | Sherpur | 116 | 23:00
26 | Bhangura | 30 | 13:00 | 92 | Lalmonirhat | 46 | 18:30 | 158 | Shikalbaha | 18 | 11:00
27 | Bheramara(GK) | 38 | 18:30 | 93 | MI_Cement | 17.7 | 01:00 | 159 | Shitalakhya | 44 | 13:00
28 | Bhulta | 212 | 00:00 | 94 | Madanganj | 19 | 11:00 | 160 | Sholosohor | 31 | 00:00
29 | Bog-Sherpur | 66 | 09:00 | 95 | Madaripur | 66 | 13:00 | 161 | Shyampur | 146 | 00:00
30 | Bogura | 102 | 10:00 | 96 | Madartek | 54.8 | 13:00 | 162 | Siddhirganj | 87 | 12:00
31 | Borhanuddin | 54 | 00:00 | 97 | Madunaghat | 31 | 12:00 | 163 | Sirajganj | 76 | 18:30
32 | Brahmanbaria | 112 | 13:00 | 98 | Magura | 44 | 18:30 | 164 | Sonargaon | 90 | 00:00
33 | Cantonment | 76 | 13:00 | 99 | Mahasthangarh | 58 | 08:00 | 165 | Sreemongol | 53 | 18:30
34 | Chandpur | 43 | 13:00 | 100 | Manikganj | 97 | 18:30 | 166 | Sreepur | 61 | 00:00
35 | Chandraghona | 25 | 13:00 | 101 | Maniknagar | 44 | 13:00 | 167 | Srinagar | 33.25 | 13:00
36 | Chapai | 56 | 08:00 | 102 | Matarbari | 35 | 18:00 | 168 | Sunamganj | 38 | 18:30
37 | Charsaidpur | 39 | 19:30 | 103 | Matuail | 42 | 00:00 | 169 | Sylhet | 22 | 18:00
38 | Chauddagram | 45 | 11:00 | 104 | Millgate | 53 | 00:00 | 170 | Sylhet-132 | 83 | 13:00
39 | Chhatak | 23 | 19:00 | 105 | Mirpur | 86 | 13:00 | 171 | TK | 21 | 18:30
40 | Chowmuhani | 134 | 13:00 | 106 | Mirsorai | 7 | 00:00 | 172 | Tangail | 148 | 07:00
41 | Chuadanga | 73 | 13:00 | 107 | Mirzapur | 35 | 07:00 | 173 | Thakurgaon | 79 | 19:00
42 | Coxsbazar | 107 | 18:00 | 108 | Mithapukur | 72 | 08:00 | 174 | Tongi | 78 | 11:00
43 | Cumilla(N) | 131 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 23 | 08:00
44 | Cumilla(S) | 111 | 13:00 | 110 | Mogbazar | 85.8 | 13:00 | 176 | Ullon | 37 | 11:00
45 | Daudkandi | 96 | 00:00 | 111 | Mongla | 28 | 02:00 | 177 | Uttara | 61 | 13:00
46 | Dhaka | 16 | 11:00 | 112 | Motijheel | 24 | 13:00 | 178 | UttaraNew | 35 | 13:00
47 | Dhamrai | 84 | 11:00 | 113 | Muktagacha | 28 | 18:00 | 179 | Zigatola | 54 | 13:00
48 | Dhanmondi | 84 | 13:00 | 114 | Munshiganj | 71 | 13:00
49 | Dohazari | 68 | 18:30 | 115 | Mymensingh | 177 | 13:00
50 | Faridpur | 95 | 00:00 | 116 | Naogaon | 111 | 09:00
51 | Fatullah | 62 | 00:00 | 117 | Narail | 39 | 19:00
52 | Fenchuganj | 27 | 12:00 | 118 | Narinda | 44 | 13:00
53 | Feni | 66 | 13:00 | 119 | Narshingdi | 140 | 00:00
54 | GPH | 15 | 00:00 | 120 | Natore | 99 | 18:30
55 | Ghatail | 52 | 07:00 | 121 | Nawabganj | 32.4 | 13:00
56 | Ghorashal | 10 | 00:00 | 122 | Netrakona | 146 | 08:00
57 | Ghorashal-230 | 98 | 17:00 | 123 | New | 53.3 | 00:00
58 | Goalpara | 22 | 13:00 | 124 | Niamatpur | 89 | 08:00
59 | Gollamari | 52 | 13:00 | 125 | Noapara | 29 | 19:00
60 | Gopalganj | 68.6 | 21:00 | 126 | PHP | 7 | 03:00
61 | Gulshan | 58 | 13:00 | 127 | Pabna | 56 | 19:00
62 | Halishahar | 45 | 13:00 | 128 | Palashbari | 104 | 08:00
63 | HaripurSBU | 140 | 23:00 | 129 | Panchagarh | 42 | 18:30
64 | Hasnabad | 60 | 14:00 | 130 | Patuakhali | 48.5 | 21:00
65 | Hathazari | 52 | 12:00 | 131 | Payra | 20 | 12:00
66 | Ishurdi | 52 | 19:00 | 132 | Postogola | 30 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9525.24 | 0 |  | 9525.24
1:00 | 8848.5 | 30 |  | 8879.5
2:00 | 8455.5 | 27 |  | 8483.5
3:00 | 8160.5 | 25 |  | 8186.5
4:00 | 7926.5 | 25 |  | 7952.5
5:00 | 7877.5 | 25 |  | 7903.5
6:00 | 8103.5 | 50 |  | 8155.5
7:00 | 8412.74 | 35 |  | 8449.74
8:00 | 9143.57 | 70 |  | 9216.57
9:00 | 9332.58 | 60 |  | 9395.28
10:00 | 9220.35 | 45 |  | 9267.35
11:00 | 9353.21 | 50 |  | 9405.46
12:00 | 9812.18 | 50 |  | 9864.18
13:00 | 10317.19 | 105 |  | 10427.19
14:00 | 8837.77 | 30 |  | 8869.12
15:00 | 8363.01 | 40 |  | 8404.81
16:00 | 8129.81 | 30 |  | 8160.81
17:00 | 8194.94 | 30 |  | 8225.94
18:00 | 8785.5 | 40 |  | 8827.5
19:00 | 9879.5 | 30 |  | 9910.5
19:30 | 9827 | 30 |  | 9858
20:00 | 9779.5 | 30 |  | 9810.5
21:00 | 9705.59 | 30 |  | 9736.59
22:00 | 9385.27 | 0 |  | 9385.27
23:00 | 8853.9 | 0 |  | 8853.9
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5258 | 4267.24 | 9525.24 | DAILY GENERATION CURVE
00:30 | 4976.5 | 4210.37 | 9186.87
01:00 | 4695 | 4153.5 | 8848.5 | 07-02-2025
01:30 | 4586.5 | 4065.5 | 8652
02:00 | 4478 | 3977.5 | 8455.5
02:30 | 4436.5 | 3871.5 | 8308
03:00 | 4395 | 3765.5 | 8160.5
03:30 | 4314.5 | 3729 | 8043.5
04:00 | 4234 | 3692.5 | 7926.5
04:30 | 4218.5 | 3683.5 | 7902
05:00 | 4203 | 3674.5 | 7877.5
05:30 | 4190 | 3800.5 | 7990.5
06:00 | 4177 | 3926.5 | 8103.5
06:30 | 4296.37 | 3961.75 | 8258.12
07:00 | 4415.74 | 3997 | 8412.74
07:30 | 4623.315 | 4154.84 | 8778.155
08:00 | 4830.89 | 4312.68 | 9143.57
08:30 | 4857.805 | 4380.27 | 9238.075
09:00 | 4884.72 | 4447.86 | 9332.58
09:30 | 4780.74 | 4495.725 | 9276.465
10:00 | 4676.76 | 4543.59 | 9220.35
10:30 | 4702.48 | 4584.3 | 9286.78
11:00 | 4728.2 | 4625.01 | 9353.21
11:30 | 4813.905 | 4768.79 | 9582.695
12:00 | 4899.61 | 4912.57 | 9812.18
12:30 | 5071.485 | 4993.2 | 10064.685
13:00 | 5243.36 | 5073.83 | 10317.19
13:30 | 4872.485 | 4704.995 | 9577.48
14:00 | 4501.61 | 4336.16 | 8837.77
14:30 | 4361.62 | 4238.77 | 8600.39
15:00 | 4221.63 | 4141.38 | 8363.01
15:30 | 4252.74 | 3993.67 | 8246.41
16:00 | 4283.85 | 3845.96 | 8129.81
16:30 | 4316.775 | 3845.6 | 8162.375
17:00 | 4349.7 | 3845.24 | 8194.94
17:30 | 4499.35 | 3990.87 | 8490.22
18:00 | 4649 | 4136.5 | 8785.5
18:30 | 5081.5 | 4251 | 9332.5
19:00 | 5514 | 4365.5 | 9879.5
19:30 | 5376.5 | 4450.5 | 9827
20:00 | 5325 | 4454.5 | 9779.5
20:30 | 5185.5 | 4557.045 | 9742.545 |  | Executive Engineer
21:00 | 5046 | 4659.59 | 9705.59 |  | Network Operation Division
21:30 | 4991 | 4554.43 | 9545.43
22:00 | 4936 | 4449.27 | 9385.27
22:30 | 4770 | 4349.585 | 9119.585
23:00 | 4604 | 4249.9 | 8853.9

## En-Curve
QF-LDC-12
Date | 07-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2605 | 1636.5 | 914 | 0 | 40 | 757.74 | 40 | 2336 | 0 | 207 | 987 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 2647 | 1655.5 | 913.5 | 0 | 38 | 755.37 | 40 | 2386.5 | 0 | 112 | 635.5 | 0 | 0 | 3.5 | 15 | 07-02-2025
01:00 | 2689 | 1674.5 | 913 | 0 | 36 | 753 | 40 | 2437 | 0 | 17 | 284 | 0 | 0 | 5 | 30
01:30 | 2694 | 1691.5 | 912.5 | 0 | 36 | 668 | 40 | 2376 | 0 | 8.5 | 216 | 0 | 0 | 9.5 | 28.5 | Energy Generated | 215.7555 |  | MKWHr
02:00 | 2699 | 1708.5 | 912 | 0 | 36 | 583 | 40 | 2315 | 0 | 0 | 148 | 0 | 0 | 14 | 27 | Energy not Served | 0.857 |  | MKWHr
02:30 | 2650.5 | 1723.5 | 870.5 | 0 | 35 | 574.5 | 40 | 2249.5 | 0 | 0 | 148 | 0 | 0 | 16.5 | 26 | Total Energy Requirement | 216.6125 |  | MKWHr
03:00 | 2602 | 1738.5 | 829 | 0 | 34 | 566 | 40 | 2184 | 0 | 0 | 148 | 0 | 0 | 19 | 25
03:30 | 2550.5 | 1721 | 776.5 | 0 | 35 | 564.5 | 40 | 2190.5 | 0 | 0 | 145.5 | 0 | 0 | 20 | 25
04:00 | 2499 | 1703.5 | 724 | 0 | 36 | 563 | 40 | 2197 | 0 | 0 | 143 | 0 | 0 | 21 | 25
04:30 | 2453 | 1698.5 | 724 | 0 | 34 | 564 | 40 | 2233 | 0 | 4 | 127 | 0 | 0 | 24.5 | 25
05:00 | 2407 | 1693.5 | 724 | 0 | 32 | 565 | 40 | 2269 | 0 | 8 | 111 | 0 | 0 | 28 | 25
05:30 | 2323 | 1772 | 724 | 0 | 32 | 612 | 40 | 2330.5 | 0 | 16.5 | 118 | 0 | 0 | 22.5 | 37.5
06:00 | 2239 | 1850.5 | 724 | 0 | 32 | 659 | 40 | 2392 | 0 | 25 | 125 | 0 | 0 | 17 | 50
06:30 | 2184.5 | 1851.5 | 724 | 0 | 32 | 664.5 | 40 | 2459 | 8.62 | 25 | 249.5 | 0 | 0 | 19.5 | 42.5
07:00 | 2130 | 1852.5 | 724 | 0 | 32 | 670 | 40 | 2526 | 17.24 | 25 | 374 | 0 | 0 | 22 | 35
07:30 | 2230.5 | 1864.5 | 676.5 | 0 | 32 | 715.5 | 40 | 2545.5 | 93.155 | 46 | 516 | 0 | 0 | 18.5 | 52.5
08:00 | 2331 | 1876.5 | 629 | 0 | 32 | 761 | 40 | 2565 | 169.07 | 67 | 658 | 0 | 0 | 15 | 70
08:30 | 2335 | 1847.5 | 629 | 0 | 34 | 759 | 40 | 2566 | 264.575 | 67 | 685 | 0 | 0 | 11 | 65
09:00 | 2339 | 1818.5 | 629 | 0 | 36 | 757 | 40 | 2567 | 360.08 | 67 | 712 | 0 | 0 | 7 | 60
09:30 | 2308 | 1834.5 | 734 | 0 | 38 | 712 | 40 | 2519.5 | 435.965 | 67 | 579.5 | 0 | 0 | 8 | 52.5
10:00 | 2277 | 1850.5 | 839 | 0 | 40 | 667 | 40 | 2472 | 511.85 | 67 | 447 | 0 | 0 | 9 | 45
10:30 | 2275 | 1869.5 | 876.5 | 0 | 44 | 665 | 40 | 2442 | 563.28 | 71 | 426.5 | 0 | 0 | 14 | 47.5
11:00 | 2273 | 1888.5 | 914 | 0 | 48 | 663 | 40 | 2412 | 614.71 | 75 | 406 | 0 | 0 | 19 | 50
11:30 | 2301 | 1897 | 914 | 0 | 52 | 709.5 | 40 | 2470.5 | 639.195 | 83 | 458 | 0 | 0 | 18.5 | 50
12:00 | 2329 | 1905.5 | 914 | 0 | 56 | 756 | 40 | 2529 | 663.68 | 91 | 510 | 0 | 0 | 18 | 50
12:30 | 2327 | 1869.5 | 914 | 0 | 56 | 756 | 40 | 2546.5 | 656.185 | 105.5 | 779.5 | 0 | 0 | 14.5 | 77.5
13:00 | 2325 | 1833.5 | 914 | 0 | 56 | 756 | 40 | 2564 | 648.69 | 120 | 1049 | 0 | 0 | 11 | 105
13:30 | 2265.5 | 1745.5 | 914 | 0 | 53 | 688 | 40 | 2387 | 614.48 | 76.5 | 779 | 0 | 0 | 14.5 | 67.5
14:00 | 2206 | 1657.5 | 914 | 0 | 50 | 620 | 40 | 2210 | 580.27 | 33 | 509 | 0 | 0 | 18 | 30
14:30 | 2218.5 | 1667.5 | 914 | 0 | 48 | 618 | 40 | 2175.5 | 518.89 | 29 | 357 | 0 | 0 | 14 | 35
15:00 | 2231 | 1677.5 | 914 | 0 | 46 | 616 | 40 | 2141 | 457.51 | 25 | 205 | 0 | 0 | 10 | 40
15:30 | 2326 | 1687 | 829 | 0 | 46 | 615.5 | 40 | 2146.5 | 363.41 | 16.5 | 164 | 0 | 0 | 12.5 | 35
16:00 | 2421 | 1696.5 | 744 | 0 | 46 | 615 | 40 | 2152 | 269.31 | 8 | 123 | 0 | 0 | 15 | 30
16:30 | 2495 | 1701.5 | 781 | 0 | 45.5 | 616.5 | 40 | 2160 | 171.375 | 8 | 128 | 0 | 0 | 15.5 | 30
17:00 | 2569 | 1706.5 | 818 | 0 | 45 | 618 | 40 | 2168 | 73.44 | 8 | 133 | 0 | 0 | 16 | 30
17:30 | 2454 | 1692 | 865.5 | 0 | 45.5 | 639.5 | 40 | 2261.5 | 36.72 | 84.5 | 354.5 | 0 | 0 | 16.5 | 35
18:00 | 2339 | 1677.5 | 913 | 0 | 46 | 661 | 40 | 2355 | 0 | 161 | 576 | 0 | 0 | 17 | 40
18:30 | 2550.5 | 1717.5 | 773 | 0 | 47 | 711.5 | 40 | 2457.5 | 0 | 166.5 | 847 | 0 | 0 | 22 | 35
19:00 | 2762 | 1757.5 | 633 | 0 | 48 | 762 | 40 | 2560 | 0 | 172 | 1118 | 0 | 0 | 27 | 30
19:30 | 2788 | 1823 | 633 | 0 | 46 | 759 | 40 | 2595 | 0 | 140 | 989 | 0 | 0 | 14 | 30
20:00 | 2793 | 1814.5 | 633 | 0 | 48 | 761 | 40 | 2595 | 0 | 140 | 937 | 0 | 0 | 18 | 30
20:30 | 2772 | 1813 | 778 | 0 | 49 | 758.545 | 40 | 2595 | 0 | 127.5 | 791 | 0 | 0 | 18.5 | 30
21:00 | 2751 | 1811.5 | 923 | 0 | 50 | 756.09 | 40 | 2595 | 0 | 115 | 645 | 0 | 0 | 19 | 30
21:30 | 2820 | 1794 | 923 | 0 | 46 | 757.43 | 40 | 2595 | 0 | 61.5 | 495.5 | 0 | 0 | 13 | 15
22:00 | 2889 | 1776.5 | 923 | 0 | 42 | 758.77 | 40 | 2595 | 0 | 8 | 346 | 0 | 0 | 7 | 0
22:30 | 2903.5 | 1749 | 923 | 0 | 41 | 719.585 | 40 | 2519 | 0 | 8 | 207 | 0 | 0 | 9.5 | 0
23:00 | 2918 | 1721.5 | 923 | 0 | 40 | 680.4 | 40 | 2443 | 0 | 8 | 68 | 0 | 0 | 12 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 05:00 | 399 | 12:00 | Payra | 422 | 19:00 | 411 | 11:00
Ashuganj | 412 | 0:00 | 391 | 16:00 | Rahanpur | 419 | 05:00 | 394 | 08:00
Bhulta | 413 | 06:00 | 397 | 12:00 | Rampal | 411 | 04:00 | 398 | 12:00
Bibiana | 412 | 14:00 | 404 | 11:00
BIPTC | 407 | 04:00 | 387 | 13:00
Bogura | 417 | 04:00 | 394 | 09:00
Gopalganj | 416 | 05:00 | 403 | 12:00
Kaliakoir | 400 | 05:00 | 379 | 14:00
Madunaghat | 410 | 00:00 | 404 | 12:00
Meghnaghat | 410 | 05:00 | 395 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 05:00 | 230 | 12:00 | Keranigonj | 237 | 06:00 | 229 | 12:00
AKSML | 238 | 19:00 | 230 | 00:00 | Khulna(S) | 241 | 05:00 | 229 | 13:00
Aminbazar | 238 | 18:00 | 232 | 12:00 | Madunaghat | 236 | 00:00 | 230 | 10:00
Ashuganj | 244 | 06:00 | 236 | 13:00 | Madunaghat-400 | 237 | 09:00 | 231 | 12:00
Ashuganj-400 | 241 | 01:00 | 232 | 17:00 | Maniknagar | 237 | 05:00 | 229 | 12:00
Baghabari | 240 | 04:00 | 229 | 12:00 | Meghnaghat | 243 | 04:00 | 238 | 12:00
Barapukuria | 228 | 14:00 | 216 | 09:00 | Meghnaghat-400 | 240 | 05:00 | 231 | 12:00
Barapukuria-230 | 228 | 14:00 | 216 | 09:00 | Mirsorai | 236 | 00:00 | 229 | 11:00
Barishal | 247 | 04:00 | 240 | 13:00 | Rajshahi | 242 | 05:00 | 222 | 12:00
Bheramara | 240 | 05:00 | 223 | 12:00 | Rampal | 238 | 05:00 | 228 | 12:00
Bhulta | 240 | 06:00 | 230 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 239 | 00:00 | 232 | 12:00 | Rampura | 238 | 05:00 | 229 | 12:00
BIPTC | 242 | 05:00 | 224 | 12:00 | Shikalbaha | 235 | 13:00 | 230 | 10:00
Bogura | 242 | 04:00 | 228 | 12:00 | Shyampur | 239 | 19:00 | 230 | 12:00
Bogura-400 | 240 | 03:00 | 228 | 08:00 | Siddhirganj | 239 | 07:00 | 237 | 00:00
Borhanuddin | 248 | 04:00 | 244 | 13:00 | Sirajgonj | 247 | 04:00 | 237 | 12:00
BSRM | 237 | 09:00 | 229 | 12:00 | Sreepur | 243 | 05:00 | 229 | 12:00
Cumilla(N) | 240 | 19:00 | 231 | 11:00 | Tongi | 236 | 07:00 | 228 | 11:00
Faridpur | 245 | 04:00 | 239 | 12:00
Fenchuganj | 244 | 09:00 | 237 | 01:00
Ghorashal | 240 | 08:00 | 235 | 00:00
Ghorashal-230 | 239 | 05:00 | 229 | 12:00
Gopalganj | 246 | 05:00 | 239 | 12:00
GPH | 236 | 00:00 | 230 | 11:00
Haripur | 240 | 19:00 | 231 | 12:00
Hasnabad | 238 | 05:00 | 232 | 12:00
Hathazari | 237 | 09:00 | 231 | 12:00
Ishurdi | 243 | 05:00 | 226 | 12:00
Jhenaidah | 240 | 05:00 | 222 | 13:00
Kaliakoir | 236 | 02:00 | 228 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 00:00 | 129 | 12:00 | Magura | 140 | 06:00 | 126 | 12:00
Agargaon | 139 | 05:00 | 133 | 12:00 | Mahasthangarh | 136 | 00:00 | 127 | 08:00
Agrabad | 135 | 00:00 | 130 | 10:00 | Manikganj | 137 | 18:30 | 134 | 07:00
AKS | 135 | 01:00 | 130 | 12:00 | Maniknagar | 135 | 08:00 | 130 | 12:00
Aminbazar | 137 | 03:00 | 134 | 10:00 | Matarbari | 127 | 04:00 | 120 | 11:00
Amnura | 141 | 05:00 | 128 | 08:00 | Matuail | 138 | 18:00 | 133 | 12:00
Ashuganj | 143 | 04:00 | 138 | 08:00 | Millgate | 139 | 03:00 | 131 | 12:00
Bagerhat | 139 | 06:00 | 130 | 12:00 | Mirpur | 137 | 05:00 | 131 | 12:00
Bajitpur | 137 | 04:00 | 131 | 12:00 | Mirzapur | 137 | 04:00 | 130 | 07:00
Bakulia | 135 | 00:00 | 129 | 11:00 | Mithapukur | 134 | 00:00 | 124 | 08:00
Banani | 139 | 08:00 | 129 | 12:00 | MI_Cement | 139.4 | 19:00 | 133.6 | 12:00
Bangabhaban | 136 | 03:00 | 130 | 12:00 | Modern | 0 | 0 | 0 | 0
Barapukuria | 137 | 00:00 | 127 | 09:00 | Mogbazar | 138 | 02:00 | 130 | 12:00
Barguna | 139 | 09:00 | 136 | 06:00 | Mongla | 138 | 04:00 | 128 | 12:00
Barishal | 137 | 05:00 | 132 | 12:00 | Motijheel | 136 | 03:00 | 130 | 12:00
Barishal-230 | 137 | 05:00 | 133 | 12:00 | Muktagacha | 129 | 06:00 | 118 | 07:00
Baroaulia | 136 | 00:00 | 131 | 11:00 | Munshiganj | 139 | 19:00 | 132 | 12:00
Baroirhat | 137 | 00:00 | 129 | 12:00 | Mymensingh | 127 | 02:00 | 116 | 07:00
Bashundhara | 138 | 00:00 | 129 | 12:00 | Naogaon | 134 | 00:00 | 125 | 08:00
BashundharaCement | 138 | 18:00 | 132 | 14:00 | Narail | 140 | 06:00 | 125 | 12:00
Beanibazar | 138 | 04:00 | 132 | 13:00 | Narinda | 135 | 08:00 | 130 | 12:00
Benapole | 138 | 04:00 | 124 | 12:00 | Narshingdi | 136 | 01:00 | 131 | 11:00
Bhaluka | 130 | 00:00 | 122 | 12:00 | Natore | 138 | 00:00 | 129 | 12:00
Bhandaria | 134 | 03:00 | 129 | 13:00 | Nawabganj | 139 | 04:00 | 134 | 12:00
Bhangura | 139 | 03:00 | 130 | 12:00 | Netrakona | 126 | 21:00 | 118 | 12:00
Bheramara | 139 | 05:00 | 130 | 11:00 | New | 139 | 19:00 | 132 | 12:00
Bheramara(GK) | 139 | 03:00 | 128 | 12:00 | Niamatpur | 140 | 01:00 | 131 | 12:00
Bhulta | 134 | 18:00 | 130 | 11:00 | Noapara | 139 | 06:00 | 128 | 13:00
Bog-Sherpur | 137 | 04:00 | 129 | 08:00 | Pabna | 138 | 05:00 | 128 | 12:00
Bogura | 138 | 03:00 | 130 | 09:00 | Palashbari | 133 | 00:00 | 120 | 09:00
Bogura-230 | 138 | 04:00 | 130 | 08:00 | Panchagarh | 141 | 00:00 | 122 | 09:00
Brahmanbaria | 139 | 06:00 | 134 | 11:00 | Patuakhali | 138 | 14:00 | 136 | 11:00
Cantonment | 139 | 05:00 | 133 | 12:00 | Payra | 139 | 22:00 | 136 | 02:00
Chandpur | 140 | 00:00 | 125 | 17:00 | PHP | 135 | 00:00 | 127 | 12:00
Chandraghona | 137 | 00:00 | 132 | 11:00 | Postogola | 141 | 19:00 | 136 | 12:00
Chapai | 139 | 02:00 | 130 | 08:00 | Purbachal | 136 | 03:00 | 129 | 12:00
Charsaidpur | 139 | 18:00 | 133 | 12:00 | Purbasadipur | 134 | 00:00 | 118 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 137 | 00:00 | 130 | 17:00 | Rahanpur | 141 | 02:00 | 134 | 09:00
Chhatak | 138 | 05:00 | 131 | 11:00 | Rahanpur-400 | 142 | 03:00 | 133 | 08:00
Chowmuhani | 136 | 00:00 | 126 | 13:00 | Rahim | 136 | 18:00 | 13.5 | 03:00
Chuadanga | 139 | 06:00 | 125 | 12:00 | Rajbari | 136 | 04:00 | 132 | 12:00
Coxsbazar | 125 | 03:00 | 120 | 12:00 | Rajendrapur | 140 | 19:00 | 132 | 13:00
Cumilla(N) | 140 | 19:00 | 133 | 11:00 | Rajshahi | 140 | 00:00 | 132 | 07:00
Cumilla(S) | 139 | 19:00 | 128 | 12:00 | Rajshahi-230 | 140 | 04:00 | 122 | 11:00
Daudkandi | 136 | 19:00 | 131 | 11:00 | Ramganj | 137 | 00:00 | 124 | 17:00
Dhaka | 135 | 01:00 | 130 | 12:00 | Rampur | 135 | 00:00 | 130 | 11:00
Dhamrai | 136 | 03:00 | 133 | 09:00 | Rampura | 136 | 05:00 | 130 | 12:00
Dhanmondi | 138 | 18:00 | 133 | 12:00 | Rangamati | 136 | 00:00 | 131 | 11:00
Dohazari | 133 | 01:00 | 126 | 11:00 | Rangpur | 133 | 00:00 | 121 | 09:00
Faridpur | 136 | 01:00 | 132 | 12:00 | Ruppur | 140 | 05:00 | 132 | 12:00
Fatullah | 140 | 18:00 | 134 | 12:00 | Saidpur | 133 | 00:00 | 122 | 08:00
Fenchuganj | 142 | 00:00 | 137 | 10:00 | Satkhira | 138 | 06:00 | 129 | 12:00
Feni | 137 | 00:00 | 126 | 17:00 | Satmasjid | 138 | 03:00 | 132 | 12:00
Ghatail | 128 | 14:00 | 119 | 07:00 | Savar | 138 | 18:00 | 131 | 12:00
Ghorashal | 143 | 08:00 | 139 | 11:00 | SevenRings | 143 | 05:00 | 138 | 12:00
Goalpara | 140 | 05:00 | 129 | 11:00 | ShahCement | 139 | 18:00 | 133 | 12:00
Gollamari | 137 | 00:00 | 132 | 12:00 | Shahjadpur | 142 | 01:00 | 135 | 11:00
Gopalganj | 138 | 04:00 | 132 | 12:00 | Shahjibazar | 140 | 09:00 | 137 | 11:00
Gopalganj-400 | 138 | 04:00 | 133 | 12:00 | Shahmirpur | 136 | 18:30 | 130 | 10:00
Gulshan | 136 | 04:00 | 129 | 12:00 | Shariatpur | 137 | 02:00 | 132 | 12:00
Halishahar | 136 | 00:00 | 130 | 16:00 | Sherpur | 120 | 22:00 | 111 | 07:00
Haripur | 137 | 18:00 | 132 | 12:00 | Shikalbaha | 124 | 00:00 | 118 | 11:00
HaripurSBU | 137 | 18:30 | 133 | 11:00 | Shikalbaha-230 | 135 | 00:00 | 130 | 10:00
Hasnabad | 141 | 18:00 | 136 | 13:00 | Shitalakhya | 139 | 18:00 | 133.6 | 12:00
Hathazari | 139 | 18:30 | 134 | 12:00 | Sholosohor | 136 | 00:00 | 132 | 11:00
Ishurdi | 141 | 04:00 | 131 | 12:00 | Shyampur | 138 | 04:00 | 134 | 12:00
Jaldhaka | 132 | 00:00 | 120 | 08:00 | Shyampur-230 | 140 | 18:30 | 134 | 12:00
Jamalpur | 122 | 15:00 | 114 | 14:00 | Siddhirganj | 138 | 18:00 | 133 | 12:00
Jashore | 138 | 06:00 | 126 | 12:00 | Sirajganj | 138 | 01:00 | 130 | 08:00
Jhenaidah | 139 | 04:00 | 128 | 12:00 | Sonargaon | 137 | 18:30 | 131 | 10:00
Jhenaidah-230 | 141 | 04:00 | 128 | 12:00 | Sreemongol | 140 | 05:00 | 135 | 11:00
Joydebpur | 142 | 18:30 | 124 | 23:00 | Sreepur | 132 | 05:00 | 32 | 05:00
Joypurhat | 134 | 00:00 | 123 | 09:00 | Srinagar | 140 | 05:00 | 134 | 12:00
Juldah | 136 | 08:00 | 129 | 11:00 | SSM | 140 | 00:00 | 136 | 11:00
Kabirpur | 141 | 18:30 | 47 | 17:00 | Sunamganj | 136 | 03:00 | 130 | 11:00
Kachua | 140 | 19:00 | 128 | 11:00 | Sylhet | 139 | 05:00 | 132 | 13:00
Kaliakoir | 142 | 01:00 | 135 | 13:00 | Sylhet-132 | 139 | 05:00 | 133 | 12:00
Kallyanpur | 136 | 02:00 | 130 | 12:00 | Tangail | 132 | 22:00 | 123 | 07:00
Kalurghat | 136 | 00:00 | 122 | 10:00 | Thakurgaon | 140 | 00:00 | 120 | 09:00
Kamrangirchar | 139 | 00:00 | 129 | 12:00 | TK | 137 | 00:00 | 132 | 09:00
Kaptai | 137 | 1:00 | 125 | 12:00 | Tongi | 140 | 07:00 | 133 | 11:00
Kazla | 135 | 01:00 | 129 | 13:00 | Ullahpara | 139 | 03:00 | 132 | 12:00
Keranigonj | 138 | 00:00 | 133 | 12:00 | Ullon | 136 | 02:00 | 130 | 11:00
Khagrachori | 136 | 00:00 | 130 | 11:00 | Uttara | 139 | 06:00 | 131 | 12:00
Khulna | 137 | 02:00 | 130 | 12:00 | UttaraNew | 139 | 04:00 | 131 | 12:00
Khulna(S) | 140 | 04:00 | 132 | 12:00 | Zigatola | 140 | 06:00 | 133 | 13:00
Khulshi | 134 | 08:00 | 128 | 11:00
Kishoreganj | 132 | 00:00 | 127 | 08:00
Kodda | 139 | 03:00 | 131 | 16:00
KSRM | 137 | 00:00 | 131 | 11:00
Kulaura | 140 | 00:00 | 137 | 12:00
Kurigram | 132 | 14:00 | 120 | 09:00
Kushtia | 139 | 02:00 | 128 | 12:00
Lalbag | 140 | 05:00 | 134 | 12:00
Lalmonirhat | 132 | 14:00 | 121 | 09:00
Madanganj | 138 | 18:00 | 132 | 14:00
Madaripur | 137 | 01:00 | 133 | 10:00
Madartek | 135 | 04:00 | 129 | 12:00
Madunaghat | 136 | 00:00 | 132 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division