## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-02-2025 | during | 09-02-2025 | during | 09-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 80 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 402 | 408 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 380 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 313 | 261 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 53 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 82 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 48 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 21 | 21 | 22.5 | 22.5 | 22.5 | 22.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16.5 | 16.5 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 26 | 26 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 4 | 106 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 17 | 17 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 60 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 2 | 46 | 36.09 | 36.09 | 36.09 | 36.09 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.654 | 1730.5 | 2228.5 | 4587.96 | 4557.96 | 2788.39 | 2758.39
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 31 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 227 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 2 | 88 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 8 | 48 | 56 | 72 | 56 | 72 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 2 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 9 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 10 | 108 | 108 | 18 | 18 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 52 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 2 | 70 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 570 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 28 | 35 | 12 | 22 | 12 | 22 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 156 | 280 | 270 | 270 | 275 | 275 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1151 | 1704 | 2535.86 | 2559.86 | 2396.5 | 2420.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 198 | 183 | 221 | 221 | 190 | 190 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 370 | 315 | 356.56 | 356.56 | 310 | 310 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 26 | 31 | 46.94 | 46.94 | 30 | 30 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 30 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 40 | 51 | 40 | 51 | 40 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 130 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 48 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 30 | 163 | 163 | 30 | 30 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 3 | 129 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 50 | 52 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 21 | 75 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 96 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1064 | 1382 | 2089.53 | 2035.53 | 1858.2 | 1804.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-02-2025 | during | 09-02-2025 | during | 09-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 18 | 23 | 210 | 210 | 25 | 25 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 58 | 115 | 115 | 56 | 56 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.93 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 143.93 | 96 | 653.3 | 601.5 | 218.3 | 166.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 28 | 28 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 36 | 40 | 40 | 36 | 36 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 290 | 290 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 988 | 1005 | 1060 | 1060 | 1005 | 1005
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89.59 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 607 | 619 | 617.1 | 617.1 | 617 | 617 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1620.59 | 1496 | 2568.1 | 2483.1 | 2358 | 2273
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 136 | 132 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 600 | 622 | 622 | 622 | 622 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT-11 Shutdown under Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1199.57 | 1191 | 1446.12 | 1445.12 | 1443 | 1442
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 31 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 4 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 33 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 195 | 210 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 212 | 179 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 386 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 52 | 92 | 90 | 90 | 90 | 90 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.43 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 750 | 757.08 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.12 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1801.05 | 1776.58 | 2515.79 | 2351.24 | 2180.01 | 2015.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 165 | 159 | 160 | 160 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 165 | 0 | 175.16 | 0 | 175.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 396.7 | 324 | 631.76 | 422 | 621.76 | 412
System Total |  |  |  |  | 27884.66 | 27066.632 | 10095.34 | 11203.08 | 18088.42 | 17516.31 | 14869.16 | 14297.05
Forecast Scenario (09-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9280 |  | 0 |  | 9280
|  |  |  | 1:00 | 8750 |  | 0 |  | 8750
|  |  |  | 2:00 | 8300 |  | 0 |  | 8300
|  |  |  | 3:00 | 8200 |  | 0 |  | 8200
|  |  |  | 4:00 | 7980 |  | 0 |  | 7980
|  |  |  | 5:00 | 7700 |  | 0 |  | 7700
|  |  |  | 6:00 | 8150 |  | 0 |  | 8150
|  |  |  | 7:00 | 9100 |  | 0 |  | 9100
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 10500 |  | 0 |  | 10500
|  |  |  | 10:00 | 10450 |  | 0 |  | 10450
|  |  |  | 11:00 | 10600 |  | 0 |  | 10600
|  |  |  | 12:00 | 11000 |  | 0 |  | 11000
|  |  |  | 13:00 | 11200 |  | 0 |  | 11200
|  |  |  | 14:00 | 10950 |  | 0 |  | 10950
|  |  |  | 15:00 | 10600 |  | 0 |  | 10600
|  |  |  | 16:00 | 10100 |  | 0 |  | 10100
|  |  |  | 17:00 | 10000 |  | 0 |  | 10000
|  |  |  | 18:00 | 11000 |  | 0 |  | 11000
|  |  |  | 18:30 | 11250 |  | 0 |  | 11250
|  |  |  | 19:00 | 11550 |  | 0 |  | 11550
|  |  |  | 19:30 | 11400 |  | 0 |  | 11400
|  |  |  | 20:00 | 11300 |  | 0 |  | 11300
|  |  |  | 21:00 | 10900 |  | 0 |  | 10900
|  |  |  | 22:00 | 10500 |  | 0 |  | 10500
|  |  |  | 23:00 | 10000 |  | 0 |  | 10000
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 11000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11550.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 237.81 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:45 hrs on 09-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-02-2025 | [28 empty] | Date: | 08-02-2025 | [28 empty] | Date: | 08-02-2025 | [28 empty] | Date: | 08-02-2025 | [28 empty] | Date: | 08-02-2025 | [19 empty] | Date: | 08-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [19 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 330 | 293 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 505 | 0 | 51 | 0 | 158 | 0 | 0 | 365 | 16 | 229 | 29 | 0 | 40 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 300 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 22 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 30 | 0 | 0 | 0 | 4540 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539 | 0 | 616.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 195 | 0 | 391 | 0 | 0 | 2.5 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 7 | 140 | 110 | 0 | 0 | 560 | 0 | 4038.92 | 8578.92 | 91.15
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 300 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 158 | 0 | 0 | 365 | 5 | 231 | 29 | 0 | 30 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 295 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 30 | 0 | 0 | 0 | 4445 | 773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 505.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 189 | 0 | 320 | 0 | 0 | 2.5 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 110 | 0 | 0 | 500 | 0 | 3554.9 | 7999.9 | 91.15
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 295 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 460 | 0 | 51 | 0 | 158 | 0 | 0 | 370 | 5 | 187 | 29 | 0 | 30 | 0 | 0 | 17 | 0 | 32 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 9 | 9 | 37 | 0 | 0 | 0 | 4361 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 413.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 186 | 0 | 310 | 0 | 0 | 2.5 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 7 | 140 | 118 | 0 | 0 | 400 | 0 | 3185.78 | 7546.78 | 91.14
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 291 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 13.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 43 | 274 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 387 | 0 | 51 | 0 | 158 | 0 | 0 | 365 | 5 | 184 | 29 | 0 | 30 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 0 | 290 | 320 | 0 | 5 | 30 | 0 | 5 | 163 | 22 | 0 | 41 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 4165.6 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 419.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 186 | 0 | 309 | 0 | 0 | 2.5 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 140 | 150 | 0 | 0 | 280 | 0 | 3088.97 | 7254.57 | 91.14
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 281 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 13.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 44 | 273 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 108 | 0 | 0 | 365 | 5 | 192 | 26 | 0 | 30 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 0 | 300 | 320 | 0 | 5 | 30 | 0 | 5 | 120 | 16 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 3909.6 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 417.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 140 | 0 | 313 | 0 | 0 | 2.5 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 140 | 220 | 0 | 0 | 280 | 0 | 3109.89 | 7019.49 | 91.13
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 298 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 302 | 0 | 5 | 0 | 108 | 0 | 0 | 365 | 5 | 188 | 26 | 0 | 30 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 0 | 315 | 320 | 0 | 5 | 30 | 0 | 5 | 120 | 16 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 3931.6 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 419.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 143 | 0 | 315 | 0 | 0 | 2.5 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 136 | 110 | 0 | 0 | 280 | 0 | 2970.67 | 6902.27 | 91.13
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 304 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 11.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 276 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 331 | 0 | 8 | 0 | 155 | 0 | 0 | 365 | 5 | 212 | 23 | 0 | 30 | 0 | 0 | 15 | 0 | 32 | 0 | 0 | 0 | 330 | 320 | 0 | 5 | 30 | 0 | 5 | 163 | 16 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 5 | 2 | 43 | 0 | 0 | 0 | 4119.6 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 418.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 0 | 2.5 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 6 | 136 | 110 | 0 | 0 | 290 | 0 | 3163.4 | 7283 | 91.12
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 298 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 1 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 485 | 0 | 51 | 0 | 185 | 0 | 0 | 370 | 13 | 183 | 23 | 0 | 30 | 0 | 0 | 15 | 0 | 32 | 0 | 4 | 0 | 320 | 320 | 0 | 28 | 30 | 0 | 5 | 163 | 16 | 0 | 0 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 36 | 0 | 1.42 | 1 | 4500.42 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 522 | 0 | 564.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.42 | 183 | 0 | 0 | 0 | 186 | 0 | 414 | 0 | 0.14 | 2.5 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.02 | 0 | 244 | 5 | 136 | 110 | 0 | 0 | 410 | 0 | 3784.46 | 8284.88 | 91.12
08:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 10 | 0 | 0 | 47 | 16 | 0 | 0 | 0 | 10 | 16 | 0 | 340 | 267 | 0 | 0 | 5 | 33 | 270 | 0 | 0 | 9 | 0 | 14 | 22 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 5 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 185 | 0 | 0 | 360 | 29 | 184 | 22 | 1 | 30 | 0 | 0 | 15 | 0 | 32 | 0 | 26 | 0 | 295 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 16 | 0 | 58 | 30 | 0 | 18 | 0 | 0 | 56 | 9 | 34 | 1 | 14.75 | 6 | 4692.75 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.88 | 619 | 0 | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 17.12 | 185 | 0 | 0 | 0 | 198 | 0 | 396 | 0 | 1.45 | 2.5 | 176 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 40 | 0.13 | 0 | 250 | 5 | 136 | 110 | 0 | 0 | 530 | 17 | 4316.08 | 9008.83 | 91.11
09:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 63 | 16 | 0 | 0 | 0 | 17 | 16 | 0 | 340 | 270 | 0 | 0 | 17 | 10 | 270 | 0 | 0 | 18 | 0 | 21.7 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3 | 40 | 0 | 6 | 275 | 0 | 0 | 1 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 187 | 0 | 0 | 360 | 29 | 182 | 23 | 16 | 30 | 0 | 15 | 15 | 0 | 36 | 0 | 47 | 0 | 295 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 58 | 30 | 0 | 18 | 0 | 0 | 56 | 9 | 12 | 1 | 27.39 | 6 | 4838.09 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.68 | 621 | 0 | 706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 34.69 | 189 | 0 | 0 | 0 | 201 | 0 | 390 | 0 | 3.05 | 2.5 | 173 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 91 | 0.31 | 0 | 250 | 4 | 136 | 110 | 0 | 0 | 550 | 17 | 4470.23 | 9308.32 | 91.11
10:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 17 | 16 | 0 | 340 | 308 | 0 | 0 | 17 | 16.5 | 300 | 0 | 0 | 26 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 0 | 0 | 4 | 40 | 0 | 4 | 275 | 0 | 0 | 27 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 17 | 40 | 0 | 189 | 0 | 0 | 360 | 29 | 212 | 23 | 17 | 30 | 0 | 17 | 15 | 0 | 36 | 0 | 63 | 0 | 315 | 320 | 0 | 36 | 29 | 0 | 5 | 163 | 16 | 0 | 58 | 30 | 0 | 18 | 0 | 0 | 56 | 9 | 12 | 2 | 39.08 | 6 | 5058.58 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.49 | 534 | 0 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 49.36 | 195 | 0 | 0 | 0 | 204 | 0 | 414 | 0 | 4.19 | 2.5 | 191 | 0 | 0 | 19 | 0 | 0 | 0 | 3.2 | 133 | 0.46 | 0 | 218 | 4 | 136 | 110 | 0 | 0 | 520 | 17 | 4544.2 | 9602.78 | 91.1
11:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 17 | 22 | 0 | 340 | 279 | 0 | 0 | 17 | 16.5 | 300 | 0 | 0 | 31 | 0 | 22 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 47 | 0 | 8 | 0 | 0 | 0 | 4 | 40 | 0 | 3 | 223 | 0 | 0 | 32 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 20 | 40 | 0 | 187 | 0 | 0 | 360 | 29 | 182 | 27 | 17 | 30 | 0 | 17 | 17 | 0 | 42 | 0 | 71 | 0 | 305 | 320 | 0 | 33 | 29 | 0 | 5 | 163 | 16 | 0 | 60 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 12 | 2 | 47.73 | 2 | 4976.23 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.76 | 595 | 0 | 712 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 97 | 0 | 56.27 | 195 | 0 | 0 | 0 | 202 | 0 | 392 | 0 | 4.78 | 2.5 | 174 | 0 | 3 | 24 | 0 | 0 | 0 | 4 | 152 | 0.56 | 0 | 307 | 4 | 136 | 110 | 0 | 0 | 580 | 17 | 4822.87 | 9799.1 | 91.1
12:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 2 | 0 | 4 | 64 | 0 | 0 | 0 | 60 | 22 | 0 | 340 | 313 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 34 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 28 | 0 | 8 | 0 | 2 | 2 | 4 | 40 | 0 | 3 | 156 | 0 | 0 | 32 | 0 | 2 | 225 | 0 | 0 | 0 | 612 | 20 | 40 | 1 | 187 | 0 | 0 | 370 | 29 | 198 | 26 | 18 | 30 | 3 | 21 | 17 | 0 | 50 | 0 | 74 | 0 | 315 | 320 | 0 | 33 | 28 | 0 | 5 | 163 | 16 | 0 | 60 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 18 | 2 | 49.93 | 6 | 5077.43 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.59 | 607 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 110 | 0 | 60.12 | 195 | 0 | 0 | 0 | 212 | 0 | 414 | 0 | 5.43 | 2.5 | 165 | 0 | 35 | 27 | 0 | 0 | 0 | 4.7 | 165 | 0.57 | 0 | 307 | 7 | 136 | 110 | 0 | 0 | 622 | 17 | 5017.91 | 10095.34 | 91.09
13:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 0 | 50 | 64 | 0 | 22 | 17 | 108 | 22 | 0 | 340 | 250 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 33 | 0 | 22 | 22 | 0 | 0 | 30 | 30 | 0 | 0 | 35 | 0 | 8 | 0 | 50 | 50 | 4 | 40 | 27 | 10 | 154 | 0 | 0 | 32 | 0 | 47 | 224 | 0 | 0 | 0 | 612 | 20 | 40 | 58 | 187 | 0 | 0 | 360 | 29 | 182 | 28 | 32 | 30 | 69 | 28 | 17 | 0 | 50 | 0 | 72 | 0 | 320 | 300 | 0 | 36 | 28 | 0 | 5 | 163 | 16 | 0 | 60 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 18 | 2 | 49.26 | 6 | 5490.76 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.94 | 600 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 8 | 104 | 0 | 58.77 | 201 | 0 | 0 | 0 | 214 | 0 | 395 | 0 | 5.23 | 2.5 | 164 | 0 | 46 | 26 | 0 | 0 | 0 | 2.6 | 163 | 0.58 | 0 | 307 | 10 | 130 | 110 | 0 | 0 | 622 | 17 | 5006.62 | 10497.38 | 91.09
14:00 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 0 | 68 | 64 | 0 | 15 | 17 | 126 | 22 | 0 | 340 | 288 | 0 | 0 | 35 | 16.5 | 270 | 0 | 0 | 29 | 0 | 21 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 26 | 0 | 8 | 0 | 12 | 12 | 3 | 40 | 17 | 8 | 155 | 0 | 0 | 32 | 0 | 17 | 224 | 0 | 0 | 0 | 612 | 18 | 51 | 10 | 187 | 0 | 0 | 370 | 29 | 190 | 30 | 34 | 30 | 100 | 29 | 17 | 0 | 52 | 0 | 63 | 0 | 295 | 320 | 0 | 36 | 28 | 0 | 5 | 120 | 16 | 0 | 60 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 18 | 2 | 38.31 | 6 | 5282.81 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.51 | 559 | 0 | 761.54 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 16 | 92 | 0 | 52.44 | 198 | 0 | 0 | 0 | 213 | 0 | 320 | 0 | 4.67 | 2.5 | 158 | 0 | 35 | 22 | 0 | 0 | 0 | 4.1 | 138 | 0.54 | 0 | 307 | 9 | 134 | 110 | 0 | 0 | 560 | 17 | 4769.3 | 10052.11 | 91.08
15:00 | 0 | 20 | 26 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 0 | 70 | 64 | 0 | 15 | 17 | 72 | 22 | 0 | 340 | 285 | 0 | 0 | 17 | 16.5 | 270 | 0 | 0 | 23 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 158 | 0 | 0 | 29 | 0 | 17 | 224 | 0 | 0 | 0 | 612 | 15 | 51 | 10 | 185 | 0 | 0 | 325 | 29 | 189 | 30 | 34 | 30 | 51 | 28 | 17 | 0 | 52 | 0 | 48 | 0 | 300 | 320 | 0 | 36 | 28 | 0 | 5 | 163 | 0 | 0 | 60 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 18 | 2 | 30.08 | 6 | 5041.58 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.91 | 620 | 0 | 763.3 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 8 | 74 | 0 | 40.85 | 201 | 0 | 0 | 0 | 183 | 0 | 323 | 0 | 3.73 | 2.5 | 143 | 0 | 0 | 17 | 0 | 0 | 0 | 2.4 | 98 | 0.4 | 0 | 307 | 9 | 132 | 110 | 0 | 0 | 590 | 17 | 4681.09 | 9722.67 | 91.08
16:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 0 | 75 | 32 | 0 | 15 | 17 | 35 | 22 | 0 | 340 | 300 | 0 | 0 | 17 | 16.5 | 270 | 0 | 0 | 14 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 29 | 0 | 8 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 155 | 0 | 0 | 19 | 0 | 17 | 224 | 0 | 0 | 0 | 612 | 9 | 51 | 10 | 147 | 0 | 0 | 350 | 29 | 200 | 30 | 50 | 30 | 17 | 29 | 17 | 0 | 24 | 0 | 26 | 0 | 305 | 320 | 0 | 36 | 28 | 0 | 5 | 163 | 8 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 19 | 1 | 18.84 | 6 | 4965.34 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.5 | 622 | 0 | 712.82 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 8 | 43 | 0 | 25.97 | 209 | 0 | 0 | 0 | 151 | 0 | 411 | 0 | 2.34 | 2.5 | 156 | 0 | 0 | 8 | 0 | 0 | 0 | 1.5 | 58 | 0.26 | 0 | 250 | 4 | 132 | 110 | 0 | 0 | 622 | 17 | 4557.89 | 9523.23 | 91.07
17:00 | 0 | 58 | 26 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 20 | 0 | 91 | 32 | 0 | 15 | 17 | 35 | 22 | 0 | 340 | 260 | 0 | 0 | 35 | 8.5 | 270 | 0 | 0 | 4 | 0 | 21 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 23 | 0 | 8 | 0 | 12 | 5 | 0 | 40 | 3 | 7 | 156 | 17 | 0 | 19 | 0 | 20 | 226 | 0 | 0 | 0 | 612 | 3 | 51 | 21 | 184 | 0 | 0 | 315 | 29 | 182 | 30 | 53 | 30 | 21 | 35 | 17 | 0 | 42 | 0 | 8 | 0 | 320 | 320 | 0 | 36 | 28 | 0 | 5 | 163 | 13 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 21 | 0 | 5.31 | 6 | 5016.81 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.53 | 621 | 0 | 658.55 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 14 | 12 | 0 | 6.05 | 210 | 0 | 0 | 0 | 176 | 0 | 383 | 0 | 0.46 | 2.5 | 157 | 0 | 30 | 2 | 34 | 0 | 0 | 0.5 | 16 | 0.78 | 0 | 307 | 4 | 132 | 110 | 0 | 0 | 600 | 17 | 4470.37 | 9487.18 | 91.07
18:00 | 0 | 105 | 26 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 25 | 35 | 0 | 94 | 48 | 0 | 34 | 21 | 90 | 22 | 0 | 420 | 292 | 0 | 0 | 35 | 8.5 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 21 | 51 | 30 | 0 | 15 | 18 | 0 | 40 | 17 | 13 | 221 | 17 | 0 | 20 | 0 | 40 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 107 | 195 | 0 | 0 | 350 | 29 | 203 | 30 | 88 | 30 | 54 | 52 | 17 | 0 | 44 | 0 | 0 | 13 | 300 | 320 | 0 | 36 | 28 | 0 | 5 | 120 | 15 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 21 | 0 | 0 | 6 | 5724.5 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 704.19 | 0 | 0 | 31 | 0 | 1 | 4 | 71 | 0 | 10 | 43 | 0 | 24 | 0 | 210 | 0 | 0 | 0 | 176 | 0 | 414 | 0 | 0 | 2.5 | 122 | 0 | 65 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 132 | 110 | 0 | 0 | 600 | 35 | 4645.69 | 10370.19 | 91.06
19:00 | 0 | 105 | 26 | 0 | 0 | 80 | 0 | 0 | 408 | 0 | 0 | 53 | 46 | 0 | 106 | 82 | 0 | 55 | 48 | 162 | 22 | 0 | 380 | 261 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 45 | 10 | 0 | 35 | 51 | 48 | 0 | 60 | 70 | 0 | 40 | 52 | 9 | 280 | 53 | 0 | 31 | 0 | 88 | 227 | 0 | 0 | 0 | 570 | 0 | 51 | 130 | 195 | 0 | 0 | 315 | 30 | 183 | 31 | 96 | 30 | 129 | 75 | 17 | 0 | 52 | 0 | 0 | 48 | 305 | 320 | 0 | 36 | 28 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 23 | 0 | 0 | 6 | 6415.5 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 757.08 | 0 | 0 | 31 | 0 | 0 | 4 | 92 | 0 | 33 | 52 | 0 | 30 | 0 | 210 | 0 | 0 | 0 | 179 | 0 | 386 | 0 | 0 | 2.5 | 159 | 0 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 600 | 35 | 4787.58 | 11203.08 | 91.06
19:30 | 0 | 105 | 26 | 0 | 0 | 100 | 0 | 0 | 409 | 0 | 0 | 54 | 54 | 0 | 80 | 48 | 0 | 55 | 55 | 162 | 22 | 0 | 380 | 292 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 33 | 51 | 48 | 0 | 24 | 36 | 0 | 40 | 51 | 26 | 282 | 17 | 0 | 32 | 0 | 105 | 227 | 0 | 0 | 0 | 570 | 0 | 51 | 136 | 195 | 0 | 0 | 315 | 30 | 183 | 29 | 96 | 30 | 100 | 57 | 17 | 0 | 44 | 0 | 0 | 48 | 305 | 320 | 0 | 36 | 28 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 17 | 58 | 9 | 24 | 0 | 0 | 6 | 6278.5 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 759.21 | 0 | 0 | 32 | 0 | 0 | 4 | 92 | 0 | 35 | 52 | 0 | 30 | 0 | 209 | 0 | 0 | 0 | 168 | 0 | 387 | 0 | 0 | 2.5 | 159 | 0 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 610 | 35 | 4755.71 | 11034.21
20:00 | 0 | 88 | 25 | 0 | 0 | 100 | 0 | 0 | 408 | 0 | 0 | 54 | 54 | 0 | 85 | 48 | 0 | 30 | 55 | 162 | 22 | 0 | 380 | 280 | 0 | 0 | 35 | 16.5 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 20 | 34 | 48 | 0 | 24 | 36 | 0 | 40 | 51 | 15 | 277 | 0 | 0 | 32 | 0 | 105 | 227 | 0 | 0 | 0 | 570 | 0 | 51 | 110 | 195 | 0 | 0 | 315 | 29 | 183 | 27 | 96 | 30 | 100 | 53 | 17 | 0 | 44 | 0 | 0 | 39 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 34 | 0 | 0 | 6 | 6105.5 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 759.41 | 0 | 0 | 32 | 0 | 0 | 4 | 92 | 0 | 38 | 52 | 0 | 30 | 0 | 209 | 0 | 0 | 0 | 168 | 0 | 386 | 0 | 0 | 2.5 | 160 | 0 | 54 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 110 | 0 | 0 | 622 | 35 | 4715.91 | 10821.41 | 91.05
21:00 | 0 | 88 | 25 | 0 | 0 | 100 | 0 | 0 | 378 | 0 | 0 | 54 | 54 | 0 | 40 | 48 | 0 | 30 | 55 | 162 | 22 | 0 | 350 | 297 | 0 | 0 | 35 | 16.5 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 34 | 48 | 0 | 0 | 36 | 0 | 40 | 51 | 26 | 278 | 0 | 0 | 33 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 195 | 0 | 0 | 320 | 30 | 185 | 23 | 95 | 30 | 100 | 53 | 17 | 0 | 52 | 0 | 0 | 0 | 305 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 14 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 24 | 0 | 0 | 6 | 5987.5 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 755.67 | 0 | 0 | 34 | 0 | 0 | 4 | 92 | 0 | 35 | 52 | 0 | 30 | 0 | 210 | 0 | 0 | 0 | 169 | 0 | 387 | 0 | 0 | 2.5 | 158 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 110 | 0 | 0 | 622 | 35 | 4739.17 | 10726.67 | 91.05
22:00 | 0 | 88 | 0 | 0 | 0 | 100 | 0 | 0 | 353 | 0 | 0 | 19 | 54 | 0 | 17 | 48 | 0 | 0 | 17 | 72 | 17 | 0 | 350 | 282 | 0 | 0 | 0 | 16.5 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 15 | 0 | 24 | 0 | 0 | 12 | 0 | 40 | 17 | 35 | 280 | 0 | 0 | 33 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 60 | 197 | 0 | 0 | 315 | 29 | 181 | 30 | 96 | 30 | 100 | 53 | 17 | 0 | 44 | 0 | 0 | 0 | 290 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 14 | 0 | 82 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 24 | 0 | 0 | 6 | 5495.5 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 0 | 758.44 | 0 | 0 | 0 | 0 | 0 | 4 | 92 | 0 | 0 | 52 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 168 | 0 | 387 | 0 | 0 | 2.5 | 160 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 138 | 110 | 0 | 0 | 622 | 35 | 4650.94 | 10146.44 | 91.04
23:00 | 0 | 88 | 0 | 0 | 0 | 100 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 17 | 17 | 17 | 0 | 350 | 289 | 0 | 0 | 0 | 16.5 | 280 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 15 | 0 | 24 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 278 | 0 | 0 | 12 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 12 | 197 | 0 | 0 | 320 | 30 | 183 | 30 | 93 | 30 | 68 | 53 | 17 | 0 | 44 | 0 | 0 | 0 | 285 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 59 | 9 | 23 | 0 | 0 | 6 | 5168 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 760.11 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 0 | 0 | 16 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 167 | 0 | 393 | 0 | 0 | 2.5 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 138 | 110 | 0 | 0 | 622 | 17 | 4482.61 | 9650.61 | 91.04
Total KWH | 0 | 1111680 | 370080 | 0 | 0 | 486375 | 0 | 0 | 9381600 | 0 | 0 | 388800 | 412560 | 0 | 976320 | 750240 | 0 | 318078 | 351343 | 1176480 | 479160 | 0 | 8369000 | 6953193 | 0 | 0 | 398660 | 528900 | 6819503 | 0 | 0 | 221994 | 0 | 436800 | 529560 | 0 | 0 | 450382 | 127964 | 23040 | 0 | 545280 | 155206 | 294096 | 0 | 175680 | 267840 | 28078 | 944640 | 326180 | 593280 | 5781818.18 | 71927 | 0 | 411840 | 0 | 730981 | 5301010 | 0 | 0 | 0 | 13025453 | 125685 | 1069160 | 796218 | 4181818 | 0 | 0 | 8538000 | 539520 | 4702000 | 655560 | 849600 | 699340 | 902880 | 651000 | 386720 | 0 | 974400 | 0 | 507045 | 119600 | 7376000 | 7733700 | 0 | 706896 | 698000 | 0 | 114768 | 3914181.8 | 370368 | 0 | 1456320 | 716064 | 0 | 436000 | 0 | 66240 | 1082400 | 184800 | 595200 | 13950 | 320560 | 102480 | 121301494.98 | 20938181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584640 | 13432730 | 0 | 15747273 | 0 | 0 | 129175 | 0 | 34944 | 23916 | 773808 | 0 | 89664 | 322483 | 721210 | 116351 | 403496 | 4685727 | 0 | 0 | 0 | 4608700 | 0 | 9005963 | 0 | 35400 | 67410 | 3948000 | 0 | 522938 | 155992 | 142953 | 0 | 0 | 24245.52 | 1036800 | 3966 | 0 | 6044000 | 150061 | 3250000 | 2848330 | 0 | 0 | 12906181.82 | 392400 | 103146938.34 | 224448433.32

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10095.34 | MW | 12:00 Hr. | Energy Generated |  |  | 224.4484 |  | MKWHr.
| Day Peak Demand |  |  | 10147.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.753 |  | MKWHr.
| Evening Peak Generation |  |  | 11203.08 | MW | 19:00 Hr. | Energy Demand |  |  | 225.2014 |  | MKWHr.
| Evening Peak Demand |  |  | 11276.08 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27.3 |  | °C
| Minimum Generation of the Day |  |  | 6902.27 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 826.67 |  | MMCFD
| Maximum Generation of the Day |  |  | 11203.08 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.0793 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.9841 | 0 | 6.2542 | 0 | 0 | 0.22199 | 0 | 0 | 40.4603 | Gas | 109.3842 | Gas | 394246060.386
| Chattogram Zone |  |  | 5.8943 | 18.8073 | 3.0351 | 0 | 0.94464 | 0.15376 | 0 | 0.54528 | 29.3804 | Coal | 55.1382 | Coal | 399691923.831
| Cumilla Zone |  |  | 20.7721 | 0 | 3.3193 | 0 | 0 | 0.50704 | 0.9744 | 0 | 25.5729 | HFO | 16.5932 | HFO | 305827884.65
| Mymensingh Zone |  |  | 0.5952 | 0 | 1.4359 | 0 | 0 | 0.33451 | 0 | 0 | 2.3656 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.5223 | Hydro | 0.94464 | Hydro | 94464
| Khulna Zone |  |  | 0 | 13.4327 | 0 | 0 | 0 | 0.58464 | 20.9382 | 0 | 34.9556 | Solar | 4.1831 | Solar | 64808246.592
| Barishal Zone |  |  | 6.2484 | 18.9502 | 0.3924 | 0 | 0 | 0.003966 | 0 | 0 | 25.5949 | Import | 37.6599 | Import | 191325011.65
| Rajshahi Zone |  |  | 18.3678 | 0 | 1.4903 | 0 | 0 | 1.1601 | 15.7473 | 0 | 36.7655 | Wind | 0.54528 | Wind | 8506368
| Rangpur Zone |  |  | 0 | 3.948 | 0.66589 | 0 | 0 | 1.217 | 0 | 0 | 5.8309
| Total |  |  | 109.3842 | 55.1382 | 16.5932 | 0 | 0.94464 | 4.1831 | 37.6599 | 0.54528 | 224.4484
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 394246060.386 |  | Hydro | 94464
|  |  |  | Coal | 399691923.831 |  | Solar | 64808246.592
|  |  |  | HFO | 305827884.65 |  | Import | 191325011.65
|  |  |  | HSD | 0 |  | Wind | 8506368
[5 empty] | Total: | 136,44,99,959 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9382 | Peak Hr Flow | 877.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8168563.69 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.7473 | Peak Hr Flow | 757.08 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 468 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9744 | Peak Hr Flow | 52.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 716 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.6599 | Peak Hr Flow | 1686.08 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4024
|  |  |  | Chattogram |  | 0 |  | 1110
|  |  |  | Cumilla |  | 0 |  | 888
|  |  |  | Mymensingh |  | 70 |  | 991
|  |  |  | Sylhet |  | 0 |  | 395
|  |  |  | Khulna |  | 0 |  | 1233
|  |  |  | Barishal |  | 0 |  | 304
|  |  |  | Rajshahi |  | 0 |  | 1106
|  |  |  | Rangpur |  | 0 |  | 797
|  |  |  | Total |  | 70 |  | 10848
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:08 | 23:27 | Siddhirganj 132/33kV S/S 132kV MTR 1 Scheduled S/D Due to Realy change of 230kV end
| 08:10 | 23:26 | Siddhirganj 230/132kV S/S MTR 1 HT Scheduled S/D Due to Relay changing work
| 08:12 |  | Netrakona 132/33kV S/S Transformer-1 (415T) HT Project Work S/D Due to X-former
Replacement works.
| 08:16 | 14:43 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT Scheduled S/D Due to Annual
maintenance
| 08:16 | 14:48 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT Scheduled S/D Due to Annual
maintenance
| 08:23 | 16:02 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Scheduled S/D Due to Annual maintenance
(dead line checking)
|  | 08:35 | Coxsbazar 132/33kV S/S Main Bus is restored.
| 08:40 | 17:24 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to
Working at the Fenchuganj end. and from Fenchuganj 230/132/33kV end Due to Deadline
checking.
| 08:42 |  | Bogura 132 KV bus- A s/d in Bogura 132/33 KV S/S.
| 08:50 | 15:02 | Ghorasal- Ishwardi 230 kV Ckt-2 Scheduled S/D from Ghorashal 230kV end Due to Cradle
guard installation for Ruppur to Dhaka line and from Ishurdi 230/132kV end Due to Cradel
guard installation of rooppur-dhaka 400Kv line . Over ISD-GHO 230 Kv lin
| 08:50 | 15:01 | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ghorashal 230kV end Due to Cradle
guard installation for Ruppur to Dhaka line and from Ishurdi 230/132kV end Due to Cradel
guard installation of rooppur-dhaka 400Kv line . Over ISD-GHO 230 Kv line
| 08:52 | 14:36 | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Due to 33kv Joragate -2 feeder Bus Ds
change
| 08:52 | 14:35 | Khulna (C) S/S Tr-3 405T HT Forced S/D Due to Due to WZPDCL
| 08:54 | 17:49 | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to DS
Maintenance
|  | 08:55 | Purbasadipur-Saidpur 132kV Ckt-1 is restored.
|  | 08:55 | Purbasadipur-Saidpur 132kV Ckt-2 is restored.
|  | 08:55 | Purbasadipur 132/33kV S/S Single Bus is restored.
| 09:19 | 17:26 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Due to Project
work
| 09:20 | 17:26 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Due to Project
work
| 09:31 | 17:28 | Bogura 230/132kV S/S Bogura (W) CKT-1 Project Work S/D
| 09:31 | 17:29 | Bogura 230/132kV S/S Bogura (W) CKT-2 Project Work S/D
| 09:31 | 17:27 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Project Work S/D Due to Due to Project work
| 09:31 | 17:29 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Project Work S/D Due to Due to Project work
| 09:36 |  | Matarbari - SS Power 400 kv L-1 was shut down for A/M
| 09:41 | 12:31 | Bogura-Bogura (New)) 132 kV Ckt-2 Forced S/D from Bogura 230/132kV end. and from Bogura
132/33kV end Due to 132KV A Bus DS maintenance work.
| 09:42 | 17:25 | Ghorasal-Joydeb-B 132kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to Deadline | [7 empty] | 10.0MW load
|  |  | checking. | [7 empty] | interrup. Joydebpur
132/33kV end
|  | 10:22 | Gopalganj 132/33kV S/S T1 HT is restored.
|  | 10:23 | Gopalganj 132/33kV S/S T1 LT is restored.
| 10:28 | 19:42 | Gopalganj 400/132kV S/S ATR-05 LT Project Work S/D
| 10:36 | 19:41 | Gopalganj 400/132kV S/S ATR-05 HT Project Work S/D
| 10:40 | 15:58 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to Due to by Pass ( Sylhet-90MW PS)
loop open
| 10:53 | 12:33 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT Scheduled S/D Due to Power
station end silicon coating.
| 11:29 | 12:40 | Tongi 230/132/33kV S/S T-2 LT Tripped showing SPS triping relays Due to None | [7 empty] | 14.0MW load
interrup.
| 12:00 |  | Day Peak Gen. 10095 MW
| 12:07 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Scheduled S/D Due to Power
Station end silicon coating work
|  | 12:10 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
|  | 12:11 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
| 12:29 | 12:40 | Tongi 230/132/33kV S/S T-3 LT Tripped showing SPS tripping. relays Due to None | [7 empty] | 24.0MW load
interrup.
| 12:29 | 12:40 | Tongi 230/132/33kV S/S T-1 LT Tripped showing SPS tripping relays Due to None | [7 empty] | 28.0MW load
interrup.
| 12:57 |  | Bogura 132 KV bus- A syn in Bogura 132/33 KV S/S.
| 12:57 |  | Bogura 132 KV bus- B s/d in Bogura 132/33 KV S/S.
|  | 13:35 | Jamalpur 132/33kV S/S Bus-B is restored.
| 13:45 | 16:50 | Jamalpur 132/33kV S/S Bus-A Project Work S/D Due to Mymensingh ckt-1 Bus D.S.
replacement.
| 14:29 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is ON with remarks:- As per instruction of NLDC
|  | 15:38 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 is restored.
|  | 16:03 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 is restored.
|  | 16:08 | Chattak-Sylhet 132 kV Ckt-1 is restored.
|  | 17:15 | Jamalpur-Mymensingh 132kV Ckt-1 is restored.
|  | 18:09 | Maniknagar-Siddhirganj 230kV Ckt-1 is restored.
|  | 18:09 | Maniknagar-Siddhirganj 230kV Ckt-1 is restored.
| 18:52 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 19:00 |  | Evening Peak Generation: 11202 MW
| 21:56 |  | Ashuganj 450 MW CCPP(South), FGMO is ON with remarks:-
| 03:20 |  | Bhulta 132/33kV S/S GT1 HT Forced S/D Due to WT-01 and WT-02 Meter burn, Diff. realy (
siemens siprotec 7UT85) burn due to PBS 33 kv fault.
| 04:00 |  | Minimum generation 7502 MW
| 07:21 |  | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Maniknagar 230/132kV end Due to
Aircraft obstruction Light installation .
| 07:38 |  | Bhulta-Rampura 230 kV Ckt-3 Scheduled S/D from Rampura 230/132kV end Due to Dead line
check and from Bhulta 400/230kV end Due to Shutdown taken by Rampura 230/132 kV grid
susstation
| 07:44 |  | Ashuganj 450 MW CCPP(South), FGMO is OFF with remarks:-
| 07:50 |  | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance.
| 07:52 |  | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 80 | 486375 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 408 | 9381600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8369000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 261 | 6953193 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 318078 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6819503 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 53 | 388800 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 82 | 750240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 48 | 351343 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 398660 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 436800 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 529560 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 479160 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16.5 | 528900 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 26 | 370080 | machine problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 106 | 976320 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1111680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1176480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 221994 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 46 | 412560 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.654 | 2228.5 | 40460326
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125685 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 31 | 411840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 944640 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5301010 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 730981 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 48 | 294096 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 155206 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 175680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 593280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 10 | 23040 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 28078 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 127964 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 52 | 326180 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 267840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 450382 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 71927 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 570 | 13025453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 35 | 545280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 280 | 5781818.18 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1704 | 29380380.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4702000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 315 | 8538000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 31 | 655560 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 539520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4181818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1069160 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 796218 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 48 | 119600 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 699340 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 129 | 902880 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 52 | 974400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 386720 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 651000 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 849600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 507045 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1382 | 25572861
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 23 | 595200 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 184800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1082400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 320560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 102480 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 66240 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 96 | 2365630
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 28 | 698000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3914181.8 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 706896 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 114768 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 716064 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1456320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 436000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 370368 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7376000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7733700 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1005 | 23522297.8
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 20938181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 584640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 619 | 13432730 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1496 | 34955551
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 150061 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 3250000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 12906181.82 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2848330 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 392400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6044000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3966 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1191 | 25594938.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 31 | 129175 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 4 | 23916 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 33 | 89664 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 210 | 4685727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 179 | 4608700 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 386 | 9005963 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 116351 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 67410 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 322483 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 773808 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 34944 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 757.08 | 15747273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 403496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 721210 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1776.58 | 36765520
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3948000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 142953 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 24245.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 522938 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 155992 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1036800 | -
Rangpur Area Total |  |  |  |  | 950 | 324 | 5830928.52
Eastern Grid Total |  |  |  |  | 16772.132 | 6415.5 | 121301494.98
Western Grid Total |  |  |  |  | 10294.5 | 4787.58 | 103146938.34
National Grid Total |  |  |  |  | 27066.632 | 11203.08 | 224448433.32
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7338.98 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3440.7 | MW
i) Dhaka area |  |  | 4024.48 |  | MW | i) Khulna area |  |  |  | 1233 | MW
ii) Chattogram area |  |  | 1110.5 |  | MW | ii) Barishal area |  |  |  | 304.3 | MW
iii) Cumilla area |  |  | 888 |  | MW | iii) Rajshahi area |  |  |  | 1106.4 | MW
iv) Mymensingh area |  |  | 921 |  | MW | iv) Rangpur area |  |  |  | 797 | MW
v) Sylhet area |  |  | 395 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10779.68 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 61 | 09:00 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 132 | 14:00 | 68 | Jamalpur | 92 | 07:00 | 134 | Purbasadipur | 121 | 19:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 109 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 75 | 13:00 | 70 | Jhenaidah | 97 | 18:30 | 136 | Rahim | 25 | 10:00
5 | Agrabad | 64 | 18:30 | 71 | Joydebpur | 118 | 18:30 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 52 | 09:00 | 72 | Joypurhat | 58 | 08:00 | 138 | Rajendrapur | 100 | 13:00
7 | Ashuganj | 60 | 00:00 | 73 | Juldah | 12 | 00:00 | 139 | Rajshahi | 99 | 13:00
8 | BSRM | 186 | 14:00 | 74 | KSRM | 34 | 19:30 | 140 | Rajshahi-230 | 41 | 20:00
9 | Bagerhat | 65 | 19:00 | 75 | Kabirpur | 209 | 19:00 | 141 | Ramganj | 92 | 18:30
10 | Bajitpur | 8 | 22:00 | 76 | Kachua | 51 | 18:30 | 142 | Rampur | 27 | 18:30
11 | Bakulia | 71 | 18:00 | 77 | Kallyanpur | 72 | 13:00 | 143 | Rangamati | 14 | 18:00
12 | Banani | 30 | 13:00 | 78 | Kalurghat | 28 | 12:00 | 144 | Rangpur | 129 | 17:00
13 | Bangabhaban | 3 | 13:00 | 79 | Kamrangirchar | 54.4 | 13:00 | 145 | Ruppur | 2.8 | 11:00
14 | Barapukuria | 65 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 4 | 04:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 100 | 13:00 | 147 | Saidpur | 104 | 08:00
16 | Barishal | 68 | 18:30 | 82 | Keranigonj | 62 | 13:00 | 148 | Satkhira | 94 | 19:00
17 | Barishal-230 | 72 | 18:30 | 83 | Khagrachori | 26 | 18:30 | 149 | Satmasjid | 76 | 13:00
18 | Baroaulia | 52 | 13:00 | 84 | Khulna | 71 | 17:00 | 150 | Savar | 170 | 15:00
19 | Baroirhat | 52 | 13:00 | 85 | Khulshi | 145 | 18:00 | 151 | SevenRings | 15.78 | 09:00
20 | Bashundhara | 138 | 18:30 | 86 | Kishoreganj | 122 | 18:30 | 152 | ShahCement | 28 | 01:00
21 | BashundharaCement | 12 | 13:00 | 87 | Kodda | 252 | 18:00 | 153 | Shahjadpur | 56 | 19:00
22 | Beanibazar | 44 | 18:30 | 88 | Kulaura | 27 | 18:00 | 154 | Shahjibazar | 83 | 18:30
23 | Benapole | 50 | 08:00 | 89 | Kurigram | 60 | 08:00 | 155 | Shahmirpur | 35.5 | 19:00
24 | Bhaluka | 122 | 11:00 | 90 | Kushtia | 106 | 18:30 | 156 | Shariatpur | 53 | 20:00
25 | Bhandaria | 36 | 20:00 | 91 | Lalbag | 59 | 13:00 | 157 | Sherpur | 114 | 00:00
26 | Bhangura | 28 | 18:00 | 92 | Lalmonirhat | 48 | 18:30 | 158 | Shikalbaha | 15 | 18:00
27 | Bheramara(GK) | 42 | 18:30 | 93 | MI_Cement | 18.2 | 15:00 | 159 | Shitalakhya | 63.2 | 13:00
28 | Bhulta | 200 | 19:30 | 94 | Madanganj | 18 | 13:00 | 160 | Sholosohor | 32 | 15:00
29 | Bog-Sherpur | 70 | 13:00 | 95 | Madaripur | 67 | 21:00 | 161 | Shyampur | 150 | 10:00
30 | Bogura | 116 | 19:00 | 96 | Madartek | 55.6 | 19:30 | 162 | Siddhirganj | 104 | 11:00
31 | Borhanuddin | 53 | 22:00 | 97 | Madunaghat | 35 | 18:00 | 163 | Sirajganj | 80 | 18:30
32 | Brahmanbaria | 110 | 13:00 | 98 | Magura | 48 | 18:30 | 164 | Sonargaon | 84 | 12:00
33 | Cantonment | 72 | 18:30 | 99 | Mahasthangarh | 62 | 08:00 | 165 | Sreemongol | 52 | 21:00
34 | Chandpur | 44 | 19:00 | 100 | Manikganj | 103 | 20:00 | 166 | Sreepur | 79 | 18:30
35 | Chandraghona | 25 | 18:00 | 101 | Maniknagar | 42 | 12:00 | 167 | Srinagar | 29.72 | 13:00
36 | Chapai | 70 | 13:00 | 102 | Matarbari | 35 | 07:00 | 168 | Sunamganj | 43 | 18:30
37 | Charsaidpur | 39 | 21:00 | 103 | Matuail | 47 | 13:00 | 169 | Sylhet | 28 | 18:30
38 | Chauddagram | 45 | 13:00 | 104 | Millgate | 65 | 15:00 | 170 | Sylhet-132 | 85 | 15:00
39 | Chhatak | 33 | 18:00 | 105 | Mirpur | 98 | 18:30 | 171 | TK | 21 | 18:00
40 | Chowmuhani | 139 | 18:30 | 106 | Mirsorai | 9 | 19:00 | 172 | Tangail | 156 | 08:00
41 | Chuadanga | 76 | 13:00 | 107 | Mirzapur | 36 | 08:00 | 173 | Thakurgaon | 84 | 18:30
42 | Coxsbazar | 113 | 18:00 | 108 | Mithapukur | 70 | 08:00 | 174 | Tongi | 85 | 11:00
43 | Cumilla(N) | 129 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 24 | 19:00
44 | Cumilla(S) | 111 | 15:00 | 110 | Mogbazar | 90.2 | 13:00 | 176 | Ullon | 38 | 13:00
45 | Daudkandi | 114 | 19:00 | 111 | Mongla | 31 | 18:30 | 177 | Uttara | 62 | 13:00
46 | Dhaka | 28 | 12:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 34 | 13:00
47 | Dhamrai | 98 | 12:00 | 113 | Muktagacha | 30 | 16:00 | 179 | Zigatola | 53 | 13:00
48 | Dhanmondi | 88.2 | 13:00 | 114 | Munshiganj | 66 | 20:00
49 | Dohazari | 70 | 18:00 | 115 | Mymensingh | 157 | 19:00
50 | Faridpur | 109 | 19:00 | 116 | Naogaon | 113 | 13:00
51 | Fatullah | 82 | 12:00 | 117 | Narail | 40 | 18:30
52 | Fenchuganj | 27 | 18:30 | 118 | Narinda | 55 | 13:00
53 | Feni | 67 | 19:00 | 119 | Narshingdi | 159 | 19:00
54 | GPH | 13 | 11:00 | 120 | Natore | 107 | 18:30
55 | Ghatail | 50 | 17:00 | 121 | Nawabganj | 29.2 | 13:00
56 | Ghorashal | 14 | 19:30 | 122 | Netrakona | 135 | 09:00
57 | Ghorashal-230 | 58 | 18:00 | 123 | New | 65.8 | 12:00
58 | Goalpara | 22 | 18:30 | 124 | Niamatpur | 86 | 09:00
59 | Gollamari | 62 | 13:00 | 125 | Noapara | 36 | 19:00
60 | Gopalganj | 76 | 19:00 | 126 | PHP | 5 | 19:30
61 | Gulshan | 62 | 14:00 | 127 | Pabna | 64 | 18:30
62 | Halishahar | 46 | 15:00 | 128 | Palashbari | 106 | 08:00
63 | HaripurSBU | 168 | 11:00 | 129 | Panchagarh | 45 | 19:00
64 | Hasnabad | 68 | 12:00 | 130 | Patuakhali | 50 | 21:00
65 | Hathazari | 55 | 19:00 | 131 | Payra | 22 | 14:00
66 | Ishurdi | 58 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8578.92 | 0 |  | 8578.92
1:00 | 7999.9 | 0 |  | 7999.9
2:00 | 7546.78 | 0 |  | 7546.78
3:00 | 7254.57 | 0 |  | 7254.57
4:00 | 7019.49 | 0 |  | 7019.49
5:00 | 6902.27 | 0 |  | 6902.27
6:00 | 7283 | 0 |  | 7283
7:00 | 8284.88 | 30 |  | 8315.88
8:00 | 9008.83 | 70 |  | 9081.83
9:00 | 9308.32 | 65 |  | 9376.32
10:00 | 9602.78 | 50 |  | 9654.78
11:00 | 9799.1 | 50 |  | 9851.1
12:00 | 10095.34 | 50 |  | 10147.34
13:00 | 10497.38 | 40 |  | 10539.38
14:00 | 10052.11 | 35 |  | 10089.11
15:00 | 9722.67 | 40 |  | 9764.67
16:00 | 9523.23 | 35 |  | 9560.23
17:00 | 9487.18 | 25 |  | 9513.18
18:00 | 10370.19 | 65 |  | 10438.19
19:00 | 11203.08 | 70 |  | 11276.08
19:30 | 11034.21 | 50 |  | 11086.21
20:00 | 10821.41 | 45 |  | 10868.41
21:00 | 10726.67 | 35 |  | 10763.67
22:00 | 10146.44 | 29 |  | 10176.44
23:00 | 9650.61 | 19 |  | 9670.61
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 08-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2888 | 1725.5 | 924 | 0 | 38 | 616.42 | 40 | 2250 | 0 | 8 | 68 | 0 | 0 | 21 | 0 | DAILY ENERGY CURVE
00:30 | 2823.5 | 1718 | 848.5 | 0 | 36 | 560.91 | 40 | 2176 | 0 | 4 | 47.5 | 0 | 0 | 35 | 0 | 08-02-2025
01:00 | 2759 | 1710.5 | 773 | 0 | 34 | 505.4 | 40 | 2102 | 0 | 0 | 27 | 0 | 0 | 49 | 0
01:30 | 2735.5 | 1709.5 | 754 | 0 | 33 | 459.34 | 40 | 1966.5 | 0 | 0 | 22.5 | 0 | 0 | 53 | 0 | Energy Generated | 224.4484 |  | MKWHr
02:00 | 2712 | 1708.5 | 735 | 0 | 32 | 413.28 | 40 | 1831 | 0 | 0 | 18 | 0 | 0 | 57 | 0 | Energy not Served | 0.753 |  | MKWHr
02:30 | 2707 | 1685.3 | 735 | 0 | 31 | 416.375 | 40 | 1727.5 | 0 | 0 | 9 | 0 | 0 | 49.5 | 0 | Total Energy Requirement | 225.2014 |  | MKWHr
03:00 | 2702 | 1662.1 | 735 | 0 | 30 | 419.47 | 40 | 1624 | 0 | 0 | 0 | 0 | 0 | 42 | 0
03:30 | 2686.5 | 1607.1 | 735 | 0 | 30 | 418.43 | 40 | 1582 | 0 | 0 | 0 | 0 | 0 | 38 | 0
04:00 | 2671 | 1552.1 | 735 | 0 | 30 | 417.39 | 40 | 1540 | 0 | 0 | 0 | 0 | 0 | 34 | 0
04:30 | 2657 | 1496.1 | 735 | 0 | 30 | 418.28 | 40 | 1540.5 | 0 | 0 | 0 | 0 | 0 | 44 | 0
05:00 | 2643 | 1440.1 | 735 | 0 | 30 | 419.17 | 40 | 1541 | 0 | 0 | 0 | 0 | 0 | 54 | 0
05:30 | 2753 | 1497.1 | 735 | 0 | 31 | 419.035 | 40 | 1587 | 0 | 0 | 3.5 | 0 | 0 | 27 | 0
06:00 | 2863 | 1554.1 | 735 | 0 | 32 | 418.9 | 40 | 1633 | 0 | 0 | 7 | 0 | 0 | 0 | 0
06:30 | 2859.5 | 1643.3 | 782 | 0 | 32 | 491.71 | 40 | 1868.5 | 8.43 | 20.5 | 38 | 0 | 0 | 0 | 15
07:00 | 2856 | 1732.5 | 829 | 0 | 32 | 564.52 | 40 | 2104 | 16.86 | 41 | 69 | 0 | 0 | 0 | 30
07:30 | 2848 | 1698.5 | 852.5 | 0 | 32 | 634.76 | 40 | 2277 | 89.595 | 58.5 | 116 | 0 | 0 | 0 | 50
08:00 | 2840 | 1664.5 | 876 | 0 | 32 | 705 | 40 | 2450 | 162.33 | 76 | 163 | 0 | 0 | 0 | 70
08:30 | 2829 | 1660.85 | 876.5 | 0 | 34 | 705.5 | 40 | 2465.5 | 251.225 | 89 | 207 | 0 | 0 | 0 | 67.5
09:00 | 2818 | 1657.2 | 877 | 0 | 36 | 706 | 40 | 2481 | 340.12 | 102 | 251 | 0 | 0 | 0 | 65
09:30 | 2864.5 | 1683.6 | 900.5 | 0 | 36 | 708 | 40 | 2415.5 | 427.95 | 102 | 269 | 0 | 0 | 8.5 | 57.5
10:00 | 2911 | 1710 | 924 | 0 | 36 | 710 | 40 | 2350 | 515.78 | 102 | 287 | 0 | 0 | 17 | 50
10:30 | 2880 | 1693 | 924 | 0 | 39 | 711 | 40 | 2420.5 | 556.94 | 149.5 | 255 | 0 | 0 | 32 | 50
11:00 | 2849 | 1676 | 924 | 0 | 42 | 712 | 40 | 2491 | 598.1 | 197 | 223 | 0 | 0 | 47 | 50
11:30 | 2885.5 | 1699 | 924 | 0 | 46 | 731 | 40 | 2480 | 622.22 | 199.5 | 282.5 | 0 | 0 | 37.5 | 50
12:00 | 2922 | 1722 | 924 | 0 | 50 | 750 | 40 | 2469 | 646.34 | 202 | 342 | 0 | 0 | 28 | 50
12:30 | 2891.5 | 1700 | 924 | 0 | 50 | 756 | 40 | 2464 | 634.36 | 202 | 603 | 0 | 0 | 31.5 | 45
13:00 | 2861 | 1678 | 924 | 0 | 50 | 762 | 40 | 2459 | 622.38 | 202 | 864 | 0 | 0 | 35 | 40
13:30 | 2828.5 | 1666.5 | 924 | 0 | 51 | 761.77 | 40 | 2405 | 584.475 | 176 | 807 | 0 | 0 | 30.5 | 37.5
14:00 | 2796 | 1655 | 924 | 0 | 52 | 761.54 | 40 | 2351 | 546.57 | 150 | 750 | 0 | 0 | 26 | 35
14:30 | 2760.5 | 1665.5 | 924 | 0 | 52 | 762.42 | 40 | 2390.5 | 481.97 | 160 | 630 | 0 | 0 | 20.5 | 37.5
15:00 | 2725 | 1676 | 924 | 0 | 52 | 763.3 | 40 | 2430 | 417.37 | 170 | 510 | 0 | 0 | 15 | 40
15:30 | 2775.5 | 1680.5 | 924 | 0 | 38 | 738.06 | 40 | 2423.5 | 330.89 | 170 | 480.5 | 0 | 0 | 22 | 37.5
16:00 | 2826 | 1685 | 924 | 0 | 24 | 712.82 | 40 | 2417 | 244.41 | 170 | 451 | 0 | 0 | 29 | 35
16:30 | 2801 | 1692 | 923.5 | 0 | 33 | 685.685 | 40 | 2435 | 157.02 | 168 | 544 | 0 | 0 | 26 | 30
17:00 | 2776 | 1699 | 923 | 0 | 42 | 658.55 | 40 | 2453 | 69.63 | 166 | 637 | 0 | 0 | 23 | 25
17:30 | 2836.5 | 1734 | 923.5 | 0 | 43 | 681.37 | 40 | 2467.5 | 34.815 | 289.5 | 856.5 | 0 | 0 | 22 | 45
18:00 | 2897 | 1769 | 924 | 0 | 44 | 704.19 | 40 | 2482 | 0 | 413 | 1076 | 0 | 0 | 21 | 65
18:30 | 2898.5 | 1761 | 900.5 | 0 | 48 | 730.635 | 40 | 2508.5 | 0 | 481.5 | 1390 | 0 | 0 | 28 | 67.5
19:00 | 2900 | 1753 | 877 | 0 | 52 | 757.08 | 40 | 2535 | 0 | 550 | 1704 | 0 | 0 | 35 | 70
19:30 | 2909 | 1801 | 877 | 0 | 44 | 759.21 | 40 | 2546 | 0 | 519 | 1506 | 0 | 0 | 33 | 50
20:00 | 2917 | 1762 | 877 | 0 | 44 | 759.41 | 40 | 2555 | 0 | 478 | 1369 | 0 | 0 | 20 | 45
20:30 | 2892 | 1768 | 899.5 | 0 | 48 | 757.54 | 40 | 2576 | 0 | 458 | 1319 | 0 | 0 | 16 | 40
21:00 | 2867 | 1774 | 922 | 0 | 52 | 755.67 | 40 | 2597 | 0 | 438 | 1269 | 0 | 0 | 12 | 35
21:30 | 2854.5 | 1759 | 923 | 0 | 48 | 757.055 | 40 | 2599.5 | 0 | 347 | 1095 | 0 | 0 | 13.5 | 32
22:00 | 2842 | 1744 | 924 | 0 | 44 | 758.44 | 40 | 2602 | 0 | 256 | 921 | 0 | 0 | 15 | 29
22:30 | 2844 | 1751.75 | 923.5 | 0 | 44 | 759.275 | 40 | 2599.5 | 0 | 211.5 | 710 | 0 | 0 | 15 | 24
23:00 | 2846 | 1759.5 | 923 | 0 | 44 | 760.11 | 40 | 2597 | 0 | 167 | 499 | 0 | 0 | 15 | 19
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4540 | 4038.92 | 8578.92 | DAILY GENERATION CURVE
00:30 | 4492.5 | 3796.91 | 8289.41
01:00 | 4445 | 3554.9 | 7999.9 | 08-02-2025
01:30 | 4403 | 3370.34 | 7773.34
02:00 | 4361 | 3185.78 | 7546.78
02:30 | 4263.3 | 3137.375 | 7400.675
03:00 | 4165.6 | 3088.97 | 7254.57
03:30 | 4037.6 | 3099.43 | 7137.03
04:00 | 3909.6 | 3109.89 | 7019.49
04:30 | 3920.6 | 3040.28 | 6960.88
05:00 | 3931.6 | 2970.67 | 6902.27
05:30 | 4025.6 | 3067.035 | 7092.635
06:00 | 4119.6 | 3163.4 | 7283
06:30 | 4310.01 | 3473.93 | 7783.94
07:00 | 4500.42 | 3784.46 | 8284.88
07:30 | 4596.585 | 4050.27 | 8646.855
08:00 | 4692.75 | 4316.08 | 9008.83
08:30 | 4765.42 | 4393.155 | 9158.575
09:00 | 4838.09 | 4470.23 | 9308.32
09:30 | 4948.335 | 4507.215 | 9455.55
10:00 | 5058.58 | 4544.2 | 9602.78
10:30 | 5017.405 | 4683.535 | 9700.94
11:00 | 4976.23 | 4822.87 | 9799.1
11:30 | 5026.83 | 4920.39 | 9947.22
12:00 | 5077.43 | 5017.91 | 10095.34
12:30 | 5284.095 | 5012.265 | 10296.36
13:00 | 5490.76 | 5006.62 | 10497.38
13:30 | 5386.785 | 4887.96 | 10274.745
14:00 | 5282.81 | 4769.3 | 10052.11
14:30 | 5162.195 | 4725.195 | 9887.39
15:00 | 5041.58 | 4681.09 | 9722.67
15:30 | 5003.46 | 4619.49 | 9622.95
16:00 | 4965.34 | 4557.89 | 9523.23
16:30 | 4991.075 | 4514.13 | 9505.205
17:00 | 5016.81 | 4470.37 | 9487.18
17:30 | 5370.655 | 4558.03 | 9928.685
18:00 | 5724.5 | 4645.69 | 10370.19
18:30 | 6070 | 4716.635 | 10786.635
19:00 | 6415.5 | 4787.58 | 11203.08
19:30 | 6278.5 | 4755.71 | 11034.21
20:00 | 6105.5 | 4715.91 | 10821.41
20:30 | 6046.5 | 4727.54 | 10774.04 |  | Executive Engineer
21:00 | 5987.5 | 4739.17 | 10726.67 |  | Network Operation Division
21:30 | 5741.5 | 4695.055 | 10436.555
22:00 | 5495.5 | 4650.94 | 10146.44
22:30 | 5331.75 | 4566.775 | 9898.525
23:00 | 5168 | 4482.61 | 9650.61

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 416 | 03:00 | 396 | 12:00 | Payra | 422 | 02:00 | 410 | 11:00
Ashuganj | 412 | 03:00 | 403 | 12:00 | Rahanpur | 419 | 03:00 | 390 | 10:00
Bhulta | 417 | 02:00 | 393 | 12:00 | Rampal | 416 | 02:00 | 393 | 12:00
Bibiana | 415 | 19:00 | 405 | 11:00
BIPTC | 406 | 01:00 | 386 | 13:00
Bogura | 418 | 03:00 | 388 | 10:00
Gopalganj | 418 | 02:00 | 400 | 12:00
Kaliakoir | 405 | 02:00 | 389 | 11:00
Madunaghat | 412 | 03:00 | 403 | 12:00
Meghnaghat | 413 | 03:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 02:00 | 227 | 12:00 | Keranigonj | 240 | 03:00 | 226 | 12:00
AKSML | 238 | 04:00 | 228 | 11:00 | Khulna(S) | 242 | 02:00 | 225 | 12:00
Aminbazar | 239 | 01:00 | 226 | 12:00 | Madunaghat | 239 | 18:30 | 230 | 12:00
Ashuganj | 244 | 01:00 | 235 | 12:00 | Madunaghat-400 | 237 | 19:00 | 231 | 11:00
Ashuganj-400 | 244 | 01:00 | 235 | 12:00 | Maniknagar | 240 | 04:00 | 227 | 12:00
Baghabari | 241 | 01:00 | 229 | 09:00 | Meghnaghat | 244 | 05:00 | 235 | 12:00
Barapukuria | 228 | 05:00 | 212 | 10:00 | Meghnaghat-400 | 242 | 03:00 | 230 | 12:00
Barapukuria-230 | 228 | 05:00 | 212 | 10:00 | Mirsorai | 241 | 19:00 | 229 | 12:00
Barishal | 248 | 05:00 | 239 | 12:00 | Rajshahi | 243 | 04:00 | 223 | 10:00
Bheramara | 241 | 03:00 | 223 | 10:00 | Rampal | 240 | 02:00 | 224 | 12:00
Bhulta | 242 | 04:00 | 228 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 241 | 03:00 | 233 | 12:00 | Rampura | 241 | 03:00 | 228 | 12:00
BIPTC | 244 | 05:00 | 224 | 10:00 | Shikalbaha | 236 | 19:00 | 227 | 12:00
Bogura | 243 | 03:00 | 225 | 10:00 | Shyampur | 240 | 04:00 | 227 | 12:00
Bogura-400 | 241 | 03:00 | 224 | 10:00 | Siddhirganj | 239 | 00:00 | 230 | 11:00
Borhanuddin | 250 | 01:00 | 245 | 11:00 | Sirajgonj | 246 | 06:00 | 237 | 10:00
BSRM | 239 | 19:00 | 229 | 11:00 | Sreepur | 244 | 03:00 | 230 | 11:00
Cumilla(N) | 238 | 05:00 | 229 | 11:00 | Tongi | 235 | 04:00 | 229 | 09:00
Faridpur | 248 | 02:00 | 236 | 12:00
Fenchuganj | 242 | 00:00 | 236 | 16:00
Ghorashal | 244 | 01:00 | 235 | 15:00
Ghorashal-230 | 240 | 02:00 | 227 | 12:00
Gopalganj | 247 | 02:00 | 237 | 12:00
GPH | 239 | 19:00 | 230 | 10:00
Haripur | 242 | 03:00 | 229 | 12:00
Hasnabad | 239 | 06:00 | 226 | 12:00
Hathazari | 240 | 19:00 | 232 | 10:00
Ishurdi | 244 | 03:00 | 226 | 10:00
Jhenaidah | 241 | 03:00 | 223 | 10:00
Kaliakoir | 239 | 02:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 128 | 12:00 | Magura | 140 | 02:00 | 127 | 11:00
Agargaon | 140 | 03:00 | 130 | 12:00 | Mahasthangarh | 136 | 02:00 | 123 | 10:00
Agrabad | 137 | 19:00 | 131 | 10:00 | Manikganj | 138 | 07:00 | 37 | 05:00
AKS | 135 | 19:00 | 130 | 02:00 | Maniknagar | 137 | 02:00 | 129 | 12:00
Aminbazar | 137 | 00:00 | 129 | 16:00 | Matarbari | 131 | 08:00 | 122 | 10:00
Amnura | 141 | 02:00 | 127 | 10:00 | Matuail | 138 | 03:00 | 130 | 12:00
Ashuganj | 145 | 02:00 | 139 | 12:00 | Millgate | 140 | 01:00 | 128 | 12:00
Bagerhat | 138 | 01:00 | 126 | 13:00 | Mirpur | 136 | 02:00 | 130 | 10:00
Bajitpur | 137 | 00:00 | 132 | 07:00 | Mirzapur | 138 | 03:00 | 131 | 12:00
Bakulia | 137 | 18:30 | 131 | 10:00 | Mithapukur | 135 | 03:00 | 119 | 10:00
Banani | 138 | 02:00 | 128 | 12:00 | MI_Cement | 139.5 | 04:00 | 131 | 12:00
Bangabhaban | 137 | 04:00 | 128 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 137 | 05:00 | 124 | 10:00 | Mogbazar | 138 | 02:00 | 130 | 12:00
Barguna | 139 | 03:00 | 135 | 12:00 | Mongla | 135 | 03:00 | 125 | 12:00
Barishal | 137 | 04:00 | 132 | 11:00 | Motijheel | 137 | 04:00 | 128 | 12:00
Barishal-230 | 138 | 02:00 | 131 | 12:00 | Muktagacha | 128 | 00:00 | 120 | 14:00
Baroaulia | 138 | 19:00 | 132 | 12:00 | Munshiganj | 137 | 01:00 | 130 | 12:00
Baroirhat | 136 | 19:00 | 129 | 11:00 | Muradnagar | N/A | N/A | N/A | N/A
Bashundhara | 140 | 03:00 | 127 | 10:00 | Mymensingh | 129 | 04:00 | 119 | 08:00
BashundharaCement | 137 | 03:00 | 130 | 12:00 | Naogaon | 134 | 00:00 | 122 | 10:00
Beanibazar | 139 | 03:00 | 131 | 12:00 | Narail | 139 | 03:00 | 125 | 13:00
Benapole | 136 | 04:00 | 123 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhaluka | 130 | 00:00 | 120 | 12:00 | Narshingdi | 137 | 02:00 | 129 | 10:00
Bhandaria | 135 | 06:00 | 128 | 19:30 | Natore | 138 | 04:00 | 127 | 10:00
Bhangura | 140 | 03:00 | 128 | 12:00 | Nawabganj | 140 | 02:00 | 132 | 12:00
Bheramara | 139 | 02:00 | 128 | 10:00 | Netrakona | 127 | 22:00 | 114 | 08:00
Bheramara(GK) | 139 | 03:00 | 128 | 10:00 | New | 141 | 03:00 | 130 | 12:00
Bhulta | 132 | 00:00 | 127 | 12:00 | Niamatpur | 141 | 03:00 | 130 | 10:00
Bog-Sherpur | 138 | 03:00 | 126 | 10:00 | Noapara | 140 | 04:00 | 127 | 12:00
Bogura | 137 | 01:00 | 126 | 10:00 | Pabna | 138 | 03:00 | 126 | 10:00
Bogura-230 | 138 | 02:00 | 127 | 10:00 | Palashbari | 132 | 04:00 | 118 | 10:00
Brahmanbaria | 140 | 01:00 | 132 | 11:00 | Panchagarh | 140 | 19:30 | 114 | 10:00
Cantonment | 139 | 02:00 | 130 | 12:00 | Patuakhali | 138 | 19:30 | 135 | 11:00
Chandpur | 140 | 19:00 | 129 | 11:00 | Payra | 139 | 01:00 | 135 | 12:00
Chandraghona | 138 | 19:00 | 132 | 12:00 | PHP | 135 | 19:00 | 128 | 12:00
Chapai | 138 | 00:00 | 128 | 10:00 | Postogola | 140 | 00:00 | 134 | 12:00
Charsaidpur | 139 | 02:00 | 131 | 12:00 | Purbachal | 138 | 02:00 | 126 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 136 | 20:00 | 129 | 12:00 | Purbasadipur | 133 | 19:30 | 111 | 10:00
Chhatak | 135 | 00:00 | 127 | 13:00 | Rahanpur | 141 | 00:00 | 133 | 10:00
Chowmuhani | 135 | 19:00 | 127 | 11:00 | Rahanpur-400 | 142 | 01:00 | 132 | 10:00
Chuadanga | 139 | 05:00 | 124 | 12:00 | Rahim | 135 | 01:00 | 130 | 12:00
Coxsbazar | 128 | 19:00 | 119 | 09:00 | Rajbari | 137 | 02:00 | 131 | 12:00
Cumilla(N) | 140 | 19:00 | 132 | 12:00 | Rajendrapur | 139 | 03:00 | 133 | 22:00
Cumilla(S) | 138 | 22:00 | 129 | 13:00 | Rajshahi | 139 | 02:00 | 129 | 10:00
Daudkandi | 135 | 00:00 | 128 | 12:00 | Rajshahi-230 | 141 | 03:00 | 124 | 13:00
Dhaka | 136 | 02:00 | 128 | 12:00 | Ramganj | 136 | 19:00 | 128 | 00:00
Dhamrai | 137 | 02:00 | 129 | 11:00 | Rampur | 137 | 19:00 | 130 | 12:00
Dhanmondi | 139 | 04:00 | 129.6 | 12:00 | Rampura | 137 | 02:00 | 129 | 12:00
Dohazari | 136 | 05:00 | 129 | 11:00 | Rangamati | 136 | 06:00 | 132 | 10:00
Faridpur | 137 | 03:00 | 131 | 12:00 | Rangpur | 132 | 03:00 | 122 | 08:00
Fatullah | 141 | 04:00 | 132 | 12:00 | Ruppur | 140 | 05:00 | 132 | 09:00
Fenchuganj | 141 | 00:00 | 137 | 12:00 | Saidpur | 133 | 20:00 | 118 | 10:00
Feni | 135 | 22:00 | 129 | 11:00 | Satkhira | 140 | 02:00 | 126 | 12:00
Ghatail | 130 | 00:00 | 120 | 18:00 | Satmasjid | 140 | 02:00 | 129 | 12:00
Ghorashal | 144 | 01:00 | 140 | 15:00 | Savar | 136 | 18:30 | 129 | 10:00
Goalpara | 139 | 02:00 | 129 | 12:00 | SevenRings | 144 | 02:00 | 138 | 12:00
Gollamari | 140 | 02:00 | 130 | 12:00 | ShahCement | 139 | 02:00 | 132 | 11:00
Gopalganj | 139 | 05:00 | 130 | 12:00 | Shahjadpur | 140 | 00:00 | 135 | 10:00
Gopalganj-400 | 139 | 02:00 | 132 | 12:00 | Shahjibazar | 141 | 01:00 | 135 | 12:00
Gulshan | 136 | 03:00 | 128 | 12:00 | Shahmirpur | 138 | 19:00 | 131 | 16:00
Halishahar | 138 | 19:00 | 131 | 16:00 | Shariatpur | 138 | 02:00 | 131 | 12:00
Haripur | 138 | 03:00 | 130 | 12:00 | Sherpur | 123 | 23:00 | 113 | 17:00
HaripurSBU | 138 | 03:00 | 131 | 11:00 | Shikalbaha | 127 | 19:00 | 120 | 00:00
Hasnabad | 140 | 00:00 | 133 | 11:00 | Shikalbaha-230 | 137 | 19:00 | 132 | 10:00
Hathazari | 140 | 19:00 | 16 | 04:00 | Shitalakhya | 139.5 | 04:00 | 131 | 12:00
Ishurdi | 142 | 03:00 | 131 | 10:00 | Sholosohor | 137 | 19:00 | 132 | 11:00
Jaldhaka | 132 | 22:00 | 114 | 10:00 | Shyampur | 138 | 00:00 | 133 | 10:00
Jamalpur | 126 | 23:00 | 117 | 07:00 | Shyampur-230 | 140 | 04:00 | 132 | 12:00
Jashore | 139 | 02:00 | 125 | 12:00 | Siddhirganj | 139 | 04:00 | 130 | 12:00
Jhenaidah | 139 | 02:00 | 127 | 12:00 | Sirajganj | 138 | 03:00 | 128 | 09:00
Jhenaidah-230 | 141 | 02:00 | 128 | 12:00 | Sonargaon | 136 | 01:00 | 128 | 12:00
Joydebpur | 141 | 18:30 | 135 | 00:00 | Sreemongol | 139 | 00:00 | 134 | 12:00
Joypurhat | 136 | 02:00 | 120 | 10:00 | Sreepur | 132 | 02:00 | 124 | 11:00
Juldah | 136 | 19:30 | 131 | 16:00 | Srinagar | 141 | 06:00 | 132 | 12:00
Kabirpur | 142 | 22:00 | 127 | 10:00 | SSM | 141 | 19:00 | 138 | 10:00
Kachua | 139 | 22:00 | 130 | 11:00 | Sunamganj | 136 | 01:00 | 126 | 15:00
Kaliakoir | 143 | 06:00 | 130 | 12:00 | Sylhet | 139 | 02:00 | 130 | 15:00
Kallyanpur | 136 | 04:00 | 129 | 11:00 | Sylhet-132 | 138 | 00:00 | 130 | 12:00
Kalurghat | 138 | 19:00 | 132 | 11:00 | Tangail | 132 | 00:00 | 126 | 17:00
Kamrangirchar | 140 | 06:00 | 127 | 12:00 | Thakurgaon | 139 | 19:30 | 112 | 10:00
Kaptai | N/A | N/A | N/A | N/A | TK | 138 | 19:00 | 133 | 04:00
Kazla | 137 | 02:00 | 129 | 12:00 | Tongi | 139 | 04:00 | 133 | 10:00
Keranigonj | 140 | 03:00 | 132 | 12:00 | Ullahpara | 140 | 04:00 | 129 | 10:00
Khagrachori | 136 | 03:00 | 131 | 12:00 | Ullon | 136 | 00:00 | 129 | 12:00
Khulna | 139 | 05:00 | 128 | 12:00 | Uttara | 137 | 02:00 | 129 | 11:00
Khulna(S) | 141 | 02:00 | 130 | 12:00 | UttaraNew | 138 | 01:00 | 129 | 12:00
Khulshi | 136 | 19:00 | 129 | 16:00 | Zigatola | 141 | 02:00 | 133 | 12:00
Kishoreganj | 133 | 00:00 | 128 | 07:00
Kodda | 141 | 13:00 | 134 | 07:00
KSRM | 138 | 19:00 | 132 | 16:00
Kulaura | 141 | 01:00 | 137 | 12:00
Kurigram | 131 | 04:00 | 118 | 10:00
Kushtia | 140 | 02:00 | 12 | 10:00
Lalbag | 141 | 03:00 | 132 | 12:00
Lalmonirhat | 132 | 05:00 | 117 | 19:00
Madanganj | 137 | 03:00 | 130 | 12:00
Madaripur | 136 | 05:00 | 132 | 12:00
Madartek | 137 | 03:00 | 128 | 12:00
Madunaghat | 137 | 18:30 | 132 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division