## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-02-2025 | [28 empty] | Date: | 10-02-2025 | [28 empty] | Date: | 10-02-2025 | [28 empty] | Date: | 10-02-2025 | [28 empty] | Date: | 10-02-2025 | [19 empty] | Date: | 10-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [19 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 226 | 0 | 0 | 305 | 0 | 0 | 0 | 54 | 0 | 17 | 32 | 0 | 0 | 0 | 17 | 17 | 0 | 300 | 244 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 153 | 0 | 0 | 12 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 10 | 197 | 0 | 0 | 305 | 29 | 183 | 24 | 68 | 0 | 17 | 26 | 16 | 0 | 50 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 54.5 | 59 | 9 | 20 | 0 | 0 | 6 | 4811.5 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 150 | 0 | 314 | 0 | 0 | 2.5 | 159 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 110 | 0 | 0 | 622 | 17 | 4426.5 | 9238 | 90.91
01:00 | 0 | 34 | 0 | 0 | 0 | 270 | 0 | 0 | 305 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 300 | 290 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 158 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 570 | 0 | 51 | 0 | 197 | 0 | 0 | 300 | 29 | 191 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 19 | 9 | 22 | 0 | 0 | 6 | 4463 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 0 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 144 | 0 | 313 | 0 | 0 | 2.5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 136 | 110 | 0 | 0 | 550 | 0 | 4054.5 | 8517.5 | 90.91
02:00 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 295 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 197 | 0 | 0 | 300 | 29 | 196 | 29 | 0 | 20 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 320 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 19 | 9 | 24 | 0 | 0 | 0 | 4385 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 158 | 0 | 327 | 0 | 0 | 2.5 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 136 | 110 | 0 | 0 | 500 | 0 | 3795.5 | 8180.5 | 90.9
03:00 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 286 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 197 | 0 | 0 | 300 | 29 | 191 | 29 | 0 | 50 | 0 | 0 | 16 | 0 | 34 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4346 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 0 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 144 | 0 | 320 | 0 | 0 | 2.5 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 136 | 125 | 0 | 0 | 500 | 0 | 3560.5 | 7906.5 | 90.9
04:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 275 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 158 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 199 | 0 | 0 | 300 | 29 | 181 | 29 | 0 | 70 | 0 | 0 | 16 | 0 | 44 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4221 | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 151 | 0 | 314 | 0 | 0 | 2.5 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 6 | 136 | 125 | 0 | 0 | 450 | 0 | 3534.5 | 7755.5 | 90.89
05:00 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 297 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 158 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 199 | 0 | 0 | 300 | 29 | 191 | 29 | 0 | 80 | 0 | 0 | 16 | 0 | 40 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 41 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4170 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 148 | 0 | 335 | 0 | 0 | 2.5 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 175 | 0 | 0 | 400 | 0 | 3367.5 | 7537.5 | 90.89
06:00 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 296 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 199 | 0 | 0 | 360 | 29 | 201 | 29 | 0 | 80 | 0 | 0 | 16 | 0 | 34 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 16 | 0 | 79 | 30 | 0 | 20 | 0 | 0 | 20 | 2 | 24 | 0 | 0 | 0 | 4321 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636 | 0 | 468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 0 | 2.5 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 136 | 220 | 0 | 0 | 410 | 0 | 3668.5 | 7989.5 | 90.88
07:00 | 0 | 20 | 0 | 0 | 0 | 125 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 7 | 70 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 291 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 1 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 158 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 590 | 1 | 51 | 0 | 189 | 0 | 0 | 365 | 29 | 222 | 29 | 0 | 70 | 0 | 0 | 16 | 0 | 32 | 0 | 3 | 0 | 320 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 57 | 9 | 24 | 0 | 1.02 | 3 | 4625.02 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | 840 | 0 | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 180 | 0 | 0 | 0 | 167 | 0 | 414 | 0 | 0.12 | 2.5 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.02 | 0 | 287 | 6 | 134 | 220 | 0 | 0 | 490 | 0 | 4323.75 | 8948.77 | 90.88
08:00 | 0 | 52 | 14 | 0 | 0 | 100 | 0 | 0 | 304 | 0 | 0 | 12 | 9 | 0 | 45 | 82 | 0 | 0 | 0 | 54 | 17 | 0 | 300 | 284 | 0 | 0 | 17 | 26 | 250 | 0 | 0 | 7 | 0 | 19 | 22 | 0 | 0 | 21 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 2 | 1 | 40 | 0 | 11 | 155 | 0 | 0 | 25 | 0 | 20 | 226 | 0 | 0 | 0 | 615 | 7 | 51 | 18 | 189 | 0 | 0 | 360 | 29 | 198 | 30 | 1 | 50 | 17 | 5 | 16 | 0 | 40 | 0 | 20 | 0 | 330 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 8 | 56 | 9 | 24 | 0 | 9.05 | 0 | 4907.05 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.08 | 937 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 0 | 11.23 | 180 | 0 | 0 | 0 | 162 | 0 | 414 | 0 | 0.96 | 2.5 | 155 | 0 | 35 | 4 | 10 | 0 | 0 | 0.8 | 26 | 0.13 | 0 | 307 | 5 | 136 | 220 | 0 | 0 | 600 | 17 | 4893.7 | 9800.75 | 90.87
09:00 | 0 | 52 | 16 | 0 | 0 | 150 | 0 | 0 | 378 | 0 | 0 | 17 | 17 | 0 | 70 | 82 | 0 | 10 | 0 | 54 | 17 | 0 | 420 | 260 | 0 | 0 | 35 | 26 | 0 | 0 | 0 | 16 | 0 | 19 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 2 | 40 | 16 | 4 | 156 | 0 | 0 | 32 | 0 | 94 | 226 | 0 | 0 | 0 | 612 | 13 | 51 | 90 | 189 | 0 | 0 | 360 | 29 | 181 | 30 | 16 | 45 | 94 | 27 | 16 | 0 | 44 | 0 | 39 | 0 | 295 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 56 | 9 | 20 | 1 | 19.4 | 4 | 5244.4 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.86 | 962 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 48 | 0 | 24.75 | 176 | 0 | 0 | 0 | 181 | 0 | 328 | 0 | 2.21 | 2.5 | 154 | 0 | 95 | 11 | 34 | 0 | 0 | 2.2 | 70 | 0.29 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 600 | 17 | 5071.81 | 10316.21 | 90.87
10:00 | 0 | 52 | 16 | 0 | 0 | 150 | 0 | 0 | 405 | 0 | 0 | 17 | 17 | 0 | 70 | 82 | 0 | 15 | 17 | 17 | 17 | 0 | 420 | 288 | 0 | 0 | 35 | 26 | 0 | 0 | 0 | 24 | 0 | 19 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 2 | 0 | 8 | 0 | 0 | 0 | 3 | 40 | 17 | 2 | 157 | 0 | 0 | 33 | 0 | 17 | 226 | 0 | 0 | 0 | 612 | 17 | 40 | 70 | 189 | 0 | 0 | 360 | 29 | 183 | 33 | 17 | 40 | 85 | 27 | 16 | 0 | 40 | 0 | 54 | 0 | 280 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 56 | 9 | 18 | 1 | 29.62 | 6 | 5160.62 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.16 | 1025 | 0 | 749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 73 | 0 | 38.21 | 175 | 0 | 0 | 0 | 181 | 0 | 310 | 0 | 3.4 | 2.5 | 154 | 0 | 35 | 18 | 0 | 0 | 0 | 3.3 | 104 | 0.44 | 0 | 250 | 4 | 100 | 220 | 0 | 0 | 600 | 17 | 5074.01 | 10234.63 | 90.87
11:00 | 0 | 52 | 21 | 0 | 0 | 150 | 0 | 0 | 408 | 0 | 0 | 17 | 17 | 0 | 90 | 82 | 0 | 15 | 17 | 17 | 17 | 0 | 420 | 288 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 28 | 0 | 18 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 0 | 0 | 4 | 40 | 17 | 2 | 157 | 0 | 0 | 20 | 0 | 17 | 226 | 0 | 0 | 0 | 614 | 20 | 40 | 50 | 179 | 0 | 0 | 357 | 29 | 183 | 33 | 17 | 40 | 34 | 9 | 16 | 0 | 40 | 0 | 64 | 0 | 295 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 56 | 9 | 12 | 2 | 37.86 | 6 | 5113.86 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.03 | 1000 | 0 | 742 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 43 | 87 | 0 | 45.88 | 176 | 0 | 0 | 0 | 176 | 0 | 310 | 0 | 4.1 | 2.5 | 162 | 0 | 35 | 23 | 0 | 0 | 0 | 4.3 | 128 | 0.55 | 0 | 250 | 4 | 100 | 220 | 0 | 0 | 610 | 17 | 5178.36 | 10292.22 | 90.86
12:00 | 0 | 52 | 25 | 0 | 0 | 190 | 0 | 0 | 410 | 0 | 0 | 17 | 18 | 0 | 124 | 82 | 0 | 15 | 17 | 17 | 17 | 0 | 450 | 305 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 30 | 0 | 18 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 8 | 0 | 32 | 0 | 0 | 0 | 4 | 40 | 17 | 3 | 158 | 0 | 0 | 19 | 0 | 17 | 223 | 0 | 0 | 0 | 612 | 20 | 40 | 50 | 177 | 0 | 0 | 350 | 29 | 200 | 33 | 17 | 42 | 34 | 9 | 16 | 0 | 48 | 0 | 68 | 0 | 300 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 58 | 9 | 12 | 2 | 41.8 | 6 | 5293.8 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.77 | 1066 | 0 | 742 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 43 | 95 | 0 | 52.52 | 176 | 0 | 0 | 0 | 176 | 0 | 410 | 0 | 4.11 | 2.5 | 157 | 0 | 35 | 27 | 0 | 0 | 0 | 4.7 | 145 | 0.6 | 0 | 274 | 4 | 130 | 220 | 0 | 0 | 622 | 17 | 5446.2 | 10740 | 90.86
13:00 | 0 | 52 | 25 | 0 | 0 | 230 | 0 | 0 | 411 | 0 | 0 | 17 | 36 | 0 | 124 | 82 | 0 | 15 | 17 | 72 | 25 | 0 | 450 | 290 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 29 | 0 | 18 | 22 | 0 | 0 | 31 | 0 | 0 | 0 | 5 | 0 | 40 | 0 | 0 | 0 | 4 | 40 | 17 | 9 | 157 | 0 | 0 | 28 | 0 | 55 | 223 | 0 | 0 | 0 | 612 | 20 | 40 | 50 | 184 | 0 | 0 | 345 | 29 | 190 | 33 | 29 | 40 | 56 | 9 | 11 | 0 | 48 | 0 | 63 | 0 | 315 | 320 | 0 | 33 | 30 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 12 | 2 | 40.87 | 6 | 5464.87 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.46 | 1134 | 0 | 738 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 19 | 52 | 96 | 0 | 49.81 | 174 | 0 | 0 | 0 | 183 | 0 | 401 | 0 | 4.32 | 2.5 | 155 | 0 | 35 | 25 | 0 | 0 | 0 | 4.8 | 136 | 0.56 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 17 | 5552.45 | 11017.32 | 90.86
14:00 | 0 | 52 | 25 | 0 | 0 | 230 | 0 | 0 | 413 | 0 | 0 | 17 | 36 | 0 | 115 | 48 | 0 | 15 | 0 | 72 | 25 | 0 | 450 | 270 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 25 | 0 | 18.2 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | 0 | 40 | 0 | 0 | 0 | 3 | 40 | 17 | 5 | 157 | 0 | 0 | 48 | 0 | 68 | 222 | 0 | 0 | 0 | 612 | 17 | 51 | 50 | 185 | 0 | 0 | 300 | 29 | 183 | 33 | 34 | 40 | 68 | 9 | 11 | 0 | 50 | 0 | 55 | 0 | 290 | 320 | 0 | 32 | 30 | 0 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 12 | 2 | 35.33 | 6 | 5338.53 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.17 | 1032 | 0 | 729.81 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 19 | 52 | 87 | 0 | 45.1 | 174 | 0 | 0 | 0 | 181 | 0 | 388 | 0 | 4.02 | 2.5 | 153 | 0 | 35 | 22 | 0 | 0 | 0 | 4.2 | 125 | 0.51 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 17 | 5391.31 | 10729.84 | 90.85
15:00 | 0 | 60 | 25 | 0 | 0 | 230 | 0 | 0 | 408 | 0 | 0 | 17 | 17 | 0 | 54 | 48 | 0 | 0 | 0 | 17 | 25 | 0 | 450 | 291 | 0 | 0 | 17 | 28 | 0 | 0 | 0 | 20 | 0 | 18.2 | 22 | 0 | 0 | 20 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 156 | 0 | 0 | 40 | 0 | 17 | 222 | 0 | 0 | 0 | 612 | 14 | 51 | 24 | 185 | 0 | 0 | 300 | 29 | 185 | 30 | 34 | 40 | 51 | 9 | 17 | 0 | 50 | 0 | 39 | 0 | 300 | 320 | 0 | 32 | 29 | 0 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 13 | 1 | 24.01 | 6 | 5022.21 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.49 | 1116 | 0 | 731.03 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 18 | 52.2 | 66 | 8 | 25.14 | 175 | 0 | 0 | 0 | 185 | 0 | 390 | 0 | 2.86 | 2.5 | 153 | 0 | 35 | 16 | 0 | 0 | 0 | 2.8 | 87 | 0.4 | 0 | 256 | 4 | 130 | 220 | 0 | 0 | 622 | 17 | 5335.42 | 10357.63 | 90.85
16:00 | 0 | 70 | 25 | 0 | 0 | 160 | 0 | 0 | 405 | 0 | 0 | 17 | 17 | 0 | 51 | 48 | 0 | 0 | 0 | 17 | 25 | 0 | 450 | 302 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 12 | 0 | 12.5 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 13 | 0 | 16 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 160 | 0 | 0 | 19 | 0 | 17 | 222 | 0 | 0 | 0 | 570 | 8 | 51 | 24 | 147 | 0 | 0 | 335 | 29 | 200 | 33 | 16 | 40 | 17 | 8 | 17 | 0 | 46 | 0 | 22 | 0 | 300 | 320 | 0 | 35 | 29 | 0 | 5 | 163 | 0 | 0 | 81 | 30 | 0 | 20 | 0 | 3 | 59 | 9 | 13 | 1 | 12.69 | 6 | 4829.19 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.92 | 1132 | 0 | 694.38 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 18 | 52.2 | 39 | 23 | 18.03 | 177 | 0 | 0 | 0 | 187 | 0 | 414 | 0 | 1.57 | 2.5 | 155 | 0 | 35 | 8 | 0 | 0 | 0 | 1.6 | 46 | 0.23 | 0 | 200 | 4 | 130 | 220 | 0 | 0 | 610 | 17 | 5180.43 | 10009.62 | 90.85
17:00 | 0 | 77 | 25 | 0 | 0 | 70 | 0 | 0 | 408 | 0 | 0 | 35 | 17 | 0 | 51 | 64 | 0 | 4 | 17 | 54 | 25 | 0 | 450 | 291 | 0 | 0 | 17 | 20 | 0 | 0 | 0 | 3 | 0 | 17 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 12 | 0 | 16 | 0 | 5 | 8 | 0 | 40 | 9 | 2 | 155 | 17 | 0 | 20 | 0 | 18 | 223 | 0 | 0 | 0 | 550 | 3 | 51 | 32 | 147 | 0 | 0 | 335 | 29 | 194 | 33 | 23 | 40 | 22 | 10 | 17 | 0 | 46 | 0 | 7 | 0 | 310 | 320 | 0 | 35 | 29 | 0 | 5 | 163 | 17 | 0 | 81 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 16 | 0 | 3.39 | 6 | 4883.39 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.83 | 1146 | 0 | 662.51 | 0 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 18 | 52.2 | 12 | 30 | 4.69 | 177 | 0 | 0 | 0 | 185 | 0 | 414 | 0 | 0.39 | 2.5 | 155 | 0 | 35 | 2 | 0 | 0 | 0 | 0.5 | 13 | 0.08 | 0 | 250 | 4 | 128 | 220 | 0 | 0 | 600 | 17 | 5102.7 | 9986.09 | 90.84
18:00 | 0 | 105 | 25 | 0 | 0 | 220 | 0 | 0 | 406 | 0 | 0 | 49 | 26 | 0 | 51 | 76 | 0 | 26 | 22 | 126 | 25 | 0 | 450 | 248 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 7 | 17 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 15 | 51 | 21 | 0 | 18 | 50 | 0 | 40 | 19 | 2 | 156 | 17 | 0 | 33 | 0 | 50 | 222 | 0 | 0 | 0 | 612 | 0 | 51 | 72 | 185 | 0 | 0 | 335 | 29 | 182 | 30 | 60 | 40 | 82 | 27 | 17 | 0 | 52 | 0 | 0 | 47 | 295 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 81 | 30 | 0 | 20 | 0 | 23 | 59 | 9 | 16 | 0 | 0 | 6 | 5587 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1198 | 0 | 712.33 | 0 | 0 | 33 | 0 | 0 | 5 | 89 | 0 | 30 | 52.2 | 0 | 30 | 0 | 178 | 0 | 0 | 0 | 183 | 0 | 320 | 0 | 0 | 2.5 | 152 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 100 | 200 | 0 | 0 | 600 | 35 | 5165.03 | 10752.03 | 90.84
19:00 | 0 | 105 | 25 | 0 | 0 | 220 | 0 | 0 | 405 | 0 | 0 | 54 | 54 | 0 | 46 | 82 | 0 | 40 | 45 | 162 | 25 | 0 | 450 | 255 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 0 | 0 | 35 | 0 | 8 | 0 | 17 | 51 | 78 | 0 | 12 | 24 | 0 | 40 | 34 | 11 | 155 | 0 | 0 | 33 | 0 | 85 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 115 | 185 | 0 | 0 | 345 | 29 | 182 | 30 | 115 | 35 | 120 | 29 | 17 | 0 | 52 | 0 | 0 | 38 | 290 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 83 | 30 | 0 | 20 | 0 | 54.5 | 59 | 9 | 18 | 0 | 0 | 6 | 5982.5 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 744.58 | 0 | 0 | 33 | 0 | 0 | 6 | 89 | 0 | 35 | 52.2 | 0 | 30 | 0 | 180 | 0 | 0 | 0 | 182 | 0 | 393 | 0 | 0 | 2.5 | 155 | 0 | 95 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 6 | 130 | 220 | 0 | 0 | 600 | 35 | 5395.28 | 11377.78 | 90.84
19:30 | 0 | 105 | 25 | 0 | 0 | 220 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 0 | 34 | 64 | 0 | 30 | 17 | 162 | 25 | 0 | 450 | 263 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 7 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 13 | 34 | 40 | 0 | 0 | 24 | 0 | 40 | 17 | 14 | 156 | 0 | 0 | 33 | 0 | 85 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 185 | 0 | 0 | 345 | 29 | 182 | 33 | 115 | 35 | 120 | 29 | 17 | 0 | 52 | 0 | 0 | 0 | 280 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 83 | 30 | 0 | 20 | 0 | 35 | 59 | 9 | 18 | 0 | 0 | 6 | 5710 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 52.2 | 0 | 30 | 0 | 180 | 0 | 0 | 0 | 182 | 0 | 392 | 0 | 0 | 2.5 | 156 | 0 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 7 | 130 | 220 | 0 | 0 | 610 | 35 | 5376.7 | 11086.7
20:00 | 0 | 105 | 25 | 0 | 0 | 220 | 0 | 0 | 404 | 0 | 0 | 54 | 17 | 0 | 34 | 64 | 0 | 15 | 17 | 108 | 25 | 0 | 450 | 283 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 34 | 40 | 0 | 0 | 24 | 0 | 40 | 0 | 20 | 156 | 0 | 0 | 33 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 187 | 0 | 0 | 345 | 29 | 187 | 33 | 115 | 35 | 100 | 29 | 17 | 0 | 44 | 0 | 0 | 0 | 285 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 19 | 0 | 0 | 6 | 5516.5 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238 | 0 | 754.83 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 52.2 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 181 | 0 | 397 | 0 | 0 | 2.5 | 156 | 0 | 73 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 7 | 130 | 220 | 0 | 0 | 600 | 35 | 5343.53 | 10860.03 | 90.84
21:00 | 0 | 88 | 25 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 23 | 17 | 0 | 34 | 64 | 0 | 15 | 17 | 108 | 25 | 0 | 450 | 281 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 155 | 0 | 0 | 25 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 24 | 197 | 0 | 0 | 345 | 27 | 182 | 33 | 115 | 40 | 85 | 29 | 17 | 0 | 46 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 20 | 0 | 0 | 6 | 5379 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 52.2 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 178 | 0 | 395 | 0 | 0 | 2.5 | 156 | 0 | 53 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 35 | 5337.7 | 10716.7 | 90.83
22:00 | 0 | 88 | 16 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 27 | 17 | 0 | 30 | 48 | 0 | 0 | 0 | 72 | 22 | 0 | 450 | 265 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 155 | 0 | 0 | 19 | 0 | 17 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 24 | 197 | 0 | 0 | 345 | 29 | 182 | 30 | 85 | 40 | 34 | 29 | 17 | 0 | 50 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 17 | 59 | 9 | 19 | 0 | 0 | 6 | 5138 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 52.2 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 176 | 0 | 392 | 0 | 0 | 2.5 | 155 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 35 | 5244.7 | 10382.7 | 90.83
23:00 | 0 | 88 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 279 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 155 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 340 | 29 | 182 | 33 | 0 | 40 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 59 | 9 | 17 | 0 | 0 | 6 | 4637 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 0 | 2.5 | 151 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 5096.5 | 9733.5 | 90.82
Total KWH | 0 | 1310400 | 360480 | 0 | 0 | 4523594 | 0 | 0 | 9018000 | 0 | 0 | 388800 | 440640 | 0 | 1046304 | 1177920 | 0 | 218128 | 210551 | 1032480 | 470160 | 0 | 9237500 | 6819375 | 0 | 0 | 403040 | 565600 | 2173710 | 0 | 0 | 196192 | 18000 | 377400 | 522000 | 0 | 0 | 476727 | 32618 | 8640 | 0 | 210720 | 128945 | 338659 | 0 | 56640 | 136320 | 25801 | 967620 | 222472 | 585120 | 3745454.54 | 31782 | 0 | 464640 | 0 | 762764 | 5413752 | 0 | 0 | 0 | 13849089 | 140130 | 1168918 | 936727 | 4482909 | 0 | 0 | 8098000 | 695520 | 4635000 | 746064 | 788160 | 981490 | 1056960 | 290640 | 387780 | 0 | 1032000 | 0 | 439927 | 68288 | 7337500 | 7707100 | 0 | 819576 | 712000 | 0 | 110112 | 3682718 | 370848 | 0 | 1940160 | 723264 | 0 | 489000 | 0 | 328680 | 1090800 | 187200 | 427200 | 11000 | 254440 | 107280 | 120215428.54 | 21136023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575280 | 22887275 | 0 | 16719693 | 0 | 0 | 37240 | 0 | 0 | 14615 | 705024 | 0 | 123266 | 688704 | 640720 | 119397 | 323248 | 4278000 | 0 | 0 | 0 | 4329045 | 0 | 9017672.7 | 0 | 28260 | 72360 | 3787000 | 0 | 865238 | 159070 | 279753 | 0 | 0 | 29137.68 | 881280 | 3834 | 0 | 6327000 | 140726 | 3046000 | 4889530 | 0 | 0 | 14065454.55 | 366000 | 116535845.93 | 236751274.47

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-02-2025 | during | 11-02-2025 | during | 11-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 190 | 220 | 100 | 100 | 100 | 100 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 410 | 405 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 255 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 40 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 17 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 82 | 82 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 45 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 18 | 17 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 20 | 20 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 124 | 46 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 72 | 72 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 54 | 36 | 54 | 17 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5860.564 | 1864 | 2079 | 4689.87 | 4675.87 | 2525.82 | 2531.82
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 226 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 85 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 32 | 78 | 64 | 80 | 64 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 11 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 8 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 8 | 17 | 2 | 1 | 2 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 158 | 155 | 150 | 150 | 150 | 150 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1170 | 1421 | 2413.86 | 2426.86 | 2332.86 | 2345.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 350 | 345 | 356.56 | 356.56 | 321 | 321 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 30 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 177 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 40 | 51 | 40 | 51 | 40 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 115 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 42 | 35 | 163 | 163 | 40 | 40 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 48 | 52 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 115 | 115 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1113 | 1343 | 2079.53 | 2025.53 | 1670.2 | 1616.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-02-2025 | during | 11-02-2025 | during | 11-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 12 | 18 | 210 | 210 | 30 | 30 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 59 | 115 | 115 | 56 | 56 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.8 | 0 | 39.5 | 0 | 39.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 145.8 | 146.5 | 642.8 | 601.5 | 196.8 | 155.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 35 | 40 | 40 | 36 | 36 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 17 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1001 | 993 | 1060 | 1060 | 1013 | 1013
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 909 | 864 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 48 | 48 | 48 | 48 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Commissioning work is in progress
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 84.77 | 0 | 94 | 0 | 94 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1066 | 1216 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | coal available to run both units upto 12/02/25
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2059.77 | 2080 | 3602.2 | 3508.2 | 2982.2 | 2888.2
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 6 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 600 | 622 | 622 | 602 | 602 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 274 | 290 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1267.6 | 1281 | 1556.12 | 1555.12 | 1533 | 1532
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 33 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 6 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 176 | 180 | 214 | 214 | 185 | 185 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 182 | 220 | 220 | 190 | 190 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 393 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 49 | 89 | 92 | 92 | 92 | 92 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.11 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 742 | 744.58 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.52 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1750.13 | 1747.28 | 2508.34 | 2343.24 | 2187.56 | 2022.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 155 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 37 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 168.28 | 0 | 168.28 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 368.7 | 287 | 622.88 | 422 | 622.88 | 422
System Total |  |  |  |  | 27884.66 | 27085.542 | 10740 | 11377.78 | 19175.6 | 18618.32 | 15064.32 | 14527.04
Forecast Scenario (11-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9130 |  | 0 |  | 9130
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8180 |  | 0 |  | 8180
|  |  |  | 3:00 | 7770 |  | 0 |  | 7770
|  |  |  | 4:00 | 7510 |  | 0 |  | 7510
|  |  |  | 5:00 | 7520 |  | 0 |  | 7520
|  |  |  | 6:00 | 7910 |  | 0 |  | 7910
|  |  |  | 7:00 | 8980 |  | 0 |  | 8980
|  |  |  | 8:00 | 9930 |  | 0 |  | 9930
|  |  |  | 9:00 | 10410 |  | 0 |  | 10410
|  |  |  | 10:00 | 10340 |  | 0 |  | 10340
|  |  |  | 11:00 | 10430 |  | 0 |  | 10430
|  |  |  | 12:00 | 10820 |  | 0 |  | 10820
|  |  |  | 13:00 | 11090 |  | 0 |  | 11090
|  |  |  | 14:00 | 10660 |  | 0 |  | 10660
|  |  |  | 15:00 | 10160 |  | 0 |  | 10160
|  |  |  | 16:00 | 9790 |  | 0 |  | 9790
|  |  |  | 17:00 | 9830 |  | 0 |  | 9830
|  |  |  | 18:00 | 10650 |  | 0 |  | 10650
|  |  |  | 18:30 | 10950 |  | 0 |  | 10950
|  |  |  | 19:00 | 11380 |  | 0 |  | 11380
|  |  |  | 19:30 | 11080 |  | 0 |  | 11080
|  |  |  | 20:00 | 10970 |  | 0 |  | 10970
|  |  |  | 21:00 | 10700 |  | 0 |  | 10700
|  |  |  | 22:00 | 10320 |  | 0 |  | 10320
|  |  |  | 23:00 | 9690 |  | 0 |  | 9690
Probable Maximum Temperature: |  |  | 26.60°C
Probable Maximum Demand at Day Peak: |  |  | 10820.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11380.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11380.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 232.67 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:27 hrs on 11-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10740 | MW | 12:00 Hr. | Energy Generated |  |  | 236.7513 |  | MKWHr.
| Day Peak Demand |  |  | 10773 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.65 |  | MKWHr.
| Evening Peak Generation |  |  | 11377.78 | MW | 19:00 Hr. | Energy Demand |  |  | 237.4013 |  | MKWHr.
| Evening Peak Demand |  |  | 11421.78 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.9 |  | °C
| Minimum Generation of the Day |  |  | 7537.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 836.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 11377.78 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.1837 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.7073 | 0 | 6.6067 | 0 | 0 | 0.19619 | 0 | 0 | 40.5103 | Gas | 110.9947 | Gas | 407848439.135
| Chattogram Zone |  |  | 5.9989 | 17.5945 | 2.6602 | 0 | 0.96762 | 0.16593 | 0 | 0.21072 | 27.5979 | Coal | 64.6613 | Coal | 475338139.5187
| Cumilla Zone |  |  | 21.1957 | 0 | 3.1408 | 0 | 0 | 0.43993 | 1.032 | 0 | 25.8084 | HFO | 17.3209 | HFO | 319700532.99
| Mymensingh Zone |  |  | 0.4272 | 0 | 1.714 | 0 | 0 | 0.26544 | 0 | 0 | 2.4066 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.8923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8923 | Hydro | 0.96762 | Hydro | 96762
| Khulna Zone |  |  | 0 | 22.8873 | 0 | 0 | 0 | 0.57528 | 21.136 | 0 | 44.5986 | Solar | 3.7083 | Solar | 57529882.058
| Barishal Zone |  |  | 8.0763 | 20.3925 | 0.366 | 0 | 0 | 0.003834 | 0 | 0 | 28.8385 | Import | 38.8877 | Import | 200202395.97
| Rajshahi Zone |  |  | 17.6971 | 0 | 1.6882 | 0 | 0 | 0.99223 | 16.7197 | 0 | 37.0972 | Wind | 0.21072 | Wind | 3287232
| Rangpur Zone |  |  | 0 | 3.787 | 1.145 | 0 | 0 | 1.0695 | 0 | 0 | 6.0015
| Total |  |  | 110.9947 | 64.6613 | 17.3209 | 0 | 0.96762 | 3.7083 | 38.8877 | 0.21072 | 236.7513
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 407848439.135 |  | Hydro | 96762
|  |  |  | Coal | 475338139.5187 |  | Solar | 57529882.058
|  |  |  | HFO | 319700532.99 |  | Import | 200202395.97
|  |  |  | HSD | 0 |  | Wind | 3287232
[5 empty] | Total: | 146,40,03,383 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.136 | Peak Hr Flow | 864.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9762654 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.7197 | Peak Hr Flow | 744.58 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 514 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.032 | Peak Hr Flow | 52.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 868 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 38.8877 | Peak Hr Flow | 1660.58 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4135
|  |  |  | Chattogram |  | 0 |  | 1059
|  |  |  | Cumilla |  | 0 |  | 915
|  |  |  | Mymensingh |  | 42 |  | 987
|  |  |  | Sylhet |  | 0 |  | 402
|  |  |  | Khulna |  | 0 |  | 1234
|  |  |  | Barishal |  | 0 |  | 291
|  |  |  | Rajshahi |  | 0 |  | 1124
|  |  |  | Rangpur |  | 0 |  | 762
|  |  |  | Total |  | 42 |  | 10909
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:09 | 16:32 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to Annual | [7 empty] | 20.0MW load
|  |  | maintenance | [7 empty] | interrup. Chandpur
132/33kV end
| 08:19 | 16:11 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
maintenance work of DEAD line check
| 08:23 | 17:57 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D
| 08:24 | 17:57 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D
| 08:28 | 17:55 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Tower Painting
| 08:28 | 17:56 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Project Work S/D Due to Tower Painting
| 08:28 | 17:56 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Project Work S/D Due to Tower Painting
| 08:29 | 17:55 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Tower Painting
| 08:46 |  | Siddirganj CCPP 335MW was shutdown at 08:46 hrs due to Titas maintenance work.
| 08:57 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is OFF with remarks:- Insufficient gas pressure for
FGMO opeartion
| 08:58 | 10:09 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Relay
Testing.
| 09:35 | 14:31 | Agrabad-Rampur 132kV Ckt-2 Scheduled S/D from Agrabad 132/33kV end Due to Annual
Maintenance
| 09:37 | 14:30 | Rampur 230/132/33 S/S Agrabad-2 Scheduled S/D Due to Anual maintenance in Agrabad grid
substation.
| 09:44 | 17:37 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D
| 09:45 | 17:37 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to hydrolic pipe change
| 10:13 | 10:38 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 10:15 | 16:37 | Bibiana 400/230kV S/S Bibiyana-III GTG Forced S/D Due to Oil leckage
| 10:20 | 13:07 | Ghorashal 230kV S/S TARFO-2 LT Scheduled S/D Due to Shutdown requsition by BPDB for | [7 empty] | 58.0MW load
|  |  | commissioning of Fertilizer (33kV outgiong-3) feeder. | [7 empty] | interrup.
| 10:38 | 17:45 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 11:02 | 12:24 | Ghorasal-Joydeb-B 132kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to Realy
Test
| 11:04 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Mahasthangarh 132/33kV end Due
to Reconducting Purpose
| 11:15 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end Due to
project work
|  | 11:21 | Bheramara 230/132kV S/S GTG (NW) is restored.
| 12:00 |  | Day peak Generation is 10736 MW
| 12:26 | 13:22 | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Relay
Test
|  | 12:48 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS is restored.
|  | 14:34 | Maniknagar-Siddhirganj 230kV Ckt-2 is restored.
|  | 16:00 | Rangpur-Saidpur 132kV Ckt-1 is restored.
| 16:04 |  | Sylhet 132/33kV S/S 75 MW ST PS Scheduled S/D Due to RTU maintenance
|  | 16:33 | Candpur- Kachua 132kV Ckt-2 is restored.
|  | 16:42 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 is restored.
|  | 16:42 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 is restored.
| 16:59 | 19:08 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Forced S/D Due to Energy Meter
Accuracy Test
| 16:59 | 19:07 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Forced S/D Due to Energy Meter
Accuracy Test
| 19:00 |  | Evening Peak Generation: 11376 MW
| 19:00 |  | Evening Peak Generation: 11376 MW.
|  | 19:18 | Bhulta-Rampura 230 kV Ckt-3 is restored.
| 20:51 | 22:12 | Patuakhali 132/33kV S/S 405T (T-1) HT Tripped showing O/C relays Due to Khepupara 33kV | [7 empty] | 13.0MW load
|  |  | fault PBS | [7 empty] | interrup.
| 20:51 | 22:13 | Patuakhali 132/33kV S/S 405T (T-1) LT Tripped showing O/C relays Due to 33kV Khepupara | [7 empty] | 13.0MW load
|  |  | PBS Feeder | [7 empty] | interrup.
| 05:00 |  | Min. Gen. 7719 MW
| 05:25 |  | Bheramara 410 MW GT was sync.
| 05:47 |  | Aminbazar-Meghnaghat 400kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing 86-2
master relay operated 86-1 Master relay operated relays.
| 07:24 |  | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance ( Removing Bird's nest from 6No Tower)
| 07:48 | 07:52 | Tangail 132/33kV S/S RPCL-2 Tripped showing REL 670 relays Due to Distance OPTD
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 220 | 4523594 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 405 | 9018000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9237500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 255 | 6819375 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 218128 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2173710 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 388800 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 82 | 1177920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 45 | 210551 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 403040 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 377400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 470160 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 565600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 360480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 46 | 1046304 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1310400 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1032480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 196192 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 440640 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 18000 | -
Dhaka Area Total |  |  |  |  | 5860.564 | 2079 | 40510274
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 140130 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 464640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 967620 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5413752 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 762764 | -
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 338659 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 128945 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 56640 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 585120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 8 | 8640 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 32618 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 222472 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 136320 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 476727 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 31782 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13849089 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 17 | 210720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 155 | 3745454.54 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1421 | 27597893.54
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4635000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8098000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 746064 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 695520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4482909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1168918 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 936727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 68288 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 981490 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1056960 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 52 | 1032000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 387780 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 290640 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 788160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 439927 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1343 | 25808383
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 427200 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 187200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1090800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 254440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 107280 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 328680 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 146.5 | 2406600
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 712000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3682718 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 819576 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 110112 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 723264 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1940160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 20 | 489000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 370848 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7337500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7707100 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 993 | 23892278
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 864 | 21136023 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 575280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1216 | 22887275 | coal available to run both units upto 12/02/25
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2080 | 44598578
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 140726 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 3046000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 14065454.55 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4889530 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 366000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6327000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3834 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1281 | 28838544.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 33 | 37240 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 6 | 14615 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 123266 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4278000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 182 | 4329045 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 393 | 9017672.7 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 119397 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 72360 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 688704 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 705024 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28260 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 744.58 | 16719693 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 323248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 640720 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1747.28 | 37097244.7
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3787000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 37 | 279753 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29137.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 865238 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 159070 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 881280 | -
Rangpur Area Total |  |  |  |  | 950 | 287 | 6001478.68
Eastern Grid Total |  |  |  |  | 16791.042 | 5982.5 | 120215428.54
Western Grid Total |  |  |  |  | 10294.5 | 5395.28 | 116535845.93
National Grid Total |  |  |  |  | 27085.542 | 11377.78 | 236751274.47
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7456.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3411.2 | MW
i) Dhaka area |  |  | 4135.31 |  | MW | i) Khulna area |  |  |  | 1234 | MW
ii) Chattogram area |  |  | 1058.9 |  | MW | ii) Barishal area |  |  |  | 291 | MW
iii) Cumilla area |  |  | 915 |  | MW | iii) Rajshahi area |  |  |  | 1124.2 | MW
iv) Mymensingh area |  |  | 945 |  | MW | iv) Rangpur area |  |  |  | 762 | MW
v) Sylhet area |  |  | 402 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10867.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 64 | 08:00 | 133 | Purbachal | 13 | 13:00
2 | AKSML | 98.1 | 11:00 | 68 | Jamalpur | 90 | 09:00 | 134 | Purbasadipur | 121 | 13:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 104 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 75 | 13:00 | 70 | Jhenaidah | 97 | 08:00 | 136 | Rahim | 32 | 15:00
5 | Agrabad | 64 | 18:00 | 71 | Joydebpur | 125 | 18:00 | 137 | Rajbari | 57 | 18:30
6 | Amnura | 59 | 08:00 | 72 | Joypurhat | 60 | 08:00 | 138 | Rajendrapur | 96 | 09:00
7 | Ashuganj | 70.5 | 00:00 | 73 | Juldah | 14 | 13:00 | 139 | Rajshahi | 68 | 21:00
8 | BSRM | 201 | 03:00 | 74 | KSRM | 30 | 06:00 | 140 | Rajshahi-230 | 75 | 13:00
9 | Bagerhat | 65 | 18:30 | 75 | Kabirpur | 211 | 18:00 | 141 | Ramganj | 94 | 18:30
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 52 | 18:00 | 142 | Rampur | 27 | 18:30
11 | Bakulia | 69 | 18:00 | 77 | Kallyanpur | 75 | 13:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 34 | 13:00 | 78 | Kalurghat | 30 | 13:00 | 144 | Rangpur | 112 | 19:30
13 | Bangabhaban | 9 | 12:00 | 79 | Kamrangirchar | 58.8 | 13:00 | 145 | Ruppur | 5.2 | 16:00
14 | Barapukuria | 63 | 08:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 5 | 00:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 90 | 13:00 | 147 | Saidpur | 103 | 09:00
16 | Barishal | 70 | 13:00 | 82 | Keranigonj | 46 | 00:00 | 148 | Satkhira | 91 | 18:30
17 | Barishal-230 | 72 | 18:30 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 80 | 14:00
18 | Baroaulia | 48 | 11:00 | 84 | Khulna | 71 | 13:00 | 150 | Savar | 174 | 18:00
19 | Baroirhat | 53 | 13:00 | 85 | Khulshi | 143 | 12:00 | 151 | SevenRings | 10.14 | 00:00
20 | Bashundhara | 130 | 18:00 | 86 | Kishoreganj | 122 | 18:00 | 152 | ShahCement | 27 | 00:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 261 | 18:00 | 153 | Shahjadpur | 65 | 18:30
22 | Beanibazar | 44 | 18:30 | 88 | Kulaura | 26 | 18:00 | 154 | Shahjibazar | 99 | 00:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 60 | 08:00 | 155 | Shahmirpur | 48 | 06:00
24 | Bhaluka | 110 | 12:00 | 90 | Kushtia | 108 | 18:30 | 156 | Shariatpur | 51 | 22:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 59 | 12:00 | 157 | Sherpur | 120 | 00:00
26 | Bhangura | 30 | 18:30 | 92 | Lalmonirhat | 52 | 08:00 | 158 | Shikalbaha | 20 | 13:00
27 | Bheramara(GK) | 42 | 18:30 | 93 | MI_Cement | 17.9 | 00:00 | 159 | Shitalakhya | 66.7 | 12:00
28 | Bhulta | 242 | 13:00 | 94 | Madanganj | 21 | 18:30 | 160 | Sholosohor | 31 | 18:00
29 | Bog-Sherpur | 68 | 08:00 | 95 | Madaripur | 68 | 21:00 | 161 | Shyampur | 140 | 03:00
30 | Bogura | 115 | 19:00 | 96 | Madartek | 58.44 | 13:00 | 162 | Siddhirganj | 100 | 09:00
31 | Borhanuddin | 54 | 22:00 | 97 | Madunaghat | 36 | 18:00 | 163 | Sirajganj | 92 | 19:30
32 | Brahmanbaria | 104 | 18:30 | 98 | Magura | 48 | 18:30 | 164 | Sonargaon | 88 | 10:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 60 | 08:00 | 165 | Sreemongol | 55 | 18:30
34 | Chandpur | 45 | 21:00 | 100 | Manikganj | 105 | 19:00 | 166 | Sreepur | 80 | 09:00
35 | Chandraghona | 27 | 18:00 | 101 | Maniknagar | 50 | 13:00 | 167 | Srinagar | 30.36 | 21:00
36 | Chapai | 61 | 13:00 | 102 | Matarbari | 36 | 19:00 | 168 | Sunamganj | 40 | 18:00
37 | Charsaidpur | 42 | 11:00 | 103 | Matuail | 64 | 12:00 | 169 | Sylhet | 34 | 19:00
38 | Chauddagram | 52 | 13:00 | 104 | Millgate | 65 | 12:00 | 170 | Sylhet-132 | 73 | 18:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 98 | 18:30 | 171 | TK | 22 | 18:00
40 | Chowmuhani | 134 | 18:00 | 106 | Mirsorai | 9 | 19:30 | 172 | Tangail | 158 | 13:00
41 | Chuadanga | 71 | 18:30 | 107 | Mirzapur | 36 | 12:00 | 173 | Thakurgaon | 85 | 08:00
42 | Coxsbazar | 110 | 18:30 | 108 | Mithapukur | 54 | 08:00 | 174 | Tongi | 97 | 15:00
43 | Cumilla(N) | 123 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 25 | 18:30
44 | Cumilla(S) | 116 | 18:00 | 110 | Mogbazar | 100.7 | 14:00 | 176 | Ullon | 35 | 13:00
45 | Daudkandi | 107 | 18:30 | 111 | Mongla | 25 | 18:30 | 177 | Uttara | 63 | 18:30
46 | Dhaka | 32 | 13:00 | 112 | Motijheel | 27 | 13:00 | 178 | UttaraNew | 61 | 15:00
47 | Dhamrai | 102 | 18:30 | 113 | Muktagacha | 31 | 12:00 | 179 | Zigatola | 52 | 13:00
48 | Dhanmondi | 100 | 13:00 | 114 | Munshiganj | 65 | 21:00
49 | Dohazari | 65 | 21:00 | 115 | Mymensingh | 177 | 13:00
50 | Faridpur | 110 | 19:00 | 116 | Naogaon | 104 | 08:00
51 | Fatullah | 73 | 12:00 | 117 | Narail | 42 | 18:30
52 | Fenchuganj | 25 | 18:00 | 118 | Narinda | 63 | 13:00
53 | Feni | 74 | 18:00 | 119 | Narshingdi | 157 | 19:30
54 | GPH | 13 | 10:00 | 120 | Natore | 108 | 18:30
55 | Ghatail | 52 | 07:00 | 121 | Nawabganj | 29.4 | 14:00
56 | Ghorashal | 12 | 10:00 | 122 | Netrakona | 140 | 08:00
57 | Ghorashal-230 | 59 | 00:00 | 123 | New | 69 | 12:00
58 | Goalpara | 14 | 08:00 | 124 | Niamatpur | 89 | 08:00
59 | Gollamari | 60 | 13:00 | 125 | Noapara | 36 | 18:30
60 | Gopalganj | 78 | 18:30 | 126 | PHP | 6 | 19:30
61 | Gulshan | 78 | 13:00 | 127 | Pabna | 68 | 18:30
62 | Halishahar | 46 | 10:00 | 128 | Palashbari | 102 | 08:00
63 | HaripurSBU | 173 | 09:00 | 129 | Panchagarh | 45 | 18:30
64 | Hasnabad | 103 | 14:00 | 130 | Patuakhali | 49 | 21:00
65 | Hathazari | 54 | 18:00 | 131 | Payra | 20 | 21:00
66 | Ishurdi | 59 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9238 | 30 |  | 9269.35
1:00 | 8517.5 | 0 |  | 8517.5
2:00 | 8180.5 | 0 |  | 8180.5
3:00 | 7906.5 | 0 |  | 7906.5
4:00 | 7755.5 | 0 |  | 7755.5
5:00 | 7537.5 | 0 |  | 7537.5
6:00 | 7989.5 | 0 |  | 7989.5
7:00 | 8948.77 | 46 |  | 8996.84
8:00 | 9800.75 | 78 |  | 9882.75
9:00 | 10316.21 | 69 |  | 10388.21
10:00 | 10234.63 | 60 |  | 10297.63
11:00 | 10292.22 | 49 |  | 10343.22
12:00 | 10740 | 32 |  | 10773
13:00 | 11017.32 | 45 |  | 11064.32
14:00 | 10729.84 | 32 |  | 10762.84
15:00 | 10357.63 | 17 |  | 10375.4
16:00 | 10009.62 | 0 |  | 10009.62
17:00 | 9986.09 | 17 |  | 10004.09
18:00 | 10752.03 | 73 |  | 10828.03
19:00 | 11377.78 | 42 |  | 11421.78
19:30 | 11086.7 | 42 |  | 11130.7
20:00 | 10860.03 | 40 |  | 10902.03
21:00 | 10716.7 | 20 |  | 10737.7
22:00 | 10382.7 | 0 |  | 10382.7
23:00 | 9733.5 | 0 |  | 9733.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4811.5 | 4426.5 | 9238 | DAILY GENERATION CURVE
00:30 | 4637.25 | 4240.5 | 8877.75
01:00 | 4463 | 4054.5 | 8517.5 | 10-02-2025
01:30 | 4424 | 3925 | 8349
02:00 | 4385 | 3795.5 | 8180.5
02:30 | 4365.5 | 3678 | 8043.5
03:00 | 4346 | 3560.5 | 7906.5
03:30 | 4283.5 | 3547.5 | 7831
04:00 | 4221 | 3534.5 | 7755.5
04:30 | 4195.5 | 3451 | 7646.5
05:00 | 4170 | 3367.5 | 7537.5
05:30 | 4245.5 | 3518 | 7763.5
06:00 | 4321 | 3668.5 | 7989.5
06:30 | 4473.01 | 3996.125 | 8469.135
07:00 | 4625.02 | 4323.75 | 8948.77
07:30 | 4766.035 | 4608.725 | 9374.76
08:00 | 4907.05 | 4893.7 | 9800.75
08:30 | 5075.725 | 4982.755 | 10058.48
09:00 | 5244.4 | 5071.81 | 10316.21
09:30 | 5202.51 | 5072.91 | 10275.42
10:00 | 5160.62 | 5074.01 | 10234.63
10:30 | 5137.24 | 5126.185 | 10263.425
11:00 | 5113.86 | 5178.36 | 10292.22
11:30 | 5203.83 | 5312.28 | 10516.11
12:00 | 5293.8 | 5446.2 | 10740
12:30 | 5379.335 | 5499.325 | 10878.66
13:00 | 5464.87 | 5552.45 | 11017.32
13:30 | 5401.7 | 5471.88 | 10873.58
14:00 | 5338.53 | 5391.31 | 10729.84
14:30 | 5180.37 | 5363.365 | 10543.735
15:00 | 5022.21 | 5335.42 | 10357.63
15:30 | 4925.7 | 5257.925 | 10183.625
16:00 | 4829.19 | 5180.43 | 10009.62
16:30 | 4856.29 | 5141.565 | 9997.855
17:00 | 4883.39 | 5102.7 | 9986.09
17:30 | 5235.195 | 5133.865 | 10369.06
18:00 | 5587 | 5165.03 | 10752.03
18:30 | 5784.75 | 5280.155 | 11064.905
19:00 | 5982.5 | 5395.28 | 11377.78
19:30 | 5710 | 5376.7 | 11086.7
20:00 | 5516.5 | 5343.53 | 10860.03
20:30 | 5447.75 | 5340.615 | 10788.365 |  | Executive Engineer
21:00 | 5379 | 5337.7 | 10716.7 |  | Network Operation Division
21:30 | 5258.5 | 5291.2 | 10549.7
22:00 | 5138 | 5244.7 | 10382.7
22:30 | 4887.5 | 5170.6 | 10058.1
23:00 | 4637 | 5096.5 | 9733.5

## En-Curve
QF-LDC-12
Date | 10-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2721 | 1629.5 | 913 | 0 | 50 | 761 | 40 | 2460 | 0 | 107 | 550.5 | 0 | 0 | 6 | 30 | DAILY ENERGY CURVE
00:30 | 2744.5 | 1648.5 | 913.5 | 0 | 48 | 745 | 40 | 2352.5 | 0 | 70.5 | 308.25 | 0 | 0 | 7 | 15 | 10-02-2025
01:00 | 2768 | 1667.5 | 914 | 0 | 46 | 729 | 40 | 2245 | 0 | 34 | 66 | 0 | 0 | 8 | 0
01:30 | 2794.5 | 1684.5 | 914 | 0 | 46 | 664.5 | 40 | 2130.5 | 0 | 17 | 47 | 0 | 0 | 11 | 0 | Energy Generated | 236.7513 |  | MKWHr
02:00 | 2821 | 1701.5 | 914 | 0 | 46 | 600 | 40 | 2016 | 0 | 0 | 28 | 0 | 0 | 14 | 0 | Energy not Served | 0.65 |  | MKWHr
02:30 | 2823 | 1695 | 822 | 0 | 40 | 581.5 | 40 | 2012.5 | 0 | 0 | 14 | 0 | 0 | 15.5 | 0 | Total Energy Requirement | 237.4013 |  | MKWHr
03:00 | 2825 | 1688.5 | 730 | 0 | 34 | 563 | 40 | 2009 | 0 | 0 | 0 | 0 | 0 | 17 | 0
03:30 | 2756 | 1685 | 725.5 | 0 | 39 | 532 | 40 | 2031.5 | 0 | 0 | 0 | 0 | 0 | 22 | 0
04:00 | 2687 | 1681.5 | 721 | 0 | 44 | 501 | 40 | 2054 | 0 | 0 | 0 | 0 | 0 | 27 | 0
04:30 | 2690.5 | 1698 | 721.5 | 0 | 42 | 483 | 40 | 1950 | 0 | 0 | 0 | 0 | 0 | 21.5 | 0
05:00 | 2694 | 1714.5 | 722 | 0 | 40 | 465 | 40 | 1846 | 0 | 0 | 0 | 0 | 0 | 16 | 0
05:30 | 2772 | 1777 | 722 | 0 | 37 | 466.5 | 40 | 1925.5 | 0 | 0 | 11 | 0 | 0 | 12.5 | 0
06:00 | 2850 | 1839.5 | 722 | 0 | 34 | 468 | 40 | 2005 | 0 | 0 | 22 | 0 | 0 | 9 | 0
06:30 | 2880 | 1839.5 | 816 | 0 | 33 | 507 | 40 | 2245 | 6.635 | 45 | 49 | 0 | 0 | 8 | 23
07:00 | 2910 | 1839.5 | 910 | 0 | 32 | 546 | 40 | 2485 | 13.27 | 90 | 76 | 0 | 0 | 7 | 46
07:30 | 2872 | 1832.5 | 886.5 | 0 | 36 | 652.5 | 40 | 2627 | 70.26 | 119 | 232.5 | 0 | 0 | 6.5 | 62
08:00 | 2834 | 1825.5 | 863 | 0 | 40 | 759 | 40 | 2769 | 127.25 | 148 | 389 | 0 | 0 | 6 | 78
08:30 | 2719.5 | 1852 | 863 | 0 | 42 | 755.5 | 40 | 2780 | 210.48 | 149 | 641.5 | 0 | 0 | 5.5 | 73.5
09:00 | 2605 | 1878.5 | 863 | 0 | 44 | 752 | 40 | 2791 | 293.71 | 150 | 894 | 0 | 0 | 5 | 69
09:30 | 2593 | 1877 | 882 | 0 | 42 | 750.5 | 40 | 2794.5 | 364.92 | 154 | 774 | 0 | 0 | 3.5 | 64.5
10:00 | 2581 | 1875.5 | 901 | 0 | 40 | 749 | 40 | 2798 | 436.13 | 158 | 654 | 0 | 0 | 2 | 60
10:30 | 2576 | 1872 | 904.5 | 0 | 40 | 745.5 | 40 | 2795.5 | 482.925 | 189 | 613 | 0 | 0 | 5 | 54.5
11:00 | 2571 | 1868.5 | 908 | 0 | 40 | 742 | 40 | 2793 | 529.72 | 220 | 572 | 0 | 0 | 8 | 49
11:30 | 2661.5 | 1896.5 | 908.5 | 0 | 44 | 742 | 40 | 2841 | 554.61 | 230 | 590 | 0 | 0 | 8 | 40.5
12:00 | 2752 | 1924.5 | 909 | 0 | 48 | 742 | 40 | 2889 | 579.5 | 240 | 608 | 0 | 0 | 8 | 32
12:30 | 2762 | 1933 | 908.5 | 0 | 48 | 740 | 40 | 2938 | 569.66 | 253.5 | 679.5 | 0 | 0 | 6.5 | 38.5
13:00 | 2772 | 1941.5 | 908 | 0 | 48 | 738 | 40 | 2987 | 559.82 | 267 | 751 | 0 | 0 | 5 | 45
13:30 | 2739 | 1905.6 | 908 | 0 | 49 | 733.905 | 40 | 2935 | 532.075 | 250 | 773.5 | 0 | 0 | 7.5 | 38.5
14:00 | 2706 | 1869.7 | 908 | 0 | 50 | 729.81 | 40 | 2883 | 504.33 | 233 | 796 | 0 | 0 | 10 | 32
14:30 | 2706.5 | 1884.2 | 909 | 0 | 50 | 730.42 | 40 | 2899 | 433.015 | 228.5 | 654.1 | 0 | 0 | 9 | 24.5
15:00 | 2707 | 1898.7 | 910 | 0 | 50 | 731.03 | 40 | 2915 | 361.7 | 224 | 512.2 | 0 | 0 | 8 | 17
15:30 | 2711 | 1894.35 | 910 | 0 | 48 | 712.705 | 40 | 2871 | 284.37 | 236.5 | 465.2 | 0 | 0 | 10.5 | 8.5
16:00 | 2715 | 1890 | 910 | 0 | 46 | 694.38 | 40 | 2827 | 207.04 | 249 | 418.2 | 0 | 0 | 13 | 0
16:30 | 2668.5 | 1899.25 | 910 | 0 | 46 | 678.445 | 40 | 2841.5 | 133.46 | 266 | 502.2 | 0 | 0 | 12.5 | 8.5
17:00 | 2622 | 1908.5 | 910 | 0 | 46 | 662.51 | 40 | 2856 | 59.88 | 283 | 586.2 | 0 | 0 | 12 | 17
17:30 | 2627 | 1867.5 | 910 | 0 | 49 | 687.42 | 40 | 2912 | 29.94 | 401 | 831.7 | 0 | 0 | 13.5 | 45
18:00 | 2632 | 1826.5 | 910 | 0 | 52 | 712.33 | 40 | 2968 | 0 | 519 | 1077.2 | 0 | 0 | 15 | 73
18:30 | 2689 | 1865 | 887 | 0 | 52 | 728.455 | 40 | 2998 | 0 | 554 | 1235.45 | 0 | 0 | 16 | 57.5
19:00 | 2746 | 1903.5 | 864 | 0 | 52 | 744.58 | 40 | 3028 | 0 | 589 | 1393.7 | 0 | 0 | 17 | 42
19:30 | 2747 | 1905.5 | 863 | 0 | 52 | 751 | 40 | 3046 | 0 | 394 | 1275.2 | 0 | 0 | 13 | 42
20:00 | 2757 | 1940 | 863 | 0 | 44 | 754.83 | 40 | 3052 | 0 | 357 | 1046.2 | 0 | 0 | 6 | 40
20:30 | 2759.5 | 1955.75 | 888 | 0 | 45 | 755.415 | 40 | 3049 | 0 | 331.5 | 961.2 | 0 | 0 | 3 | 30
21:00 | 2762 | 1971.5 | 913 | 0 | 46 | 756 | 40 | 3046 | 0 | 306 | 876.2 | 0 | 0 | 0 | 20
21:30 | 2756.5 | 1962 | 913 | 0 | 48 | 757 | 40 | 3042.5 | 0 | 257 | 773.7 | 0 | 0 | 0 | 10
22:00 | 2751 | 1952.5 | 913 | 0 | 50 | 758 | 40 | 3039 | 0 | 208 | 671.2 | 0 | 0 | 0 | 0
22:30 | 2754.5 | 1934.5 | 913 | 0 | 48 | 756.5 | 40 | 3040.5 | 0 | 164 | 407.1 | 0 | 0 | 0 | 0
23:00 | 2758 | 1916.5 | 913 | 0 | 46 | 755 | 40 | 3042 | 0 | 120 | 143 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 413 | 05:00 | 390 | 12:00 | Payra | 421 | 04:00 | 410 | 12:00
Ashuganj | 413 | 3:00 | 390 | 16:00 | Rahanpur | 419 | 04:00 | 400 | 12:00
Bhulta | 413 | 04:00 | 389 | 12:00 | Rampal | 412 | 05:00 | 393 | 13:00
Bibiana | 417 | 03:00 | 404 | 12:00
BIPTC | 405 | 03:00 | 388 | 10:00
Bogura | 417 | 04:00 | 392 | 08:00
Gopalganj | 415 | 04:00 | 397 | 12:00
Kaliakoir | 404 | 05:00 | 387 | 16:00
Madunaghat | 409 | 05:00 | 398 | 13:00
Meghnaghat | 409 | 04:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 04:00 | 225 | 12:00 | Keranigonj | 237 | 04:00 | 224 | 12:00
AKSML | 236 | 05:00 | 225 | 12:00 | Khulna(S) | 241 | 04:00 | 226 | 13:00
Aminbazar | 237 | 01:00 | 225 | 12:00 | Madunaghat | 235 | 00:00 | 228 | 12:00
Ashuganj | 246 | 03:00 | 233 | 16:00 | Madunaghat-400 | 235 | 05:00 | 228 | 13:00
Ashuganj-400 | 246 | 03:00 | 233 | 16:00 | Maniknagar | 237 | 04:00 | 223 | 12:00
Baghabari | 241 | 04:00 | 228 | 12:00 | Meghnaghat | 243 | 03:00 | 232 | 16:00
Barapukuria | 227 | 00:00 | 217 | 07:00 | Meghnaghat-400 | 240 | 04:00 | 228 | 12:00
Barapukuria-230 | 227 | 00:00 | 217 | 07:00 | Mirsorai | 236 | 00:00 | 226 | 15:00
Barishal | 246 | 02:00 | 237 | 12:00 | Rajshahi | 241 | 04:00 | 224 | 08:00
Bheramara | 240 | 04:00 | 222 | 12:00 | Rampal | 239 | 04:00 | 224 | 13:00
Bhulta | 240 | 05:00 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 241 | 00:00 | 231 | 15:00 | Rampura | 239 | 04:00 | 223 | 12:00
BIPTC | 242 | 04:00 | 225 | 12:00 | Shikalbaha | 236 | 23:00 | 226 | 15:00
Bogura | 242 | 04:00 | 227 | 08:00 | Shyampur | 238 | 04:00 | 225 | 12:00
Bogura-400 | 241 | 04:00 | 225 | 08:00 | Siddhirganj | 239 | 00:00 | 226 | 12:00
Borhanuddin | 248 | 01:00 | 244 | 12:00 | Sirajgonj | 246 | 03:00 | 238 | 08:00
BSRM | 237 | 05:00 | 226 | 16:00 | Sreepur | 241 | 04:00 | 232 | 17:00
Cumilla(N) | 237 | 00:00 | 227 | 12:00 | Tongi | 235 | 04:00 | 222 | 17:00
Faridpur | 246 | 03:00 | 235 | 12:00
Fenchuganj | 242 | 01:00 | 235 | 15:00
Ghorashal | 240 | 00:00 | 230 | 15:00
Ghorashal-230 | 238 | 04:00 | 226 | 12:00
Gopalganj | 246 | 04:00 | 234 | 12:00
GPH | 235 | 00:00 | 227 | 15:00
Haripur | 238 | 00:00 | 226 | 12:00
Hasnabad | 235 | 01:00 | 224 | 12:00
Hathazari | 237 | 02:00 | 228 | 12:00
Ishurdi | 242 | 04:00 | 226 | 12:00
Jhenaidah | 240 | 04:00 | 222 | 12:00
Kaliakoir | 236 | 05:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 125 | 12:00 | Magura | 139 | 02:00 | 127 | 12:00
Agargaon | 138 | 00:00 | 130 | 12:00 | Mahasthangarh | 137 | 04:00 | 124 | 08:00
Agrabad | 135 | 00:00 | 129 | 12:00 | Manikganj | 138 | 00:00 | 134 | 16:00
AKS | 134 | 00:00 | 128 | 12:00 | Maniknagar | 136 | 03:00 | 10 | 07:00
Aminbazar | 137 | 01:00 | 129 | 12:00 | Matarbari | 126 | 00:00 | 121 | 13:00
Amnura | 139 | 03:00 | 127 | 08:00 | Matuail | 136 | 00:00 | 129 | 12:00
Ashuganj | 142 | 05:00 | 138 | 12:00 | Millgate | 138 | 02:00 | 128 | 12:00
Bagerhat | 138 | 04:00 | 126 | 12:00 | Mirpur | 137 | 03:00 | 129 | 12:00
Bajitpur | 137 | 00:00 | 131 | 11:00 | Mirzapur | 137 | 00:00 | 130 | 16:00
Bakulia | 134 | 00:00 | 130 | 12:00 | Mithapukur | 135 | 05:00 | 118 | 08:00
Banani | 136 | 03:00 | 124 | 13:00 | MI_Cement | 137.5 | 06:00 | 130 | 12:00
Bangabhaban | 135 | 00:00 | 126 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 00:00 | 127 | 07:00 | Mogbazar | 137 | 04:00 | 125 | 13:00
Barguna | 139 | 00:00 | 135 | 12:00 | Mongla | 136 | 00:00 | 127 | 12:00
Barishal | 136 | 02:00 | 130 | 12:00 | Motijheel | 135 | 00:00 | 126 | 12:00
Barishal-230 | 137 | 02:00 | 131 | 12:00 | Muktagacha | 129 | 00:00 | 117 | 07:00
Baroaulia | 135 | 18:30 | 132 | 00:00 | Munshiganj | 137 | 04:00 | 129 | 12:00
Baroirhat | 134 | 00:00 | 126 | 16:00 | Muradnagar | 138 | 4:00 | 131 | 17:00
Bashundhara | 136 | 00:00 | 123 | 12:00 | Mymensingh | 129 | 00:00 | 117 | 13:00
BashundharaCement | 136 | 00:00 | 128 | 12:00 | Naogaon | 136 | 04:00 | 122 | 08:00
Beanibazar | 137 | 04:00 | 131 | 16:00 | Narail | 140 | 03:00 | 126 | 12:00
Benapole | 138 | 03:00 | 123 | 12:00 | Narinda | 136 | 3:00 | 126 | 12:00
Bhaluka | 129 | 00:00 | 121 | 12:00 | Narshingdi | 135 | 06:00 | 124 | 12:00
Bhandaria | 135 | 06:00 | 127 | 12:00 | Natore | 138 | 00:00 | 128 | 08:00
Bhangura | 140 | 04:00 | 129 | 12:00 | Nawabganj | 139 | 00:00 | 131 | 12:00
Bheramara | 139 | 04:00 | 128 | 12:00 | Netrakona | 126 | 00:00 | 114 | 07:00
Bheramara(GK) | 138 | 03:00 | 129 | 08:00 | New | 138 | 03:00 | 128 | 15:00
Bhulta | 132 | 01:00 | 123 | 12:00 | Niamatpur | 141 | 03:00 | 130 | 07:00
Bog-Sherpur | 138 | 04:00 | 126 | 08:00 | Noapara | 140 | 03:00 | 127 | 12:00
Bogura | 137 | 00:00 | 126 | 08:00 | Pabna | 138 | 04:00 | 125 | 12:00
Bogura-230 | 138 | 03:00 | 127 | 08:00 | Palashbari | 133 | 02:00 | 119 | 12:00
Brahmanbaria | 139 | 05:00 | 132 | 12:00 | Panchagarh | 139 | 19:30 | 120 | 07:00
Cantonment | 138 | 02:00 | 130 | 12:00 | Patuakhali | 138 | 19:30 | 134 | 12:00
Chandpur | 139 | 09:00 | 126 | 15:00 | Payra | 138 | 00:00 | 135 | 12:00
Chandraghona | 138 | 19:30 | 131 | 12:00 | PHP | 133 | 00:00 | 125 | 13:00
Chapai | 139 | 04:00 | 130 | 12:00 | Postogola | 140 | 00:00 | 132 | 12:00
Charsaidpur | 138 | 03:00 | 129 | 12:00 | Purbachal | 136 | 02:00 | 123 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 00:00 | 126 | 15:00 | Purbasadipur | 134 | 19:30 | 118 | 07:00
Chhatak | 137 | 01:00 | 130 | 13:00 | Rahanpur | 141 | 02:00 | 133 | 07:00
Chowmuhani | 133 | 00:00 | 125 | 12:00 | Rahanpur-400 | 142 | 04:00 | 135 | 08:00
Chuadanga | 140 | 05:00 | 124 | 12:00 | Rahim | 136 | 04:00 | 128 | 12:00
Coxsbazar | 126 | 03:00 | 120 | 11:00 | Rajbari | 136 | 02:00 | 129 | 13:00
Cumilla(N) | 139 | 00:00 | 131 | 15:00 | Rajendrapur | 138 | 13:00 | 131 | 15:00
Cumilla(S) | 137 | 00:00 | 129 | 12:00 | Rajshahi | 138 | 00:00 | 130 | 07:00
Daudkandi | 135 | 00:00 | 125 | 12:00 | Rajshahi-230 | 139 | 04:00 | 124 | 12:00
Dhaka | 135 | 00:00 | 125 | 12:00 | Ramganj | 135 | 00:00 | 124 | 15:00
Dhamrai | 136 | 03:00 | 127 | 15:00 | Rampur | 135 | 00:00 | 129 | 12:00
Dhanmondi | 138 | 04:00 | 129 | 12:00 | Rampura | 136 | 04:00 | 125 | 12:00
Dohazari | 133 | 00:00 | 127 | 11:00 | Rangamati | 135 | 00:00 | 130 | 12:00
Faridpur | 136 | 03:00 | 130 | 13:00 | Rangpur | 132 | 01:00 | 117 | 08:00
Fatullah | 139 | 04:00 | 131 | 12:00 | Ruppur | 141 | 03:00 | 132 | 08:00
Fenchuganj | 141 | 01:00 | 136 | 15:00 | Saidpur | 134 | 00:00 | 120 | 07:00
Feni | 133 | 00:00 | 123 | 01:00 | Satkhira | 139 | 04:00 | 126 | 12:00
Ghatail | 130 | 00:00 | 120 | 07:00 | Satmasjid | 138 | 03:00 | 129 | 13:00
Ghorashal | 142 | 00:00 | 137 | 15:00 | Savar | 136 | 18:00 | 128 | 12:00
Goalpara | 139 | 02:00 | 129 | 12:00 | SevenRings | 144 | 04:00 | 137 | 15:00
Gollamari | 139 | 03:00 | 129 | 12:00 | ShahCement | 138 | 03:00 | 129 | 12:00
Gopalganj | 138 | 04:00 | 130 | 12:00 | Shahjadpur | 141 | 04:00 | 133 | 07:00
Gopalganj-400 | 138 | 03:00 | 131 | 12:00 | Shahjibazar | 141 | 06:00 | 134 | 15:00
Gulshan | 134 | 00:00 | 125 | 12:00 | Shahmirpur | 135 | 18:00 | 130 | 11:00
Halishahar | 136 | 02:00 | 132 | 10:00 | Shariatpur | 138 | 03:00 | 131 | 12:00
Haripur | 136 | 00:00 | 129 | 12:00 | Sherpur | 124 | 00:00 | 114 | 08:00
HaripurSBU | 136 | 00:00 | 129 | 12:00 | Shikalbaha | 125 | 05:00 | 119 | 11:00
Hasnabad | 139 | 00:00 | 132 | 12:00 | Shikalbaha-230 | 136 | 18:00 | 130 | 11:00
Hathazari | 137 | 18:30 | 132 | 15:00 | Shitalakhya | 137.5 | 06:00 | 130 | 12:00
Ishurdi | 142 | 03:00 | 132 | 08:00 | Sholosohor | 135 | 00:00 | 130 | 12:00
Jaldhaka | 134 | 03:00 | 118 | 07:00 | Shyampur | 136 | 01:00 | 130 | 16:00
Jamalpur | 127 | 00:00 | 116 | 08:00 | Shyampur-230 | 139 | 00:00 | 131 | 12:00
Jashore | 138 | 02:00 | 125 | 12:00 | Siddhirganj | 137 | 00:00 | 129 | 12:00
Jhenaidah | 139 | 00:00 | 128 | 12:00 | Sirajganj | 138 | 03:00 | 126 | 08:00
Jhenaidah-230 | 141 | 04:00 | 129 | 12:00 | Sonargaon | 136 | 00:00 | 127 | 12:00
Joydebpur | 140 | 10:00 | 133 | 16:00 | Sreemongol | 140 | 03:00 | 133 | 12:00
Joypurhat | 135 | 02:00 | 119 | 08:00 | Sreepur | 131 | 05:00 | 124 | 14:00
Juldah | 136 | 18:00 | 130 | 12:00 | Srinagar | 139 | 02:00 | 131 | 12:00
Kabirpur | 142 | 22:00 | 126 | 16:00 | SSM | 138 | 18:00 | 130 | 22:00
Kachua | 138 | 19:00 | 127 | 16:00 | Sunamganj | 138 | 04:00 | 129 | 13:00
Kaliakoir | 143 | 00:00 | 128 | 12:00 | Sylhet | 139 | 04:00 | 132 | 12:00
Kallyanpur | 135 | 02:00 | 127 | 12:00 | Sylhet-132 | 140 | 03:00 | 132 | 12:00
Kalurghat | 135 | 00:00 | 131 | 12:00 | Tangail | 132 | 00:00 | 125 | 07:00
Kamrangirchar | 139 | 00:00 | 126 | 12:00 | Thakurgaon | 138 | 19:30 | 118 | 07:00
Kaptai | 137 | 1:00 | 133 | 17:00 | TK | 136 | 18:00 | 130 | 12:00
Kazla | 136 | 05:00 | 124 | 13:00 | Tongi | 139 | 04:00 | 130 | 15:00
Keranigonj | 138 | 00:00 | 130 | 12:00 | Ullahpara | 138 | 00:00 | 128 | 08:00
Khagrachori | 135 | 04:00 | 129 | 12:00 | Ullon | 134 | 00:00 | 125 | 12:00
Khulna | 138 | 04:00 | 127 | 12:00 | Uttara | 137 | 04:00 | 36 | 05:00
Khulna(S) | 140 | 04:00 | 130 | 12:00 | UttaraNew | 137 | 00:00 | 128 | 12:00
Khulshi | 134 | 00:00 | 128 | 11:00 | Zigatola | 140 | 05:00 | 132 | 12:00
Kishoreganj | 133 | 00:00 | 125 | 08:00
Kodda | 140 | 00:00 | 133 | 14:00
KSRM | 138 | 00:00 | 130 | 12:00
Kulaura | 140 | 00:00 | 135 | 15:00
Kurigram | 132 | 19:30 | 117 | 08:00
Kushtia | 139 | 02:00 | 128 | 12:00
Lalbag | 136 | 19:00 | 131 | 12:00
Lalmonirhat | 132 | 19:30 | 120 | 17:00
Madanganj | 136 | 00:00 | 128 | 12:00
Madaripur | 136 | 03:00 | 131 | 12:00
Madartek | 136 | 04:00 | 126 | 12:00
Madunaghat | 135 | 05:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division