## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10976.64 | MW | 12:00 Hr. | Energy Generated |  |  | 238.3355 |  | MKWHr.
| Day Peak Demand |  |  | 11063.64 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.127 |  | MKWHr.
| Evening Peak Generation |  |  | 11537.07 | MW | 19:00 Hr. | Energy Demand |  |  | 239.4625 |  | MKWHr.
| Evening Peak Demand |  |  | 11652.07 | MW | 19:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 7719.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 807.58 |  | MMCFD
| Maximum Generation of the Day |  |  | 11537.07 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.5236 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.0654 | 0 | 7.0244 | 0 | 0 | 0.1731 | 0 | 0 | 40.263 | Gas | 106.0246 | Gas | 390067645.485
| Chattogram Zone |  |  | 5.7824 | 18.2473 | 4.7088 | 0 | 0.95904 | 0.14453 | 0 | 0.012 | 29.854 | Coal | 66.7664 | Coal | 491431678.8585
| Cumilla Zone |  |  | 16.9646 | 0 | 5.037 | 0 | 0 | 0.35524 | 1.0637 | 0 | 23.4205 | HFO | 23.5223 | HFO | 430975591.84
| Mymensingh Zone |  |  | 0.35808 | 0 | 1.8964 | 0 | 0 | 0.18581 | 0 | 0 | 2.4402 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.1673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1673 | Hydro | 0.95904 | Hydro | 95904
| Khulna Zone |  |  | 1.1508 | 24.5745 | 0 | 0 | 0 | 0.45288 | 21.1927 | 0 | 47.371 | Solar | 3.3101 | Solar | 51309361.306
| Barishal Zone |  |  | 8.0293 | 20.1645 | 0.2664 | 0 | 0 | 0.003277 | 0 | 0 | 28.4636 | Import | 37.7412 | Import | 190735246.61
| Rajshahi Zone |  |  | 16.5066 | 0 | 2.1613 | 0 | 0 | 0.94156 | 15.4848 | 0 | 35.0942 | Wind | 0.012 | Wind | 187200
| Rangpur Zone |  |  | 0 | 3.78 | 2.428 | 0 | 0 | 1.0537 | 0 | 0 | 7.2617
| Total |  |  | 106.0246 | 66.7664 | 23.5223 | 0 | 0.95904 | 3.3101 | 37.7412 | 0.012 | 238.3355
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 390067645.485 |  | Hydro | 95904
|  |  |  | Coal | 491431678.8585 |  | Solar | 51309361.306
|  |  |  | HFO | 430975591.84 |  | Import | 190735246.61
|  |  |  | HSD | 0 |  | Wind | 187200
[5 empty] | Total: | 155,48,02,628 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1927 | Peak Hr Flow | 868.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10114690.995 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.4848 | Peak Hr Flow | 759.87 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 552 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0637 | Peak Hr Flow | 48.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 870 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.7412 | Peak Hr Flow | 1675.87 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 25 |  | 4171
|  |  |  | Chattogram |  | 0 |  | 1124
|  |  |  | Cumilla |  | 0 |  | 938
|  |  |  | Mymensingh |  | 85 |  | 986
|  |  |  | Sylhet |  | 0 |  | 404
|  |  |  | Khulna |  | 0 |  | 1286
|  |  |  | Barishal |  | 0 |  | 315
|  |  |  | Rajshahi |  | 0 |  | 1118
|  |  |  | Rangpur |  | 0 |  | 780
|  |  |  | Total |  | 110 |  | 11122
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:08 | 13:43 | Rangpur-Saidpur 132kV Ckt-2 Project Work S/D from Saidpur 132/33kV end. and from Rangpur
132/33kV end Due to G to G Project
| 08:12 | 17:52 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D
| 08:12 | 17:52 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D
| 08:13 | 17:52 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Project Work S/D Due to Tower Painting
| 08:13 | 17:52 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Project Work S/D Due to Tower Painting
| 08:16 | 17:53 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Tower Painting
| 08:17 | 17:53 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Tower Painting
| 08:19 | 14:44 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D
| 08:20 | 14:44 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D
| 08:20 | 16:57 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance
| 08:25 | 16:49 | Gopalganj-Madhumati 132kV Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to Yearly
Maintenance
| 08:27 | 14:30 | Chapai 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to T2 Transformer main tank oil
leakage maintenance
| 08:27 | 14:32 | Chapai 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to T 2 maintenance
| 08:29 | 16:58 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
Works at Fenchuganj end. and from Fenchuganj 230/132/33kV end Due to Deadline checking
| 08:30 | 17:23 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance B-Baria SS end
| 08:34 | 16:33 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to Annual
maintenance work and from Kachua 132/33kV end Due to Annual maintenance work
| 08:35 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 08:52 | 15:46 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
Maintenance
| 08:55 | 16:09 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Project Work S/D
| 08:56 | 15:25 | Anowara-Sikalbaha 230 kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end.
| 08:57 | 17:54 | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Dead
Line Checking
| 09:34 | 12:58 | Sirajganj 132/33kV S/S Solar Park 1 Project Work S/D Due to RTU & SCADA Commissioning
work.
| 09:40 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Project Work S/D from Kishoreganj 132/33kV end Due to
Shifting to New Control Room and from Mymensingh 132/33kV end Due to NLDC reporting desk
-2
| 09:53 | 10:24 | Bhaluka 132/33kV S/S Bus A Project Work S/D Due to TR-3 project work jumpering.
|  | 10:01 | Aminbazar-Airport(Old) 230kV Ckt-2 is restored.
| 10:01 | 15:26 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 HT Scheduled S/D Due to 132 kv & 33kv
Energy meter testing. 33 kv TR-1 multifunction meter change.
| 10:01 | 15:26 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 LT Scheduled S/D Due to 132kv & 33kv
energy meter testing. 33 kv TR-1 MFM change.
| 10:02 | 19:01 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance
| 10:38 |  | Bhaluka 132/33kV S/S Bus B Project Work S/D Due to TR-3 project work jumpering
| 10:42 | 13:45 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Relay
Testing Work
| 10:46 | 20:08 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work
| 11:00 | 12:47 | Bhandaria 132/33kV S/S Transformer-2 LT Project Work S/D
| 11:01 | 12:46 | Bhandaria 132/33kV S/S Transformer-2 HT Project Work S/D
|  | 11:17 | Sylhet 132/33kV S/S 75 MW ST PS is restored.
| 11:37 | 12:12 | Meghnaghat 400/230kV S/S Meghnaghat-Reliance PP 400KV Ckt-1 Scheduled S/D Due to Testing
for SAS operation
| 11:59 | 12:00 | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Relay
Testing Work by SPMD
| 12:20 | 12:58 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Pt checking by pdb
| 12:26 | 13:35 | Meghnaghat 400/230kV S/S Meghnaghat-Reliance PP 400KV Ckt-2 Scheduled S/D Due to Testing
of SAS operation
| 12:49 | 19:47 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end.
| 13:12 | 17:25 | Sirajganj 132/33kV S/S Solar Park 2 Project Work S/D Due to RTU & SCADA Commissioning
work.
| 15:20 |  | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 Project Work S/D Due to Meter Testing
Purpose
| 15:58 | 16:50 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 LT Scheduled S/D Due to 132 kv & 33kv
energy meter testing. 33kv TR-1 & TR-2 side magnetic contact change in PT CKT.
| 15:58 | 16:50 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 HT Scheduled S/D Due to 132 kv & 33kv
energy meter testing. 33kv TR-1 & TR-2 side magnetic contact change in PT CKT.
| 17:11 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown with remarks:- ST
| 17:11 |  | Sirajgonj 225MW CCPP Unit-3 ST Shutdown with remarks:- As per instruction of NLDC
| 17:23 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown with remarks:- GT
| 17:23 |  | Sirajgonj 225MW CCPP Unit-3 GT Shutdown with remarks:- As per instruction of NLDC
| 17:24 |  | Sirajgonj 225MW CCPP Unit-3 ST Ready with remarks:- None
| 17:24 |  | Sirajgonj 225MW CCPP Unit-3 GT Ready with remarks:- None
| 19:00 |  | Evening peak Generation is 11535 MW
| 19:47 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
|  | 20:08 | Aminbazar-Meghnaghat 400kV Ckt-1 is restored.
|  | 22:00 | Tongi 230/132/33kV S/S T-01 HT is restored.
|  | 22:05 | Tongi 230/132/33kV S/S T-01 LT is restored.
| 22:50 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- Unit-1
| 22:50 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U1
| 22:50 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U1
| 22:50 |  | Rampal 1320 MW (BIFPCL) Unit-1 was shutdown due to coal shortage.
| 22:51 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-1
| 22:51 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-2
| 01:38 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing Dist.
Relay relays Due to General trip
| 02:29 |  | Aminbazar-Meghnaghat 400kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing 67
relays Due to Dist.Relay
| 02:40 |  | Aminbazar-Meghnaghat 400kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing 86
relays Due to Dist zoon -1
| 04:55 | 05:14 | Bogura-Sirajganj 230 kV Ckt-1 Tripped from Bogura 230/132kV end showing (Relay REL-316*4)
Z1 DIST. TRIP, PHASE L1 FAULT, EARTH FAULT, AR BLOCKED, PERMT CLOSE, (Relay REL-521)
Z1 DIST.PROT. TRIP, PHASE L1 FAULT, EARTH FAULT relays.
| 05:00 |  | Minimum Generation: 7813 MW.
| 05:32 |  | Ashuganj South 360MW ST was sync.
| 05:32 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 06:59 |  | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Dead line
check and from Bhulta 400/230kVend.
| 07:35 |  | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D
| 07:35 |  | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D
| 07:59 |  | Mirzapur 132/33kV S/S Transformer-01(E05) LT Tripped showing OC,EF relays Due to 33 Kv | [7 empty] | 25.0MW load
|  |  | Jamurki PBS feeder fult | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 5492937 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9320400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9406500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 266 | 6967244 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 518826 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 388800 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 818400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 397244 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 402453 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.5 | 409200 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527760 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 498600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 442800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 82 | 1441584 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1048320 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1195200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 173103 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 630000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 26 | 183600 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2061.5 | 40262971
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134190 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 397920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 959040 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5333592 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1194327 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 82 | 676176 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 400364 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 254400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 448800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 36480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 10340 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 52691 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 46 | 559525 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 304320 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 563291 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 90 | 269309 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13287271 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 1 | 12000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 273 | 4960000 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1767 | 29854036
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4794000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 3644000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 688032 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 694080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 187 | 4432727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1187394 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 134 | 1883490 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 40 | 44048 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1111060 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 1972320 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1063680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 413340 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 292320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 844800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 355245 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1047 | 23420536
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 358080 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 199200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1088400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 175310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 115920 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 492840 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 127 | 2440250
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 715000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3639436 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 810504 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 110448 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 712128 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1851840 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 452000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 447816 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7561500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 7866600 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1081 | 24167272
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 868 | 21192727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 100 | 1150848 | Commissioning work is in progress
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 452880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1258 | 24574550 | coal available to run both units upto 12/02/25
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2226 | 47371005
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 143688 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 134 | 2817000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 13902545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5068650 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 266400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6262000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3277 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1275 | 28463560.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 33 | 206995 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 111986 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 149 | 3999909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 2592155 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9828945.5 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 182563 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 85554 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 549389 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 891820 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 33 | 109632 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 108960 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 759.87 | 15484773 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 291000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 625540 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1599.57 | 35094241.5
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 153 | 3780000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1088620 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20930.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1339342 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 121959 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 910800 | -
Rangpur Area Total |  |  |  |  | 950 | 353 | 7261651.76
Eastern Grid Total |  |  |  |  | 16856.242 | 6083.5 | 120145065
Western Grid Total |  |  |  |  | 10294.5 | 5453.57 | 118190458.71
National Grid Total |  |  |  |  | 27150.742 | 11537.07 | 238335523.71
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7513.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3498.7 | MW
i) Dhaka area |  |  | 4145.74 |  | MW | i) Khulna area |  |  |  | 1285.9 | MW
ii) Chattogram area |  |  | 1124.4 |  | MW | ii) Barishal area |  |  |  | 314.6 | MW
iii) Cumilla area |  |  | 938 |  | MW | iii) Rajshahi area |  |  |  | 1118.2 | MW
iv) Mymensingh area |  |  | 901 |  | MW | iv) Rangpur area |  |  |  | 780 | MW
v) Sylhet area |  |  | 404 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11011.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 09:00 | 133 | Postogola | 44 | 13:00
2 | AKSML | 24.9 | 18:00 | 68 | Jamalpur | 87 | 07:00 | 134 | Purbachal | 14 | 13:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 114 | 13:00 | 135 | Purbasadipur | 122 | 12:00
4 | Agargaon | 77 | 13:00 | 70 | Jhenaidah | 98 | 08:00 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 70 | 18:00 | 71 | Joydebpur | 139 | 19:00 | 137 | Rahim | 30 | 18:00
6 | Amnura | 50 | 13:00 | 72 | Joypurhat | 60 | 08:00 | 138 | Rajbari | 56 | 18:30
7 | Ashuganj | 79 | 10:00 | 73 | Juldah | 11 | 23:00 | 139 | Rajendrapur | 112 | 13:00
8 | BSRM | 201 | 12:00 | 74 | KSRM | 34 | 07:00 | 140 | Rajshahi | 68 | 20:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 215 | 21:00 | 141 | Rajshahi-230 | 76 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 55 | 18:30 | 142 | Ramganj | 94 | 18:30
11 | Bakulia | 71 | 18:00 | 77 | Kallyanpur | 66 | 10:00 | 143 | Rampur | 28 | 18:30
12 | Banani | 34 | 12:00 | 78 | Kalurghat | 32 | 12:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 10 | 15:00 | 79 | Kamrangirchar | 58.66 | 19:00 | 145 | Rangpur | 112 | 19:00
14 | Barapukuria | 60 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 5.4 | 15:00
15 | Barguna | 12 | 00:00 | 81 | Kazla | 91 | 19:30 | 147 | SSM | 10 | 00:00
16 | Barishal | 89 | 14:00 | 82 | Keranigonj | 58 | 21:00 | 148 | Saidpur | 106 | 10:00
17 | Barishal-230 | 68 | 18:30 | 83 | Khagrachori | 24 | 18:00 | 149 | Satkhira | 96 | 19:00
18 | Baroaulia | 52 | 11:00 | 84 | Khulna | 74 | 13:00 | 150 | Satmasjid | 81 | 13:00
19 | Baroirhat | 49 | 18:30 | 85 | Khulshi | 147 | 18:30 | 151 | Savar | 182 | 16:00
20 | Bashundhara | 149 | 13:00 | 86 | Kishoreganj | 114 | 09:00 | 152 | SevenRings | 6.25 | 11:00
21 | BashundharaCement | 12 | 12:00 | 87 | Kodda | 200 | 00:00 | 153 | ShahCement | 37 | 23:00
22 | Beanibazar | 44 | 18:30 | 88 | Kulaura | 28 | 18:30 | 154 | Shahjadpur | 65 | 18:30
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 59 | 18:00 | 155 | Shahjibazar | 112 | 18:30
24 | Bhaluka | 114 | 12:00 | 90 | Kushtia | 112 | 18:30 | 156 | Shahmirpur | 48 | 09:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 62 | 13:00 | 157 | Shariatpur | 54 | 21:00
26 | Bhangura | 31 | 18:30 | 92 | Lalmonirhat | 50 | 08:00 | 158 | Sherpur | 116 | 00:00
27 | Bheramara(GK) | 42 | 18:30 | 93 | MI_Cement | 17.5 | 11:00 | 159 | Shikalbaha | 16 | 18:00
28 | Bhulta | 274 | 17:00 | 94 | Madanganj | 23 | 18:00 | 160 | Shitalakhya | 66.2 | 12:00
29 | Bog-Sherpur | 68 | 18:30 | 95 | Madaripur | 71 | 19:30 | 161 | Sholosohor | 32 | 17:00
30 | Bogura | 114 | 13:00 | 96 | Madartek | 63.03 | 18:30 | 162 | Shyampur | 144 | 11:00
31 | Borhanuddin | 53 | 20:00 | 97 | Madunaghat | 35 | 18:00 | 163 | Siddhirganj | 104 | 09:00
32 | Brahmanbaria | 106 | 21:00 | 98 | Magura | 48 | 18:30 | 164 | Sirajganj | 96 | 19:00
33 | Cantonment | 98 | 14:00 | 99 | Mahasthangarh | 60 | 08:00 | 165 | Sonargaon | 94 | 18:30
34 | Chandpur | 46 | 19:30 | 100 | Manikganj | 109 | 19:00 | 166 | Sreemongol | 46 | 18:00
35 | Chandraghona | 25 | 18:30 | 101 | Maniknagar | 56 | 13:00 | 167 | Sreepur | 82 | 18:00
36 | Chapai | 73 | 13:00 | 102 | Matarbari | 35 | 18:00 | 168 | Srinagar | 30.6 | 21:00
37 | Charsaidpur | 41 | 10:00 | 103 | Matuail | 61 | 12:00 | 169 | Sunamganj | 40 | 18:00
38 | Chauddagram | 44 | 18:00 | 104 | Millgate | 70 | 15:00 | 170 | Sylhet | 28 | 00:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 111 | 14:00 | 171 | Sylhet-132 | 81 | 14:00
40 | Chowmuhani | 142 | 18:30 | 106 | Mirsorai | 9 | 18:30 | 172 | TK | 22 | 18:00
41 | Chuadanga | 74 | 18:30 | 107 | Mirzapur | 38 | 07:00 | 173 | Tangail | 156 | 07:00
42 | Coxsbazar | 112 | 18:30 | 108 | Mithapukur | 52 | 08:00 | 174 | Thakurgaon | 82 | 19:00
43 | Cumilla(N) | 129 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 90 | 18:30
44 | Cumilla(S) | 122 | 13:00 | 110 | Mogbazar | 99.5 | 14:00 | 176 | Ullahpara | 25 | 08:00
45 | Daudkandi | 93 | 18:30 | 111 | Mongla | 41 | 18:00 | 177 | Ullon | 38 | 14:00
46 | Dhaka | 32 | 13:00 | 112 | Motijheel | 30 | 13:00 | 178 | Uttara | 72 | 13:00
47 | Dhamrai | 106 | 09:00 | 113 | Muktagacha | 28 | 11:00 | 179 | UttaraNew | 48 | 08:00
48 | Dhanmondi | 89 | 13:00 | 114 | Munshiganj | 68 | 20:00 | 180 | Zigatola | 68 | 19:00
49 | Dohazari | 71 | 18:30 | 115 | Muradnagar | N/A | N/A
50 | Faridpur | 109 | 20:00 | 116 | Mymensingh | 168 | 13:00
51 | Fatullah | 73 | 12:00 | 117 | Naogaon | 118 | 13:00
52 | Fenchuganj | 29 | 18:00 | 118 | Narail | 43 | 19:00
53 | Feni | 76 | 13:00 | 119 | Narinda | 63 | 13:00
54 | GPH | 9 | 01:00 | 120 | Narshingdi | 158 | 18:30
55 | Ghatail | 54 | 07:00 | 121 | Natore | 108 | 19:30
56 | Ghorashal | 12 | 19:30 | 122 | Nawabganj | 31.4 | 14:00
57 | Ghorashal-230 | 55 | 08:00 | 123 | Netrakona | 130 | 09:00
58 | Goalpara | 22 | 21:00 | 124 | New | 71 | 12:00
59 | Gollamari | 62 | 13:00 | 125 | Niamatpur | 85 | 09:00
60 | Gopalganj | 79.4 | 19:00 | 126 | Noapara | 37.5 | 18:30
61 | Gulshan | 84 | 13:00 | 127 | PHP | 8 | 06:00
62 | Halishahar | 47 | 16:00 | 128 | Pabna | 68 | 18:30
63 | HaripurSBU | 173 | 17:00 | 129 | Palashbari | 98 | 08:00
64 | Hasnabad | 104 | 18:00 | 130 | Panchagarh | 45 | 18:30
65 | Hathazari | 58 | 13:00 | 131 | Patuakhali | 56 | 21:00
66 | Ishurdi | 58 | 19:00 | 132 | Payra | 20 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9399.5 | 0 |  | 9399.5
1:00 | 8825.5 | 0 |  | 8825.5
2:00 | 8263.5 | 0 |  | 8263.5
3:00 | 7875.5 | 0 |  | 7875.5
4:00 | 7724.5 | 0 |  | 7724.5
5:00 | 7719.5 | 0 |  | 7719.5
6:00 | 8084.5 | 0 |  | 8084.5
7:00 | 9004.82 | 40 |  | 9046.62
8:00 | 9931.6 | 88 |  | 10023.6
9:00 | 10187.57 | 76 |  | 10266.57
10:00 | 10311.19 | 42 |  | 10355.19
11:00 | 10515.56 | 33 |  | 10549.56
12:00 | 10976.64 | 83 |  | 11063.64
13:00 | 11303.38 | 95 |  | 11402.66
14:00 | 10901.16 | 97 |  | 11002.16
15:00 | 10387.39 | 93 |  | 10484.39
16:00 | 10135.38 | 74 |  | 10212.38
17:00 | 10098.21 | 73 |  | 10174.21
18:00 | 10762.15 | 104 |  | 10871.15
19:00 | 11537.07 | 110 |  | 11652.07
19:30 | 11182.88 | 114 |  | 11301.88
20:00 | 11074.47 | 74 |  | 11151.47
21:00 | 10890.37 | 45 |  | 10937.37
22:00 | 10443.38 | 0 |  | 10443.38
23:00 | 9876.97 | 0 |  | 9876.97
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 11-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2758 | 1913.5 | 913 | 0 | 44 | 754 | 40 | 2836 | 0 | 67 | 74 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2757 | 1926 | 911 | 0 | 41 | 636.5 | 40 | 2653.5 | 0 | 93.5 | 54 | 0 | 0 | 0 | 0 | 11-02-2025
01:00 | 2756 | 1938.5 | 909 | 0 | 38 | 519 | 40 | 2471 | 0 | 120 | 34 | 0 | 0 | 0 | 0
01:30 | 2738.5 | 1877.5 | 909 | 0 | 37 | 470.5 | 40 | 2377.5 | 0 | 60 | 34 | 0 | 0 | 0.5 | 0 | Energy Generated | 238.3355 |  | MKWHr
02:00 | 2721 | 1816.5 | 909 | 0 | 36 | 422 | 40 | 2284 | 0 | 0 | 34 | 0 | 0 | 1 | 0 | Energy not Served | 1.127 |  | MKWHr
02:30 | 2718 | 1829 | 817 | 0 | 35 | 422.5 | 40 | 2189 | 0 | 0 | 17 | 0 | 0 | 2 | 0 | Total Energy Requirement | 239.4625 |  | MKWHr
03:00 | 2715 | 1841.5 | 725 | 0 | 34 | 423 | 40 | 2094 | 0 | 0 | 0 | 0 | 0 | 3 | 0
03:30 | 2716 | 1778 | 723 | 0 | 34 | 423.5 | 40 | 2084 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
04:00 | 2717 | 1714.5 | 721 | 0 | 34 | 424 | 40 | 2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2714 | 1715.5 | 721 | 0 | 34 | 424 | 40 | 2072 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
05:00 | 2711 | 1716.5 | 721 | 0 | 34 | 424 | 40 | 2070 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 2738.5 | 1778 | 721 | 0 | 34 | 424 | 40 | 2145.5 | 0 | 4 | 15.5 | 0 | 0 | 1.5 | 0
06:00 | 2766 | 1839.5 | 721 | 0 | 34 | 424 | 40 | 2221 | 0 | 8 | 31 | 0 | 0 | 0 | 0
06:30 | 2785 | 1865 | 817 | 0 | 35 | 427 | 40 | 2494 | 4.66 | 21 | 56 | 0 | 0 | 0 | 20
07:00 | 2804 | 1890.5 | 913 | 0 | 36 | 430 | 40 | 2767 | 9.32 | 34 | 81 | 0 | 0 | 0 | 40
07:30 | 2779.5 | 1911 | 913 | 0 | 37 | 551 | 40 | 2867 | 49.71 | 50 | 270 | 0 | 0 | 0 | 64
08:00 | 2755 | 1931.5 | 913 | 0 | 38 | 672 | 40 | 2967 | 90.1 | 66 | 459 | 0 | 0 | 0 | 88
08:30 | 2567.5 | 1936.1 | 888.5 | 0 | 38 | 713.5 | 40 | 2973.5 | 143.985 | 74 | 683.5 | 0 | 0 | 1 | 82
09:00 | 2380 | 1940.7 | 864 | 0 | 38 | 755 | 40 | 2980 | 197.87 | 82 | 908 | 0 | 0 | 2 | 76
09:30 | 2324 | 1897.35 | 888.5 | 0 | 39 | 755.5 | 40 | 2974.5 | 264.03 | 73.5 | 992 | 0 | 0 | 1 | 59
10:00 | 2268 | 1854 | 913 | 0 | 40 | 756 | 40 | 2969 | 330.19 | 65 | 1076 | 0 | 0 | 0 | 42
10:30 | 2272.5 | 1885.75 | 912.5 | 0 | 44 | 757 | 40 | 2951 | 399.625 | 89.5 | 1061.5 | 0 | 0 | 0 | 37.5
11:00 | 2277 | 1917.5 | 912 | 0 | 48 | 758 | 40 | 2933 | 469.06 | 114 | 1047 | 0 | 0 | 0 | 33
11:30 | 2352.5 | 1952 | 912.5 | 0 | 50 | 758 | 40 | 3000.5 | 503.1 | 135 | 1042.5 | 0 | 0 | 0 | 58
12:00 | 2428 | 1986.5 | 913 | 0 | 52 | 758 | 40 | 3068 | 537.14 | 156 | 1038 | 0 | 0 | 0 | 83
12:30 | 2419 | 1909 | 913 | 0 | 54 | 757.5 | 40 | 3077 | 545.51 | 214.5 | 1210.5 | 0 | 0 | 0 | 89
13:00 | 2410 | 1831.5 | 913 | 0 | 56 | 757 | 40 | 3086 | 553.88 | 273 | 1383 | 0 | 0 | 0 | 95
13:30 | 2324 | 1782 | 912.5 | 0 | 53 | 757 | 40 | 3059.5 | 520.77 | 246.5 | 1407 | 0 | 0 | 0 | 96
14:00 | 2238 | 1732.5 | 912 | 0 | 50 | 757 | 40 | 3033 | 487.66 | 220 | 1431 | 0 | 0 | 0 | 97
14:30 | 2232.5 | 1749 | 912.5 | 0 | 51 | 756.965 | 40 | 3087.5 | 411.81 | 246.5 | 1156.5 | 0 | 0 | 0 | 95
15:00 | 2227 | 1765.5 | 913 | 0 | 52 | 756.93 | 40 | 3142 | 335.96 | 273 | 882 | 0 | 0 | 0 | 93
15:30 | 2301 | 1798.75 | 913 | 0 | 52 | 711.195 | 40 | 3050 | 265.44 | 285 | 844.5 | 0 | 0 | 0.5 | 83.5
16:00 | 2375 | 1832 | 913 | 0 | 52 | 665.46 | 40 | 2958 | 194.92 | 297 | 807 | 0 | 0 | 1 | 74
16:30 | 2420.5 | 1869.5 | 913 | 0 | 47 | 663.895 | 40 | 2891 | 125.4 | 323.5 | 820.5 | 0 | 0 | 2.5 | 73.5
17:00 | 2466 | 1907 | 913 | 0 | 42 | 662.33 | 40 | 2824 | 55.88 | 350 | 834 | 0 | 0 | 4 | 73
17:30 | 2418.5 | 1903 | 912.5 | 0 | 45 | 698.24 | 40 | 2857.5 | 28.44 | 460.5 | 1063 | 0 | 0 | 3.5 | 88.5
18:00 | 2371 | 1899 | 912 | 0 | 48 | 734.15 | 40 | 2891 | 1 | 571 | 1292 | 0 | 0 | 3 | 104
18:30 | 2391.5 | 1902 | 890 | 0 | 48 | 747.01 | 40 | 3042 | 0.5 | 544.5 | 1542.1 | 0 | 0 | 2 | 107
19:00 | 2412 | 1905 | 868 | 0 | 48 | 759.87 | 40 | 3193 | 0 | 518 | 1792.2 | 0 | 0 | 1 | 110
19:30 | 2368 | 1997 | 865 | 0 | 48 | 762.68 | 40 | 3189 | 0 | 411 | 1502.2 | 0 | 0 | 0 | 114
20:00 | 2372 | 1966.5 | 865 | 0 | 46 | 761.77 | 40 | 3146 | 0 | 411 | 1466.2 | 0 | 0 | 0 | 74
20:30 | 2404 | 1961.75 | 892.5 | 0 | 46 | 758.97 | 40 | 3132 | 0 | 411.5 | 1335.7 | 0 | 0 | 0 | 59.5
21:00 | 2436 | 1957 | 920 | 0 | 46 | 756.17 | 40 | 3118 | 0 | 412 | 1205.2 | 0 | 0 | 0 | 45
21:30 | 2483.5 | 1929 | 920.5 | 0 | 46 | 752.175 | 40 | 3065 | 0 | 355.5 | 1075.2 | 0 | 0 | 0 | 22.5
22:00 | 2531 | 1901 | 921 | 0 | 46 | 748.18 | 40 | 3012 | 0 | 299 | 945.2 | 0 | 0 | 0 | 0
22:30 | 2570 | 1935.25 | 920.5 | 0 | 45 | 754.225 | 40 | 2769 | 0 | 288 | 838.2 | 0 | 0 | 0 | 0
23:00 | 2609 | 1969.5 | 920 | 0 | 44 | 760.27 | 40 | 2526 | 0 | 277 | 731.2 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4524 | 4875.5 | 9399.5 | DAILY GENERATION CURVE
00:30 | 4496.5 | 4616 | 9112.5
01:00 | 4469 | 4356.5 | 8825.5 | 11-02-2025
01:30 | 4301.5 | 4243 | 8544.5
02:00 | 4134 | 4129.5 | 8263.5
02:30 | 4089 | 3980.5 | 8069.5
03:00 | 4044 | 3831.5 | 7875.5
03:30 | 3981 | 3819 | 7800
04:00 | 3918 | 3806.5 | 7724.5
04:30 | 3920 | 3802 | 7722
05:00 | 3922 | 3797.5 | 7719.5
05:30 | 4042 | 3860 | 7902
06:00 | 4162 | 3922.5 | 8084.5
06:30 | 4328.075 | 4216.585 | 8544.66
07:00 | 4494.15 | 4510.67 | 9004.82
07:30 | 4670.97 | 4797.24 | 9468.21
08:00 | 4847.79 | 5083.81 | 9931.6
08:30 | 4904.075 | 5155.51 | 10059.585
09:00 | 4960.36 | 5227.21 | 10187.57
09:30 | 4982.505 | 5266.875 | 10249.38
10:00 | 5004.65 | 5306.54 | 10311.19
10:30 | 5033.955 | 5379.42 | 10413.375
11:00 | 5063.26 | 5452.3 | 10515.56
11:30 | 5128.52 | 5617.58 | 10746.1
12:00 | 5193.78 | 5782.86 | 10976.64
12:30 | 5330.21 | 5809.8 | 11140.01
13:00 | 5466.64 | 5836.74 | 11303.38
13:30 | 5416.6 | 5685.67 | 11102.27
14:00 | 5366.56 | 5534.6 | 10901.16
14:30 | 5174.44 | 5469.835 | 10644.275
15:00 | 4982.32 | 5405.07 | 10387.39
15:30 | 5010.58 | 5250.805 | 10261.385
16:00 | 5038.84 | 5096.54 | 10135.38
16:30 | 5089.44 | 5027.355 | 10116.795
17:00 | 5140.04 | 4958.17 | 10098.21
17:30 | 5438.27 | 4991.91 | 10430.18
18:00 | 5736.5 | 5025.65 | 10762.15
18:30 | 5910 | 5239.61 | 11149.61
19:00 | 6083.5 | 5453.57 | 11537.07
19:30 | 5729.5 | 5453.38 | 11182.88
20:00 | 5667 | 5407.47 | 11074.47
20:30 | 5622.25 | 5360.17 | 10982.42 |  | Executive Engineer
21:00 | 5577.5 | 5312.87 | 10890.37 |  | Network Operation Division
21:30 | 5443.5 | 5223.375 | 10666.875
22:00 | 5309.5 | 5133.88 | 10443.38
22:30 | 5278.75 | 4881.425 | 10160.175
23:00 | 5248 | 4628.97 | 9876.97

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 410 | 05:00 | 384 | 12:00 | Payra | 419 | 03:00 | 407 | 12:00
Ashuganj | 412 | 0:00 | 391 | 16:00 | Rahanpur | 416 | 02:00 | 400 | 08:00
Bhulta | 410 | 05:00 | 382 | 12:00 | Rampal | 409 | 04:00 | 391 | 12:00
Bibiana | 416 | 06:00 | 397 | 17:00
BIPTC | 404 | 03:00 | 389 | 13:00
Bogura | 415 | 04:00 | 396 | 07:00
Gopalganj | 412 | 02:00 | 391 | 12:00
Kaliakoir | 402 | 05:00 | 382 | 17:00
Madunaghat | 407 | 03:00 | 398 | 12:00
Meghnaghat | 408 | 05:00 | 382 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 02:00 | 219 | 12:00 | Keranigonj | 235 | 02:00 | 219 | 12:00
AKSML | 235 | 04:00 | 225 | 12:00 | Khulna(S) | 239 | 03:00 | 224 | 12:00
Aminbazar | 235 | 05:00 | 221 | 12:00 | Madunaghat | 235 | 10:00 | 227 | 12:00
Ashuganj | 243 | 03:00 | 228 | 12:00 | Madunaghat-400 | 234 | 05:00 | 228 | 16:00
Ashuganj-400 | 241 | 01:00 | 232 | 17:00 | Maniknagar | 235 | 04:00 | 219 | 12:00
Baghabari | 239 | 01:00 | 228 | 12:00 | Meghnaghat | 242 | 03:00 | 228 | 11:00
Barapukuria | 227 | 14:00 | 214 | 08:00 | Meghnaghat-400 | 239 | 05:00 | 223 | 12:00
Barapukuria-230 | 227 | 14:00 | 214 | 08:00 | Mirsorai | 237 | 19:00 | 224 | 12:00
Barishal | 244 | 04:00 | 234 | 12:00 | Rajshahi | 241 | 04:00 | 223 | 12:00
Bheramara | 238 | 03:00 | 222 | 12:00 | Rampal | 236 | 02:00 | 222 | 12:00
Bhulta | 238 | 05:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 239 | 02:00 | 227 | 15:00 | Rampura | 237 | 02:00 | 219 | 12:00
BIPTC | 241 | 04:00 | 223 | 12:00 | Shikalbaha | 235 | 17:00 | 225 | 16:00
Bogura | 241 | 04:00 | 228 | 08:00 | Shyampur | 236 | 04:00 | 220 | 12:00
Bogura-400 | 239 | 04:00 | 228 | 08:00 | Siddhirganj | 236 | 04:00 | 222 | 12:00
Borhanuddin | 247 | 01:00 | 241 | 12:00 | Sirajgonj | 246 | 04:00 | 236 | 12:00
BSRM | 235 | 02:00 | 223 | 12:00 | Sreepur | 241 | 02:00 | 228 | 12:00
Cumilla(N) | 237 | 06:00 | 23 | 22:00 | Tongi | 234 | 03:00 | 220 | 12:00
Faridpur | 243 | 04:00 | 231 | 12:00
Fenchuganj | 242 | 05:00 | 227 | 15:00
Ghorashal | 240 | 00:00 | 230 | 17:00
Ghorashal-230 | 237 | 02:00 | 222 | 12:00
Gopalganj | 242 | 04:00 | 230 | 12:00
GPH | 234 | 02:00 | 224 | 16:00
Haripur | 238 | 05:00 | 221 | 12:00
Hasnabad | 235 | 00:00 | 220 | 12:00
Hathazari | 236 | 19:00 | 227 | 12:00
Ishurdi | 241 | 05:00 | 225 | 12:00
Jhenaidah | 238 | 04:00 | 221 | 12:00
Kaliakoir | 234 | 05:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 01:00 | 123 | 12:00 | Magura | 138 | 01:00 | 125 | 12:00
Agargaon | 137 | 02:00 | 126 | 12:00 | Mahasthangarh | 136 | 02:00 | 126 | 08:00
Agrabad | 135 | 18:00 | 128 | 12:00 | Manikganj | 138 | 08:00 | 130 | 17:00
AKS | 133 | 03:00 | 127 | 12:00 | Maniknagar | 135 | 04:00 | 124 | 12:00
Aminbazar | 136 | 03:00 | 128 | 10:00 | Matarbari | 128 | 09:00 | 120 | 12:00
Amnura | 141 | 22:00 | 128 | 13:00 | Matuail | 136 | 01:00 | 125 | 12:00
Ashuganj | 141 | 03:00 | 138 | 12:00 | Millgate | 137 | 02:00 | 125 | 12:00
Bagerhat | 137 | 03:00 | 123 | 12:00 | Mirpur | 135 | 03:00 | 124 | 12:00
Bajitpur | 136 | 06:00 | 131 | 11:00 | Mirzapur | 137 | 05:00 | 127 | 12:00
Bakulia | 136 | 18:00 | 129 | 12:00 | Mithapukur | 137 | 20:00 | 121 | 09:00
Banani | 134 | 02:00 | 121 | 12:00 | MI_Cement | 136.4 | 04:00 | 126 | 12:00
Bangabhaban | 135 | 04:00 | 123 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 14:00 | 127 | 07:00 | Mogbazar | 136 | 05:00 | 123 | 12:00
Barguna | 138 | 07:00 | 134 | 12:00 | Mongla | 136 | 01:00 | 123 | 12:00
Barishal | 135 | 05:00 | 128 | 12:00 | Motijheel | 135 | 04:00 | 123 | 12:00
Barishal-230 | 136 | 02:00 | 129 | 12:00 | Muktagacha | 128 | 06:00 | 118 | 17:00
Baroaulia | 134 | 18:00 | 131 | 10:00 | Munshiganj | 135 | 02:00 | 125 | 12:00
Baroirhat | 133 | 09:00 | 126 | 12:00 | Muradnagar | 135 | 04:00 | 124 | 12:00
Bashundhara | 137 | 04:00 | 122 | 12:00 | Mymensingh | 130 | 08:00 | 116 | 12:00
BashundharaCement | 135 | 05:00 | 126 | 12:00 | Naogaon | 134 | 01:00 | 122 | 08:00
Beanibazar | 137 | 01:00 | 129 | 12:00 | Narail | 138 | 04:00 | 124 | 12:00
Benapole | 137 | 03:00 | 120 | 13:00 | Narinda | 135 | 04:00 | 124 | 12:00
Bhaluka | 128 | 01:00 | 119 | 12:00 | Narshingdi | 132 | 00:00 | 121 | 12:00
Bhandaria | 134 | 03:00 | 125 | 12:00 | Natore | 137 | 02:00 | 129 | 12:00
Bhangura | 139 | 03:00 | 128 | 12:00 | Nawabganj | 139 | 06:00 | 125 | 15:00
Bheramara | 137 | 03:00 | 129 | 12:00 | Netrakona | 127 | 04:00 | 115 | 12:00
Bheramara(GK) | 138 | 03:00 | 129 | 12:00 | New | 137 | 03:00 | 126 | 12:00
Bhulta | 129 | 05:00 | 120 | 12:00 | Niamatpur | 139 | 01:00 | 133 | 08:00
Bog-Sherpur | 137 | 04:00 | 127 | 08:00 | Noapara | 137 | 02:00 | 125 | 12:00
Bogura | 137 | 02:00 | 129 | 13:00 | Pabna | 136 | 02:00 | 124 | 12:00
Bogura-230 | 138 | 04:00 | 129 | 08:00 | Palashbari | 131 | 03:00 | 117 | 08:00
Brahmanbaria | 138 | 02:00 | 128 | 12:00 | Panchagarh | 141 | 23:00 | 125 | 08:00
Cantonment | 138 | 05:00 | 126 | 12:00 | Patuakhali | 137 | 07:00 | 133 | 12:00
Chandpur | 138 | 18:30 | 127 | 00:00 | Payra | 138 | 01:00 | 134 | 12:00
Chandraghona | 135 | 03:00 | 130 | 11:00 | PHP | 131 | 03:00 | 125 | 12:00
Chapai | 139 | 03:00 | 129 | 12:00 | Postogola | 140 | 04:00 | 129 | 12:00
Charsaidpur | 136 | 02:00 | 126 | 12:00 | Purbachal | 135 | 01:00 | 122 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 133 | 03:00 | 127 | 12:00 | Purbasadipur | 134 | 19:30 | 118 | 07:00
Chhatak | 136 | 05:00 | 127 | 18:30 | Rahanpur | 141 | 04:00 | 134 | 12:00
Chowmuhani | 132 | 08:00 | 125 | 12:00 | Rahanpur-400 | 141 | 02:00 | 134 | 12:00
Chuadanga | 137 | 04:00 | 124 | 12:00 | Rahim | 135 | 04:00 | 126 | 13:00
Coxsbazar | 125 | 06:00 | 119 | 12:00 | Rajbari | 135 | 00:00 | 127 | 12:00
Cumilla(N) | 137 | 02:00 | 131 | 15:00 | Rajendrapur | 137 | 10:00 | 130 | 11:00
Cumilla(S) | 136 | 05:00 | 128 | 13:00 | Rajshahi | 139 | 05:00 | 130 | 12:00
Daudkandi | 133 | 01:00 | 122 | 12:00 | Rajshahi-230 | 139 | 03:00 | 124 | 12:00
Dhaka | 135 | 02:00 | 123 | 12:00 | Ramganj | 133 | 09:00 | 125 | 00:00
Dhamrai | 135 | 05:00 | 124 | 12:00 | Rampur | 135 | 19:00 | 127 | 12:00
Dhanmondi | 136.5 | 05:00 | 125 | 13:00 | Rampura | 135 | 05:00 | 122 | 12:00
Dohazari | 133 | 19:00 | 127 | 16:00 | Rangamati | 135 | 19:00 | 129 | 12:00
Faridpur | 135 | 02:00 | 128 | 12:00 | Rangpur | 135 | 14:00 | 118 | 07:00
Fatullah | 138 | 04:00 | 127 | 12:00 | Ruppur | 139 | 03:00 | 131 | 12:00
Fenchuganj | 141 | 04:00 | 133 | 17:00 | Saidpur | 134 | 23:00 | 124 | 08:00
Feni | 148 | 18:00 | 120 | 15:00 | Satkhira | 137 | 04:00 | 123 | 13:00
Ghatail | 130 | 08:00 | 118 | 12:00 | Satmasjid | 137 | 04:00 | 127 | 12:00
Ghorashal | 142 | 01:00 | 137 | 12:00 | Savar | 135 | 18:00 | 126 | 11:00
Goalpara | 139 | 04:00 | 126 | 12:00 | SevenRings | 142 | 02:00 | 137 | 12:00
Gollamari | 138 | 04:00 | 124 | 12:00 | ShahCement | 136 | 02:00 | 126 | 12:00
Gopalganj | 137 | 04:00 | 127 | 12:00 | Shahjadpur | 138 | 00:00 | 132 | 11:00
Gopalganj-400 | 137 | 02:00 | 129 | 12:00 | Shahjibazar | 140 | 06:00 | 130 | 12:00
Gulshan | 134 | 04:00 | 122 | 12:00 | Shahmirpur | 136 | 18:00 | 130 | 12:00
Halishahar | 134 | 10:00 | 130 | 05:00 | Shariatpur | 137 | 03:00 | 128 | 12:00
Haripur | 135 | 02:00 | 126 | 12:00 | Sherpur | 126 | 08:00 | 113 | 12:00
HaripurSBU | 135 | 02:00 | 127 | 13:00 | Shikalbaha | 123 | 00:00 | 119 | 12:00
Hasnabad | 138 | 01:00 | 129 | 12:00 | Shikalbaha-230 | 136 | 17:00 | 130 | 12:00
Hathazari | 137 | 18:30 | 132 | 12:00 | Shitalakhya | 136.4 | 04:00 | 126 | 12:00
Ishurdi | 140 | 04:00 | 131 | 12:00 | Sholosohor | 135 | 18:30 | 130 | 12:00
Jaldhaka | 133 | 19:30 | 120 | 08:00 | Shyampur | 137 | 06:00 | 130 | 13:00
Jamalpur | 128 | 00:00 | 115 | 12:00 | Shyampur-230 | 138 | 04:00 | 126 | 12:00
Jashore | 139 | 02:00 | 122 | 13:00 | Siddhirganj | 136 | 04:00 | 126 | 12:00
Jhenaidah | 138 | 03:00 | 127 | 12:00 | Sirajganj | 138 | 05:00 | 128 | 08:00
Jhenaidah-230 | 140 | 05:00 | 127 | 12:00 | Sonargaon | 135 | 05:00 | 124 | 15:00
Joydebpur | 140 | 18:00 | 132 | 21:00 | Sreemongol | 139 | 01:00 | 131 | 17:00
Joypurhat | 134 | 01:00 | 120 | 08:00 | Sreepur | 131 | 03:00 | 123 | 12:00
Juldah | 135 | 18:00 | 129 | 12:00 | Srinagar | 139 | 04:00 | 128 | 12:00
Kabirpur | 142 | 06:00 | 124 | 12:00 | SSM | 140 | 18:00 | 134 | 09:00
Kachua | 136 | 19:00 | 129 | 12:00 | Sunamganj | 136 | 04:00 | 127 | 13:00
Kaliakoir | 143 | 00:00 | 126 | 12:00 | Sylhet | 137 | 02:00 | 130 | 12:00
Kallyanpur | 134 | 04:00 | 124 | 12:00 | Sylhet-132 | 138 | 01:00 | 130 | 12:00
Kalurghat | 135 | 00:00 | 131 | 16:00 | Tangail | 131 | 00:00 | 123 | 11:00
Kamrangirchar | 139 | 06:00 | 122 | 12:00 | Thakurgaon | 140 | 23:00 | 122 | 08:00
Kaptai | 137 | 1:00 | 125 | 12:00 | TK | 136 | 18:00 | 130 | 12:00
Kazla | 135 | 03:00 | 123 | 13:00 | Tongi | 138 | 00:00 | 128 | 12:00
Keranigonj | 138 | 04:00 | 128 | 12:00 | Ullahpara | 138 | 03:00 | 128 | 12:00
Khagrachori | 135 | 05:00 | 129 | 12:00 | Ullon | 134 | 01:00 | 122 | 12:00
Khulna | 137 | 02:00 | 125 | 12:00 | Uttara | 136 | 04:00 | 124 | 12:00
Khulna(S) | 139 | 05:00 | 128 | 12:00 | UttaraNew | 135 | 01:00 | 124 | 12:00
Khulshi | 134 | 19:00 | 127 | 12:00 | Zigatola | 139 | 05:00 | 128 | 16:00
Kishoreganj | 132 | 21:00 | 126 | 12:00
Kodda | 140 | 00:00 | 131 | 18:00
KSRM | 136 | 19:00 | 130 | 12:00
Kulaura | 141 | 03:00 | 133 | 12:00
Kurigram | 133 | 14:00 | 122 | 07:00
Kushtia | 138 | 04:00 | 128 | 12:00
Lalbag | 139 | 05:00 | 128 | 12:00
Lalmonirhat | 133 | 20:00 | 121 | 08:00
Madanganj | 135 | 04:00 | 126 | 12:00
Madaripur | 135 | 04:00 | 130 | 12:00
Madartek | 134 | 02:00 | 122 | 12:00
Madunaghat | 136 | 19:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-02-2025 | during | 12-02-2025 | during | 12-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 240 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 407 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 314 | 266 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 17 | 18.5 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 15 | 22 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 82 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 27 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 40 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 54 | 17 | 54 | 17 | 54 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1857 | 2061.5 | 4810.87 | 4805.87 | 2782.79 | 2787.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 226 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 40 | 82 | 64 | 84 | 64 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 85 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 12 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 4.42 | 0 | 4.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 46 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 90 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 1 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 157 | 273 | 270 | 270 | 150 | 150 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1291 | 1767 | 2533.28 | 2551.86 | 2413.28 | 2431.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 356.56 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 27 | 30 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 187 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 40 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 130 | 134 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 40 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 90 | 136 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 52 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 72 | 0 | 72 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 899 | 1047 | 2097.53 | 2025.53 | 1596.2 | 1524.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-02-2025 | during | 12-02-2025 | during | 12-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 6 | 18 | 210 | 210 | 30 | 30 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 59 | 115 | 115 | 59 | 59 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 12.78 | 0 | 43 | 0 | 43 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 17 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 110.78 | 127 | 646.3 | 601.5 | 219.3 | 174.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 32 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 341 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 400 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1036 | 1081 | 1060 | 1060 | 1014 | 1014
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 868 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 34 | 100 | 410 | 410 | 250 | 250 | Commissioning work is in progress
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 83.42 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1232 | 1258 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | coal available to run both units upto 12/02/25
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2262.42 | 2226 | 3584.2 | 3504.2 | 3214.2 | 3134.2
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 134 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 610 | 590 | 622 | 622 | 602 | 602 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1288.61 | 1275 | 1556.12 | 1555.12 | 1533 | 1532
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 33 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 164 | 149 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 35 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 41 | 88 | 92 | 92 | 92 | 92 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 33 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.12 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 758 | 759.87 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.61 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1724.23 | 1599.57 | 2503.34 | 2338.24 | 2241.56 | 2076.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 70 | 70 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 150 | 153 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 85 | 105 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 154 | 0 | 99.71 | 0 | 169.36 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 507.6 | 353 | 625.31 | 492 | 624.96 | 422
System Total |  |  |  |  | 27884.66 | 27150.742 | 10976.64 | 11537.07 | 19416.95 | 18934.32 | 15639.29 | 15097.01
Forecast Scenario (12-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9260 |  | 0 |  | 9260
|  |  |  | 1:00 | 8510 |  | 0 |  | 8510
|  |  |  | 2:00 | 8180 |  | 0 |  | 8180
|  |  |  | 3:00 | 7900 |  | 0 |  | 7900
|  |  |  | 4:00 | 7750 |  | 0 |  | 7750
|  |  |  | 5:00 | 7530 |  | 0 |  | 7530
|  |  |  | 6:00 | 7990 |  | 0 |  | 7990
|  |  |  | 7:00 | 8990 |  | 0 |  | 8990
|  |  |  | 8:00 | 9880 |  | 0 |  | 9880
|  |  |  | 9:00 | 10380 |  | 0 |  | 10380
|  |  |  | 10:00 | 10290 |  | 0 |  | 10290
|  |  |  | 11:00 | 10340 |  | 0 |  | 10340
|  |  |  | 12:00 | 10770 |  | 0 |  | 10770
|  |  |  | 13:00 | 11060 |  | 0 |  | 11060
|  |  |  | 14:00 | 10760 |  | 0 |  | 10760
|  |  |  | 15:00 | 10370 |  | 0 |  | 10370
|  |  |  | 16:00 | 10010 |  | 0 |  | 10010
|  |  |  | 17:00 | 10000 |  | 0 |  | 10000
|  |  |  | 18:00 | 10820 |  | 0 |  | 10820
|  |  |  | 18:30 | 11150 |  | 0 |  | 11150
|  |  |  | 19:00 | 11420 |  | 0 |  | 11420
|  |  |  | 19:30 | 11130 |  | 0 |  | 11130
|  |  |  | 20:00 | 10900 |  | 0 |  | 10900
|  |  |  | 21:00 | 10730 |  | 0 |  | 10730
|  |  |  | 22:00 | 10380 |  | 0 |  | 10380
|  |  |  | 23:00 | 9730 |  | 0 |  | 9730
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 10770.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11420.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11420.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 233.95 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:10 hrs on 12-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-02-2025 | [28 empty] | Date: | 11-02-2025 | [28 empty] | Date: | 11-02-2025 | [28 empty] | Date: | 11-02-2025 | [28 empty] | Date: | 11-02-2025 | [19 empty] | Date: | 11-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [19 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 273 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 152 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 590 | 0 | 51 | 0 | 199 | 0 | 0 | 345 | 29 | 182 | 30 | 0 | 40 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 59 | 9 | 18 | 0 | 0 | 6 | 4524 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1011 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 2.5 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 4875.5 | 9399.5 | 90.82
01:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 283 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 199 | 0 | 0 | 340 | 29 | 187 | 30 | 0 | 40 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 19 | 9 | 18 | 0 | 0 | 6 | 4469 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 0 | 519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 2.5 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 130 | 220 | 0 | 0 | 550 | 0 | 4356.5 | 8825.5 | 90.82
02:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 272 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 433 | 0 | 51 | 0 | 199 | 0 | 0 | 345 | 29 | 182 | 30 | 0 | 40 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 19 | 9 | 20 | 0 | 0 | 6 | 4134 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 0 | 2.5 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 130 | 220 | 0 | 0 | 530 | 0 | 4129.5 | 8263.5 | 90.81
03:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 298 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 199 | 0 | 0 | 340 | 29 | 203 | 30 | 0 | 45 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 315 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 0 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 4044 | 725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 2.5 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 0 | 470 | 0 | 3831.5 | 7875.5 | 90.81
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 296 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 128 | 0 | 0 | 345 | 29 | 200 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 10 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 3918 | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 2.5 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 128 | 220 | 0 | 0 | 450 | 0 | 3806.5 | 7724.5 | 90.81
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 288 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 128 | 0 | 0 | 345 | 29 | 190 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 320 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 10 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 3922 | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 2.5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 126 | 220 | 0 | 0 | 450 | 0 | 3797.5 | 7719.5 | 90.8
06:00 | 0 | 8 | 0 | 0 | 0 | 230 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 265 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 156 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 195 | 0 | 0 | 345 | 29 | 196 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 325 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 82 | 30 | 0 | 20 | 0 | 0 | 19 | 0 | 30 | 0 | 0 | 0 | 4162 | 721 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 131 | 0 | 414 | 0 | 0 | 2.5 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 6 | 126 | 220 | 0 | 0 | 470 | 0 | 3922.5 | 8084.5 | 90.8
07:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 298 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 156 | 0 | 0 | 2 | 0 | 0 | 226 | 0 | 0 | 0 | 577 | 1 | 51 | 0 | 189 | 0 | 0 | 345 | 27 | 205 | 27 | 0 | 50 | 0 | 0 | 17 | 0 | 36 | 0 | 1 | 0 | 310 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 81 | 30 | 0 | 20 | 0 | 0 | 56 | 9 | 20 | 0 | 1.15 | 2 | 4494.15 | 913 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1005 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 179 | 0 | 0 | 0 | 154 | 0 | 409 | 0 | 0.1 | 2.5 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.11 | 0 | 307 | 5 | 126 | 220 | 0 | 0 | 570 | 0 | 4510.67 | 9004.82 | 90.8
08:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 385 | 0 | 0 | 12 | 16 | 0 | 17 | 32 | 0 | 12 | 0 | 72 | 17 | 0 | 450 | 266 | 0 | 0 | 17 | 23 | 0 | 0 | 0 | 4 | 0 | 18 | 22 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 8 | 155 | 0 | 0 | 0 | 0 | 26 | 226 | 0 | 0 | 0 | 612 | 7 | 51 | 50 | 189 | 0 | 0 | 325 | 28 | 182 | 24 | 1 | 50 | 49 | 3 | 17 | 0 | 38 | 0 | 5 | 0 | 315 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 20 | 0 | 0 | 56 | 9 | 18 | 0 | 8.79 | 0 | 4847.79 | 913 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.98 | 1117 | 0 | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3.47 | 179 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 0.19 | 2.5 | 154 | 0 | 35 | 4 | 40 | 0 | 0 | 0.6 | 29 | 0.07 | 0 | 307 | 5 | 126 | 220 | 0 | 0 | 622 | 17 | 5083.81 | 9931.6 | 90.79
09:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 332 | 0 | 0 | 17 | 17 | 0 | 71 | 32 | 0 | 55 | 17 | 72 | 17 | 0 | 450 | 280 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 14 | 0 | 17.2 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 16 | 0 | 1 | 4 | 2 | 40 | 0 | 3 | 156 | 5 | 0 | 19 | 0 | 60 | 226 | 0 | 0 | 0 | 612 | 13 | 51 | 120 | 189 | 0 | 0 | 0 | 29 | 230 | 24 | 16 | 50 | 106 | 9 | 17 | 0 | 38 | 0 | 17 | 0 | 320 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 20 | 0 | 35 | 56 | 9 | 11 | 1 | 7.16 | 4 | 4960.36 | 864 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.01 | 1150 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 30 | 0 | 7.1 | 173 | 0 | 0 | 0 | 131 | 0 | 414 | 0 | 0.64 | 5.5 | 155 | 0 | 50 | 4 | 70 | 0 | 0 | 1.7 | 72 | 0.26 | 0 | 307 | 5 | 126 | 220 | 0 | 0 | 600 | 17 | 5227.21 | 10187.57 | 90.79
10:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 365 | 0 | 0 | 17 | 30 | 0 | 123 | 16 | 0 | 15 | 17 | 30 | 17 | 0 | 450 | 285 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 21 | 0 | 17.5 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 12 | 12 | 0 | 40 | 25 | 2 | 156 | 17 | 0 | 25 | 0 | 98 | 226 | 0 | 0 | 0 | 613 | 17 | 40 | 128 | 187 | 0 | 0 | 0 | 29 | 229 | 24 | 17 | 50 | 136 | 9 | 17 | 0 | 40 | 0 | 26 | 0 | 285 | 320 | 0 | 32 | 30 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 35 | 56 | 9 | 6 | 1 | 21.15 | 6 | 5004.65 | 913 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.41 | 1199 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 64 | 0 | 13.17 | 153 | 0 | 0 | 0 | 111 | 0 | 360 | 0 | 1.14 | 5.5 | 151 | 0 | 95 | 15 | 85 | 0 | 0 | 2.9 | 109 | 0.42 | 0 | 250 | 5 | 80 | 220 | 0 | 0 | 600 | 17 | 5306.54 | 10311.19 | 90.79
11:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 408 | 0 | 0 | 17 | 36 | 0 | 129 | 16 | 0 | 15 | 17 | 17 | 25 | 0 | 450 | 300 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 15 | 0 | 17 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 12 | 0 | 40 | 34 | 2 | 156 | 17 | 0 | 25 | 0 | 105 | 226 | 0 | 0 | 0 | 613 | 19 | 40 | 128 | 187 | 0 | 0 | 0 | 29 | 192 | 27 | 17 | 45 | 85 | 9 | 17 | 0 | 48 | 0 | 49 | 0 | 330 | 320 | 0 | 32 | 30 | 0 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 56 | 19 | 6 | 2 | 21.26 | 6 | 5063.26 | 912 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.42 | 1162 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 43 | 90 | 0 | 43.91 | 151 | 0 | 0 | 0 | 120 | 0 | 360 | 0 | 2.58 | 5.5 | 152 | 0 | 95 | 21 | 85 | 0 | 0 | 3.6 | 140 | 0.29 | 0 | 250 | 4 | 80 | 220 | 0 | 0 | 600 | 17 | 5452.3 | 10515.56 | 90.78
12:00 | 0 | 27 | 0 | 0 | 0 | 230 | 0 | 0 | 407 | 0 | 0 | 17 | 36 | 0 | 132 | 48 | 0 | 15 | 17 | 40 | 25 | 0 | 450 | 314 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 28 | 0 | 17 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 12 | 0 | 40 | 34 | 3 | 157 | 17 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 612 | 19 | 40 | 130 | 187 | 0 | 0 | 0 | 29 | 200 | 27 | 16 | 45 | 90 | 9 | 17 | 0 | 52 | 0 | 57 | 0 | 341 | 320 | 0 | 32 | 30 | 0 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 58 | 9 | 6 | 2 | 12.78 | 6 | 5193.78 | 913 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.42 | 1232 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 35 | 104 | 0 | 47.61 | 164 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 5.12 | 5.5 | 150 | 0 | 95 | 20 | 85 | 0 | 0 | 3.6 | 154 | 0.61 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 610 | 17 | 5782.86 | 10976.64 | 90.78
13:00 | 0 | 61 | 0 | 0 | 0 | 230 | 0 | 0 | 408 | 0 | 0 | 17 | 36 | 0 | 131 | 82 | 0 | 32 | 35 | 126 | 25 | 0 | 380 | 247 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 33 | 50 | 0 | 40 | 47 | 8 | 155 | 53 | 0 | 0 | 0 | 105 | 224 | 0 | 0 | 0 | 612 | 19 | 40 | 130 | 187 | 0 | 0 | 0 | 29 | 182 | 27 | 32 | 45 | 139 | 9 | 17 | 0 | 56 | 0 | 59 | 0 | 330 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 18 | 0 | 34 | 58 | 9 | 6 | 2 | 26.64 | 6 | 5466.64 | 913 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.78 | 1238 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 35 | 107 | 0 | 57.42 | 170 | 0 | 0 | 0 | 143 | 0 | 414 | 0 | 4.82 | 5.5 | 152 | 0 | 95 | 20 | 102 | 0 | 0 | 2.7 | 147 | 0.52 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 622 | 17 | 5836.74 | 11303.38 | 90.78
14:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 366 | 0 | 0 | 17 | 36 | 0 | 134 | 32 | 0 | 40 | 35 | 126 | 25 | 0 | 340 | 265 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 50 | 50 | 3 | 40 | 68 | 3 | 213 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 612 | 17 | 51 | 135 | 185 | 0 | 0 | 0 | 29 | 183 | 30 | 35 | 45 | 170 | 9 | 17 | 0 | 50 | 0 | 54 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 8 | 2 | 34.56 | 6 | 5366.56 | 912 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.39 | 1124 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 43 | 94 | 0 | 48.54 | 169 | 0 | 0 | 0 | 123 | 0 | 350 | 0 | 4.54 | 5.5 | 155 | 0 | 95 | 18 | 105 | 0 | 0 | 2.1 | 123 | 0.53 | 0 | 307 | 5 | 80 | 220 | 0 | 0 | 622 | 17 | 5534.6 | 10901.16 | 90.77
15:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 361 | 0 | 0 | 17 | 36 | 0 | 125 | 20 | 0 | 15 | 35 | 90 | 25 | 0 | 340 | 276 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 19 | 15 | 19 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 12 | 12 | 2 | 40 | 17 | 2 | 275 | 0 | 0 | 7 | 0 | 51 | 225 | 0 | 0 | 0 | 612 | 13 | 51 | 80 | 185 | 0 | 0 | 0 | 29 | 182 | 20 | 34 | 45 | 51 | 9 | 17 | 0 | 52 | 0 | 38 | 0 | 290 | 320 | 0 | 32 | 30 | 0 | 5 | 120 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 12 | 1 | 24.32 | 6 | 4982.32 | 913 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.13 | 1170 | 0 | 756.93 | 0 | 0 | 32 | 0 | 0 | 0 | 40 | 0 | 20 | 43 | 69 | 18 | 36.74 | 160 | 0 | 0 | 0 | 131 | 0 | 350 | 0 | 3.5 | 5.5 | 156 | 0 | 53 | 11 | 34 | 0 | 0 | 1.9 | 64 | 0.37 | 0 | 307 | 5 | 80 | 220 | 0 | 0 | 622 | 17 | 5405.07 | 10387.39 | 90.77
16:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 362 | 0 | 0 | 17 | 36 | 0 | 123 | 16 | 0 | 15 | 17 | 90 | 25 | 0 | 340 | 282 | 0 | 0 | 35 | 19 | 0 | 0 | 0 | 12 | 35 | 18.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 78 | 0 | 0 | 12 | 1 | 40 | 17 | 2 | 274 | 0 | 0 | 31 | 0 | 17 | 221 | 0 | 0 | 0 | 612 | 7 | 51 | 50 | 185 | 0 | 0 | 0 | 29 | 183 | 30 | 49 | 45 | 51 | 9 | 17 | 0 | 52 | 0 | 22 | 0 | 305 | 365 | 0 | 32 | 30 | 0 | 5 | 163 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 12 | 1 | 14.34 | 6 | 5038.84 | 913 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.15 | 1064 | 0 | 665.46 | 0 | 0 | 33 | 0 | 0 | 0 | 40 | 0 | 20 | 8 | 41 | 25 | 21.1 | 153 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 2.1 | 5.5 | 158 | 0 | 53 | 5 | 34 | 0 | 0 | 1.1 | 37 | 0.13 | 0 | 250 | 4 | 80 | 220 | 0 | 0 | 600 | 17 | 5096.54 | 10135.38 | 90.77
17:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 390 | 0 | 0 | 17 | 54 | 0 | 124 | 16 | 0 | 15 | 17 | 90 | 25 | 0 | 400 | 289 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 4 | 35 | 18.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 0 | 78 | 0 | 0 | 12 | 0 | 40 | 17 | 2 | 276 | 0 | 0 | 33 | 0 | 17 | 222 | 0 | 0 | 0 | 612 | 2 | 51 | 50 | 185 | 0 | 0 | 0 | 29 | 196 | 30 | 53 | 45 | 51 | 11 | 17 | 0 | 42 | 0 | 5 | 0 | 310 | 370 | 0 | 32 | 30 | 0 | 5 | 163 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 12 | 0 | 3.54 | 6 | 5140.04 | 913 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.74 | 1062 | 0 | 662.33 | 0 | 0 | 33 | 0 | 0 | 0 | 88 | 0 | 20 | 8 | 11 | 30 | 4.73 | 153 | 0 | 0 | 0 | 121 | 0 | 414 | 0 | 0.4 | 5.5 | 154 | 0 | 53 | 2 | 34 | 0 | 0 | 0.4 | 13 | 0.07 | 0 | 200 | 4 | 130 | 220 | 0 | 0 | 520 | 17 | 4958.17 | 10098.21 | 90.76
18:00 | 0 | 65 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 54 | 36 | 0 | 107 | 98 | 0 | 22 | 27 | 162 | 25 | 0 | 400 | 260 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 0 | 35 | 18.5 | 22 | 0 | 0 | 35 | 15 | 3 | 0 | 3 | 85 | 82 | 0 | 36 | 50 | 0 | 40 | 17 | 2 | 273 | 60 | 0 | 33 | 0 | 43 | 225 | 0 | 0 | 0 | 612 | 0 | 51 | 84 | 195 | 0 | 0 | 0 | 29 | 182 | 30 | 108 | 45 | 78 | 27 | 17 | 0 | 48 | 0 | 0 | 26 | 315 | 370 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 20 | 58 | 9 | 16 | 0 | 0 | 6 | 5736.5 | 912 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1070 | 0 | 734.15 | 0 | 0 | 33 | 0 | 13 | 0 | 88 | 15 | 29 | 25 | 0 | 30 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 155 | 0 | 62 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 6 | 130 | 220 | 0 | 0 | 520 | 17 | 5025.65 | 10762.15 | 90.76
19:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 0 | 82 | 64 | 0 | 55 | 55 | 162 | 25 | 0 | 420 | 266 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 0 | 26 | 18.5 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 1 | 85 | 82 | 0 | 50 | 50 | 0 | 40 | 46 | 12 | 273 | 90 | 0 | 33 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 134 | 187 | 0 | 0 | 0 | 29 | 182 | 30 | 115 | 50 | 136 | 28 | 17 | 0 | 48 | 0 | 0 | 40 | 295 | 400 | 0 | 32 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 18 | 0 | 0 | 6 | 6083.5 | 868 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1258 | 0 | 759.87 | 0 | 0 | 33 | 0 | 33 | 0 | 88 | 35 | 0 | 52.2 | 0 | 30 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 153 | 0 | 95 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 590 | 17 | 5453.57 | 11537.07 | 90.76
19:30 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 54 | 54 | 0 | 34 | 64 | 0 | 55 | 55 | 126 | 25 | 0 | 420 | 315 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 17 | 18.5 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 85 | 24 | 0 | 12 | 12 | 0 | 40 | 51 | 12 | 273 | 17 | 0 | 33 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 140 | 187 | 0 | 0 | 0 | 29 | 215 | 30 | 115 | 50 | 136 | 28 | 17 | 0 | 48 | 0 | 0 | 0 | 335 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 20 | 0 | 0 | 6 | 5729.5 | 865 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223 | 0 | 762.68 | 0 | 0 | 33 | 0 | 35 | 0 | 88 | 35 | 0 | 52.2 | 0 | 30 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 152 | 0 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 17 | 5453.38 | 11182.88
20:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 0 | 34 | 64 | 0 | 55 | 55 | 72 | 25 | 0 | 420 | 298 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 85 | 24 | 0 | 12 | 12 | 0 | 40 | 51 | 20 | 276 | 17 | 0 | 33 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 140 | 185 | 0 | 0 | 20 | 29 | 198 | 30 | 115 | 50 | 136 | 29 | 17 | 0 | 46 | 0 | 0 | 0 | 315 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 58 | 9 | 20 | 0 | 0 | 6 | 5667 | 865 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 0 | 761.77 | 0 | 0 | 33 | 0 | 35 | 0 | 88 | 35 | 0 | 52.2 | 0 | 30 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 153 | 0 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 17 | 5407.47 | 11074.47 | 90.75
21:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 0 | 34 | 64 | 0 | 55 | 17 | 17 | 25 | 0 | 420 | 294 | 0 | 0 | 35 | 23 | 0 | 0 | 0 | 0 | 17 | 19.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 85 | 24 | 0 | 12 | 12 | 0 | 40 | 51 | 21 | 275 | 0 | 0 | 33 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 140 | 185 | 0 | 0 | 80 | 29 | 193 | 30 | 115 | 50 | 136 | 29 | 17 | 0 | 46 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 57 | 9 | 21 | 0 | 0 | 6 | 5577.5 | 920 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 756.17 | 0 | 0 | 33 | 0 | 0 | 0 | 89 | 0 | 0 | 52.2 | 0 | 30 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 152 | 0 | 95 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 17 | 5312.87 | 10890.37 | 90.75
22:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 36 | 0 | 29 | 64 | 0 | 15 | 0 | 17 | 25 | 0 | 370 | 277 | 0 | 0 | 17 | 23 | 0 | 0 | 0 | 0 | 0 | 19.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 51 | 24 | 0 | 12 | 12 | 0 | 40 | 17 | 27 | 275 | 0 | 0 | 33 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 80 | 195 | 0 | 0 | 185 | 29 | 183 | 30 | 87 | 50 | 136 | 29 | 17 | 0 | 46 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 20 | 0 | 0 | 6 | 5309.5 | 921 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 748.18 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 52.2 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 156 | 0 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 17 | 5133.88 | 10443.38 | 90.75
23:00 | 0 | 70 | 0 | 0 | 0 | 220 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 16 | 64 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 306 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 29 | 24 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 275 | 0 | 0 | 33 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 80 | 195 | 0 | 0 | 250 | 29 | 211 | 30 | 24 | 45 | 136 | 29 | 17 | 0 | 44 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 20 | 0 | 0 | 6 | 5248 | 920 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 760.27 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 52.2 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 155 | 0 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 0 | 4628.97 | 9876.97 | 90.74
Total KWH | 0 | 1048320 | 0 | 0 | 0 | 5492937 | 0 | 0 | 9320400 | 0 | 0 | 388800 | 630000 | 0 | 1441584 | 818400 | 0 | 518826 | 397244 | 1195200 | 498600 | 0 | 9406500 | 6967244 | 0 | 0 | 402453 | 442800 | 0 | 0 | 0 | 173103 | 183600 | 409200 | 527760 | 0 | 0 | 563291 | 52691 | 36480 | 0 | 12000 | 400364 | 676176 | 0 | 254400 | 304320 | 10340 | 959040 | 559525 | 448800 | 4960000 | 269309 | 0 | 397920 | 0 | 1194327 | 5333592 | 0 | 0 | 0 | 13287271 | 134190 | 1187394 | 1883490 | 4432727 | 0 | 0 | 3644000 | 694080 | 4794000 | 688032 | 844800 | 1111060 | 1972320 | 292320 | 413340 | 0 | 1063680 | 0 | 355245 | 44048 | 7561500 | 7866600 | 0 | 810504 | 715000 | 0 | 110448 | 3639436 | 447816 | 0 | 1851840 | 712128 | 0 | 452000 | 0 | 492840 | 1088400 | 199200 | 358080 | 10500 | 175310 | 115920 | 120145065 | 21192727 | 1150848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452880 | 24574550 | 0 | 15484773 | 0 | 0 | 206995 | 0 | 109632 | 0 | 891820 | 108960 | 111986 | 549389 | 625540 | 182563 | 291000 | 3999909 | 0 | 0 | 0 | 2592155 | 0 | 9828945.5 | 0 | 25020 | 85554 | 3780000 | 0 | 1339342 | 121959 | 1088620 | 0 | 0 | 20930.76 | 910800 | 3277 | 0 | 6262000 | 143688 | 2817000 | 5068650 | 0 | 0 | 13902545.45 | 266400 | 118190458.71 | 238335523.71