## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-02-2025 | during | 13-02-2025 | during | 13-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 250 | 252 | 240 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 403 | 371 | 400.75 | 400.75 | 351 | 351 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 292 | 251 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 98 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 30 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 14 | 19 | 22.5 | 22.5 | 22.5 | 22.5 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 60 | 124 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 54 | 17 | 54 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1846 | 2027 | 4802.87 | 4797.87 | 2574.04 | 2579.04
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 31 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 226 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 40 | 80 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 51 | 85 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 14 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 46 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.75 | 0 | 4.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 100 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 37 | 81 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 25 | 108 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 1 | 1 | 5 | 1 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 277 | 388 | 270 | 270 | 270 | 270 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1595 | 2194 | 2526.61 | 2552.86 | 2526.61 | 2552.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 203 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 360 | 360 | 356.56 | 356.56 | 356.56 | 356.56 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 30 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 194 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 88 | 124 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 16 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 144 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 106 | 70 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 50 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 19 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 51 | 0 | 62 | 0 | 62 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1305 | 1461.2 | 1924.53 | 1862.53 | 1892.76 | 1830.76
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-02-2025 | during | 13-02-2025 | during | 13-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 15 | 18 | 210 | 210 | 18 | 18 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 58 | 115 | 115 | 59 | 59 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.16 | 0 | 43 | 0 | 43 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 0 | 0 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 169.16 | 139.5 | 646.3 | 601.5 | 185.3 | 140.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 20 | 29 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 32 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 23 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 990 | 1004 | 1060 | 1060 | 1021 | 1021
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 922 | 875 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 25 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 210 | 316 | 410 | 410 | 410 | 410 | Commissioning work is in progress
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 83.37 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 582 | 593 | 1234.2 | 1234.2 | 617 | 617 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1797.37 | 1809 | 3576.2 | 3498.2 | 2749 | 2671
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 132 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 600 | 622 | 622 | 622 | 622 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1301.59 | 1299 | 1556.12 | 1555.12 | 1553 | 1552
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 33 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 21 | 36 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 214 | 214 | 0.01 | 0.01 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 320 | 413.79 | 413.79 | 320.01 | 320.01 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 30 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 92 | 92 | 92 | 92 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.14 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 764.64 | 763 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.72 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1430.5 | 1447.7 | 2498.34 | 2338.24 | 1750.58 | 1590.48
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 60 | 68 | 65 | 65 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 157 | 160 | 160 | 160 | 160 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 40 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 3.6 | 0 | 3.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 154 | 0 | 151.36 | 0 | 151.36 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 515.8 | 427 | 669.96 | 487 | 669.96 | 487
System Total |  |  |  |  | 27884.66 | 27150.742 | 10950.42 | 11808.4 | 19260.93 | 18753.32 | 14922.25 | 14424.64
Forecast Scenario (13-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9400 |  | 95.5 |  | 9500
|  |  |  | 1:00 | 8820 |  | 95.5 |  | 8920
|  |  |  | 2:00 | 8260 |  | 95.5 |  | 8360
|  |  |  | 3:00 | 7870 |  | 95.5 |  | 7970
|  |  |  | 4:00 | 7720 |  | 95.5 |  | 7820
|  |  |  | 5:00 | 7720 |  | 95.5 |  | 7820
|  |  |  | 6:00 | 8080 |  | 95.5 |  | 8180
|  |  |  | 7:00 | 9040 |  | 95.5 |  | 9140
|  |  |  | 8:00 | 10020 |  | 95.5 |  | 10120
|  |  |  | 9:00 | 10260 |  | 95.5 |  | 10360
|  |  |  | 10:00 | 10350 |  | 95.5 |  | 10450
|  |  |  | 11:00 | 10550 |  | 95.5 |  | 10650
|  |  |  | 12:00 | 11060 |  | 95.5 |  | 11160
|  |  |  | 13:00 | 11400 |  | 95.5 |  | 11500
|  |  |  | 14:00 | 11000 |  | 95.5 |  | 11100
|  |  |  | 15:00 | 10480 |  | 95.5 |  | 10580
|  |  |  | 16:00 | 10210 |  | 95.5 |  | 10310
|  |  |  | 17:00 | 10170 |  | 95.5 |  | 10270
|  |  |  | 18:00 | 10870 |  | 95.5 |  | 10970
|  |  |  | 18:30 | 11300 |  | 95.5 |  | 11400
|  |  |  | 19:00 | 11650 |  | 95.5 |  | 11750
|  |  |  | 19:30 | 11300 |  | 95.5 |  | 11400
|  |  |  | 20:00 | 11150 |  | 95.5 |  | 11250
|  |  |  | 21:00 | 10930 |  | 95.5 |  | 11030
|  |  |  | 22:00 | 10440 |  | 95.5 |  | 10540
|  |  |  | 23:00 | 9870 |  | 95.5 |  | 9970
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 11160.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11750.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11650.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 237.32 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:06 hrs on 13-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-02-2025 | [28 empty] | Date: | 12-02-2025 | [28 empty] | Date: | 12-02-2025 | [28 empty] | Date: | 12-02-2025 | [28 empty] | Date: | 12-02-2025 | [19 empty] | Date: | 12-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [19 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 0 | 0 | 0 | 220 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 247 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 272 | 0 | 0 | 33 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 20 | 197 | 0 | 0 | 200 | 29 | 183 | 30 | 0 | 40 | 136 | 29 | 17 | 0 | 42 | 0 | 0 | 0 | 290 | 320 | 0 | 32 | 30 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 21 | 0 | 0 | 6 | 4840 | 921 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 0 | 763.66 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 157 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 0 | 4553.16 | 9393.16 | 90.74
01:00 | 0 | 17 | 0 | 0 | 0 | 220 | 0 | 0 | 397 | 0 | 0 | 0 | 18 | 0 | 70 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 420 | 268 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 275 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 99 | 29 | 182 | 30 | 0 | 40 | 34 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 290 | 320 | 0 | 32 | 30 | 0 | 5 | 163 | 22 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 19 | 9 | 23 | 0 | 0 | 6 | 4511 | 921 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 0 | 4382.5 | 8893.5 | 90.74
02:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 293 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 277 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 62 | 29 | 200 | 30 | 0 | 45 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 280 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4206.5 | 921 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563 | 0 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 134 | 220 | 0 | 0 | 560 | 0 | 4015.5 | 8222 | 90.73
03:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 289 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 274 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 18 | 29 | 193 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 300 | 320 | 0 | 32 | 30 | 0 | 5 | 163 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4152.5 | 753 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 5 | 134 | 220 | 0 | 0 | 520 | 0 | 3826.5 | 7979 | 90.73
04:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 260 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 613 | 0 | 51 | 0 | 195 | 0 | 0 | 58 | 29 | 182 | 30 | 0 | 0 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4105 | 731 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 0 | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 5 | 134 | 220 | 0 | 0 | 520 | 0 | 3722.5 | 7827.5 | 90.73
05:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 270 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 276 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 58 | 29 | 182 | 30 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 23 | 0 | 81 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 4114 | 731 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 5 | 134 | 220 | 0 | 0 | 470 | 0 | 3699.5 | 7813.5 | 90.72
06:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 275 | 17 | 0 | 1 | 0 | 1 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 1 | 195 | 0 | 0 | 125 | 29 | 200 | 30 | 0 | 0 | 4 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 81 | 30 | 0 | 18 | 0 | 0 | 12 | 3 | 32 | 0 | 0 | 0 | 4217 | 731 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 599.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 0 | 35 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 134 | 220 | 0 | 0 | 490 | 0 | 3849.92 | 8066.92 | 90.72
07:00 | 0 | 34 | 0 | 0 | 0 | 226 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 17 | 72 | 17 | 0 | 370 | 300 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 0 | 40 | 23 | 35 | 277 | 17 | 0 | 18 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 1 | 51 | 46 | 185 | 0 | 0 | 143 | 29 | 203 | 30 | 0 | 0 | 50 | 0 | 17 | 0 | 44 | 0 | 3 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 5 | 120 | 17 | 0 | 81 | 30 | 0 | 18 | 0 | 9 | 56 | 9 | 30 | 0 | 0.7 | 6 | 4782.7 | 921 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 553 | 0 | 767.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 0 | 0.39 | 149 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.05 | 0 | 152 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 2 | 0.11 | 0 | 299 | 5 | 132 | 220 | 0 | 0 | 520 | 0 | 4263.21 | 9045.91 | 90.72
08:00 | 0 | 42 | 0 | 0 | 0 | 220 | 0 | 0 | 401 | 0 | 0 | 15 | 0 | 0 | 44 | 20 | 0 | 38 | 18 | 162 | 0 | 0 | 420 | 248 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 4 | 0 | 14 | 22 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 70 | 1 | 40 | 46 | 0 | 278 | 108 | 0 | 0 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 6 | 51 | 88 | 185 | 0 | 0 | 170 | 29 | 182 | 30 | 1 | 0 | 92 | 6 | 17 | 0 | 46 | 0 | 17 | 0 | 325 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 81 | 30 | 0 | 18 | 0 | 31 | 56 | 9 | 22 | 0 | 4.45 | 6 | 5370.45 | 908 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.85 | 577 | 0 | 761.21 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 12 | 0 | 52.2 | 22 | 0 | 3.54 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.32 | 0 | 155 | 0 | 80 | 1 | 65 | 0 | 0 | 0.6 | 15 | 0.12 | 0 | 307 | 4 | 132 | 220 | 0 | 0 | 570 | 17 | 4577.84 | 9948.29 | 90.71
09:00 | 0 | 50 | 0 | 0 | 0 | 220 | 0 | 0 | 397 | 0 | 0 | 17 | 0 | 0 | 70 | 32 | 0 | 55 | 17 | 162 | 0 | 0 | 420 | 255 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 11 | 0 | 14 | 22 | 0 | 0 | 35 | 15 | 21 | 0 | 0 | 0 | 24 | 0 | 70 | 70 | 2 | 40 | 87 | 2 | 274 | 53 | 0 | 17 | 0 | 87 | 226 | 0 | 0 | 0 | 612 | 12 | 51 | 125 | 184 | 0 | 0 | 235 | 29 | 182 | 27 | 16 | 0 | 155 | 9 | 17 | 0 | 48 | 0 | 18 | 0 | 280 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 17 | 0 | 81 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 22 | 1 | 8.69 | 4 | 5645.69 | 873 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.23 | 592 | 0 | 761.25 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 35 | 0 | 52.2 | 48 | 0 | 7.62 | 139 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.73 | 0 | 154 | 0 | 95 | 3 | 113 | 0 | 0 | 0.5 | 26 | 0.2 | 0 | 307 | 3 | 132 | 220 | 0 | 0 | 600 | 17 | 4825.73 | 10471.42 | 90.71
10:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 407 | 0 | 0 | 17 | 0 | 0 | 52 | 16 | 0 | 30 | 35 | 108 | 25 | 0 | 420 | 278 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 18 | 0 | 14 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 51 | 40 | 0 | 24 | 24 | 3 | 40 | 51 | 2 | 275 | 53 | 0 | 33 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 16 | 43 | 80 | 185 | 0 | 0 | 330 | 29 | 182 | 12 | 17 | 0 | 100 | 10 | 17 | 0 | 28 | 0 | 45 | 5 | 280 | 320 | 0 | 35 | 5 | 0 | 5 | 120 | 17 | 0 | 81 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 18 | 2 | 17.19 | 6 | 5449.19 | 921 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.22 | 598 | 0 | 757.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 73 | 0 | 21.44 | 134 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.54 | 0 | 152 | 0 | 53 | 10 | 49 | 0 | 0 | 1.4 | 67 | 0.52 | 0 | 250 | 5 | 132 | 220 | 0 | 0 | 600 | 17 | 4793.81 | 10243 | 90.71
11:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 36 | 36 | 0 | 30 | 35 | 72 | 25 | 0 | 450 | 273 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 25 | 0 | 14 | 10 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 51 | 40 | 0 | 24 | 24 | 4 | 40 | 34 | 2 | 274 | 17 | 0 | 33 | 0 | 45 | 226 | 0 | 0 | 0 | 612 | 18 | 43 | 80 | 175 | 0 | 0 | 370 | 29 | 194 | 30 | 16 | 0 | 104 | 9 | 17 | 0 | 88 | 0 | 57 | 16 | 300 | 320 | 0 | 32 | 15 | 0 | 5 | 163 | 17 | 0 | 81 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 16 | 2 | 30.23 | 6 | 5604.23 | 923 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.04 | 556 | 0 | 710.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 43 | 88 | 25 | 52.17 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.14 | 0 | 155 | 40 | 53 | 23 | 34 | 0 | 0 | 1.9 | 141 | 0.26 | 0 | 307 | 5 | 132 | 220 | 0 | 0 | 600 | 17 | 4961.48 | 10565.71 | 90.71
12:00 | 0 | 52 | 0 | 0 | 0 | 250 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 60 | 48 | 0 | 30 | 35 | 72 | 25 | 0 | 450 | 292 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 27 | 10 | 14 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 51 | 40 | 0 | 50 | 50 | 4 | 40 | 37 | 2 | 277 | 25 | 0 | 33 | 0 | 68 | 226 | 0 | 0 | 0 | 612 | 18 | 51 | 88 | 182 | 0 | 0 | 360 | 29 | 203 | 30 | 19 | 0 | 144 | 9 | 17 | 0 | 106 | 0 | 51 | 16 | 300 | 320 | 0 | 32 | 20 | 0 | 5 | 163 | 23 | 0 | 79 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 15 | 2 | 43.16 | 6 | 5905.16 | 922 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.37 | 582 | 0 | 764.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 43 | 96 | 30 | 56.72 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.14 | 0 | 158 | 60 | 70 | 30 | 40 | 0 | 0 | 3.8 | 154 | 0.59 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 17 | 5045.26 | 10950.42 | 90.7
13:00 | 0 | 52 | 0 | 0 | 0 | 250 | 0 | 0 | 406 | 0 | 0 | 17 | 0 | 0 | 70 | 48 | 0 | 33 | 35 | 54 | 25 | 0 | 450 | 273 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 26 | 17 | 14 | 22 | 0 | 0 | 35 | 45 | 10 | 0 | 2 | 48 | 60 | 0 | 70 | 70 | 3 | 40 | 69 | 2 | 276 | 53 | 0 | 33 | 0 | 93 | 224 | 0 | 0 | 0 | 612 | 17 | 51 | 105 | 182 | 0 | 0 | 370 | 29 | 182 | 27 | 34 | 0 | 177 | 9 | 17 | 0 | 96 | 0 | 58 | 47 | 305 | 400 | 0 | 32 | 5 | 0 | 5 | 163 | 23 | 0 | 80 | 30 | 0 | 18 | 0 | 20 | 59 | 9 | 15 | 2 | 44.14 | 6 | 6211.14 | 921 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.11 | 604 | 0 | 760.55 | 0 | 0 | 0 | 0 | 22 | 0 | 49 | 0 | 23 | 43 | 96 | 30 | 55.88 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 5.11 | 0 | 163 | 65 | 94 | 30 | 70 | 0 | 0 | 4.5 | 159 | 0.28 | 0 | 282 | 5 | 130 | 220 | 0 | 0 | 622 | 17 | 5138.43 | 11349.57 | 90.7
14:00 | 0 | 52 | 0 | 0 | 0 | 250 | 0 | 0 | 406 | 0 | 0 | 17 | 0 | 0 | 70 | 64 | 0 | 40 | 17 | 54 | 25 | 0 | 420 | 306 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 22 | 17 | 20 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 1 | 51 | 63 | 0 | 24 | 38 | 3 | 40 | 92 | 2 | 275 | 17 | 0 | 33 | 0 | 105 | 223 | 0 | 0 | 0 | 580 | 16 | 51 | 80 | 182 | 0 | 0 | 357 | 29 | 200 | 27 | 34 | 0 | 181 | 9 | 17 | 0 | 74 | 0 | 52 | 39 | 305 | 370 | 0 | 32 | 5 | 0 | 5 | 140 | 23 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 15 | 2 | 36.77 | 6 | 5957.77 | 922 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.34 | 610 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 23 | 43 | 88 | 30 | 50.22 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 4.37 | 2.5 | 163 | 65 | 73 | 26 | 34 | 0 | 0 | 4.2 | 134 | 0.51 | 0 | 250 | 5 | 100 | 220 | 0 | 0 | 622 | 17 | 4933.14 | 10890.91 | 90.69
15:00 | 0 | 52 | 0 | 0 | 0 | 247 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 70 | 64 | 0 | 40 | 17 | 54 | 25 | 0 | 450 | 274 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 17 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 51 | 62 | 0 | 24 | 38 | 2 | 40 | 85 | 2 | 275 | 17 | 0 | 33 | 0 | 51 | 223 | 0 | 0 | 0 | 612 | 12 | 40 | 80 | 182 | 0 | 0 | 365 | 29 | 182 | 27 | 34 | 0 | 183 | 8 | 17 | 0 | 72 | 0 | 40 | 39 | 315 | 320 | 0 | 32 | 8 | 0 | 5 | 163 | 23 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 14 | 1 | 27.49 | 6 | 5846.49 | 923 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 608 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 23 | 43 | 70 | 30 | 40.94 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 3.49 | 2.5 | 179 | 65 | 70 | 19 | 34 | 0 | 0 | 2.9 | 101 | 0.37 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 17 | 4909.2 | 10755.69 | 90.69
16:00 | 0 | 52 | 0 | 0 | 0 | 246 | 0 | 0 | 395 | 0 | 0 | 35 | 0 | 0 | 58 | 70 | 0 | 40 | 17 | 54 | 25 | 0 | 450 | 261 | 0 | 0 | 40 | 22 | 0 | 0 | 0 | 10 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 51 | 72 | 0 | 24 | 38 | 1 | 40 | 34 | 2 | 275 | 17 | 0 | 33 | 0 | 51 | 222 | 0 | 0 | 0 | 612 | 7 | 40 | 30 | 182 | 0 | 0 | 350 | 29 | 183 | 30 | 47 | 0 | 100 | 9 | 17 | 0 | 72 | 0 | 22 | 39 | 310 | 320 | 0 | 32 | 15 | 0 | 5 | 163 | 23 | 0 | 81 | 30 | 0 | 18 | 0 | 32 | 58 | 9 | 15 | 1 | 15.23 | 6 | 5645.23 | 923 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.95 | 596 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 23 | 16 | 43 | 30 | 22.92 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 1.9 | 2.5 | 130 | 66 | 72 | 10 | 34 | 0 | 0 | 1.5 | 56 | 0.21 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 610 | 17 | 4705.98 | 10351.21 | 90.69
17:00 | 0 | 52 | 0 | 0 | 0 | 247 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 51 | 98 | 2 | 40 | 35 | 54 | 25 | 0 | 450 | 295 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 2 | 17 | 14 | 22 | 0 | 0 | 35 | 15 | 2 | 0 | 2 | 51 | 78 | 3 | 24 | 38 | 0 | 40 | 34 | 3 | 275 | 17 | 0 | 33 | 1 | 51 | 222 | 0 | 0 | 0 | 613 | 0 | 40 | 30 | 138 | 0 | 0 | 280 | 29 | 195 | 27 | 54 | 0 | 51 | 9 | 17 | 17 | 68 | 16 | 6 | 39 | 320 | 320 | 0 | 35 | 12 | 0 | 5 | 163 | 23 | 0 | 32 | 30 | 0 | 18 | 0 | 35 | 58 | 9 | 16 | 0 | 3.98 | 6 | 5535.98 | 922 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.85 | 618 | 0 | 762 | 0 | 0 | 0 | 0 | 13 | 0 | 49 | 25 | 23 | 16 | 12 | 30 | 4.82 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.39 | 2.5 | 167 | 67 | 72 | 3 | 34 | 0 | 0 | 0.6 | 15 | 0.29 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 600 | 17 | 4687.45 | 10223.43 | 90.69
18:00 | 0 | 52 | 0 | 0 | 0 | 200 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 52 | 133 | 15 | 42 | 35 | 54 | 25 | 0 | 450 | 273 | 0 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 50 | 29 | 0 | 1 | 82 | 78 | 17 | 100 | 100 | 0 | 40 | 41 | 3 | 322 | 53 | 0 | 33 | 15 | 75 | 224 | 0 | 0 | 0 | 612 | 0 | 40 | 53 | 190 | 0 | 0 | 365 | 29 | 182 | 30 | 104 | 0 | 70 | 18 | 17 | 42 | 72 | 25 | 0 | 39 | 300 | 320 | 0 | 32 | 12 | 0 | 5 | 120 | 24 | 0 | 82 | 30 | 0 | 18 | 0 | 38 | 59 | 9 | 16 | 0 | 0 | 4 | 6129 | 923 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 762 | 0 | 0 | 33 | 0 | 46 | 0 | 88 | 60 | 33 | 47 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 152 | 67 | 95 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 130 | 180 | 0 | 0 | 600 | 17 | 4941.5 | 11070.5 | 90.69
19:00 | 0 | 52 | 0 | 0 | 0 | 252 | 0 | 0 | 371 | 0 | 0 | 35 | 0 | 0 | 124 | 98 | 95 | 55 | 55 | 54 | 25 | 0 | 450 | 251 | 0 | 0 | 30 | 22 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 100 | 46 | 0 | 1 | 85 | 80 | 17 | 100 | 100 | 0 | 40 | 81 | 14 | 388 | 108 | 0 | 31 | 25 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 124 | 194 | 0 | 0 | 360 | 29 | 182 | 30 | 115 | 0 | 120 | 28 | 17 | 50 | 70 | 52.2 | 0 | 39 | 300 | 320 | 0 | 32 | 29 | 0 | 5 | 163 | 24 | 0 | 83 | 30 | 0 | 18 | 0 | 54.5 | 58 | 9 | 18 | 0 | 0 | 0 | 6825.7 | 875 | 316 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 0 | 763 | 0 | 0 | 33 | 0 | 70 | 0 | 88 | 50 | 36 | 52.2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 5.5 | 157 | 68 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 7 | 132 | 220 | 0 | 0 | 600 | 17 | 4982.7 | 11808.4 | 90.68
19:30 | 0 | 52 | 0 | 0 | 0 | 252 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 0 | 110 | 98 | 45 | 55 | 55 | 54 | 25 | 0 | 450 | 287 | 0 | 0 | 30 | 22 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 50 | 50 | 0 | 0 | 85 | 80 | 0 | 50 | 100 | 0 | 40 | 92 | 10 | 470 | 59 | 0 | 46 | 25 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 195 | 0 | 0 | 360 | 29 | 188 | 30 | 115 | 0 | 68 | 28 | 17 | 34 | 68 | 16 | 0 | 39 | 315 | 320 | 0 | 32 | 29 | 0 | 5 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 54.5 | 58 | 9 | 18 | 0 | 0 | 0 | 6581.5 | 875 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 759 | 0 | 0 | 33 | 0 | 70 | 0 | 88 | 35 | 36 | 52.2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 5.5 | 130 | 68 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 610 | 17 | 4981.7 | 11563.2 | 90.68
20:00 | 0 | 52 | 0 | 0 | 0 | 252 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 0 | 109 | 98 | 15 | 55 | 55 | 54 | 25 | 0 | 450 | 271 | 0 | 0 | 32 | 22 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 50 | 58 | 0 | 0 | 68 | 80 | 0 | 50 | 50 | 0 | 40 | 99 | 17 | 470 | 53 | 0 | 43 | 25 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 195 | 0 | 0 | 360 | 29 | 182 | 30 | 115 | 0 | 68 | 28 | 17 | 34 | 68 | 16 | 0 | 39 | 295 | 320 | 0 | 35 | 29 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 54.5 | 58 | 9 | 19 | 0 | 0 | 0 | 6461.5 | 875 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 761 | 0 | 0 | 33 | 0 | 35 | 0 | 88 | 35 | 38 | 52.2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 5.5 | 125 | 68 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 610 | 17 | 4951.7 | 11413.2 | 90.67
21:00 | 0 | 52 | 0 | 0 | 0 | 252 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 0 | 88 | 98 | 0 | 55 | 17 | 54 | 25 | 0 | 450 | 280 | 0 | 0 | 32 | 22 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 50 | 57 | 0 | 0 | 68 | 80 | 0 | 50 | 50 | 0 | 40 | 110 | 29 | 470 | 53 | 0 | 40 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 195 | 0 | 0 | 360 | 29 | 182 | 30 | 115 | 0 | 68 | 29 | 14 | 0 | 66 | 0 | 0 | 39 | 290 | 320 | 0 | 36 | 29 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 25 | 59 | 9 | 20 | 0 | 0 | 0 | 6305 | 922 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623 | 0 | 761 | 0 | 0 | 33 | 0 | 0 | 0 | 88 | 0 | 36 | 52.2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 5.5 | 164 | 70 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 220 | 0 | 0 | 622 | 17 | 4948.7 | 11253.7 | 90.67
22:00 | 0 | 52 | 0 | 0 | 0 | 256 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 0 | 68 | 98 | 0 | 55 | 0 | 17 | 22 | 0 | 450 | 285 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 50 | 0 | 40 | 110 | 23 | 472 | 0 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 613 | 0 | 51 | 70 | 195 | 0 | 0 | 360 | 29 | 182 | 30 | 79 | 0 | 68 | 29 | 14 | 0 | 60 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 29 | 0 | 5 | 120 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 18 | 0 | 0 | 0 | 5743 | 922 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 759 | 0 | 0 | 33 | 0 | 0 | 0 | 88 | 0 | 35 | 52.2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 160 | 72 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 220 | 0 | 0 | 622 | 17 | 4958.7 | 10701.7 | 90.67
23:00 | 0 | 52 | 0 | 0 | 0 | 256 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 98 | 0 | 55 | 0 | 17 | 22 | 0 | 450 | 273 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 40 | 110 | 37 | 364 | 0 | 0 | 19 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 195 | 0 | 0 | 357 | 29 | 184 | 30 | 0 | 0 | 68 | 29 | 14 | 0 | 58 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 18 | 0 | 0 | 0 | 5453 | 923 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 158 | 72 | 74 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 134 | 220 | 0 | 0 | 622 | 17 | 4828.5 | 10281.5 | 90.66
Total KWH | 0 | 967680 | 0 | 0 | 0 | 5605063 | 0 | 0 | 9216000 | 0 | 0 | 388800 | 33120 | 0 | 1122048 | 1188000 | 176389 | 758375 | 396416 | 1190880 | 479160 | 0 | 9963000 | 6763171 | 0 | 0 | 412600 | 544700 | 0 | 0 | 0 | 160065 | 172800 | 357600 | 501120 | 0 | 0 | 688745 | 572073 | 288960 | 0 | 4800 | 737531 | 934922 | 42441 | 685440 | 821760 | 23520 | 980604 | 1298030 | 420480 | 7410909.09 | 717600 | 0 | 569760 | 90189 | 1515491 | 5274727 | 0 | 0 | 0 | 14765453 | 123255 | 1152628 | 1478690 | 4466182 | 0 | 0 | 6204000 | 682080 | 4653000 | 692712 | 838080 | 200910 | 2079360 | 294840 | 403790 | 134520 | 1394880 | 101376 | 347927 | 424288 | 7304000 | 7782800 | 0 | 798048 | 544000 | 0 | 114384 | 3754227 | 498600 | 0 | 1910400 | 717120 | 0 | 452000 | 0 | 542520 | 1100400 | 187200 | 457920 | 12450 | 233660 | 81120 | 130403789.09 | 21092363 | 5414688 | 0 | 12480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405360 | 14334550 | 0 | 17256249 | 0 | 0 | 160070 | 0 | 308256 | 0 | 822848 | 290592 | 253165 | 744538 | 649590 | 374558 | 319504 | 1695727 | 0 | 0 | 0 | 0 | 0 | 9328800 | 0 | 27000 | 47736 | 3807000 | 802909 | 1429631 | 154695 | 950332 | 0 | 0 | 22675.44 | 877680 | 3049 | 21024 | 6764000 | 140781 | 3118000 | 5292390 | 0 | 0 | 14274909.09 | 295200 | 111492349.53 | 241896138.62

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10950.42 | MW | 12:00 Hr. | Energy Generated |  |  | 241.8961 |  | MKWHr.
| Day Peak Demand |  |  | 11013.42 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.956 |  | MKWHr.
| Evening Peak Generation |  |  | 11808.4 | MW | 19:00 Hr. | Energy Demand |  |  | 242.8521 |  | MKWHr.
| Evening Peak Demand |  |  | 11871.4 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28 |  | °C
| Minimum Generation of the Day |  |  | 7813.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 816.31 |  | MMCFD
| Maximum Generation of the Day |  |  | 11808.4 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.7551 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.4298 | 0 | 6.8071 | 0 | 0 | 0.16007 | 0 | 0 | 40.397 | Gas | 106.9519 | Gas | 391550328.27
| Chattogram Zone |  |  | 5.6952 | 22.1764 | 8.9629 | 0 | 0.9806 | 0.14677 | 0 | 0.0048 | 37.9667 | Coal | 62.1597 | Coal | 452396211.7369
| Cumilla Zone |  |  | 18.4553 | 0 | 5.3512 | 0 | 0 | 0.34793 | 1.3949 | 0 | 25.5493 | HFO | 28.6951 | HFO | 529865580.62
| Mymensingh Zone |  |  | 0.45792 | 0 | 1.9112 | 0 | 0 | 0.24611 | 0 | 0 | 2.6153 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8756 | Hydro | 0.9806 | Hydro | 98060.4
| Khulna Zone |  |  | 5.4147 | 14.3346 | 0.01248 | 0 | 0 | 0.40536 | 21.0924 | 0 | 41.2594 | Solar | 3.3604 | Solar | 52238627.514
| Barishal Zone |  |  | 8.5512 | 21.0389 | 0.31622 | 0 | 0 | 0.003049 | 0 | 0 | 29.9094 | Import | 39.7435 | Import | 207813134.65
| Rajshahi Zone |  |  | 11.0723 | 0 | 2.954 | 0 | 0 | 0.99609 | 17.2562 | 0 | 32.2786 | Wind | 0.0048 | Wind | 74880
| Rangpur Zone |  |  | 0 | 4.6099 | 2.38 | 0 | 0 | 1.0551 | 0 | 0 | 8.0449
| Total |  |  | 106.9519 | 62.1597 | 28.6951 | 0 | 0.9806 | 3.3604 | 39.7435 | 0.0048 | 241.8961
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 391550328.27 |  | Hydro | 98060.4
|  |  |  | Coal | 452396211.7369 |  | Solar | 52238627.514
|  |  |  | HFO | 529865580.62 |  | Import | 207813134.65
|  |  |  | HSD | 0 |  | Wind | 74880
[5 empty] | Total: | 163,40,36,823 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0924 | Peak Hr Flow | 875.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8426234000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.2562 | Peak Hr Flow | 763.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 552 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3949 | Peak Hr Flow | 70.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 870 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.7435 | Peak Hr Flow | 1708.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4373
|  |  |  | Chattogram |  | 0 |  | 1163
|  |  |  | Cumilla |  | 0 |  | 966
|  |  |  | Mymensingh |  | 60 |  | 981
|  |  |  | Sylhet |  | 0 |  | 391
|  |  |  | Khulna |  | 0 |  | 1298
|  |  |  | Barishal |  | 0 |  | 314
|  |  |  | Rajshahi |  | 0 |  | 1135
|  |  |  | Rangpur |  | 0 |  | 782
|  |  |  | Total |  | 60 |  | 11403
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 08:11 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Overcurrent protection relay. relays Due | [7 empty] | 9.5MW load
|  |  | to Due to 33kV outgoing feeder(Kushumhati-8) breaker insulation failure. | [7 empty] | interrup.
| 08:01 | 08:12 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent protection relay. relays Due | [7 empty] | 9.5MW load
|  |  | to Due to 33kV outgoing feeder(Kusumhati-8) breaker insulation failure. | [7 empty] | interrup.
| 08:23 | 19:04 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance.(Deep Cleaning)
| 08:24 | 16:46 | Gopalganj-Madhumati 132kV Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to Yearly
maintenance
| 08:26 | 15:51 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance work.
|  | 08:29 | Mirzapur 132/33kV S/S Transformer-01(E05) LT is restored.
| 08:31 | 16:22 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Scheduled S/D Due to Yearly
Maintenance
| 08:32 | 16:20 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Dead line checking.
| 08:34 | 15:43 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D
| 08:41 | 16:37 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end.
| 08:41 | 17:50 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
Works at Fenchuganj End and from Fenchuganj 230/132/33kV end Due to Deadline checking
| 08:51 |  | Aminbazar-Meghnaghat 400kV Ckt-1 Forced S/D from Meghnaghat 400/230kV end Due to Shutdown | [7 empty] | 100.0MW load
|  |  | for maintenance work. | [7 empty] | interrup.
Meghnaghat
400/230kV end
| 08:52 | 20:34 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to Shutdown | [7 empty] | 100.0MW load
|  |  | for maintenance work. | [7 empty] | interrup.
Meghnaghat
400/230kV end
| 08:53 | 17:45 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project work
| 09:01 | 16:30 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-01 Scheduled S/D Due to Yearly
Maintenance
| 09:02 | 16:31 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
Maintenance
| 09:04 | 16:11 | Anowara-Sikalbaha 230 kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end.
| 09:09 | 13:41 | GPH 230/33kV S/S Transformer-01(D05) HT Scheduled S/D Due to maintenance work for gph
| 09:13 | 17:48 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D
| 09:13 | 17:48 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D
| 09:14 | 17:48 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Project Work S/D Due to Project Work(Tower
Painting)
| 09:14 | 17:48 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Project Work S/D Due to Project Work(Tower Painting)
| 09:15 | 17:44 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Project
Work(Tower Painting)
| 09:15 | 17:45 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Project
Work(Tower Painting)
| 09:25 | 16:33 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to Schedule Shutdown
| 09:26 |  | Bhulta 132/33kV S/S GT1 HT Forced S/D Due to GT-1 winding temperature meter change. | [7 empty] | 15.0MW load
interrup.
| 09:54 | 17:58 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Interlock update work.
| 09:54 | 17:58 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Interlock update work
| 09:54 |  | Rangpur-Saidpur 132kV Ckt-2 Project Work S/D from Saidpur 132/33kV end Due to As the
instruction of ALDC, Bogura (499264) and from Rangpur 132/33kV end Due to Breaker pole
replace.
| 09:58 | 10:10 | Cumilla(S) 132/33kV S/S TR-4 LT Scheduled S/D | [7 empty] | 22.0MW load
interrup.
| 09:58 | 10:10 | Cumilla(S) 132/33kV S/S TR-4 HT Scheduled S/D | [7 empty] | 22.0MW load
interrup.
| 10:13 | 11:01 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Forced S/D Due to Emergency redhot
maintenance work.
| 10:14 | 10:59 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Forced S/D Due to Emergency redhot
maintenance work.
| 10:18 | 10:25 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 10:18 | 21:05 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end.
| 10:18 |  | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to None | [7 empty] | 30.0MW load
interrup.
| 10:19 |  | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to None | [7 empty] | 30.0MW load
interrup.
| 10:19 | 10:25 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 11:09 | 15:41 | New Tongi-Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 11:26 | 12:54 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Forced S/D Due to 33 KV CT emergency
maintenance
| 11:26 | 12:52 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Forced S/D Due to 33 KV CT emergency
maintenance.
| 11:38 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
|  | 11:40 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT is restored.
|  | 11:40 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT is restored.
| 11:41 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Oil sentrifusing &
protection test by SPMD
| 11:42 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Oil sentrifusing &
protection test by SPMD
| 11:51 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 12:00 |  | Day Peak generation = 10,951MW
| 12:54 |  | Madunaghat 132/33kV S/S TR-1(507T) HT Scheduled S/D Due to Oil leakage maintenance
| 12:54 |  | Madunaghat 132/33kV S/S TR-1(507T) LT Scheduled S/D Due to Oil leakage maintenance
| 13:10 | 14:33 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to Emergency
maintenance work at 33KV CT R phase
| 13:10 | 14:34 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D Due to Emergency
maintenance work at 33KV CT R phase.
| 14:14 | 15:34 | Tongi 230/132/33kV S/S T-1 HT Scheduled S/D Due to Shutdown taken by DESCO.
|  | 14:16 | Keranigonj 230/132/33kV S/S TR-1 HT is restored.
|  | 14:17 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
|  | 15:22 | Aminbazar-Kaliakoir 230kV Ckt-2 is restored.
|  | 16:10 | Bhulta-Rampura 230 kV Ckt-4 is restored.
|  | 16:28 | Kabirpur -Tongi 132kV Ckt-1 is restored.
|  | 20:34 | Aminbazar-Meghnaghat 400kV Ckt-2 is restored.
| 05:00 |  | Minimum Generation is 8223 MW
| 07:12 |  | Chowmuhani 132/33kV S/S TR2 Forced S/D Due to REB Sader PBS Feeder B-Phase Red HOT Maint | [7 empty] | 25.0MW load
|  |  | Works under Tr-2 Bus. | [7 empty] | interrup.
| 07:27 |  | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Bhulta 400/230kV end. and from Rampura
230/132kV end Due to Dead line check
| 07:37 |  | Keranigonj 230/132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance and
renovation work.
| 07:38 |  | Keranigonj 230/132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintence and renovation
work.
| 07:58 |  | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 252 | 5605063 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 371 | 9216000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9963000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 251 | 6763171 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 758375 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 388800 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 98 | 1188000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 396416 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 30 | 412600 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 357600 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 501120 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 479160 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 544700 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 176389 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 124 | 1122048 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 967680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1190880 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160065 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 33120 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 172800 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2027 | 40396987
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 90189 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 123255 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 31 | 569760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 980604 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5274727 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1515491 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 80 | 934922 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 737531 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 685440 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 14 | 420480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 46 | 288960 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 572073 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 42441 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 81 | 1298030 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 821760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 688745 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 108 | 717600 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14765453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 1 | 4800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 388 | 7410909.09 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2194 | 37966690.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4653000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 360 | 6204000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 692712 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 682080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 194 | 4466182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1152628 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 124 | 1478690 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 424288 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 200910 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2079360 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 70 | 1394880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 101376 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 403790 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 50 | 134520 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 294840 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 838080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 347927 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1461.2 | 25549263
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 457920 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 187200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1100400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 233660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 81120 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 542520 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 139.5 | 2615270
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 29 | 544000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3754227 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 798048 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 114384 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 717120 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1910400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 452000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 498600 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7304000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7782800 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1004 | 23875579
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 875 | 21092363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 25 | 12480 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 316 | 5414688 | Commissioning work is in progress
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 405360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 593 | 14334550 | coal available to run both units upto 12/02/25
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1809 | 41259441
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 21024 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 140781 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 3118000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 14274909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5292390 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 295200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6764000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3049 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1299 | 29909353.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 33 | 160070 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 36 | 253165 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 1695727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 320 | 9328800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 374558 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 47736 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 744538 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 822848 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 308256 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 290592 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 763 | 17256249 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 319504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 649590 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1447.7 | 32278633
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 68 | 802909 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3807000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 950332 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 22675.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1429631 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 154695 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 877680 | -
Rangpur Area Total |  |  |  |  | 950 | 427 | 8044922.44
Eastern Grid Total |  |  |  |  | 16856.242 | 6825.7 | 130403789.09
Western Grid Total |  |  |  |  | 10294.5 | 4982.7 | 111492349.53
National Grid Total |  |  |  |  | 27150.742 | 11808.4 | 241896138.62
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7813.32 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3528.8 | MW
i) Dhaka area |  |  | 4372.82 |  | MW | i) Khulna area |  |  |  | 1297.9 | MW
ii) Chattogram area |  |  | 1163 |  | MW | ii) Barishal area |  |  |  | 313.5 | MW
iii) Cumilla area |  |  | 965.5 |  | MW | iii) Rajshahi area |  |  |  | 1135.4 | MW
iv) Mymensingh area |  |  | 921 |  | MW | iv) Rangpur area |  |  |  | 782 | MW
v) Sylhet area |  |  | 391 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11342.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 59 | 18:00 | 133 | Postogola | 43 | 13:00
2 | AKSML | 20 | 18:00 | 68 | Jamalpur | 92 | 18:00 | 134 | Purbachal | 16 | 13:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 114 | 13:00 | 135 | Purbasadipur | 123 | 12:00
4 | Agargaon | 81 | 13:00 | 70 | Jhenaidah | 99 | 18:30 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 74 | 18:00 | 71 | Joydebpur | 150 | 18:30 | 137 | Rahim | 32 | 10:00
6 | Amnura | 50 | 08:00 | 72 | Joypurhat | 54 | 08:00 | 138 | Rajbari | 63 | 18:30
7 | Ashuganj | 76 | 13:00 | 73 | Juldah | 12 | 00:00 | 139 | Rajendrapur | 124 | 18:30
8 | BSRM | 201 | 23:00 | 74 | KSRM | 27 | 09:00 | 140 | Rajshahi | 68 | 21:00
9 | Bagerhat | 65 | 19:30 | 75 | Kabirpur | 262 | 18:00 | 141 | Rajshahi-230 | 70 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 56 | 18:00 | 142 | Ramganj | 96 | 18:00
11 | Bakulia | 76 | 18:30 | 77 | Kallyanpur | 69 | 12:00 | 143 | Rampur | 29 | 18:00
12 | Banani | 21 | 13:00 | 78 | Kalurghat | 34 | 15:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 10 | 14:00 | 79 | Kamrangirchar | 64.4 | 13:00 | 145 | Rangpur | 113 | 14:00
14 | Barapukuria | 58 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 5.6 | 15:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 94 | 13:00 | 147 | SSM | 7 | 23:00
16 | Barishal | 85 | 13:00 | 82 | Keranigonj | 61 | 20:00 | 148 | Saidpur | 104 | 09:00
17 | Barishal-230 | 80 | 18:30 | 83 | Khagrachori | 26 | 18:30 | 149 | Satkhira | 98 | 08:00
18 | Baroaulia | 55 | 11:00 | 84 | Khulna | 64 | 13:00 | 150 | Satmasjid | 80 | 14:00
19 | Baroirhat | 50 | 18:30 | 85 | Khulshi | 147 | 19:30 | 151 | Savar | 190 | 11:00
20 | Bashundhara | 128 | 13:00 | 86 | Kishoreganj | 106 | 19:30 | 152 | SevenRings | 6.77 | 17:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 176 | 18:00 | 153 | ShahCement | 33 | 02:00
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 28 | 18:00 | 154 | Shahjadpur | 65 | 18:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 69 | 08:00 | 155 | Shahjibazar | 97 | 18:30
24 | Bhaluka | 114 | 09:00 | 90 | Kushtia | 103 | 18:30 | 156 | Shahmirpur | 44 | 00:00
25 | Bhandaria | 36 | 21:00 | 91 | Lalbag | 68 | 14:00 | 157 | Shariatpur | 55 | 21:00
26 | Bhangura | 33 | 18:30 | 92 | Lalmonirhat | 52 | 08:00 | 158 | Sherpur | 120 | 23:00
27 | Bheramara(GK) | 43 | 18:30 | 93 | MI_Cement | 18 | 13:00 | 159 | Shikalbaha | 23 | 18:00
28 | Bhulta | 252 | 00:00 | 94 | Madanganj | 21 | 13:00 | 160 | Shitalakhya | 67.3 | 12:00
29 | Bog-Sherpur | 68 | 09:00 | 95 | Madaripur | 69 | 19:00 | 161 | Sholosohor | 35 | 15:00
30 | Bogura | 113 | 19:30 | 96 | Madartek | 62.71 | 13:00 | 162 | Shyampur | 152 | 10:00
31 | Borhanuddin | 56 | 21:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Siddhirganj | 106 | 12:00
32 | Brahmanbaria | 110 | 18:00 | 98 | Magura | 48 | 18:30 | 164 | Sirajganj | 92 | 19:00
33 | Cantonment | 98 | 13:00 | 99 | Mahasthangarh | 60 | 08:00 | 165 | Sonargaon | 102 | 18:00
34 | Chandpur | 49 | 20:00 | 100 | Manikganj | 110 | 18:30 | 166 | Sreemongol | 43 | 19:00
35 | Chandraghona | 27 | 18:00 | 101 | Maniknagar | 56 | 13:00 | 167 | Sreepur | 75 | 12:00
36 | Chapai | 71 | 08:00 | 102 | Matarbari | 37 | 18:00 | 168 | Srinagar | 32.89 | 14:00
37 | Charsaidpur | 36 | 00:00 | 103 | Matuail | 64 | 12:00 | 169 | Sunamganj | 40 | 19:00
38 | Chauddagram | 48 | 13:00 | 104 | Millgate | 76 | 16:00 | 170 | Sylhet | 24 | 18:30
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 116 | 19:00 | 171 | Sylhet-132 | 83 | 18:30
40 | Chowmuhani | 142 | 18:00 | 106 | Mirsorai | 9 | 18:30 | 172 | TK | 23.2 | 18:30
41 | Chuadanga | 75 | 18:30 | 107 | Mirzapur | 41 | 14:00 | 173 | Tangail | 158 | 13:00
42 | Coxsbazar | 114 | 18:30 | 108 | Mithapukur | 50 | 18:30 | 174 | Thakurgaon | 85 | 18:30
43 | Cumilla(N) | 146 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 118 | 11:00
44 | Cumilla(S) | 138 | 12:00 | 110 | Mogbazar | 105.4 | 14:00 | 176 | Ullahpara | 27 | 18:30
45 | Daudkandi | 106 | 13:00 | 111 | Mongla | 40 | 14:00 | 177 | Ullon | 38 | 13:00
46 | Dhaka | 34 | 13:00 | 112 | Motijheel | 29 | 13:00 | 178 | Uttara | 66 | 13:00
47 | Dhamrai | 110 | 11:00 | 113 | Muktagacha | 27 | 07:00 | 179 | UttaraNew | 35 | 18:30
48 | Dhanmondi | 111 | 13:00 | 114 | Munshiganj | 69 | 20:00 | 180 | Zigatola | 66 | 11:00
49 | Dohazari | 79 | 18:00 | 115 | Muradnagar | 0 | 18:00
50 | Faridpur | 109 | 18:30 | 116 | Mymensingh | 166 | 13:00
51 | Fatullah | 75 | 12:00 | 117 | Naogaon | 110 | 08:00
52 | Fenchuganj | 28 | 18:00 | 118 | Narail | 42 | 18:30
53 | Feni | 82 | 18:00 | 119 | Narinda | 65 | 12:00
54 | GPH | 11 | 23:00 | 120 | Narshingdi | 161 | 19:00
55 | Ghatail | 54 | 07:00 | 121 | Natore | 111 | 18:30
56 | Ghorashal | 11 | 12:00 | 122 | Nawabganj | 32.6 | 13:00
57 | Ghorashal-230 | 61 | 22:00 | 123 | Netrakona | 130 | 08:00
58 | Goalpara | 24 | 13:00 | 124 | New | 87 | 15:00
59 | Gollamari | 62 | 13:00 | 125 | Niamatpur | 88 | 08:00
60 | Gopalganj | 79.6 | 18:30 | 126 | Noapara | 38 | 19:00
61 | Gulshan | 86 | 13:00 | 127 | PHP | 10 | 15:00
62 | Halishahar | 49 | 15:00 | 128 | Pabna | 68 | 18:30
63 | HaripurSBU | 172 | 10:00 | 129 | Palashbari | 95 | 13:00
64 | Hasnabad | 101 | 13:00 | 130 | Panchagarh | 47 | 18:30
65 | Hathazari | 60 | 13:00 | 131 | Patuakhali | 54 | 21:00
66 | Ishurdi | 63 | 19:00 | 132 | Payra | 20 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9393.16 | 0 |  | 9393.16
1:00 | 8893.5 | 0 |  | 8893.5
2:00 | 8222 | 0 |  | 8222
3:00 | 7979 | 0 |  | 7979
4:00 | 7827.5 | 0 |  | 7827.5
5:00 | 7813.5 | 0 |  | 7813.5
6:00 | 8066.92 | 0 |  | 8066.92
7:00 | 9045.91 | 34 |  | 9081.91
8:00 | 9948.29 | 81 |  | 10033.29
9:00 | 10471.42 | 78 |  | 10553.42
10:00 | 10243 | 86 |  | 10333
11:00 | 10565.71 | 54 |  | 10621.71
12:00 | 10950.42 | 60 |  | 11013.42
13:00 | 11349.57 | 89 |  | 11442.57
14:00 | 10890.91 | 74 |  | 10967.91
15:00 | 10755.69 | 70 |  | 10828.69
16:00 | 10351.21 | 55 |  | 10408.21
17:00 | 10223.43 | 45 |  | 10270.43
18:00 | 11070.5 | 65 |  | 11138.5
19:00 | 11808.4 | 60 |  | 11871.4
19:30 | 11563.2 | 55 |  | 11620.2
20:00 | 11413.2 | 55 |  | 11470.2
21:00 | 11253.7 | 50 |  | 11305.7
22:00 | 10701.7 | 0 |  | 10701.7
23:00 | 10281.5 | 0 |  | 10281.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4840 | 4553.16 | 9393.16 | DAILY GENERATION CURVE
00:30 | 4675.5 | 4467.83 | 9143.33
01:00 | 4511 | 4382.5 | 8893.5 | 12-02-2025
01:30 | 4358.75 | 4199 | 8557.75
02:00 | 4206.5 | 4015.5 | 8222
02:30 | 4179.5 | 3921 | 8100.5
03:00 | 4152.5 | 3826.5 | 7979
03:30 | 4128.75 | 3774.5 | 7903.25
04:00 | 4105 | 3722.5 | 7827.5
04:30 | 4109.5 | 3711 | 7820.5
05:00 | 4114 | 3699.5 | 7813.5
05:30 | 4165.5 | 3774.71 | 7940.21
06:00 | 4217 | 3849.92 | 8066.92
06:30 | 4499.85 | 4056.565 | 8556.415
07:00 | 4782.7 | 4263.21 | 9045.91
07:30 | 5076.575 | 4420.525 | 9497.1
08:00 | 5370.45 | 4577.84 | 9948.29
08:30 | 5508.07 | 4701.785 | 10209.855
09:00 | 5645.69 | 4825.73 | 10471.42
09:30 | 5547.44 | 4809.77 | 10357.21
10:00 | 5449.19 | 4793.81 | 10243
10:30 | 5526.71 | 4877.645 | 10404.355
11:00 | 5604.23 | 4961.48 | 10565.71
11:30 | 5754.695 | 5003.37 | 10758.065
12:00 | 5905.16 | 5045.26 | 10950.42
12:30 | 6058.15 | 5091.845 | 11149.995
13:00 | 6211.14 | 5138.43 | 11349.57
13:30 | 6084.455 | 5035.785 | 11120.24
14:00 | 5957.77 | 4933.14 | 10890.91
14:30 | 5902.13 | 4921.17 | 10823.3
15:00 | 5846.49 | 4909.2 | 10755.69
15:30 | 5745.86 | 4807.59 | 10553.45
16:00 | 5645.23 | 4705.98 | 10351.21
16:30 | 5590.605 | 4696.715 | 10287.32
17:00 | 5535.98 | 4687.45 | 10223.43
17:30 | 5832.49 | 4814.475 | 10646.965
18:00 | 6129 | 4941.5 | 11070.5
18:30 | 6477.35 | 4962.1 | 11439.45
19:00 | 6825.7 | 4982.7 | 11808.4
19:30 | 6581.5 | 4981.7 | 11563.2
20:00 | 6461.5 | 4951.7 | 11413.2
20:30 | 6383.25 | 4950.2 | 11333.45 |  | Executive Engineer
21:00 | 6305 | 4948.7 | 11253.7 |  | Network Operation Division
21:30 | 6024 | 4953.7 | 10977.7
22:00 | 5743 | 4958.7 | 10701.7
22:30 | 5598 | 4893.6 | 10491.6
23:00 | 5453 | 4828.5 | 10281.5

## En-Curve
QF-LDC-12
Date | 12-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2528 | 1903.5 | 921 | 0 | 42 | 763.66 | 40 | 2561 | 0 | 176 | 458 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2476.5 | 1909 | 921 | 0 | 41 | 763.33 | 40 | 2553.5 | 0 | 96.5 | 342.5 | 0 | 0 | 0 | 0 | 12-02-2025
01:00 | 2425 | 1914.5 | 921 | 0 | 40 | 763 | 40 | 2546 | 0 | 17 | 227 | 0 | 0 | 0 | 0
01:30 | 2407.5 | 1902.25 | 921 | 0 | 38 | 667.5 | 40 | 2459.5 | 0 | 8.5 | 113.5 | 0 | 0 | 0 | 0 | Energy Generated | 241.8961 |  | MKWHr
02:00 | 2390 | 1890 | 921 | 0 | 36 | 572 | 40 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0.956 |  | MKWHr
02:30 | 2362 | 1896.5 | 837 | 0 | 35 | 564.5 | 40 | 2365.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 242.8521 |  | MKWHr
03:00 | 2334 | 1903 | 753 | 0 | 34 | 557 | 40 | 2358 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2317 | 1889.75 | 742 | 0 | 35 | 560.5 | 40 | 2319 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2300 | 1876.5 | 731 | 0 | 36 | 564 | 40 | 2280 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2301.5 | 1878 | 731 | 0 | 35 | 564 | 40 | 2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2303 | 1879.5 | 731 | 0 | 34 | 564 | 40 | 2262 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2344.5 | 1866.75 | 731 | 0 | 35 | 581.96 | 40 | 2301 | 0 | 0 | 40 | 0 | 0 | 0 | 0
06:00 | 2386 | 1854 | 731 | 0 | 36 | 599.92 | 40 | 2340 | 0 | 0 | 80 | 0 | 0 | 0 | 0
06:30 | 2365.5 | 1849 | 826 | 0 | 40 | 683.77 | 40 | 2376.5 | 5.645 | 17 | 353 | 0 | 0 | 0 | 17
07:00 | 2345 | 1844 | 921 | 0 | 44 | 767.62 | 40 | 2413 | 11.29 | 34 | 626 | 0 | 0 | 0 | 34
07:30 | 2393 | 1853 | 914.5 | 0 | 45 | 764.415 | 40 | 2456 | 50.085 | 48 | 933.1 | 0 | 0 | 0 | 57.5
08:00 | 2441 | 1862 | 908 | 0 | 46 | 761.21 | 40 | 2499 | 88.88 | 62 | 1240.2 | 0 | 0 | 0 | 81
08:30 | 2509 | 1843 | 890.5 | 0 | 47 | 761.23 | 40 | 2519 | 122.425 | 84 | 1393.7 | 0 | 0 | 0 | 79.5
09:00 | 2577 | 1824 | 873 | 0 | 48 | 761.25 | 40 | 2539 | 155.97 | 106 | 1547.2 | 0 | 0 | 0 | 78
09:30 | 2622.5 | 1818.5 | 897 | 0 | 38 | 759.47 | 40 | 2513 | 242.64 | 135 | 1291.1 | 0 | 0 | 0 | 82
10:00 | 2668 | 1813 | 921 | 0 | 28 | 757.69 | 40 | 2487 | 329.31 | 164 | 1035 | 0 | 0 | 0 | 86
10:30 | 2702.5 | 1846 | 922 | 0 | 58 | 734.33 | 40 | 2515.5 | 418.025 | 195 | 973 | 0 | 0 | 0 | 70
11:00 | 2737 | 1879 | 923 | 0 | 88 | 710.97 | 40 | 2544 | 506.74 | 226 | 911 | 0 | 0 | 0 | 54
11:30 | 2683 | 1906 | 922.5 | 0 | 97 | 737.805 | 40 | 2581 | 540.76 | 247 | 1003 | 0 | 0 | 0 | 57
12:00 | 2629 | 1933 | 922 | 0 | 106 | 764.64 | 40 | 2618 | 574.78 | 268 | 1095 | 0 | 0 | 0 | 60
12:30 | 2637 | 1926.5 | 921.5 | 0 | 101 | 762.595 | 40 | 2621 | 577.4 | 321 | 1241 | 0 | 0 | 1 | 74.5
13:00 | 2645 | 1920 | 921 | 0 | 96 | 760.55 | 40 | 2624 | 580.02 | 374 | 1387 | 0 | 0 | 2 | 89
13:30 | 2608 | 1914.75 | 921.5 | 0 | 85 | 760.775 | 40 | 2594.5 | 542.715 | 381 | 1270.5 | 0 | 0 | 1.5 | 81.5
14:00 | 2571 | 1909.5 | 922 | 0 | 74 | 761 | 40 | 2565 | 505.41 | 388 | 1154 | 0 | 0 | 1 | 74
14:30 | 2543 | 1919 | 922.5 | 0 | 73 | 761 | 40 | 2616.5 | 437.8 | 387.5 | 1122.5 | 0 | 0 | 0.5 | 72
15:00 | 2515 | 1928.5 | 923 | 0 | 72 | 761 | 40 | 2668 | 370.19 | 387 | 1091 | 0 | 0 | 0 | 70
15:30 | 2518 | 1919.5 | 923 | 0 | 72 | 760 | 40 | 2632 | 287.95 | 395 | 1006 | 0 | 0 | 0 | 62.5
16:00 | 2521 | 1910.5 | 923 | 0 | 72 | 759 | 40 | 2596 | 205.71 | 403 | 921 | 0 | 0 | 0 | 55
16:30 | 2493 | 1885.5 | 922.5 | 0 | 70 | 760.5 | 40 | 2621.5 | 129.32 | 420 | 944 | 0 | 0 | 1 | 50
17:00 | 2465 | 1860.5 | 922 | 0 | 68 | 762 | 40 | 2647 | 52.93 | 437 | 967 | 0 | 0 | 2 | 45
17:30 | 2529.5 | 1851 | 922.5 | 0 | 70 | 762 | 40 | 2657 | 26.465 | 511 | 1276 | 0 | 0 | 1.5 | 55
18:00 | 2594 | 1841.5 | 923 | 0 | 72 | 762 | 40 | 2667 | 0 | 585 | 1585 | 0 | 0 | 1 | 65
18:30 | 2599 | 1887.5 | 899 | 0 | 71 | 762.5 | 40 | 2696 | 0 | 584 | 1899.45 | 0 | 0 | 1 | 62.5
19:00 | 2604 | 1933.5 | 875 | 0 | 70 | 763 | 40 | 2725 | 0 | 583 | 2213.9 | 0 | 0 | 1 | 60
19:30 | 2633 | 1982.5 | 875 | 0 | 68 | 759 | 40 | 2823 | 0 | 558 | 1824.7 | 0 | 0 | 0 | 55
20:00 | 2650 | 1957.5 | 875 | 0 | 68 | 761 | 40 | 2796 | 0 | 543 | 1722.7 | 0 | 0 | 0 | 55
20:30 | 2657 | 1965 | 898.5 | 0 | 67 | 761 | 40 | 2832 | 0 | 542 | 1570.95 | 0 | 0 | 0 | 52.5
21:00 | 2664 | 1972.5 | 922 | 0 | 66 | 761 | 40 | 2868 | 0 | 541 | 1419.2 | 0 | 0 | 0 | 50
21:30 | 2681.5 | 1952 | 922 | 0 | 63 | 760 | 40 | 2861 | 0 | 478.5 | 1219.7 | 0 | 0 | 0 | 25
22:00 | 2699 | 1931.5 | 922 | 0 | 60 | 759 | 40 | 2854 | 0 | 416 | 1020.2 | 0 | 0 | 0 | 0
22:30 | 2695 | 1929 | 922.5 | 0 | 59 | 764.5 | 40 | 2781.5 | 0 | 378 | 922.1 | 0 | 0 | 0 | 0
23:00 | 2691 | 1926.5 | 923 | 0 | 58 | 770 | 40 | 2709 | 0 | 340 | 824 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 408 | 04:00 | 387 | 12:00 | Payra | 420 | 05:00 | 409 | 12:00
Ashuganj | 408 | 6:00 | 387 | 16:00 | Rahanpur | 415 | 04:00 | 399 | 12:00
Bhulta | 404 | 05:00 | 385 | 12:00 | Rampal | 409 | 04:00 | 391 | 12:00
Bibiana | 408 | 00:00 | 395 | 12:00
BIPTC | 404 | 03:00 | 388 | 13:00
Bogura | 412 | 03:00 | 394 | 10:00
Gopalganj | 412 | 04:00 | 394 | 12:00
Kaliakoir | 396 | 08:00 | 379 | 12:00
Madunaghat | 408 | 09:00 | 401 | 12:00
Meghnaghat | 403 | 03:00 | 386 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 04:00 | 219 | 12:00 | Keranigonj | 233 | 04:00 | 220 | 15:00
AKSML | 236 | 08:00 | 229 | 01:00 | Khulna(S) | 238 | 04:00 | 224 | 12:00
Aminbazar | 235 | 03:00 | 222 | 11:00 | Madunaghat | 237 | 19:00 | 229 | 12:00
Ashuganj | 240 | 08:00 | 232 | 12:00 | Madunaghat-400 | 237 | 19:00 | 230 | 05:00
Ashuganj-400 | 238 | 6:00 | 226 | 16:00 | Maniknagar | 235 | 04:00 | 221 | 12:00
Baghabari | 239 | 05:00 | 228 | 13:00 | Meghnaghat | 240 | 08:00 | 230 | 11:00
Barapukuria | 226 | 04:00 | 217 | 07:00 | Meghnaghat-400 | 235 | 03:00 | 225 | 12:00
Barapukuria-230 | 226 | 20:00 | 217 | 7:00 | Mirsorai | 240 | 08:00 | 227 | 17:00
Barishal | 243 | 04:00 | 235 | 12:00 | Rajshahi | 240 | 05:00 | 225 | 12:00
Bheramara | 238 | 04:00 | 224 | 12:00 | Rampal | 236 | 04:00 | 223 | 12:00
Bhulta | 234 | 03:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 03:00 | 225 | 12:00 | Rampura | 234 | 03:00 | 220 | 12:00
BIPTC | 240 | 04:00 | 226 | 12:00 | Shikalbaha | 237 | 19:00 | 229 | 16:00
Bogura | 242 | 05:00 | 228 | 12:00 | Shyampur | 233 | 04:00 | 221 | 12:00
Bogura-400 | 239 | 04:00 | 228 | 10:00 | Siddhirganj | 235 | 04:00 | 224 | 11:00
Borhanuddin | 247 | 06:00 | 242 | 12:00 | Sirajgonj | 246 | 06:00 | 234 | 12:00
BSRM | 238 | 08:00 | 227 | 12:00 | Sreepur | 239 | 05:00 | 229 | 12:00
Cumilla(N) | 233 | 00:00 | 225 | 17:00 | Tongi | 232 | 01:00 | 222 | 11:00
Faridpur | 243 | 05:00 | 231 | 12:00
Fenchuganj | 237 | 08:00 | 227 | 12:00
Ghorashal | 240 | 01:00 | 230 | 11:00
Ghorashal-230 | 234 | 03:00 | 224 | 12:00
Gopalganj | 242 | 04:00 | 232 | 12:00
GPH | 237 | 08:00 | 228 | 11:00
Haripur | 235 | 05:00 | 222 | 12:00
Hasnabad | 234 | 07:00 | 222 | 12:00
Hathazari | 238 | 18:00 | 230 | 02:00
Ishurdi | 240 | 04:00 | 230 | 13:00
Jhenaidah | 238 | 05:00 | 222 | 12:00
Kaliakoir | 231 | 04:00 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 123 | 12:00 | Magura | 139 | 04:00 | 128 | 12:00
Agargaon | 136 | 04:00 | 126 | 12:00 | Mahasthangarh | 136 | 04:00 | 127 | 12:00
Agrabad | 136 | 18:00 | 131 | 13:00 | Manikganj | 139 | 00:00 | 130 | 15:00
AKS | 134 | 18:00 | 129 | 13:00 | Maniknagar | 132 | 00:00 | 124 | 12:00
Aminbazar | 138 | 07:00 | 125 | 14:00 | Matarbari | 132 | 21:00 | 120 | 10:00
Amnura | 142 | 20:00 | 128 | 12:00 | Matuail | 134 | 04:00 | 127 | 12:00
Ashuganj | 142 | 05:00 | 139 | 16:00 | Millgate | 136 | 00:00 | 128 | 12:00
Bagerhat | 135 | 03:00 | 125 | 12:00 | Mirpur | 134 | 02:00 | 125 | 12:00
Bajitpur | 137 | 03:00 | 131 | 11:00 | Mirzapur | 136 | 00:00 | 127 | 12:00
Bakulia | 136 | 08:00 | 131 | 02:00 | Mithapukur | 136 | 19:30 | 127 | 10:00
Banani | 133 | 03:00 | 123 | 12:00 | MI_Cement | 135 | 04:00 | 128 | 12:00
Bangabhaban | 133 | 01:00 | 124 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 19:30 | 129 | 07:00 | Mogbazar | 135 | 04:00 | 124 | 12:00
Barguna | 138 | 04:00 | 135 | 12:00 | Mongla | 135 | 03:00 | 124 | 12:00
Barishal | 134 | 04:00 | 129 | 12:00 | Motijheel | 163 | 07:00 | 124 | 12:00
Barishal-230 | 135 | 04:00 | 130 | 12:00 | Muktagacha | 129 | 00:00 | 129 | 00:00
Baroaulia | 136 | 18:00 | 132 | 04:00 | Munshiganj | 134 | 08:00 | 126 | 12:00
Baroirhat | 133 | 00:00 | 127 | 12:00 | Muradnagar | 133 | 18:00 | 131 | 23:00
Bashundhara | 137 | 05:00 | 123 | 12:00 | Mymensingh | 128 | 00:00 | 114 | 08:00
BashundharaCement | 135 | 06:00 | 127 | 12:00 | Naogaon | 135 | 04:00 | 125 | 08:00
Beanibazar | 135 | 03:00 | 128 | 13:00 | Narail | 137 | 04:00 | 126 | 12:00
Benapole | 137 | 04:00 | 122 | 12:00 | Narinda | 132 | 0:00 | 124 | 12:00
Bhaluka | 130 | 03:00 | 118 | 12:00 | Narshingdi | 132 | 05:00 | 122 | 16:00
Bhandaria | 134 | 03:00 | 125 | 13:00 | Natore | 137 | 00:00 | 132 | 12:00
Bhangura | 138 | 04:00 | 128 | 12:00 | Nawabganj | 137 | 04:00 | 131 | 10:00
Bheramara | 138 | 04:00 | 132 | 12:00 | Netrakona | 125 | 00:00 | 112 | 13:00
Bheramara(GK) | 139 | 04:00 | 133 | 12:00 | New | 137 | 00:00 | 129 | 12:00
Bhulta | 129 | 03:00 | 121 | 17:00 | Niamatpur | 140 | 04:00 | 132 | 08:00
Bog-Sherpur | 136 | 03:00 | 127 | 12:00 | Noapara | 136 | 03:00 | 125 | 12:00
Bogura | 136 | 00:00 | 129 | 12:00 | Pabna | 137 | 04:00 | 125 | 12:00
Bogura-230 | 138 | 04:00 | 129 | 12:00 | Palashbari | 132 | 02:00 | 118 | 12:00
Brahmanbaria | 136 | 05:00 | 128 | 17:00 | Panchagarh | 140 | 20:00 | 128 | 10:00
Cantonment | 136 | 04:00 | 127 | 12:00 | Patuakhali | 137 | 07:00 | 134 | 12:00
Chandpur | 138 | 18:00 | 127 | 23:00 | Payra | 138 | 04:00 | 135 | 11:00
Chandraghona | 136 | 18:00 | 132 | 12:00 | PHP | 135 | 19:00 | 123 | 00:00
Chapai | 136 | 01:00 | 130 | 09:00 | Postogola | 137 | 04:00 | 130 | 12:00
Charsaidpur | 135 | 08:00 | 127 | 12:00 | Purbachal | 134 | 03:00 | 122 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 18:30 | 127 | 15:00 | Purbasadipur | 134 | 20:00 | 123 | 10:00
Chhatak | 134 | 01:00 | 126 | 13:00 | Rahanpur | 139 | 04:00 | 134 | 12:00
Chowmuhani | 135 | 01:00 | 125 | 17:00 | Rahanpur-400 | 141 | 04:00 | 135 | 08:00
Chuadanga | 137 | 02:00 | 126 | 12:00 | Rahim | 133 | 05:00 | 126 | 12:00
Coxsbazar | 126 | 08:00 | 122 | 10:00 | Rajbari | 134 | 04:00 | 128 | 12:00
Cumilla(N) | 137 | 08:00 | 132 | 14:00 | Rajendrapur | 138 | 08:00 | 128 | 18:00
Cumilla(S) | 136 | 18:30 | 124 | 12:00 | Rajshahi | 138 | 00:00 | 131 | 12:00
Daudkandi | 133 | 05:00 | 125 | 12:00 | Rajshahi-230 | 139 | 03:00 | 125 | 12:00
Dhaka | 133 | 01:00 | 124 | 12:00 | Ramganj | 133 | 00:00 | 123 | 16:00
Dhamrai | 133 | 01:00 | 124 | 12:00 | Rampur | 138 | 18:30 | 131 | 15:00
Dhanmondi | 135 | 02:00 | 127 | 12:00 | Rampura | 133 | 03:00 | 123 | 12:00
Dohazari | 133 | 18:00 | 128 | 07:00 | Rangamati | 136 | 08:00 | 131 | 11:00
Faridpur | 135 | 03:00 | 129 | 12:00 | Rangpur | 135 | 20:00 | 126 | 07:00
Fatullah | 136 | 04:00 | 129 | 12:00 | Ruppur | 139 | 04:00 | 134 | 12:00
Fenchuganj | 138 | 02:00 | 133 | 12:00 | Saidpur | 134 | 20:00 | 124 | 10:00
Feni | 133 | 18:30 | 127 | 04:00 | Satkhira | 136 | 04:00 | 124 | 13:00
Ghatail | 129 | 00:00 | 120 | 12:00 | Satmasjid | 136 | 04:00 | 126 | 12:00
Ghorashal | 141 | 00:00 | 135 | 15:00 | Savar | 134 | 04:00 | 124 | 14:00
Goalpara | 139 | 04:00 | 127 | 12:00 | SevenRings | 142 | 08:00 | 135 | 11:00
Gollamari | 138 | 04:00 | 128 | 12:00 | ShahCement | 135 | 03:00 | 127 | 12:00
Gopalganj | 136 | 04:00 | 129 | 12:00 | Shahjadpur | 140 | 00:00 | 132 | 11:00
Gopalganj-400 | 137 | 05:00 | 130 | 12:00 | Shahjibazar | 138 | 03:00 | 129 | 17:00
Gulshan | 133 | 01:00 | 123 | 12:00 | Shahmirpur | 137 | 18:00 | 131 | 01:00
Halishahar | 137 | 18:00 | 132 | 00:00 | Shariatpur | 136 | 05:00 | 128 | 12:00
Haripur | 133 | 03:00 | 127 | 12:00 | Sherpur | 125 | 00:00 | 120 | 04:00
HaripurSBU | 133 | 05:00 | 127 | 12:00 | Shikalbaha | 126 | 18:00 | 120 | 02:00
Hasnabad | 138 | 04:00 | 110 | 17:00 | Shikalbaha-230 | 139 | 19:00 | 130 | 16:00
Hathazari | 139 | 18:00 | 132 | 10:00 | Shitalakhya | 135 | 04:00 | 128 | 12:00
Ishurdi | 140 | 04:00 | 134 | 12:00 | Sholosohor | 136 | 08:00 | 132 | 02:00
Jaldhaka | 133 | 20:00 | 122 | 10:00 | Shyampur | 135 | 00:00 | 128 | 12:00
Jamalpur | 129 | 00:00 | 116 | 12:00 | Shyampur-230 | 136 | 08:00 | 128 | 12:00
Jashore | 136 | 03:00 | 124 | 12:00 | Siddhirganj | 134 | 03:00 | 127 | 12:00
Jhenaidah | 139 | 05:00 | 128 | 12:00 | Sirajganj | 137 | 04:00 | 127 | 12:00
Jhenaidah-230 | 139 | 04:00 | 129 | 12:00 | Sonargaon | 132 | 03:00 | 124 | 16:00
Joydebpur | 140 | 07:00 | 128 | 11:00 | Sreemongol | 137 | 06:00 | 129 | 17:00
Joypurhat | 133 | 02:00 | 122 | 12:00 | Sreepur | 130 | 00:00 | 123 | 12:00
Juldah | 139 | 18:00 | 131 | 23:00 | Srinagar | 136 | 04:00 | 131 | 12:00
Kabirpur | 141 | 18:30 | 126 | 12:00 | SSM | 140 | 04:00 | 133 | 08:00
Kachua | 137 | 00:00 | 128 | 04:00 | Sunamganj | 135 | 03:00 | 126 | 12:00
Kaliakoir | 142 | 00:00 | 126 | 12:00 | Sylhet | 136 | 04:00 | 128 | 17:00
Kallyanpur | 134 | 05:00 | 127 | 12:00 | Sylhet-132 | 135 | 00:00 | 129 | 12:00
Kalurghat | 136 | 18:00 | 132 | 00:00 | Tangail | 131 | 00:00 | 120 | 12:00
Kamrangirchar | 137 | 06:00 | 127 | 10:00 | Thakurgaon | 139 | 20:00 | 126 | 10:00
Kaptai | N/A | N/A | N/A | N/A | TK | 137 | 08:00 | 133 | 00:00
Kazla | 134 | 06:00 | 123 | 13:00 | Tongi | 138 | 01:00 | 130 | 17:00
Keranigonj | 136 | 03:00 | 131 | 12:00 | Ullahpara | 139 | 04:00 | 128 | 12:00
Khagrachori | 135 | 08:00 | 131 | 11:00 | Ullon | 132 | 00:00 | 124 | 13:00
Khulna | 137 | 03:00 | 126 | 12:00 | Uttara | 134 | 04:00 | 124 | 12:00
Khulna(S) | 138 | 04:00 | 128 | 12:00 | UttaraNew | 134 | 03:00 | 123 | 12:00
Khulshi | 136 | 19:00 | 131 | 00:00 | Zigatola | 137 | 05:00 | 130 | 11:00
Kishoreganj | 136 | 03:00 | 126 | 12:00
Kodda | 139 | 00:00 | 127 | 10:00
KSRM | 137 | 01:00 | 132 | 14:00
Kulaura | 137 | 04:00 | 132 | 12:00
Kurigram | 132 | 19:30 | 122 | 07:00
Kushtia | 138 | 02:00 | 130 | 13:00
Lalbag | 137 | 04:00 | 130 | 10:00
Lalmonirhat | 132 | 19:00 | 123 | 10:00
Madanganj | 135 | 06:00 | 127 | 12:00
Madaripur | 136 | 04:00 | 131 | 17:00
Madartek | 132 | 01:00 | 123 | 13:00
Madunaghat | 136 | 18:00 | 131 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division