## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9665.5 | 0 |  | 9665.5
1:00 | 9112.5 | 0 |  | 9112.5
2:00 | 8771.5 | 0 |  | 8771.5
3:00 | 8498.5 | 0 |  | 8498.5
4:00 | 8244.5 | 0 |  | 8244.5
5:00 | 8223 | 0 |  | 8223
6:00 | 8521.3 | 0 |  | 8521.3
7:00 | 9261.38 | 80 |  | 9345.38
8:00 | 10026.12 | 100 |  | 10130.12
9:00 | 10618.66 | 90 |  | 10712.66
10:00 | 10744.07 | 80 |  | 10828.07
11:00 | 10975.71 | 60 |  | 11038.71
12:00 | 11397.27 | 50 |  | 11449.52
13:00 | 11617.42 | 130 |  | 11753.42
14:00 | 11268.63 | 100 |  | 11372.63
15:00 | 10913.05 | 91 |  | 11008.05
16:00 | 10654.63 | 96 |  | 10754.63
17:00 | 10587.81 | 101 |  | 10693.81
18:00 | 11246.05 | 81 |  | 11331.05
19:00 | 11942.9 | 122 |  | 12069.9
19:30 | 11540.07 | 116 |  | 11661.07
20:00 | 11400.34 | 116 |  | 11521.34
21:00 | 11258.78 | 89 |  | 11351.78
22:00 | 10867.71 | 51 |  | 10920.71
23:00 | 10490.23 | 11 |  | 10501.23
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 13-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2649 | 1811.5 | 922 | 0 | 56 | 760 | 40 | 2612 | 0 | 203 | 612 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2664.5 | 1849 | 922.5 | 0 | 55 | 762 | 40 | 2619.5 | 0 | 143.5 | 333 | 0 | 0 | 0 | 0 | 13-02-2025
01:00 | 2680 | 1886.5 | 923 | 0 | 54 | 764 | 40 | 2627 | 0 | 84 | 54 | 0 | 0 | 0 | 0
01:30 | 2690 | 1883.5 | 923 | 0 | 53 | 710 | 40 | 2534 | 0 | 68 | 40.5 | 0 | 0 | 0 | 0 | Energy Generated | 247.6001 |  | MKWHr
02:00 | 2700 | 1880.5 | 923 | 0 | 52 | 656 | 40 | 2441 | 0 | 52 | 27 | 0 | 0 | 0 | 0 | Energy not Served | 1.448 |  | MKWHr
02:30 | 2709 | 1903.5 | 879 | 0 | 52 | 612.5 | 40 | 2374 | 0 | 43 | 22 | 0 | 0 | 0 | 0 | Total Energy Requirement | 249.0481 |  | MKWHr
03:00 | 2718 | 1926.5 | 835 | 0 | 52 | 569 | 40 | 2307 | 0 | 34 | 17 | 0 | 0 | 0 | 0
03:30 | 2700 | 1931.5 | 785.5 | 0 | 51 | 517 | 40 | 2321 | 0 | 17 | 8.5 | 0 | 0 | 0 | 0
04:00 | 2682 | 1936.5 | 736 | 0 | 50 | 465 | 40 | 2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2680.5 | 1926.75 | 735.5 | 0 | 50 | 466 | 40 | 2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2679 | 1917 | 735 | 0 | 50 | 467 | 40 | 2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2689.5 | 1909.9 | 735 | 0 | 49 | 511 | 40 | 2410 | 0 | 13.5 | 14.25 | 0 | 0 | 0 | 0
06:00 | 2700 | 1902.8 | 735 | 0 | 48 | 555 | 40 | 2485 | 0 | 27 | 28.5 | 0 | 0 | 0 | 0
06:30 | 2710 | 1900.4 | 830 | 0 | 49 | 634 | 40 | 2559.5 | 4.74 | 55.5 | 108.2 | 0 | 0 | 0 | 40
07:00 | 2720 | 1898 | 925 | 0 | 50 | 713 | 40 | 2634 | 9.48 | 84 | 187.9 | 0 | 0 | 0 | 80
07:30 | 2732 | 1898.5 | 901.5 | 0 | 55 | 738 | 40 | 2647 | 43.3 | 85.5 | 502.95 | 0 | 0 | 0 | 90
08:00 | 2744 | 1899 | 878 | 0 | 60 | 763 | 40 | 2660 | 77.12 | 87 | 818 | 0 | 0 | 0 | 100
08:30 | 2730 | 1871 | 878.5 | 0 | 64 | 763 | 40 | 2658 | 133.39 | 108 | 1076.5 | 0 | 0 | 0 | 95
09:00 | 2716 | 1843 | 879 | 0 | 68 | 763 | 40 | 2656 | 189.66 | 129 | 1335 | 0 | 0 | 0 | 90
09:30 | 2615 | 1877.25 | 901.5 | 0 | 68 | 762.5 | 40 | 2691 | 260.115 | 177 | 1289 | 0 | 0 | 0 | 85
10:00 | 2514 | 1911.5 | 924 | 0 | 68 | 762 | 40 | 2726 | 330.57 | 225 | 1243 | 0 | 0 | 0 | 80
10:30 | 2462.5 | 1897 | 924.5 | 0 | 69 | 760 | 40 | 2764 | 407.39 | 241.5 | 1294 | 0 | 0 | 0 | 70
11:00 | 2411 | 1882.5 | 925 | 0 | 70 | 758 | 40 | 2802 | 484.21 | 258 | 1345 | 0 | 0 | 0 | 60
11:30 | 2417 | 1904 | 925 | 0 | 74 | 758 | 40 | 2874 | 536.99 | 265 | 1392.5 | 0 | 0 | 0 | 55
12:00 | 2423 | 1925.5 | 925 | 0 | 78 | 758 | 40 | 2946 | 589.77 | 272 | 1440 | 0 | 0 | 0 | 50
12:30 | 2304.5 | 1922.5 | 925 | 0 | 76 | 758.5 | 40 | 2954.5 | 574.845 | 316 | 1635.5 | 0 | 0 | 0 | 90
13:00 | 2186 | 1919.5 | 925 | 0 | 74 | 759 | 40 | 2963 | 559.92 | 360 | 1831 | 0 | 0 | 0 | 130
13:30 | 2175 | 1838 | 925 | 0 | 76 | 759.065 | 40 | 2962 | 537.96 | 369 | 1761 | 0 | 0 | 0 | 115
14:00 | 2164 | 1756.5 | 925 | 0 | 78 | 759.13 | 40 | 2961 | 516 | 378 | 1691 | 0 | 0 | 0 | 100
14:30 | 2164.5 | 1759.5 | 924.5 | 0 | 75 | 759.11 | 40 | 2957.5 | 429.73 | 383 | 1597.5 | 0 | 0 | 0.5 | 95.5
15:00 | 2165 | 1762.5 | 924 | 0 | 72 | 759.09 | 40 | 2954 | 343.46 | 388 | 1504 | 0 | 0 | 1 | 91
15:30 | 2172.5 | 1776 | 924.5 | 0 | 73 | 758.89 | 40 | 2945 | 294.45 | 387 | 1409.5 | 0 | 0 | 3 | 93.5
16:00 | 2180 | 1789.5 | 925 | 0 | 74 | 758.69 | 40 | 2936 | 245.44 | 386 | 1315 | 0 | 0 | 5 | 96
16:30 | 2188.5 | 1792.5 | 925 | 0 | 72 | 758.37 | 40 | 2931 | 158.85 | 422.5 | 1327 | 0 | 0 | 5.5 | 98.5
17:00 | 2197 | 1795.5 | 925 | 0 | 70 | 758.05 | 40 | 2926 | 72.26 | 459 | 1339 | 0 | 0 | 6 | 101
17:30 | 2198 | 1811 | 924.5 | 0 | 73 | 758.3 | 40 | 2928 | 36.13 | 528.5 | 1612.5 | 0 | 0 | 7 | 91
18:00 | 2199 | 1826.5 | 924 | 0 | 76 | 758.55 | 40 | 2930 | 0 | 598 | 1886 | 0 | 0 | 8 | 81
18:30 | 2336.5 | 1859.5 | 901 | 0 | 73 | 759.375 | 40 | 2932.5 | 0 | 609 | 2076.6 | 0 | 0 | 7 | 101.5
19:00 | 2474 | 1892.5 | 878 | 0 | 70 | 760.2 | 40 | 2935 | 0 | 620 | 2267.2 | 0 | 0 | 6 | 122
19:30 | 2588 | 1893.5 | 878 | 0 | 70 | 760.07 | 40 | 2941 | 0 | 568 | 1794.5 | 0 | 0 | 7 | 116
20:00 | 2610 | 1920.5 | 878 | 0 | 68 | 760.34 | 40 | 2958 | 0 | 550 | 1608.5 | 0 | 0 | 7 | 116
20:30 | 2632.5 | 1921.25 | 878 | 0 | 67 | 761.06 | 40 | 2960 | 0 | 528.5 | 1529.75 | 0 | 0 | 11.5 | 102.5
21:00 | 2655 | 1922 | 878 | 0 | 66 | 761.78 | 40 | 2962 | 0 | 507 | 1451 | 0 | 0 | 16 | 89
21:30 | 2536 | 1942.75 | 901.5 | 0 | 65 | 760.495 | 40 | 2962.5 | 0 | 482 | 1360 | 0 | 0 | 13 | 70
22:00 | 2417 | 1963.5 | 925 | 0 | 64 | 759.21 | 40 | 2963 | 0 | 457 | 1269 | 0 | 0 | 10 | 51
22:30 | 2389 | 1937 | 925 | 0 | 68 | 756.97 | 40 | 2941 | 0 | 389 | 1224 | 0 | 0 | 9 | 31
23:00 | 2361 | 1910.5 | 925 | 0 | 72 | 754.73 | 40 | 2919 | 0 | 321 | 1179 | 0 | 0 | 8 | 11
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5040 | 4625.5 | 9665.5 | DAILY GENERATION CURVE
00:30 | 4837.5 | 4551.5 | 9389
01:00 | 4635 | 4477.5 | 9112.5 | 13-02-2025
01:30 | 4584.5 | 4357.5 | 8942
02:00 | 4534 | 4237.5 | 8771.5
02:30 | 4546 | 4089 | 8635
03:00 | 4558 | 3940.5 | 8498.5
03:30 | 4525.5 | 3846 | 8371.5
04:00 | 4493 | 3751.5 | 8244.5
04:30 | 4483.5 | 3750.25 | 8233.75
05:00 | 4474 | 3749 | 8223
05:30 | 4486.65 | 3885.5 | 8372.15
06:00 | 4499.3 | 4022 | 8521.3
06:30 | 4647.855 | 4243.485 | 8891.34
07:00 | 4796.41 | 4464.97 | 9261.38
07:30 | 5028.76 | 4614.99 | 9643.75
08:00 | 5261.11 | 4765.01 | 10026.12
08:30 | 5498.47 | 4823.92 | 10322.39
09:00 | 5735.83 | 4882.83 | 10618.66
09:30 | 5721.22 | 4960.145 | 10681.365
10:00 | 5706.61 | 5037.46 | 10744.07
10:30 | 5814.725 | 5045.165 | 10859.89
11:00 | 5922.84 | 5052.87 | 10975.71
11:30 | 6016.46 | 5170.03 | 11186.49
12:00 | 6110.08 | 5287.19 | 11397.27
12:30 | 6205.14 | 5302.205 | 11507.345
13:00 | 6300.2 | 5317.22 | 11617.42
13:30 | 6221.995 | 5221.03 | 11443.025
14:00 | 6143.79 | 5124.84 | 11268.63
14:30 | 6067.92 | 5022.92 | 11090.84
15:00 | 5992.05 | 4921 | 10913.05
15:30 | 5915 | 4868.84 | 10783.84
16:00 | 5837.95 | 4816.68 | 10654.63
16:30 | 5851.92 | 4769.3 | 10621.22
17:00 | 5865.89 | 4721.92 | 10587.81
17:30 | 6160.445 | 4756.485 | 10916.93
18:00 | 6455 | 4791.05 | 11246.05
18:30 | 6642.1 | 4952.375 | 11594.475
19:00 | 6829.2 | 5113.7 | 11942.9
19:30 | 6548.5 | 4991.57 | 11540.07
20:00 | 6428.5 | 4971.84 | 11400.34
20:30 | 6388.5 | 4941.06 | 11329.56 |  | Executive Engineer
21:00 | 6348.5 | 4910.28 | 11258.78 |  | Network Operation Division
21:30 | 6118.25 | 4944.995 | 11063.245
22:00 | 5888 | 4979.71 | 10867.71
22:30 | 5730 | 4948.97 | 10678.97
23:00 | 5572 | 4918.23 | 10490.23

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11397.27 | MW | 12:00 Hr. | Energy Generated |  |  | 247.6001 |  | MKWHr.
| Day Peak Demand |  |  | 11449.52 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.448 |  | MKWHr.
| Evening Peak Generation |  |  | 11942.9 | MW | 19:00 Hr. | Energy Demand |  |  | 249.0481 |  | MKWHr.
| Evening Peak Demand |  |  | 12069.9 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30.4 |  | °C
| Minimum Generation of the Day |  |  | 8223 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 792.12 |  | MMCFD
| Maximum Generation of the Day |  |  | 11942.9 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.9647 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.6695 | 0 | 7.3965 | 0 | 0 | 0.15727 | 0 | 0 | 41.2233 | Gas | 105.722 | Gas | 385544264.63
| Chattogram Zone |  |  | 5.8085 | 24.8491 | 10.5714 | 0 | 0.93088 | 0.13473 | 0 | 0.07056 | 42.3652 | Coal | 66.1512 | Coal | 483280041.1702
| Cumilla Zone |  |  | 16.8712 | 0 | 6.4978 | 0 | 0 | 0.32263 | 1.5302 | 0 | 25.2219 | HFO | 32.1516 | HFO | 597210259.28
| Mymensingh Zone |  |  | 0.42144 | 0 | 2.0401 | 0 | 0 | 0.26147 | 0 | 0 | 2.723 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7904 | Hydro | 0.93088 | Hydro | 93088
| Khulna Zone |  |  | 6.7573 | 14.1164 | 0.091776 | 0 | 0 | 0.42048 | 21.128 | 0 | 42.514 | Solar | 3.3836 | Solar | 53863893.95
| Barishal Zone |  |  | 8.0371 | 21.7978 | 0.24442 | 0 | 0 | 0.001951 | 0 | 0 | 30.0812 | Import | 39.1902 | Import | 203367300.8
| Rajshahi Zone |  |  | 10.3664 | 0 | 2.6016 | 0 | 0 | 0.81607 | 16.532 | 0 | 30.3161 | Wind | 0.07056 | Wind | 1100736
| Rangpur Zone |  |  | 0 | 5.3879 | 2.708 | 0 | 0 | 1.2691 | 0 | 0 | 9.365
| Total |  |  | 105.722 | 66.1512 | 32.1516 | 0 | 0.93088 | 3.3836 | 39.1902 | 0.07056 | 247.6001
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 385544264.63 |  | Hydro | 93088
|  |  |  | Coal | 483280041.1702 |  | Solar | 53863893.95
|  |  |  | HFO | 597210259.28 |  | Import | 203367300.8
|  |  |  | HSD | 0 |  | Wind | 1100736
[5 empty] | Total: | 172,44,59,583 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.128 | Peak Hr Flow | 878.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10447054.637 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.532 | Peak Hr Flow | 760.20 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 588 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5302 | Peak Hr Flow | 70.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 844 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.1902 | Peak Hr Flow | 1708.20 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4381
|  |  |  | Chattogram |  | 0 |  | 1186
|  |  |  | Cumilla |  | 0 |  | 967
|  |  |  | Mymensingh |  | 122 |  | 1041
|  |  |  | Sylhet |  | 0 |  | 396
|  |  |  | Khulna |  | 0 |  | 1274
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 1140
|  |  |  | Rangpur |  | 0 |  | 758
|  |  |  | Total |  | 122 |  | 11455
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 225MW CCPP Unit-3 GT |  |  | 141
|  | 7 | Sirajgonj 225MW CCPP Unit-3 ST |  |  | 79
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1012 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1678.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 14:07 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to Annual
Maintenance.
| 08:09 | 14:03 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Annual
Maintenance.
| 08:12 | 16:41 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project Work IDRNPP
| 08:13 | 19:04 | Sirajganj 132/33kV S/S T3-(435) LT Project Work S/D Due to T-3 Punch list rectification
work.
| 08:14 | 19:03 | Sirajganj 132/33kV S/S T3-(435) HT Project Work S/D Due to T-3 Punch list rectification
work.
| 08:14 | 12:16 | Chowmuhani 132/33kV S/S TR1-415T HT Tripped showing Lockout RY Trip TR. PRD. relays Due | [7 empty] | 30.0MW load
|  |  | to Chow (33/11kv) T-4 trans Breaker trip Chow (33/11kv) T-3 Trans Y-Phase Incoming Loop | [7 empty] | interrup.
Cut-off. And Verious feeder under ground cable Flashing and firing.
| 08:14 | 12:18 | Chowmuhani 132/33kV S/S TR1 Tripped showing 132KV Protection Trip Instt. E/F. relays Due | [7 empty] | 30.0MW load
|  |  | to Chow (33/11kv) T-4 trans Breaker trip Chow (33/11kv) T-3 Trans Y-Phase Incoming Loop | [7 empty] | interrup.
Cut-off. And Verious feeder under ground cable Flashing and firing.
| 08:14 | 08:52 | Chowmuhani 132/33kV S/S TR3 Tripped showing Over Current relays Due to Chow (33/11kv) T-4 | [7 empty] | 40.0MW load
|  |  | trans Breaker trip Chow (33/11kv) T-3 Trans Y-Phase Incoming Loop Cut-off. And Verious | [7 empty] | interrup.
feeder under ground cable Flashing and firing.
| 08:19 | 09:40 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to MFT / IED Changing
Work
| 08:19 | 09:38 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to MFT / IED Changing
Work
| 08:20 | 16:35 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual maintenance works at Fenchuganj SS and from Fenchuganj 230/132/33kV end Due to
Deadline checking
| 08:34 | 14:56 | Gopalganj-Madhumati 132kV Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to Yearly
maintenance
| 08:37 | 16:50 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Annual Maintenance.
| 08:47 | 14:33 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D Due to Annual
Maintenance
| 08:48 | 18:45 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Inter lock implemantation work
| 08:49 | 18:45 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Inter lock implemantation work
|  | 08:54 | Chowmuhani 132/33kV S/S TR2 is restored.
| 09:01 | 18:04 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D
| 09:01 | 18:04 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D
| 09:01 | 18:03 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Project Work S/D Due to Tower painting
| 09:01 | 18:03 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Project Work S/D Due to Tower painting
| 09:03 |  | GPH 230/33kV S/S Transformer -2 (D07) HT Scheduled S/D Due to general maintenanace
| 09:04 | 18:05 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Tower painting
| 09:04 | 18:05 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Tower painting
| 09:32 |  | Ghorashal GT-4 tripped.
| 09:35 |  | Ghorasal Repowered CCPP Unit-4 Tripped with remarks:- GBC Trip
| 10:22 | 05:05 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to low voltage.
| 11:12 |  | Ghorashal GT-4 was sync.
| 11:12 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 11:27 | 13:18 | BIPTC S/S Baharampur-1 Scheduled S/D Due to Due to CVT Oil leakage rectification
| 11:42 |  | Ashuganj South 360MW tripped due to GBC tripping.
| 11:43 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 11:44 | 12:38 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to 33kV UG Cable Maintenance
| 11:45 | 12:37 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D
| 11:59 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to low voltage.
| 12:00 |  | Day Peak Gen. 11397 MW
| 12:12 |  | Sirajgonj 225MW CCPP Unit-3 GT Planned Shutdown with remarks:- 4th Minor Inspection of GT
| 12:13 |  | Sirajgonj 225MW CCPP Unit-3 ST Planned Shutdown with remarks:- 4th Minor Inspection of GT
| 12:46 | 21:55 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to SPMD
WORK
| 13:16 | 14:58 | Kodda-Rajendrapur 132kV Ckt-2 Project Work S/D from Rajendrapur 132/33kV end.
| 13:42 |  | Sirajgonj 225MW CCPP Unit-1 GT Synchronized with remarks:- GT has been synchronized with
grid as per NLDC demand and ST startup process is going on.
| 13:42 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 14:35 | 14:46 | Goalpara 132/33kV S/S T-6 LT Tripped showing E/F relays Due to Trip due to 33KV
therokhada Feeder Fault
| 14:35 | 14:46 | Goalpara 132/33kV S/S T-5 LT Tripped showing E/F relays Due to Trip due to 33KV
therokhada Feeder Fault
|  | 15:04 | Bhulta-Rampura 230 kV Ckt-4 is restored.
| 16:11 | 20:30 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to Shutdown
requested by NLDC
|  | 16:19 | Mirpur 132/33kV S/S Main Bus is restored.
| 17:19 | 17:42 | Rampur 230/132/33 S/S Halishahar-2 Tripped showing REL 670 relays Due to Distance
| 17:25 |  | Sirajgonj Gas 225MW Unit-1 ST was sync.
| 17:25 |  | Sirajgonj 225MW CCPP Unit-1 ST Synchronized with remarks:- ST has been synchronized with
grid as per NLDC demand.
| 17:25 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 17:38 |  | Ashuganj South 360MW GT was sync.
| 17:38 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 17:51 |  | Amtoli-RNPL 400kV ckt-1 was switched on from Amtoli end for the first time.
|  | 18:06 | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 is restored.
|  | 21:52 | Rangpur-Saidpur 132kV Ckt-2 is restored.
| 02:09 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
| 03:03 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 05:33 |  | Ghorasal Repowered CCPP Unit-4 Tripped
| 05:33 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 07:11 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to River
crossing tower work. and from Tongi 230/132/33kV end Due to S/D taken by NLDC
| 07:14 |  | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to Dead line checking and disk
cleaning
| 07:46 |  | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Forced S/D Due to Maintenance at Aminbazar
Substation
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 175 | 5212094 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 415 | 9540000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9937000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 248 | 6925091 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 825004 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 259560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 133 | 1232160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 265291 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 265465 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 371400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 523080 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 573480 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 587400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 951949 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 128 | 1427904 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 1116480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 1920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 810720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 157268 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 35 | 240000 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 1966 | 41223266
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 159483.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114210 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 547680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 930880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5401505 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1553127 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 71 | 954288 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 68 | 782614 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 89 | 1160640 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 407040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 401280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 145 | 910800 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 42056 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1526357 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 89 | 1248000 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 661145 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 145 | 623927 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14339998 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 6 | 70560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 10509090.91 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2457 | 42365201.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4834000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 175 | 4976000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 31 | 724104 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 478080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 184 | 4332364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1154698 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 120 | 1891854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 47 | 554896 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2881440 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 70 | 1530240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 146784 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 371980 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 149340 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 309960 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 563520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 322627 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1288.2 | 25221887
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 421440 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 194400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1135200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 102480 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 39 | 608040 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 131 | 2723030
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 28 | 701000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3726000 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 810864 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 115728 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 715200 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2022720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 287000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 450096 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7235500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 302 | 7726300 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 987 | 23790408
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 878 | 21128000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 29 | 65280 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 30 | 26496 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 209 | 6757344 | Commissioning work is in progress
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 420480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 616 | 14116360 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1762 | 42513960
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 26016 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 151274 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2983000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 14837818.18 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4902780 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 218400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6960000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1951 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1297 | 30081239.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 11518 | machine problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 36 | 246050 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 121 | 1106091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9203346 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 317108 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 56970 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 203515 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 804560 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 96 | 701472 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 317376 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 760.2 | 16532000 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 279000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 512770 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1621.7 | 30316076
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 68 | 1635927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3752000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1174588 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32946.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1533424 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189224 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1046880 | -
Rangpur Area Total |  |  |  |  | 950 | 433 | 9364989.6
Eastern Grid Total |  |  |  |  | 16856.242 | 6829.2 | 135323792.51
Western Grid Total |  |  |  |  | 10294.5 | 5113.7 | 112276264.78
National Grid Total |  |  |  |  | 27150.742 | 11942.9 | 247600057.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-02-2025 | during | 14-02-2025 | during | 14-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 175 | 240 | 230 | 240 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 415 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 248 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 17 | 35 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 133 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 0 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19 | 19 | 22.5 | 22.5 | 22.5 | 22.5 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 22 | 25 | 25 | 25 | 25 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 24 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 58 | 128 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 162 | 162 | 54 | 54 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 54 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1919 | 1966 | 4795.87 | 4797.87 | 2507.82 | 2490.82
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 226 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105 | 87 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 65 | 71 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 51 | 68 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 89 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 15 | 30 | 25 | 30 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 13 | 51 | 108 | 108 | 32 | 32 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.8 | 0 | 3.8 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 145 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 60 | 89 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 25 | 145 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 6 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 575 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2046 | 2457 | 2855.66 | 2857.86 | 2680.66 | 2700.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 215 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 175 | 356.56 | 356.56 | 150 | 150 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 27 | 31 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 11 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 184 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 96 | 120 | 145 | 145 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 39 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 134 | 200 | 200 | 200 | 150 | 150 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 78 | 70 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 27 | 113 | 113 | 9 | 28 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 69 | 115 | 115 | 34 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 965 | 1288.2 | 2085.53 | 2030.53 | 1449.2 | 1494.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-02-2025 | during | 14-02-2025 | during | 14-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 15 | 18 | 210 | 210 | 18 | 18 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 115 | 115 | 59 | 59 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.08 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 39 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 169.08 | 131 | 645.3 | 601.5 | 206.3 | 162.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 27 | 28 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 32 | 40 | 40 | 35 | 35 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 350 | 302 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1011 | 987 | 1040 | 1060 | 1001 | 1001
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 925 | 878 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 29 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 30 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 355 | 209 | 410 | 410 | 360 | 360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79.78 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 619 | 616 | 1234.2 | 1234.2 | 617 | 617 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1978.78 | 1762 | 3586.2 | 3498.2 | 2709 | 2621
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 610 | 600 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1272.58 | 1297 | 1556.12 | 1555.12 | 1553 | 1552
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 36 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 121 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 25 | 0 | 52.2 | 52.2 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 89 | 92 | 92 | 49 | 88 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 96 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.82 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 758 | 760.2 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.31 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1473.63 | 1621.7 | 2334.34 | 2189.24 | 1958.36 | 1852.26
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 67 | 68 | 70 | 70 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 157 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 50 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 3.6 | 0 | 3.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 95 | 95 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 27 | 0 | 27 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 163 | 0 | 150.28 | 0 | 150.28 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 562.2 | 433 | 662.88 | 482 | 637.88 | 457
System Total |  |  |  |  | 27884.66 | 27150.742 | 11397.27 | 11942.9 | 19561.9 | 19072.32 | 14703.22 | 14331.64
Forecast Scenario (14-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9720 |  | 0 |  | 9720
|  |  |  | 1:00 | 9080 |  | 0 |  | 9080
|  |  |  | 2:00 | 8680 |  | 0 |  | 8680
|  |  |  | 3:00 | 8380 |  | 0 |  | 8380
|  |  |  | 4:00 | 8150 |  | 0 |  | 8150
|  |  |  | 5:00 | 8100 |  | 0 |  | 8100
|  |  |  | 6:00 | 8350 |  | 0 |  | 8350
|  |  |  | 7:00 | 8650 |  | 0 |  | 8650
|  |  |  | 8:00 | 9410 |  | 0 |  | 9410
|  |  |  | 9:00 | 9590 |  | 0 |  | 9590
|  |  |  | 10:00 | 9460 |  | 0 |  | 9460
|  |  |  | 11:00 | 9600 |  | 0 |  | 9600
|  |  |  | 12:00 | 10060 |  | 0 |  | 10060
|  |  |  | 13:00 | 10620 |  | 0 |  | 10620
|  |  |  | 14:00 | 9060 |  | 0 |  | 9060
|  |  |  | 15:00 | 8600 |  | 0 |  | 8600
|  |  |  | 16:00 | 8360 |  | 0 |  | 8360
|  |  |  | 17:00 | 8420 |  | 0 |  | 8420
|  |  |  | 18:00 | 9020 |  | 0 |  | 9020
|  |  |  | 18:30 | 9600 |  | 0 |  | 9600
|  |  |  | 19:00 | 10110 |  | 0 |  | 10110
|  |  |  | 19:30 | 10050 |  | 0 |  | 10050
|  |  |  | 20:00 | 10010 |  | 0 |  | 10010
|  |  |  | 21:00 | 9930 |  | 0 |  | 9930
|  |  |  | 22:00 | 9580 |  | 0 |  | 9580
|  |  |  | 23:00 | 9050 |  | 0 |  | 9050
Probable Maximum Temperature: |  |  | 28.30°C
Probable Maximum Demand at Day Peak: |  |  | 10060.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10110.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10110.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 219.99 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:17 hrs on 14-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7849.95 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3484.9 | MW
i) Dhaka area |  |  | 4381.45 |  | MW | i) Khulna area |  |  |  | 1274 | MW
ii) Chattogram area |  |  | 1186.5 |  | MW | ii) Barishal area |  |  |  | 312.5 | MW
iii) Cumilla area |  |  | 967 |  | MW | iii) Rajshahi area |  |  |  | 1140.4 | MW
iv) Mymensingh area |  |  | 919 |  | MW | iv) Rangpur area |  |  |  | 758 | MW
v) Sylhet area |  |  | 396 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11334.85 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 63 | 08:00 | 133 | Postogola | 43 | 13:00
2 | AKSML | 20 | 18:30 | 68 | Jamalpur | 90 | 21:00 | 134 | Purbachal | 16 | 13:00
3 | Aftabnagar | 28 | 18:00 | 69 | Jashore | 118 | 13:00 | 135 | Purbasadipur | 124 | 12:00
4 | Agargaon | 86 | 13:00 | 70 | Jhenaidah | 97 | 18:30 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 76 | 18:30 | 71 | Joydebpur | 152 | 19:00 | 137 | Rahim | 39 | 16:00
6 | Amnura | 52 | 08:00 | 72 | Joypurhat | 55 | 08:00 | 138 | Rajbari | 56 | 18:30
7 | Ashuganj | 76 | 12:00 | 73 | Juldah | 12 | 00:00 | 139 | Rajendrapur | 116 | 13:00
8 | BSRM | 189 | 04:00 | 74 | KSRM | 28 | 14:00 | 140 | Rajshahi | 70 | 20:00
9 | Bagerhat | 71 | 18:30 | 75 | Kabirpur | 247 | 12:00 | 141 | Rajshahi-230 | 72 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 56 | 18:00 | 142 | Ramganj | 100 | 18:30
11 | Bakulia | 77 | 13:00 | 77 | Kallyanpur | 69 | 18:00 | 143 | Rampur | 31 | 14:00
12 | Banani | 22 | 11:00 | 78 | Kalurghat | 34 | 15:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 10 | 10:00 | 79 | Kamrangirchar | 63.2 | 13:00 | 145 | Rangpur | 110 | 13:00
14 | Barapukuria | 60 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 5.2 | 16:00
15 | Barguna | 14 | 18:00 | 81 | Kazla | 101 | 16:00 | 147 | SSM | 22 | 09:00
16 | Barishal | 78 | 13:00 | 82 | Keranigonj | 52 | 00:00 | 148 | Saidpur | 107 | 09:00
17 | Barishal-230 | 80 | 18:30 | 83 | Khagrachori | 24 | 19:00 | 149 | Satkhira | 100 | 19:00
18 | Baroaulia | 61 | 12:00 | 84 | Khulna | 67 | 13:00 | 150 | Satmasjid | 84 | 13:00
19 | Baroirhat | 50 | 19:00 | 85 | Khulshi | 156 | 13:00 | 151 | Savar | 192 | 10:00
20 | Bashundhara | 142 | 13:00 | 86 | Kishoreganj | 116 | 18:30 | 152 | SevenRings | 8.97 | 10:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 184 | 15:00 | 153 | ShahCement | 27 | 10:00
22 | Beanibazar | 46 | 18:00 | 88 | Kulaura | 29 | 18:00 | 154 | Shahjadpur | 64 | 18:30
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 68 | 08:00 | 155 | Shahjibazar | 99 | 18:30
24 | Bhaluka | 118 | 11:00 | 90 | Kushtia | 112 | 18:30 | 156 | Shahmirpur | 41 | 16:00
25 | Bhandaria | 36 | 21:00 | 91 | Lalbag | 74 | 13:00 | 157 | Shariatpur | 50 | 14:00
26 | Bhangura | 34 | 18:30 | 92 | Lalmonirhat | 48 | 18:30 | 158 | Sherpur | 122 | 00:00
27 | Bheramara(GK) | 42 | 18:30 | 93 | MI_Cement | 12.2 | 13:00 | 159 | Shikalbaha | 28 | 12:00
28 | Bhulta | 236 | 12:00 | 94 | Madanganj | 22 | 13:00 | 160 | Shitalakhya | 72.7 | 12:00
29 | Bog-Sherpur | 68 | 09:00 | 95 | Madaripur | 73 | 19:00 | 161 | Sholosohor | 34 | 13:00
30 | Bogura | 120 | 18:30 | 96 | Madartek | 63.79 | 13:00 | 162 | Shyampur | 166 | 11:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madunaghat | 38 | 19:30 | 163 | Siddhirganj | 110 | 10:00
32 | Brahmanbaria | 114 | 18:30 | 98 | Magura | 46 | 18:30 | 164 | Sirajganj | 92 | 08:00
33 | Cantonment | 106 | 13:00 | 99 | Mahasthangarh | 56 | 08:00 | 165 | Sonargaon | 93 | 15:00
34 | Chandpur | 50 | 19:00 | 100 | Manikganj | 113 | 19:00 | 166 | Sreemongol | 50 | 18:00
35 | Chandraghona | 26 | 19:00 | 101 | Maniknagar | 58 | 13:00 | 167 | Sreepur | 87 | 09:00
36 | Chapai | 71 | 12:00 | 102 | Matarbari | 36 | 18:30 | 168 | Srinagar | 31.8 | 21:00
37 | Charsaidpur | 38 | 12:00 | 103 | Matuail | 65 | 12:00 | 169 | Sunamganj | 40 | 18:00
38 | Chauddagram | 49 | 14:00 | 104 | Millgate | 73 | 16:00 | 170 | Sylhet | 26 | 19:30
39 | Chhatak | 24 | 18:00 | 105 | Mirpur | 116 | 18:30 | 171 | Sylhet-132 | 85 | 18:30
40 | Chowmuhani | 147 | 18:30 | 106 | Mirsorai | 9 | 18:30 | 172 | TK | 18.2 | 00:00
41 | Chuadanga | 74 | 13:00 | 107 | Mirzapur | 37 | 22:00 | 173 | Tangail | 154 | 12:00
42 | Coxsbazar | 116 | 18:00 | 108 | Mithapukur | 56 | 08:00 | 174 | Thakurgaon | 84 | 19:00
43 | Cumilla(N) | 151 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 124 | 11:00
44 | Cumilla(S) | 113 | 12:00 | 110 | Mogbazar | 108.3 | 13:00 | 176 | Ullahpara | 27 | 08:00
45 | Daudkandi | 102 | 18:30 | 111 | Mongla | 30 | 18:30 | 177 | Ullon | 38 | 13:00
46 | Dhaka | 36 | 12:00 | 112 | Motijheel | 30 | 13:00 | 178 | Uttara | 73 | 13:00
47 | Dhamrai | 110 | 11:00 | 113 | Muktagacha | 26 | 18:00 | 179 | UttaraNew | 34 | 12:00
48 | Dhanmondi | 118 | 13:00 | 114 | Munshiganj | 67 | 14:00 | 180 | Zigatola | 65 | 13:00
49 | Dohazari | 87 | 19:00 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 112 | 19:00 | 116 | Mymensingh | 168 | 19:00
51 | Fatullah | 77 | 12:00 | 117 | Naogaon | 111 | 13:00
52 | Fenchuganj | 26 | 18:00 | 118 | Narail | 36 | 08:00
53 | Feni | 82 | 18:30 | 119 | Narinda | 70.5 | 13:00
54 | GPH | 13 | 09:00 | 120 | Narshingdi | 168 | 19:00
55 | Ghatail | 50 | 18:00 | 121 | Natore | 111 | 13:00
56 | Ghorashal | 11 | 00:00 | 122 | Nawabganj | 30.4 | 13:00
57 | Ghorashal-230 | 58 | 20:00 | 123 | Netrakona | 133 | 09:00
58 | Goalpara | 28 | 13:00 | 124 | New | 75 | 11:00
59 | Gollamari | 64 | 13:00 | 125 | Niamatpur | 88 | 13:00
60 | Gopalganj | 82 | 18:30 | 126 | Noapara | 38 | 19:00
61 | Gulshan | 92 | 13:00 | 127 | PHP | 7 | 07:00
62 | Halishahar | 46 | 15:00 | 128 | Pabna | 68 | 13:00
63 | HaripurSBU | 179 | 09:00 | 129 | Palashbari | 100 | 08:00
64 | Hasnabad | 104 | 18:30 | 130 | Panchagarh | 44 | 18:30
65 | Hathazari | 59 | 13:00 | 131 | Patuakhali | 53 | 21:00
66 | Ishurdi | 61 | 18:30 | 132 | Payra | 22 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 03:00 | 388 | 13:00 | Payra | 418 | 05:00 | 408 | 12:00
Ashuganj | 410 | 0:00 | 392 | 12:00 | Rahanpur | 414 | 03:00 | 398 | 08:00
Bhulta | 404 | 05:00 | 374 | 12:00 | Rampal | 407 | 03:00 | 392 | 12:00
Bibiana | 409 | 19:00 | 392 | 12:00
BIPTC | 404 | 04:00 | 386 | 13:00
Bogura | 411 | 03:00 | 394 | 08:00
Gopalganj | 409 | 03:00 | 393 | 12:00
Kaliakoir | 391 | 19:00 | 381 | 11:00
Madunaghat | 406 | 09:00 | 399 | 13:00
Meghnaghat | 402 | 04:00 | 381 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 03:00 | 220 | 13:00 | Keranigonj | 231 | 03:00 | 216 | 12:00
AKSML | 238 | 18:30 | 227 | 01:00 | Khulna(S) | 238 | 03:00 | 224 | 13:00
Aminbazar | 232 | 07:00 | 221 | 14:00 | Madunaghat | 236 | 08:00 | 228 | 01:00
Ashuganj | 240 | 03:00 | 224 | 12:00 | Madunaghat-400 | 236 | 19:00 | 229 | 02:00
Ashuganj-400 | 240 | 03:00 | 224 | 12:00 | Maniknagar | 234 | 04:00 | 216 | 12:00
Baghabari | 239 | 02:00 | 225 | 12:00 | Meghnaghat | 238 | 08:00 | 225 | 12:00
Barapukuria | 227 | 19:00 | 218 | 07:00 | Meghnaghat-400 | 233 | 03:00 | 221 | 11:00
Barapukuria-230 | 227 | 19:00 | 218 | 07:00 | Mirsorai | 239 | 19:00 | 226 | 12:00
Barishal | 243 | 06:00 | 234 | 12:00 | Rajshahi | 238 | 04:00 | 224 | 12:00
Bheramara | 239 | 03:00 | 223 | 12:00 | Rampal | 236 | 03:00 | 223 | 12:00
Bhulta | 234 | 03:00 | 216 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 08:00 | 223 | 12:00 | Rampura | 233 | 03:00 | 215 | 12:00
BIPTC | 241 | 03:00 | 224 | 12:00 | Shikalbaha | 239 | 19:00 | 226 | 01:00
Bogura | 241 | 05:00 | 228 | 08:00 | Shyampur | 231 | 03:00 | 217 | 12:00
Bogura-400 | 238 | 03:00 | 227 | 08:00 | Siddhirganj | 234 | 07:00 | 218 | 12:00
Borhanuddin | 246 | 03:00 | 241 | 12:00 | Sirajgonj | 246 | 05:00 | 232 | 12:00
BSRM | 237 | 08:00 | 225 | 12:00 | Sreepur | 240 | 03:00 | 223 | 12:00
Cumilla(N) | 233 | 08:00 | 221 | 12:00 | Tongi | 231 | 04:00 | 212 | 11:00
Faridpur | 240 | 03:00 | 230 | 12:00
Fenchuganj | 237 | 18:30 | 229 | 01:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 234 | 03:00 | 216 | 12:00
Gopalganj | 240 | 03:00 | 230 | 12:00
GPH | 237 | 19:00 | 228 | 02:00
Haripur | 232 | 03:00 | 216 | 12:00
Hasnabad | 233 | 04:00 | 217 | 12:00
Hathazari | 239 | 19:00 | 229 | 01:00
Ishurdi | 242 | 03:00 | 225 | 12:00
Jhenaidah | 236 | 04:00 | 221 | 12:00
Kaliakoir | 226 | 19:00 | 214 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 03:00 | 120 | 12:00 | Magura | 138 | 04:00 | 126 | 12:00
Agargaon | 135 | 03:00 | 124 | 12:00 | Mahasthangarh | 136 | 03:00 | 126 | 08:00
Agrabad | 135 | 08:00 | 130 | 01:00 | Manikganj | 136 | 19:00 | 131 | 12:00
AKS | 134 | 02:00 | 130 | 00:00 | Maniknagar | 132 | 04:00 | 121 | 12:00
Aminbazar | 132 | 00:00 | 125 | 14:00 | Matarbari | 127 | 09:00 | 121 | 00:00
Amnura | 141 | 00:00 | 128 | 08:00 | Matuail | 132 | 02:00 | 123.6 | 12:00
Ashuganj | 141 | 05:00 | 135 | 12:00 | Millgate | 136 | 03:00 | 120 | 12:00
Bagerhat | 135 | 03:00 | 124 | 12:00 | Mirpur | 132 | 00:00 | 122 | 12:00
Bajitpur | 135 | 02:00 | 129 | 11:00 | Mirzapur | 134 | 03:00 | 126 | 12:00
Bakulia | 136 | 09:00 | 129 | 01:00 | Mithapukur | 136 | 19:30 | 123 | 07:00
Banani | 132 | 03:00 | 119 | 12:00 | MI_Cement | 134 | 05:00 | 125 | 12:00
Bangabhaban | 133 | 05:00 | 120 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 137 | 20:00 | 128 | 07:00 | Mogbazar | 133 | 05:00 | 120 | 12:00
Barguna | 138 | 19:30 | 132 | 12:00 | Mongla | 135 | 05:00 | 125 | 12:00
Barishal | 134 | 04:00 | 128 | 12:00 | Motijheel | 133 | 05:00 | 120 | 12:00
Barishal-230 | 135 | 05:00 | 128 | 12:00 | Muktagacha | 128 | 19:00 | 118 | 12:00
Baroaulia | 137 | 19:00 | 132 | 00:00 | Munshiganj | 133 | 06:00 | 124 | 12:00
Baroirhat | 135 | 19:00 | 125 | 12:00 | Muradnagar | 134 | 19:00 | 126 | 12:00
Bashundhara | 134 | 07:00 | 119 | 12:00 | Mymensingh | 126 | 19:00 | 115 | 12:00
BashundharaCement | 133 | 03:00 | 124 | 12:00 | Naogaon | 136 | 19:00 | 123 | 07:00
Beanibazar | 135 | 03:00 | 125 | 12:00 | Narail | 138 | 03:00 | 126 | 12:00
Benapole | 136 | 04:00 | 121 | 12:00 | Narinda | 132 | 04:00 | 121 | 12:00
Bhaluka | 128 | 02:00 | 117 | 12:00 | Narshingdi | 132 | 07:00 | 118 | 13:00
Bhandaria | 131 | 05:00 | 125 | 13:00 | Natore | 137 | 00:00 | 130 | 12:00
Bhangura | 137 | 01:00 | 127 | 12:00 | Nawabganj | 139 | 05:00 | 128 | 12:00
Bheramara | 139 | 00:00 | 132 | 12:00 | Netrakona | 125 | 00:00 | 113 | 10:00
Bheramara(GK) | 138 | 00:00 | 132 | 12:00 | New | 137 | 05:00 | 121 | 12:00
Bhulta | 126 | 00:00 | 119 | 12:00 | Niamatpur | 139 | 05:00 | 131 | 09:00
Bog-Sherpur | 136 | 03:00 | 127 | 08:00 | Noapara | 136 | 03:00 | 125 | 12:00
Bogura | 137 | 04:00 | 129 | 09:00 | Pabna | 136 | 02:00 | 122 | 12:00
Bogura-230 | 138 | 04:00 | 129 | 08:00 | Palashbari | 132 | 03:00 | 117 | 08:00
Brahmanbaria | 139 | 18:00 | 125 | 12:00 | Panchagarh | 141 | 14:00 | 123 | 07:00
Cantonment | 135 | 03:00 | 124 | 12:00 | Patuakhali | 138 | 20:00 | 131 | 12:00
Chandpur | 139 | 18:00 | 121 | 01:00 | Payra | 138 | 19:30 | 133 | 12:00
Chandraghona | 136 | 09:00 | 132 | 07:00 | PHP | 134 | 19:00 | 125 | 01:00
Chapai | 138 | 03:00 | 129 | 08:00 | Postogola | 137 | 06:00 | 128 | 12:00
Charsaidpur | 134 | 06:00 | 124 | 12:00 | Purbachal | 133 | 03:00 | 120 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 08:00 | 127 | 12:00 | Purbasadipur | 136 | 22:00 | 120 | 07:00
Chhatak | 135 | 06:00 | 125 | 12:00 | Rahanpur | 140 | 04:00 | 134 | 08:00
Chowmuhani | 132 | 08:00 | 122 | 01:00 | Rahanpur-400 | 140 | 03:00 | 134 | 08:00
Chuadanga | 137 | 03:00 | 124 | 12:00 | Rahim | 131 | 03:00 | 123 | 12:00
Coxsbazar | 125 | 07:00 | 120 | 12:00 | Rajbari | 133 | 03:00 | 127 | 12:00
Cumilla(N) | 136 | 09:00 | 128 | 12:00 | Rajendrapur | 134 | 04:00 | 122 | 13:00
Cumilla(S) | 136 | 08:00 | 126 | 12:00 | Rajshahi | 138 | 00:00 | 131 | 12:00
Daudkandi | 131 | 05:00 | 124 | 12:00 | Rajshahi-230 | 138 | 04:00 | 124 | 12:00
Dhaka | 133 | 04:00 | 121 | 12:00 | Ramganj | 135 | 19:00 | 120 | 02:00
Dhamrai | 132 | 03:00 | 120 | 12:00 | Rampur | 137 | 19:00 | 129 | 02:00
Dhanmondi | 133 | 06:00 | 123.5 | 12:00 | Rampura | 132 | 03:00 | 120 | 12:00
Dohazari | 135 | 19:00 | 128 | 03:00 | Rangamati | 136 | 19:00 | 131 | 02:00
Faridpur | 135 | 04:00 | 128 | 12:00 | Rangpur | 134 | 20:00 | 118 | 07:00
Fatullah | 135 | 04:00 | 125 | 12:00 | Ruppur | 140 | 00:00 | 133 | 12:00
Fenchuganj | 138 | 03:00 | 131 | 12:00 | Saidpur | 134 | 19:00 | 122 | 07:00
Feni | 134 | 08:00 | 125 | 01:00 | Satkhira | 136 | 04:00 | 124 | 12:00
Ghatail | 129 | 19:00 | 119 | 12:00 | Satmasjid | 134 | 03:00 | 123 | 12:00
Ghorashal | 140 | 00:00 | 132 | 12:00 | Savar | 131 | 05:00 | 122 | 14:00
Goalpara | 138 | 03:00 | 128 | 13:00 | SevenRings | 142 | 08:00 | 131 | 11:00
Gollamari | 137 | 03:00 | 128 | 12:00 | ShahCement | 134 | 06:00 | 124 | 12:00
Gopalganj | 135 | 03:00 | 128 | 00:00 | Shahjadpur | 142 | 03:00 | 131 | 12:00
Gopalganj-400 | 136 | 03:00 | 129 | 12:00 | Shahjibazar | 137 | 02:00 | 127 | 12:00
Gulshan | 133 | 08:00 | 119 | 12:00 | Shahmirpur | 139 | 19:00 | 129 | 02:00
Halishahar | 138 | 19:00 | 131 | 01:00 | Shariatpur | 135 | 05:00 | 128 | 12:00
Haripur | 133 | 05:00 | 124 | 12:00 | Sherpur | 123 | 13:00 | 112 | 04:00
HaripurSBU | 139 | 03:00 | 124 | 12:00 | Shikalbaha | 126 | 18:30 | 119 | 02:00
Hasnabad | 137 | 04:00 | 126 | 13:00 | Shikalbaha-230 | 139 | 19:00 | 124 | 14:00
Hathazari | 138 | 19:00 | 133 | 12:00 | Shitalakhya | 134 | 05:00 | 125 | 12:00
Ishurdi | 141 | 03:00 | 133 | 12:00 | Sholosohor | 137 | 19:00 | 131 | 12:00
Jaldhaka | 133 | 20:00 | 126 | 08:00 | Shyampur | 134 | 04:00 | 125 | 12:00
Jamalpur | 128 | 19:00 | 112 | 05:00 | Shyampur-230 | 135 | 03:00 | 125 | 12:00
Jashore | 135 | 03:00 | 123 | 12:00 | Siddhirganj | 133 | 06:00 | 124 | 12:00
Jhenaidah | 138 | 04:00 | 127 | 12:00 | Sirajganj | 137 | 03:00 | 128 | 07:00
Jhenaidah-230 | 139 | 03:00 | 128 | 12:00 | Sonargaon | 131 | 03:00 | 122 | 12:00
Joydebpur | 137 | 03:00 | 126 | 12:00 | Sreemongol | 137 | 05:00 | 127 | 12:00
Joypurhat | 135 | 03:00 | 120 | 08:00 | Sreepur | 130 | 03:00 | 121 | 12:00
Juldah | 139 | 19:00 | 130 | 01:00 | Srinagar | 138 | 03:00 | 128 | 12:00
Kabirpur | 140 | 00:00 | 118 | 12:00 | SSM | 141 | 19:00 | 134 | 16:00
Kachua | 139 | 19:00 | 124 | 01:00 | Sunamganj | 134 | 04:00 | 124 | 12:00
Kaliakoir | 140 | 18:00 | 123 | 13:00 | Sylhet | 136 | 06:00 | 126 | 12:00
Kallyanpur | 134 | 06:00 | 127 | 12:00 | Sylhet-132 | 136 | 06:00 | 126 | 12:00
Kalurghat | 137 | 09:00 | 131 | 01:00 | Tangail | 130 | 03:00 | 120 | 12:00
Kamrangirchar | 136 | 01:00 | 127 | 12:00 | Thakurgaon | 141 | 23:00 | 120 | 07:00
Kaptai | 135 | 4:00 | 124 | 12:00 | TK | 137 | 09:00 | 132 | 04:00
Kazla | 132 | 04:00 | 120 | 13:00 | Tongi | 136 | 03:00 | 124 | 11:00
Keranigonj | 138 | 04:00 | 127 | 12:00 | Ullahpara | 137 | 00:00 | 128 | 12:00
Khagrachori | 136 | 19:00 | 130 | 12:00 | Ullon | 131 | 05:00 | 121 | 12:00
Khulna | 135 | 03:00 | 126 | 12:00 | Uttara | 132 | 00:00 | 122 | 12:00
Khulna(S) | 138 | 03:00 | 127 | 12:00 | UttaraNew | 133 | 00:00 | 122 | 12:00
Khulshi | 136 | 09:00 | 130 | 04:00 | Zigatola | 138 | 04:00 | 127 | 13:00
Kishoreganj | 134 | 05:00 | 126 | 12:00
Kodda | 138 | 18:00 | 126 | 09:00
KSRM | 138 | 19:00 | 131 | 07:00
Kulaura | 137 | 04:00 | 129 | 12:00
Kurigram | 132 | 23:00 | 118 | 07:00
Kushtia | 139 | 02:00 | 130 | 12:00
Lalbag | 137 | 03:00 | 128 | 12:00
Lalmonirhat | 132 | 23:00 | 122 | 07:00
Madanganj | 133 | 03:00 | 124 | 12:00
Madaripur | 133 | 00:00 | 129 | 12:00
Madartek | 132 | 05:00 | 119 | 12:00
Madunaghat | 136 | 09:00 | 131 | 01:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-02-2025 | [28 empty] | Date: | 13-02-2025 | [28 empty] | Date: | 13-02-2025 | [28 empty] | Date: | 13-02-2025 | [28 empty] | Date: | 13-02-2025 | [19 empty] | Date: | 13-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [19 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 0 | 0 | 0 | 256 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 17 | 22 | 0 | 450 | 258 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 37 | 273 | 0 | 0 | 19 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 157 | 0 | 0 | 357 | 8 | 219 | 30 | 0 | 0 | 68 | 29 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 18 | 0 | 0 | 0 | 5040 | 922 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 155 | 72 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 7 | 100 | 180 | 0 | 0 | 622 | 17 | 4625.5 | 9665.5 | 90.66
01:00 | 0 | 52 | 0 | 0 | 0 | 256 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 260 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 157 | 0 | 0 | 357 | 5 | 225 | 30 | 0 | 0 | 0 | 0 | 14 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 20 | 0 | 0 | 2 | 4635 | 923 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 126 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 0 | 4477.5 | 9112.5 | 90.66
02:00 | 0 | 52 | 0 | 0 | 0 | 256 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 265 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 276 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 540 | 0 | 51 | 0 | 157 | 0 | 0 | 357 | 5 | 226 | 30 | 0 | 0 | 0 | 0 | 14 | 0 | 52 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 23 | 0 | 0 | 0 | 4534 | 923 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 128 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 7 | 134 | 220 | 0 | 0 | 622 | 0 | 4237.5 | 8771.5 | 90.65
03:00 | 0 | 34 | 0 | 0 | 0 | 254 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 260 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 274 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 185 | 0 | 0 | 357 | 5 | 225 | 30 | 0 | 0 | 0 | 0 | 14 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 8 | 9 | 23 | 0 | 0 | 0 | 4558 | 835 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 151 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 134 | 220 | 0 | 0 | 580 | 0 | 3940.5 | 8498.5 | 90.65
04:00 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 285 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 274 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 185 | 0 | 0 | 357 | 5 | 183 | 30 | 0 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4493 | 736 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 154 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 132 | 220 | 0 | 0 | 622 | 0 | 3751.5 | 8244.5 | 90.65
05:00 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 280 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 187 | 0 | 0 | 357 | 5 | 183 | 30 | 0 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4474 | 735 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463 | 0 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 155 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 132 | 220 | 0 | 0 | 622 | 0 | 3749 | 8223 | 90.64
06:00 | 0 | 2 | 0 | 0 | 0 | 253 | 0 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 275 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 275 | 0 | 0 | 0.5 | 0 | 0 | 226 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 187 | 0 | 0 | 357 | 7 | 180 | 30 | 0 | 0 | 0 | 0 | 14 | 0 | 48 | 0 | 0 | 0 | 295 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 19 | 9 | 23 | 0 | 0 | 0 | 4499.3 | 735 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 158 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 132 | 220 | 0 | 0 | 622 | 0 | 4022 | 8521.3 | 90.64
07:00 | 0 | 52 | 0 | 0 | 0 | 252 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 2.9 | 54 | 22 | 0 | 420 | 313 | 0 | 0 | 10 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 275 | 0 | 0 | 16 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 187 | 0 | 0 | 357 | 17 | 210 | 30 | 0 | 0 | 0 | 3 | 14 | 0 | 50 | 0 | 1 | 0 | 290 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 23 | 0 | 0.51 | 1 | 4796.41 | 925 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.49 | 605 | 0 | 713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0.04 | 0 | 156 | 70 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 0.12 | 0 | 294 | 6 | 130 | 220 | 0 | 0 | 622 | 0 | 4464.97 | 9261.38 | 90.64
08:00 | 0 | 52 | 0 | 0 | 0 | 254 | 0 | 0 | 364 | 0 | 0 | 7 | 0 | 0 | 43 | 32 | 0 | 10 | 17 | 54 | 22 | 0 | 420 | 278 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 2 | 0 | 14 | 22 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 0 | 3 | 0 | 50 | 50 | 1 | 40 | 19 | 3 | 272 | 53 | 0 | 18 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 4 | 51 | 43 | 187 | 0 | 0 | 353 | 29 | 199 | 30 | 2 | 0 | 63 | 9 | 14 | 0 | 60 | 0 | 1 | 0 | 305 | 320 | 0 | 36 | 30 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 18 | 0 | 23 | 57 | 9 | 21 | 0 | 5.11 | 0 | 5261.11 | 878 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.54 | 619 | 0 | 763 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.27 | 0 | 158 | 70 | 72 | 7 | 78 | 0 | 0 | 0.9 | 41 | 0.6 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 0 | 4765.01 | 10026.12 | 90.63
09:00 | 0 | 52 | 0 | 0 | 0 | 251 | 0 | 0 | 357 | 0 | 0 | 17 | 0 | 0 | 70 | 32 | 0 | 55 | 17 | 54 | 25 | 0 | 450 | 277 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 7 | 10 | 14 | 22 | 0 | 0 | 35 | 45 | 8 | 0 | 0 | 0 | 35 | 0 | 89 | 100 | 2 | 40 | 66 | 3 | 275 | 53 | 0 | 27 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 102 | 157 | 0 | 0 | 360 | 20 | 209 | 30 | 16 | 0 | 155 | 9 | 16 | 0 | 68 | 0 | 26 | 0 | 300 | 320 | 0 | 36 | 30 | 0 | 5 | 120 | 16 | 0 | 82 | 30 | 0 | 20 | 0 | 35 | 59 | 9 | 19 | 0 | 11.83 | 6 | 5735.83 | 879 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.27 | 619 | 0 | 763 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 12 | 0 | 6.49 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.63 | 0 | 162 | 71 | 95 | 16 | 102 | 0 | 0 | 2.3 | 92 | 0.14 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 610 | 0 | 4882.83 | 10618.66 | 90.63
10:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 0 | 0 | 55 | 32 | 0 | 55 | 17 | 54 | 25 | 0 | 450 | 283 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 12 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 51 | 73 | 0 | 89 | 100 | 3 | 40 | 106 | 2 | 361 | 17 | 0 | 32 | 1 | 61 | 227 | 0 | 0 | 0 | 612 | 15 | 51 | 70 | 175 | 0 | 0 | 360 | 10 | 215 | 30 | 17 | 0 | 120 | 9 | 14 | 14 | 68 | 0 | 36 | 0 | 310 | 320 | 0 | 33 | 29 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 7 | 59 | 9 | 16 | 1 | 27.61 | 6 | 5706.61 | 924 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.19 | 620 | 0 | 762 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 25 | 0 | 25 | 16 | 0 | 22.43 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.2 | 2.5 | 158 | 68 | 95 | 24 | 49 | 0 | 0 | 3.9 | 127 | 0.24 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 600 | 0 | 5037.46 | 10744.07 | 90.62
11:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 50 | 48 | 38 | 55 | 35 | 54 | 25 | 0 | 450 | 297 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 28 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 51 | 65 | 0 | 50 | 50 | 3 | 40 | 110 | 2 | 470 | 17 | 0 | 33 | 24 | 87 | 227 | 0 | 0 | 0 | 612 | 17 | 51 | 70 | 183 | 0 | 0 | 300 | 10 | 220 | 30 | 17 | 0 | 120 | 9 | 14 | 17 | 70 | 13 | 49 | 25 | 300 | 320 | 0 | 32 | 28 | 0 | 5 | 163 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 15 | 1 | 36.84 | 6 | 5922.84 | 925 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.23 | 585 | 0 | 758 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 35 | 0 | 25 | 74 | 0 | 27.86 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.13 | 2.5 | 160 | 68 | 95 | 29 | 49 | 0 | 0 | 4.7 | 155 | 0.45 | 0 | 307 | 5 | 130 | 180 | 0 | 0 | 600 | 0 | 5052.87 | 10975.71 | 90.62
12:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 58 | 48 | 45 | 55 | 35 | 54 | 17 | 0 | 450 | 306 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 31 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 13 | 0 | 0 | 51 | 65 | 0 | 50 | 60 | 4 | 40 | 110 | 2 | 575 | 25 | 0 | 33 | 25 | 87 | 226 | 0 | 0 | 0 | 612 | 18 | 51 | 96 | 182 | 0 | 0 | 0 | 11 | 215 | 27 | 17 | 0 | 134 | 9 | 10 | 17 | 78 | 16 | 63 | 39 | 305 | 350 | 0 | 32 | 27 | 0 | 5 | 163 | 17 | 0 | 82 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 15 | 2 | 43.08 | 6 | 6110.08 | 925 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.78 | 619 | 0 | 758 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 50 | 0 | 25 | 96 | 0 | 53.31 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.82 | 2.5 | 156 | 67 | 95 | 26 | 50 | 0 | 0 | 5.2 | 163 | 0.58 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 610 | 0 | 5287.19 | 11397.27 | 90.62
13:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 406 | 0 | 0 | 17 | 0 | 0 | 60 | 48 | 81 | 55 | 0 | 54 | 25 | 0 | 450 | 274 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 29 | 17 | 19 | 22 | 0 | 0 | 35 | 115 | 23 | 0 | 0 | 51 | 57 | 0 | 89 | 100 | 1 | 40 | 110 | 2 | 575 | 35 | 0 | 33 | 25 | 87 | 226 | 0 | 0 | 0 | 612 | 18 | 51 | 140 | 182 | 0 | 0 | 0 | 27 | 182 | 30 | 34 | 0 | 193 | 9 | 16 | 17 | 74 | 16 | 53 | 39 | 305 | 320 | 0 | 34 | 28 | 0 | 5 | 163 | 8 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 12 | 2 | 39.2 | 6 | 6300.2 | 925 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.82 | 620 | 0 | 759 | 0 | 0 | 0 | 0 | 98 | 0 | 49 | 70 | 17 | 25 | 92 | 30 | 49.68 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.31 | 2.5 | 160 | 67 | 95 | 30 | 106 | 0 | 0 | 5.4 | 155 | 0.51 | 0 | 307 | 5 | 100 | 220 | 0 | 0 | 622 | 0 | 5317.22 | 11617.42 | 90.61
14:00 | 0 | 52 | 0 | 0 | 0 | 250 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 63 | 48 | 145 | 55 | 0 | 54 | 25 | 0 | 350 | 253 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 26 | 17 | 20 | 22 | 0 | 0 | 35 | 115 | 48 | 0 | 0 | 51 | 63 | 0 | 89 | 100 | 3 | 40 | 51 | 2 | 575 | 35 | 0 | 33 | 25 | 87 | 221 | 0 | 0 | 0 | 612 | 16 | 51 | 138 | 180 | 0 | 0 | 0 | 29 | 183 | 31 | 34 | 0 | 155 | 9 | 16 | 17 | 78 | 16 | 52 | 46 | 300 | 320 | 0 | 31 | 29 | 0 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 49 | 9 | 12 | 2 | 34.79 | 6 | 6143.79 | 925 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.3 | 620 | 0 | 759.13 | 0 | 0 | 0 | 0 | 70 | 0 | 49 | 35 | 22 | 0 | 88 | 30 | 49.78 | 20 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 4.11 | 2.5 | 158 | 67 | 95 | 25 | 71 | 0 | 0 | 4.6 | 141 | 0.42 | 0 | 307 | 5 | 100 | 220 | 0 | 0 | 622 | 0 | 5124.84 | 11268.63 | 90.61
15:00 | 0 | 52 | 0 | 0 | 0 | 246 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 95 | 48 | 95 | 55 | 17 | 54 | 25 | 0 | 350 | 288 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 17 | 19 | 22 | 0 | 0 | 35 | 65 | 50 | 0 | 1 | 51 | 71 | 0 | 89 | 100 | 2 | 40 | 51 | 2 | 575 | 35 | 0 | 33 | 8 | 87 | 221 | 0 | 0 | 0 | 612 | 12 | 40 | 124 | 180 | 0 | 0 | 0 | 29 | 183 | 28 | 21 | 0 | 155 | 9 | 17 | 0 | 72 | 0 | 35 | 47 | 285 | 320 | 0 | 29 | 29 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 12 | 2 | 29.05 | 6 | 5992.05 | 924 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.42 | 617 | 0 | 759.09 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 23 | 0 | 70 | 30 | 33.62 | 20 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 3.5 | 2.5 | 154 | 67 | 95 | 9 | 70 | 0 | 0 | 3.5 | 68 | 0.37 | 0 | 307 | 5 | 100 | 220 | 0 | 0 | 622 | 0 | 4921 | 10913.05 | 90.6
16:00 | 0 | 52 | 0 | 0 | 0 | 246 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 95 | 48 | 95 | 55 | 17 | 54 | 25 | 0 | 350 | 291 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 10 | 17 | 19 | 22 | 0 | 0 | 35 | 65 | 51 | 0 | 5 | 51 | 71 | 0 | 50 | 50 | 1 | 40 | 51 | 2 | 575 | 35 | 0 | 33 | 0 | 87 | 222 | 0 | 0 | 0 | 612 | 6 | 51 | 70 | 180 | 0 | 0 | 0 | 29 | 183 | 31 | 17 | 0 | 155 | 9 | 17 | 0 | 74 | 0 | 22 | 47 | 290 | 320 | 0 | 31 | 29 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 12 | 1 | 17.95 | 6 | 5837.95 | 925 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.96 | 610 | 0 | 758.69 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 21 | 0 | 43 | 30 | 18.59 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1.64 | 2.5 | 155 | 67 | 95 | 11 | 70 | 0 | 0 | 2.1 | 76 | 0.2 | 0 | 307 | 4 | 100 | 220 | 0 | 0 | 610 | 0 | 4816.68 | 10654.63 | 90.6
17:00 | 0 | 52 | 0 | 0 | 0 | 246 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 95 | 64 | 95 | 55 | 17 | 54 | 25 | 0 | 350 | 286 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3 | 17 | 19 | 22 | 0 | 0 | 35 | 65 | 50 | 0 | 6 | 84 | 79 | 0 | 50 | 50 | 0 | 40 | 51 | 7 | 575 | 35 | 0 | 33 | 0 | 87 | 222 | 0 | 0 | 0 | 612 | 1 | 51 | 70 | 180 | 0 | 0 | 0 | 29 | 183 | 31 | 25 | 0 | 155 | 9 | 17 | 0 | 70 | 0 | 5 | 47 | 295 | 320 | 0 | 32 | 29 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 17 | 0 | 4.89 | 6 | 5865.89 | 925 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.46 | 609 | 0 | 758.05 | 0 | 0 | 16 | 0 | 0 | 0 | 49 | 0 | 21 | 0 | 13 | 30 | 5.88 | 38 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0.53 | 2.5 | 156 | 67 | 95 | 3 | 70 | 0 | 0 | 0.5 | 23 | 0 | 0 | 307 | 4 | 100 | 220 | 0 | 0 | 600 | 17 | 4721.92 | 10587.81 | 90.59
18:00 | 0 | 52 | 0 | 0 | 0 | 175 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 95 | 133 | 113 | 55 | 17 | 54 | 22 | 0 | 400 | 300 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 30 | 19 | 22 | 0 | 0 | 35 | 149 | 50 | 0 | 8 | 84 | 71 | 9 | 89 | 100 | 0 | 40 | 66 | 7 | 575 | 72 | 0 | 33 | 5 | 105 | 220 | 0 | 0 | 0 | 612 | 0 | 51 | 92 | 180 | 0 | 0 | 51 | 29 | 196 | 31 | 68 | 0 | 175 | 19 | 17 | 17 | 76 | 40 | 0 | 47 | 300 | 320 | 0 | 35 | 28 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 17 | 0 | 0 | 6 | 6455 | 924 | 209 | 0 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 0 | 758.55 | 0 | 0 | 0 | 0 | 9 | 0 | 89 | 35 | 30 | 0 | 0 | 30 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 155 | 67 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 6 | 130 | 180 | 0 | 0 | 600 | 17 | 4791.05 | 11246.05 | 90.59
19:00 | 0 | 52 | 0 | 0 | 0 | 175 | 0 | 0 | 415 | 0 | 0 | 17 | 0 | 0 | 128 | 133 | 95 | 55 | 17 | 54 | 22 | 0 | 420 | 248 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 35 | 19 | 22 | 0 | 0 | 35 | 145 | 51 | 0 | 6 | 68 | 71 | 17 | 89 | 89 | 0 | 40 | 110 | 15 | 575 | 145 | 0 | 33 | 25 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 120 | 184 | 0 | 0 | 175 | 29 | 182 | 31 | 69 | 0 | 200 | 27 | 17 | 34 | 70 | 52.2 | 0 | 47 | 300 | 302 | 0 | 32 | 28 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 39 | 59 | 9 | 18 | 0 | 0 | 6 | 6829.2 | 878 | 209 | 0 | 29 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 0 | 760.2 | 0 | 0 | 0 | 0 | 96 | 0 | 89 | 70 | 36 | 0 | 0 | 30 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 157 | 68 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 7 | 130 | 220 | 0 | 0 | 600 | 17 | 5113.7 | 11942.9 | 90.58
19:30 | 0 | 52 | 0 | 0 | 0 | 196 | 0 | 0 | 400 | 0 | 0 | 17 | 0 | 0 | 128 | 98 | 0 | 55 | 55 | 17 | 22 | 0 | 420 | 267 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 35 | 19 | 22 | 0 | 0 | 35 | 65 | 27 | 0 | 7 | 84 | 71 | 0 | 89 | 89 | 0 | 40 | 110 | 15 | 575 | 108 | 0 | 33 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 117 | 184 | 0 | 0 | 250 | 29 | 182 | 31 | 69 | 0 | 200 | 27 | 17 | 0 | 70 | 0 | 0 | 47 | 280 | 302 | 0 | 34 | 30 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 54.5 | 59 | 9 | 21 | 0 | 0 | 6 | 6548.5 | 878 | 209 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 760.07 | 0 | 0 | 0 | 0 | 35 | 0 | 89 | 10 | 36 | 0 | 0 | 30 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 154 | 68 | 95 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 610 | 35 | 4991.57 | 11540.07
20:00 | 0 | 52 | 0 | 0 | 0 | 195 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 131 | 98 | 0 | 55 | 55 | 17 | 22 | 0 | 420 | 293 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 7 | 84 | 71 | 0 | 89 | 89 | 0 | 40 | 110 | 15 | 575 | 35 | 0 | 33 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 120 | 184 | 0 | 0 | 246 | 29 | 183 | 31 | 69 | 0 | 200 | 27 | 17 | 0 | 68 | 0 | 0 | 47 | 280 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 54.5 | 59 | 9 | 21 | 0 | 0 | 6 | 6428.5 | 878 | 209 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 760.34 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 36 | 0 | 0 | 30 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 158 | 69 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 35 | 4971.84 | 11400.34 | 90.58
21:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 100 | 98 | 0 | 55 | 0 | 17 | 22 | 0 | 420 | 270 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 19.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 16 | 84 | 71 | 0 | 100 | 89 | 0 | 40 | 110 | 25 | 575 | 35 | 0 | 33 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 139 | 184 | 0 | 0 | 250 | 28 | 182 | 31 | 69 | 0 | 200 | 29 | 17 | 0 | 66 | 0 | 0 | 47 | 295 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 40 | 59 | 9 | 22 | 0 | 0 | 6 | 6348.5 | 878 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 0 | 761.78 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 36 | 8 | 0 | 30 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 5.5 | 160 | 69 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 35 | 4910.28 | 11258.78 | 90.57
22:00 | 0 | 52 | 0 | 0 | 0 | 205 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 96 | 98 | 0 | 30 | 0 | 17 | 22 | 0 | 420 | 293 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | 34 | 71 | 0 | 50 | 50 | 0 | 40 | 110 | 25 | 576 | 0 | 0 | 24 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 137 | 194 | 0 | 0 | 18 | 29 | 193 | 31 | 64 | 0 | 200 | 29 | 17 | 0 | 64 | 0 | 0 | 47 | 310 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 20 | 0 | 0 | 6 | 5888 | 925 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613 | 0 | 759.21 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 35 | 34 | 0 | 30 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 162 | 71 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 220 | 0 | 0 | 622 | 35 | 4979.71 | 10867.71 | 90.57
23:00 | 0 | 52 | 0 | 0 | 0 | 140 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 75 | 82 | 0 | 30 | 0 | 17 | 22 | 0 | 420 | 270 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 7 | 34 | 0 | 50 | 50 | 0 | 40 | 110 | 21 | 575 | 0 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 137 | 195 | 0 | 0 | 45 | 29 | 182 | 31 | 0 | 0 | 200 | 29 | 17 | 0 | 72 | 0 | 0 | 0 | 280 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 19 | 0 | 0 | 6 | 5572 | 925 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 0 | 754.73 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 35 | 34 | 0 | 30 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 156 | 71 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 134 | 220 | 0 | 0 | 622 | 35 | 4918.23 | 10490.23 | 90.56
Total KWH | 0 | 1116480 | 0 | 0 | 0 | 5212094 | 0 | 0 | 9540000 | 0 | 0 | 259560 | 0 | 0 | 1427904 | 1232160 | 951949 | 825004 | 265291 | 810720 | 573480 | 1920 | 9937000 | 6925091 | 0 | 0 | 265465 | 587400 | 0 | 0 | 0 | 157268 | 240000 | 371400 | 523080 | 0 | 0 | 661145 | 910800 | 401280 | 0 | 70560 | 782614 | 954288 | 42056 | 1160640 | 1248000 | 20520 | 930880 | 1526357 | 407040 | 10509090.91 | 623927 | 0 | 547680 | 159483.6 | 1553127 | 5401505 | 0 | 0 | 0 | 14339998 | 114210 | 1154698 | 1891854 | 4332364 | 0 | 0 | 4976000 | 478080 | 4834000 | 724104 | 563520 | 0 | 2881440 | 309960 | 371980 | 149340 | 1530240 | 146784 | 322627 | 554896 | 7235500 | 7726300 | 0 | 810864 | 701000 | 0 | 115728 | 3726000 | 450096 | 0 | 2022720 | 715200 | 0 | 287000 | 0 | 608040 | 1135200 | 194400 | 421440 | 9750 | 251720 | 102480 | 135323792.51 | 21128000 | 6757344 | 0 | 65280 | 26496 | 0 | 0 | 0 | 0 | 0 | 0 | 420480 | 14116360 | 0 | 16532000 | 0 | 0 | 11518 | 0 | 701472 | 0 | 804560 | 317376 | 246050 | 203515 | 512770 | 317108 | 279000 | 1106091 | 0 | 0 | 0 | 0 | 0 | 9203346 | 0 | 24300 | 56970 | 3752000 | 1635927 | 1533424 | 189224 | 1174588 | 0 | 0 | 32946.6 | 1046880 | 1951 | 26016 | 6960000 | 151274 | 2983000 | 4902780 | 0 | 0 | 14837818.18 | 218400 | 112276264.78 | 247600057.29