## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-02-2025 | during | 15-02-2025 | during | 15-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 150 | 250 | 240 | 230 | 240 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 405 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 282 | 277 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 14.5 | 11 | 22.5 | 22.5 | 22.5 | 22.5 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 16 | 25 | 25 | 25 | 25 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 0 | 0 | Under Maintenance
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 26 | 32 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 54 | 17 | 54 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1515.5 | 1677 | 4627.07 | 4623.07 | 2627.59 | 2623.59
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 227 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 22 | 51 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 32 | 24 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 17 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 28 | 32 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 37 | 108 | 108 | 32 | 32 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.67 | 0 | 3.67 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 20 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 22 | 35 | 116 | 116 | 35 | 35 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 0 | 0 | 8 | 0 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 575 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1653 | 1727 | 2942.53 | 2975.86 | 2670.53 | 2703.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 370 | 360 | 356.56 | 356.56 | 356 | 356 | HGPI Maintenance Work is going on.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 29 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 98 | 20 | 145 | 145 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 48 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 27 | 17 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 52 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 6 | 28 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 51 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 61 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1132 | 1081 | 2085.53 | 2030.53 | 1890.2 | 1835.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-02-2025 | during | 15-02-2025 | during | 15-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 25 | 32 | 210 | 210 | 35 | 35 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 37 | 200 | 200 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 87 | 115 | 115 | 57 | 57 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.68 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 17 | 38 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 169.68 | 200 | 653.3 | 601.5 | 229.3 | 177.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 29 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 35 | 35 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 994 | 1009 | 1057 | 1057 | 1018 | 1018
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 878 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 180 | 206 | 410 | 410 | 230 | 230 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89.04 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234.2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1193.04 | 1084 | 3588.2 | 3498.2 | 1964 | 1874
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 132 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 590 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1319.6 | 1291 | 1555.12 | 1555.12 | 1555.12 | 1555.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 36 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 13 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 175 | 182 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 30 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 41 | 40 | 92 | 92 | 92 | 92 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.91 | 0 | 5.55 | 0 | 5.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 758.34 | 764 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.85 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1618.6 | 1476.5 | 2339.79 | 2179.24 | 2007.01 | 1846.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 71 | 70 | 70 | 70 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 166 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 3.6 | 0 | 3.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 182 | 0 | 162.46 | 0 | 162.46 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 581 | 320 | 673.06 | 482 | 668.06 | 477
System Total |  |  |  |  | 27884.66 | 27150.742 | 10176.42 | 9865.5 | 19521.6 | 19002.52 | 14629.81 | 14110.73
Forecast Scenario (15-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8770 |  | 0 |  | 8770
|  |  |  | 1:00 | 8200 |  | 0 |  | 8200
|  |  |  | 2:00 | 7740 |  | 0 |  | 7740
|  |  |  | 3:00 | 7450 |  | 0 |  | 7450
|  |  |  | 4:00 | 7210 |  | 0 |  | 7210
|  |  |  | 5:00 | 7100 |  | 0 |  | 7100
|  |  |  | 6:00 | 7480 |  | 0 |  | 7480
|  |  |  | 7:00 | 8510 |  | 0 |  | 8510
|  |  |  | 8:00 | 9280 |  | 0 |  | 9280
|  |  |  | 9:00 | 9570 |  | 0 |  | 9570
|  |  |  | 10:00 | 9850 |  | 0 |  | 9850
|  |  |  | 11:00 | 10050 |  | 0 |  | 10050
|  |  |  | 12:00 | 10340 |  | 0 |  | 10340
|  |  |  | 13:00 | 10730 |  | 0 |  | 10730
|  |  |  | 14:00 | 10280 |  | 0 |  | 10280
|  |  |  | 15:00 | 9960 |  | 0 |  | 9960
|  |  |  | 16:00 | 9760 |  | 0 |  | 9760
|  |  |  | 17:00 | 9710 |  | 0 |  | 9710
|  |  |  | 18:00 | 10630 |  | 0 |  | 10630
|  |  |  | 18:30 | 11050 |  | 0 |  | 11050
|  |  |  | 19:00 | 11349.93 |  | 114.6668 |  | 11470
|  |  |  | 19:30 | 11280 |  | 0 |  | 11280
|  |  |  | 20:00 | 11060 |  | 0 |  | 11060
|  |  |  | 21:00 | 10960 |  | 0 |  | 10960
|  |  |  | 22:00 | 10370 |  | 0 |  | 10370
|  |  |  | 23:00 | 9870 |  | 0 |  | 9870
Probable Maximum Temperature: |  |  | 29.00°C
Probable Maximum Demand at Day Peak: |  |  | 10340.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 115
Probable Maximum Demand at Evening Peak: |  |  | 11470.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.22993 MKWHr. |  | 20 | 15 | 15 | 10 | 0 | 20 | 0 | 20 | 15 | 115
*** This report is generated digitally from Operation Information System (OIS) at 10:36 hrs on 15-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-02-2025 | [28 empty] | Date: | 14-02-2025 | [28 empty] | Date: | 14-02-2025 | [28 empty] | Date: | 14-02-2025 | [28 empty] | Date: | 14-02-2025 | [19 empty] | Date: | 14-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [19 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 70 | 82 | 0 | 0 | 0 | 17 | 22 | 0 | 420 | 270 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 40 | 575 | 0 | 0 | 19 | 0 | 95 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 195 | 0 | 0 | 50 | 29 | 182 | 31 | 0 | 0 | 200 | 29 | 17 | 0 | 60 | 0 | 0 | 0 | 280 | 320 | 0 | 35 | 30 | 0 | 5 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 19 | 0 | 0 | 6 | 5400 | 925 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 | 756.82 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 34 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 157 | 71 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 134 | 220 | 0 | 0 | 622 | 35 | 4606.32 | 10006.32 | 90.56
01:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 22 | 0 | 420 | 296 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 35 | 576 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 50 | 29 | 199 | 31 | 0 | 0 | 51 | 28 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 19 | 9 | 19 | 0 | 0 | 6 | 4833 | 925 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 757.06 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 160 | 71 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 134 | 220 | 0 | 0 | 622 | 0 | 4421.56 | 9254.56 | 90.55
02:00 | 0 | 52 | 0 | 0 | 0 | 219 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 310 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 575 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 88 | 29 | 207 | 31 | 0 | 0 | 0 | 29 | 17 | 0 | 56 | 0 | 0 | 0 | 315 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 19 | 9 | 26 | 0 | 0 | 6 | 4797 | 925 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 755.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 158 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 4000.72 | 8797.72 | 90.55
03:00 | 0 | 52 | 0 | 0 | 0 | 219 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 300 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 575 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 80 | 29 | 199 | 31 | 0 | 0 | 0 | 0 | 17 | 0 | 57 | 0 | 0 | 0 | 325 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 1 | 4723 | 924 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 162 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3963.32 | 8686.32 | 90.54
04:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 306 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 35 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 576 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 110 | 29 | 200 | 31 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4747 | 736 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 163 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3783.41 | 8530.41 | 90.54
05:00 | 0 | 52 | 0 | 0 | 0 | 220 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 22 | 0 | 320 | 243 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 35 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 40 | 0 | 38 | 575 | 17 | 0 | 0 | 0 | 4 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 3 | 197 | 0 | 0 | 147 | 29 | 181 | 31 | 0 | 0 | 5 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 290 | 300 | 0 | 35 | 30 | 0 | 2 | 120 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 2 | 19 | 9 | 34 | 0 | 0 | 0 | 4640 | 736 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 161 | 71 | 20 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 622 | 17 | 3751.74 | 8391.74 | 90.53
06:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 8 | 0 | 17 | 17 | 0 | 320 | 300 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 35 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0 | 40 | 14 | 38 | 575 | 17 | 0 | 11 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 40 | 197 | 0 | 0 | 170 | 29 | 204 | 31 | 0 | 0 | 51 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 285 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 19 | 9 | 34 | 0 | 0 | 0 | 4759 | 736 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 158 | 71 | 35 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 560 | 35 | 3487.95 | 8246.95 | 90.53
07:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 15 | 0.4 | 17 | 17 | 0 | 320 | 300 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 2 | 0 | 14.5 | 15 | 0 | 0 | 35 | 30 | 21 | 0 | 1 | 0 | 0 | 0 | 24 | 24 | 0 | 40 | 17 | 39 | 575 | 17 | 0 | 18 | 0 | 34 | 226 | 0 | 0 | 0 | 613 | 0 | 51 | 40 | 187 | 0 | 0 | 260 | 29 | 194 | 31 | 0 | 0 | 51 | 0 | 17 | 0 | 44 | 0 | 2 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 57 | 9 | 34 | 0 | 2.13 | 4 | 4924.03 | 830 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 0 | 0 | 750.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4 | 0 | 1.81 | 172 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.17 | 2.5 | 154 | 71 | 35 | 1 | 34 | 0 | 0 | 0 | 6 | 0 | 0 | 289 | 6 | 100 | 180 | 0 | 0 | 560 | 35 | 3789.14 | 8713.17 | 90.52
08:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 15 | 17 | 17 | 17 | 0 | 350 | 283 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 11 | 0 | 14.5 | 15 | 0 | 0 | 35 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0 | 40 | 17 | 38 | 576 | 17 | 0 | 18 | 0 | 34 | 226 | 0 | 0 | 0 | 613 | 0 | 51 | 43 | 187 | 0 | 0 | 370 | 29 | 182 | 28 | 0 | 0 | 51 | 5 | 17 | 0 | 46 | 0 | 12 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 58 | 9 | 34 | 1 | 15.44 | 1 | 5150.94 | 925 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.18 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 19.02 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.64 | 5.5 | 158 | 70 | 35 | 7 | 34 | 0 | 0 | 1.1 | 51 | 0 | 0 | 307 | 5 | 134 | 220 | 0 | 0 | 560 | 35 | 4181.44 | 9332.38 | 90.52
09:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 20 | 17 | 17 | 17 | 0 | 350 | 248 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 20 | 0 | 15.5 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 2 | 40 | 17 | 37 | 575 | 0 | 0 | 19 | 0 | 59 | 227 | 0 | 0 | 0 | 613 | 12 | 51 | 63 | 187 | 0 | 0 | 380 | 29 | 182 | 30 | 0 | 0 | 85 | 9 | 17 | 0 | 52 | 0 | 25 | 0 | 285 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 33 | 2 | 30.05 | 0 | 5163.55 | 878 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.47 | 0 | 0 | 758.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 38.68 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.31 | 5.5 | 158 | 72 | 35 | 17 | 34 | 0 | 0 | 2.6 | 101 | 0.31 | 0 | 307 | 5 | 100 | 220 | 0 | 0 | 550 | 35 | 4220.94 | 9384.49 | 90.51
10:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 15 | 17 | 17 | 0 | 0 | 400 | 269 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 0 | 15 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3 | 40 | 17 | 37 | 575 | 0 | 0 | 19 | 0 | 34 | 226 | 0 | 0 | 0 | 613 | 15 | 51 | 50 | 187 | 0 | 0 | 375 | 29 | 182 | 32 | 0 | 0 | 17 | 9 | 17 | 0 | 54 | 0 | 50 | 0 | 290 | 320 | 0 | 32 | 30 | 0 | 2 | 120 | 23 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 59 | 9 | 29 | 2 | 41.68 | 4 | 5045.68 | 923 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.65 | 0 | 0 | 756.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 89 | 0 | 50.47 | 174 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 4.52 | 5.5 | 160 | 72 | 35 | 25 | 34 | 0 | 0 | 3.8 | 145 | 0.48 | 0 | 250 | 5 | 100 | 220 | 0 | 0 | 550 | 35 | 4248.59 | 9294.27 | 90.51
11:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 15 | 0 | 17 | 17 | 0 | 400 | 307 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 33 | 0 | 14.5 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 40 | 17 | 37 | 575 | 0 | 0 | 19 | 0 | 17 | 225 | 0 | 0 | 0 | 613 | 14 | 43 | 57 | 185 | 0 | 0 | 370 | 29 | 192 | 32 | 0 | 0 | 17 | 9 | 17 | 0 | 54 | 0 | 58 | 0 | 310 | 320 | 0 | 35 | 29 | 0 | 2 | 120 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 17 | 59 | 9 | 25 | 2 | 48.43 | 6 | 5091.93 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.77 | 0 | 0 | 757.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 104 | 0 | 60.61 | 175 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 5.26 | 2.5 | 163 | 71 | 52 | 30 | 34 | 0 | 0 | 4.7 | 169 | 0.57 | 0 | 302 | 5 | 130 | 220 | 0 | 0 | 560 | 35 | 4423.68 | 9515.61 | 90.5
12:00 | 0 | 34 | 0 | 0 | 0 | 150 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 15 | 0 | 17 | 22 | 0 | 420 | 282 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 34 | 0 | 14.5 | 15 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 12 | 12 | 4 | 40 | 20 | 28 | 575 | 17 | 0 | 19 | 0 | 22 | 224 | 0 | 0 | 0 | 612 | 14 | 51 | 98 | 185 | 0 | 0 | 370 | 29 | 182 | 32 | 16 | 0 | 27 | 6 | 17 | 0 | 58 | 0 | 61 | 0 | 305 | 320 | 0 | 35 | 29 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 59 | 9 | 25 | 2 | 51.68 | 6 | 5464.18 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.04 | 0 | 0 | 758.34 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 13 | 8 | 108 | 30 | 62.85 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.91 | 2.5 | 161 | 71 | 95 | 33 | 34 | 0 | 0 | 5 | 182 | 0.6 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 35 | 4712.24 | 10176.42 | 90.5
13:00 | 0 | 34 | 0 | 0 | 0 | 150 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 0 | 50 | 0 | 17 | 0 | 0 | 420 | 272 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 33 | 17 | 14.5 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 32 | 0 | 100 | 100 | 3 | 40 | 71 | 29 | 575 | 17 | 0 | 19 | 0 | 75 | 225 | 0 | 0 | 0 | 612 | 16 | 51 | 137 | 185 | 0 | 0 | 375 | 29 | 182 | 31 | 17 | 0 | 91 | 9 | 17 | 0 | 62 | 0 | 61 | 0 | 305 | 320 | 0 | 34 | 28 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 58 | 9 | 25 | 2 | 49.3 | 6 | 5898.8 | 925 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.23 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 18 | 8 | 111 | 30 | 63.3 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.63 | 2.5 | 140 | 71 | 95 | 32 | 34 | 0 | 0 | 5.2 | 180 | 0.59 | 0 | 307 | 5 | 130 | 180 | 0 | 0 | 622 | 35 | 4663.45 | 10562.25 | 90.49
14:00 | 0 | 52 | 0 | 0 | 0 | 150 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 420 | 292 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 17 | 12 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 7 | 0 | 24 | 0 | 0 | 0 | 3 | 40 | 34 | 33 | 505 | 0 | 0 | 7 | 0 | 34 | 225 | 0 | 0 | 0 | 550 | 15 | 51 | 0 | 185 | 0 | 0 | 250 | 29 | 182 | 32 | 17 | 0 | 100 | 9 | 17 | 0 | 54 | 0 | 54 | 0 | 270 | 320 | 0 | 31 | 29 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 26 | 2 | 43.3 | 6 | 4921.3 | 925 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.63 | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 18 | 8 | 100 | 30 | 54.42 | 174 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 5.01 | 2.5 | 133 | 71 | 35 | 27 | 34 | 0 | 0 | 5 | 151 | 0.51 | 0 | 250 | 5 | 130 | 180 | 0 | 0 | 560 | 17 | 4226.07 | 9147.37 | 90.49
15:00 | 0 | 17 | 0 | 0 | 0 | 175 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 0 | 420 | 310 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 22 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 24 | 0 | 0 | 0 | 2 | 40 | 0 | 34 | 505 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 550 | 12 | 51 | 0 | 184 | 0 | 0 | 250 | 29 | 198 | 32 | 17 | 0 | 17 | 9 | 17 | 0 | 48 | 0 | 39 | 0 | 300 | 320 | 0 | 34 | 29 | 0 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 30 | 2 | 34.6 | 6 | 4743.6 | 925 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.66 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 18 | 0 | 78 | 30 | 43.54 | 174 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.89 | 2.5 | 155 | 71 | 0 | 21 | 0 | 0 | 0 | 3.5 | 119 | 0.38 | 0 | 250 | 4 | 130 | 180 | 0 | 0 | 560 | 17 | 4046.47 | 8790.07 | 90.48
16:00 | 0 | 17 | 0 | 0 | 0 | 175 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 420 | 295 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 14 | 0 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 24 | 0 | 0 | 0 | 1 | 40 | 0 | 40 | 502 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 550 | 7 | 51 | 0 | 184 | 0 | 0 | 250 | 29 | 188 | 32 | 17 | 0 | 0 | 9 | 17 | 0 | 50 | 0 | 20 | 0 | 320 | 320 | 0 | 31 | 29 | 0 | 2 | 163 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 32 | 1 | 18.67 | 6 | 4804.67 | 844 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.74 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 18 | 0 | 50 | 30 | 25.68 | 174 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.32 | 2.5 | 165 | 70 | 0 | 11 | 0 | 0 | 0 | 1.8 | 70 | 0.23 | 0 | 250 | 4 | 130 | 220 | 0 | 0 | 560 | 17 | 3875.27 | 8679.94 | 90.48
17:00 | 0 | 17 | 0 | 0 | 0 | 150 | 0 | 0 | 405 | 0 | 0 | 35 | 0 | 0 | 2 | 16 | 1 | 4 | 14 | 17 | 17 | 0 | 420 | 282 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 5 | 0 | 13 | 7 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 24 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 577 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 51 | 1 | 184 | 0 | 0 | 360 | 29 | 182 | 32 | 17 | 0 | 0 | 9 | 17 | 0 | 46 | 0 | 6 | 0 | 320 | 320 | 0 | 35 | 29 | 0 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 32 | 0 | 5.7 | 6 | 4993.7 | 736 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6 | 0 | 0 | 659 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 18 | 0 | 14 | 30 | 6.24 | 177 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.56 | 2.5 | 167 | 70 | 0 | 3 | 30 | 0 | 0 | 0.5 | 20 | 0.08 | 0 | 307 | 4 | 100 | 220 | 0 | 0 | 560 | 17 | 3707.48 | 8701.18 | 90.47
18:00 | 0 | 27 | 0 | 0 | 0 | 225 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 0 | 32 | 16 | 0 | 15 | 17 | 35 | 17 | 0 | 350 | 278 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 12 | 10 | 7 | 0 | 0 | 28 | 10 | 4 | 0 | 0 | 17 | 24 | 0 | 3 | 3 | 0 | 40 | 29 | 33 | 578 | 17 | 0 | 11 | 0 | 22 | 222 | 0 | 0 | 0 | 612 | 0 | 51 | 20 | 155 | 0 | 0 | 360 | 29 | 182 | 29 | 23 | 0 | 26 | 23 | 17 | 0 | 52 | 0 | 0 | 48 | 280 | 320 | 0 | 35 | 29 | 0 | 2 | 120 | 16 | 0 | 22 | 30 | 0 | 18 | 0 | 12 | 58 | 9 | 32 | 0 | 0 | 6 | 5132 | 922 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 659 | 0 | 0 | 4 | 0 | 0 | 0 | 90 | 0 | 18 | 19 | 0 | 30 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 166 | 70 | 35 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 100 | 180 | 0 | 0 | 540 | 35 | 4018.5 | 9150.5 | 90.47
19:00 | 0 | 52 | 0 | 0 | 0 | 250 | 0 | 0 | 402 | 0 | 0 | 35 | 0 | 0 | 32 | 16 | 0 | 15 | 30 | 35 | 16 | 0 | 400 | 277 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 17 | 11 | 22 | 0 | 0 | 35 | 0 | 37 | 0 | 0 | 17 | 24 | 0 | 12 | 12 | 0 | 40 | 34 | 32 | 575 | 0 | 0 | 19 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 20 | 197 | 0 | 0 | 360 | 29 | 182 | 29 | 51 | 0 | 17 | 28 | 17 | 0 | 52 | 0 | 0 | 48 | 300 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 25 | 0 | 86 | 30 | 0 | 18 | 0 | 38 | 87 | 37 | 32 | 0 | 0 | 6 | 5694 | 878 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 | 36 | 0 | 0 | 0 | 40 | 0 | 0 | 8 | 0 | 30 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 166 | 70 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 590 | 35 | 4171.5 | 9865.5 | 90.46
19:30 | 0 | 34 | 0 | 0 | 0 | 241 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 17 | 16 | 0 | 15 | 35 | 35 | 16 | 0 | 450 | 316 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 17 | 11 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 24 | 0 | 0 | 12 | 0 | 40 | 34 | 32 | 575 | 0 | 0 | 19 | 0 | 17 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 360 | 29 | 206 | 29 | 51 | 0 | 17 | 28 | 17 | 0 | 52 | 0 | 0 | 48 | 330 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 25 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 87 | 37 | 32 | 0 | 0 | 6 | 5641 | 878 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 169 | 70 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 35 | 4025.5 | 9666.5
20:00 | 0 | 34 | 0 | 0 | 0 | 218 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 17 | 16 | 0 | 15 | 35 | 35 | 16 | 0 | 450 | 281 | 0 | 0 | 35 | 28 | 0 | 0 | 0 | 0 | 17 | 11 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 24 | 0 | 0 | 12 | 0 | 40 | 34 | 32 | 575 | 0 | 0 | 19 | 0 | 17 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 360 | 29 | 183 | 29 | 51 | 0 | 17 | 28 | 17 | 0 | 50 | 0 | 0 | 48 | 310 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 25 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 87 | 37 | 32 | 0 | 0 | 6 | 5534 | 878 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 169 | 70 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 35 | 4035.5 | 9569.5 | 90.46
21:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 17 | 16 | 0 | 450 | 297 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 7 | 11 | 14 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 32 | 575 | 0 | 0 | 19 | 0 | 0 | 228 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 199 | 0 | 0 | 360 | 29 | 188 | 29 | 51 | 0 | 0 | 28 | 17 | 0 | 52 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 90 | 37 | 30 | 0 | 0 | 6 | 5219 | 924 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 167 | 70 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 220 | 0 | 0 | 560 | 35 | 3999.05 | 9218.05 | 90.45
22:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 450 | 280 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 575 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 199 | 0 | 0 | 360 | 29 | 182 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 65 | 37 | 49 | 0 | 0 | 6 | 4982 | 925 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 169 | 70 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 220 | 0 | 0 | 560 | 6 | 3938.01 | 8920.01 | 90.45
23:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 270 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 575 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 570 | 0 | 51 | 0 | 199 | 0 | 0 | 360 | 29 | 182 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 280 | 320 | 0 | 32 | 30 | 0 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 35 | 37 | 72 | 0 | 0 | 6 | 4815 | 925 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 162 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 100 | 220 | 0 | 0 | 500 | 0 | 3759.68 | 8574.68 | 90.44
Total KWH | 0 | 917760 | 0 | 0 | 0 | 5565563 | 0 | 0 | 9302400 | 0 | 0 | 125640 | 0 | 0 | 356544 | 386400 | 14051 | 273768 | 133364 | 371520 | 396360 | 0 | 9667500 | 6977949 | 0 | 0 | 121510 | 650000 | 0 | 0 | 0 | 231034 | 92400 | 325800 | 379440 | 0 | 0 | 634800 | 135491 | 108480 | 0 | 39360 | 48490 | 238104 | 0 | 274560 | 360000 | 20383 | 959220 | 532761 | 861120 | 13563636.36 | 107055 | 0 | 281760 | 0 | 722618 | 5299520 | 0 | 0 | 0 | 14350907 | 99630 | 1180574 | 737472 | 4533091 | 0 | 0 | 6666000 | 697920 | 4651000 | 746352 | 284160 | 0 | 936480 | 308280 | 404180 | 0 | 1240320 | 0 | 379918 | 147664 | 7292000 | 7687100 | 0 | 817488 | 706000 | 0 | 54528 | 3694009 | 519000 | 0 | 1963200 | 728160 | 0 | 126000 | 0 | 255240 | 1153200 | 326400 | 693120 | 15150 | 343000 | 109680 | 124323584.36 | 21605818 | 4717152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585360 | 749091 | 0 | 17535272 | 0 | 0 | 34777 | 0 | 0 | 3518 | 439600 | 0 | 111499 | 122107 | 771160 | 227059 | 426748 | 4462791 | 0 | 0 | 0 | 0 | 0 | 9067854 | 0 | 36660 | 71154 | 3923000 | 1655999 | 686995 | 206667 | 600710 | 0 | 0 | 32977.08 | 1193040 | 2503 | 0 | 6916000 | 148422 | 2889000 | 5112520 | 0 | 0 | 13998545.45 | 573600 | 98907598.53 | 223231182.89

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10176.42 | MW | 12:00 Hr. | Energy Generated |  |  | 223.2312 |  | MKWHr.
| Day Peak Demand |  |  | 10207.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.235 |  | MKWHr.
| Evening Peak Generation |  |  | 9865.5 | MW | 19:00 Hr. | Energy Demand |  |  | 223.4662 |  | MKWHr.
| Evening Peak Demand |  |  | 9865.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.7 |  | °C
| Minimum Generation of the Day |  |  | 8246.95 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 792.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 10562.25 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.9 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.265 | 0 | 2.793 | 0 | 0 | 0.23103 | 0 | 0 | 36.289 | Gas | 109.0543 | Gas | 400527864.04
| Chattogram Zone |  |  | 6.1606 | 27.9145 | 3.4441 | 0 | 0.95922 | 0.12001 | 0 | 0.03936 | 38.6379 | Coal | 55.1572 | Coal | 393106044.8933
| Cumilla Zone |  |  | 18.8791 | 0 | 2.4141 | 0 | 0 | 0.37992 | 1.2403 | 0 | 22.9134 | HFO | 13.2955 | HFO | 244338088.25
| Mymensingh Zone |  |  | 0.69312 | 0 | 1.8445 | 0 | 0 | 0.35815 | 0 | 0 | 2.8958 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.5875 | Hydro | 0.95922 | Hydro | 95922
| Khulna Zone |  |  | 4.7172 | 0.74909 | 0 | 0 | 0 | 0.58536 | 21.6058 | 0 | 27.6574 | Solar | 4.3442 | Solar | 68423358.848
| Barishal Zone |  |  | 8.1499 | 20.9145 | 0.5736 | 0 | 0 | 0.002503 | 0 | 0 | 29.6406 | Import | 40.3814 | Import | 209963524.44
| Rajshahi Zone |  |  | 13.6018 | 0 | 0.93856 | 0 | 0 | 1.2346 | 17.5353 | 0 | 33.3102 | Wind | 0.03936 | Wind | 614016
| Rangpur Zone |  |  | 0 | 5.579 | 1.2877 | 0 | 0 | 1.4327 | 0 | 0 | 8.2994
| Total |  |  | 109.0543 | 55.1572 | 13.2955 | 0 | 0.95922 | 4.3442 | 40.3814 | 0.03936 | 223.2312
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 400527864.04 |  | Hydro | 95922
|  |  |  | Coal | 393106044.8933 |  | Solar | 68423358.848
|  |  |  | HFO | 244338088.25 |  | Import | 209963524.44
|  |  |  | HSD | 0 |  | Wind | 614016
[5 empty] | Total: | 131,70,68,818 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6058 | Peak Hr Flow | 878.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 11001981.916 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.5353 | Peak Hr Flow | 764.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 468 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2403 | Peak Hr Flow | 52.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 848 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.3814 | Peak Hr Flow | 1694.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3060
|  |  |  | Chattogram |  | 0 |  | 1090
|  |  |  | Cumilla |  | 0 |  | 880
|  |  |  | Mymensingh |  | 0 |  | 976
|  |  |  | Sylhet |  | 0 |  | 357
|  |  |  | Khulna |  | 0 |  | 1135
|  |  |  | Barishal |  | 0 |  | 295
|  |  |  | Rajshahi |  | 0 |  | 1009
|  |  |  | Rangpur |  | 0 |  | 699
|  |  |  | Total |  | 0 |  | 9501
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 225MW CCPP Unit-3 GT |  |  | 141
|  | 7 | Sirajgonj 225MW CCPP Unit-3 ST |  |  | 79
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1012 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1678.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D
| 08:05 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D
| 08:20 | 16:30 | Madanganj 132/33kV S/S GT-2 HT Scheduled S/D Due to Yearly maintenance
| 08:23 | 16:56 | Sirajganj 132/33kV S/S T3-(435) LT Project Work S/D Due to PGNS(G2G) project, has taken
shutdown for 33kV T3 & T4 Section DS Clamps Replacement Work.
| 08:23 | 16:57 | Sirajganj 132/33kV S/S T4-(445) LT Project Work S/D Due to PGNS(G2G) project, has taken
shutdown for 33kV T3 & T4 Section DS Clamps Replacement Work.
| 08:24 | 16:50 | Sirajganj 132/33kV S/S T3-(435) HT Project Work S/D Due to PGNS(G2G) project, has taken
shutdown for 33kV T3 & T4 Section DS Clamps Replacement Work.
| 08:24 | 16:50 | Sirajganj 132/33kV S/S T4-(445) HT Project Work S/D Due to PGNS(G2G) project, has taken
shutdown for 33kV T3 & T4 Section DS Clamps Replacement Work.
| 08:25 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Conductor
stringing to Tower no 4&5 Amin bazar CKT-1.
| 08:37 |  | Gopalganj(N)-Payra 400KV Ckt-1 Scheduled S/D from Payra 400kV end Due to Line-1 has been
taken shutdown for insulator painting
| 08:37 |  | Payra 1320 MW record a general event:- Line-1 Shutdown has been taken for insulator
painting
| 10:08 | 10:58 | Chowmuhani 132/33kV S/S TR3-435T LT Scheduled S/D Due to Station Auxiliary TR fuse | [7 empty] | 15.0MW load
|  |  | replacement. | [7 empty] | interrup.
| 10:08 | 10:58 | Chowmuhani 132/33kV S/S TR3-435T HT Scheduled S/D Due to Station Auxiliary TR fuse | [7 empty] | 15.0MW load
|  |  | replacement. | [7 empty] | interrup.
| 11:28 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
|  | 11:35 | GPH 230/33kV S/S Transformer -2 (D07) HT is restored.
| 12:00 |  | Day Peak Generation: 10172 MW.
|  | 12:22 | Kabirpur -Tongi 132kV Ckt-2 is restored.
| 19:00 |  | Evening Peak Gen. 9865 MW
|  | 23:37 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
| 06:02 |  | Coxsbazar 132/33kV S/S Main Bus Scheduled S/D Due to CB commissioning & replacement | [7 empty] | 90.0MW load
interrup.
| 07:03 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Project Work S/D from Lalmonirhat 132/33kV end Due to | [7 empty] | 32.0MW load
|  |  | G2G project work on main bus and from Rangpur 132/33kVend. | [7 empty] | interrup.
Lalmonirhat
132/33kV end
| 07:09 |  | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance and
renovation work .
| 07:09 |  | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance and
renovation work .
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 250 | 5565563 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 9302400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9667500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 277 | 6977949 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 273768 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 125640 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 386400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 30 | 133364 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 121510 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 325800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 379440 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16 | 396360 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 650000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 14051 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 32 | 356544 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 917760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 371520 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 231034 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 92400 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 1677 | 36289003
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 99630 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 281760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 959220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5299520 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 722618 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 238104 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 48490 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 274560 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 32 | 861120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 108480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20383 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 135491 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 532761 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 360000 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 634800 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 107055 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14350907 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 0 | 39360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 13563636.36 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1727 | 38637895.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4651000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 360 | 6666000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 29 | 746352 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 697920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4533091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1180574 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 737472 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 48 | 147664 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 936480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 52 | 1240320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 404180 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 308280 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 284160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 379918 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1081 | 22913411
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 32 | 693120 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 37 | 326400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1153200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 343000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 109680 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 38 | 255240 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 200 | 2895790
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 706000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3694009 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 817488 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 54528 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 728160 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1963200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 126000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 519000 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7292000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7687100 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1009 | 23587485
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 878 | 21605818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 206 | 4717152 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 585360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 749091 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1084 | 27657421
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 148422 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 2889000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 13998545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5112520 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 573600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6916000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2503 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1291 | 29640590.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 36 | 34777 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 3518 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 111499 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4462791 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9067854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 227059 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 71154 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 122107 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 439600 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 764 | 17535272 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 426748 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 771160 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1476.5 | 33310199
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1655999 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 166 | 3923000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 600710 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32977.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 686995 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206667 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1193040 | -
Rangpur Area Total |  |  |  |  | 950 | 320 | 8299388.08
Eastern Grid Total |  |  |  |  | 16856.242 | 5694 | 124323584.36
Western Grid Total |  |  |  |  | 10294.5 | 4171.5 | 98907598.53
National Grid Total |  |  |  |  | 27150.742 | 9865.5 | 223231182.89
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6363.77 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3137.4 | MW
i) Dhaka area |  |  | 3060.27 |  | MW | i) Khulna area |  |  |  | 1135 | MW
ii) Chattogram area |  |  | 1090.5 |  | MW | ii) Barishal area |  |  |  | 294.6 | MW
iii) Cumilla area |  |  | 880 |  | MW | iii) Rajshahi area |  |  |  | 1008.8 | MW
iv) Mymensingh area |  |  | 976 |  | MW | iv) Rangpur area |  |  |  | 699 | MW
v) Sylhet area |  |  | 357 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9501.17 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 58 | 08:00 | 133 | Postogola | 36 | 12:00
2 | AKSML | 18 | 16:00 | 68 | Jamalpur | 102 | 18:30 | 134 | Purbachal | 16 | 13:00
3 | Aftabnagar | 24 | 13:00 | 69 | Jashore | 107 | 13:00 | 135 | Purbasadipur | 128 | 12:00
4 | Agargaon | 74 | 13:00 | 70 | Jhenaidah | 93 | 08:00 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 64 | 18:30 | 71 | Joydebpur | 108 | 00:00 | 137 | Rahim | 32 | 02:00
6 | Amnura | 51 | 08:00 | 72 | Joypurhat | 57 | 09:00 | 138 | Rajbari | 48 | 18:30
7 | Ashuganj | 74 | 00:00 | 73 | Juldah | 12 | 00:00 | 139 | Rajendrapur | 96 | 13:00
8 | BSRM | 196 | 15:00 | 74 | KSRM | 24 | 00:00 | 140 | Rajshahi | 70 | 13:00
9 | Bagerhat | 62 | 19:30 | 75 | Kabirpur | 192 | 00:00 | 141 | Rajshahi-230 | 66 | 12:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 54 | 13:00 | 142 | Ramganj | 106 | 13:00
11 | Bakulia | 67 | 13:00 | 77 | Kallyanpur | 69 | 13:00 | 143 | Rampur | 30 | 13:00
12 | Banani | 14 | 00:00 | 78 | Kalurghat | 24 | 10:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 3 | 00:00 | 79 | Kamrangirchar | 51.4 | 00:00 | 145 | Rangpur | 119 | 13:00
14 | Barapukuria | 60 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 4 | 09:00
15 | Barguna | 14 | 00:00 | 81 | Kazla | 90 | 00:00 | 147 | SSM | 15 | 01:00
16 | Barishal | 68 | 00:00 | 82 | Keranigonj | 40 | 13:00 | 148 | Saidpur | 100 | 10:00
17 | Barishal-230 | 70 | 19:30 | 83 | Khagrachori | 24 | 18:00 | 149 | Satkhira | 91 | 18:30
18 | Baroaulia | 50 | 13:00 | 84 | Khulna | 60 | 13:00 | 150 | Satmasjid | 78 | 13:00
19 | Baroirhat | 49 | 13:00 | 85 | Khulshi | 144 | 17:00 | 151 | Savar | 154 | 12:00
20 | Bashundhara | 119 | 12:00 | 86 | Kishoreganj | 110 | 13:00 | 152 | SevenRings | 15.63 | 11:00
21 | BashundharaCement | 2 | 00:00 | 87 | Kodda | 151 | 00:00 | 153 | ShahCement | 23 | 00:00
22 | Beanibazar | 44 | 19:30 | 88 | Kulaura | 27 | 13:00 | 154 | Shahjadpur | 55 | 08:00
23 | Benapole | 50 | 08:00 | 89 | Kurigram | 60 | 08:00 | 155 | Shahjibazar | 89 | 00:00
24 | Bhaluka | 100 | 13:00 | 90 | Kushtia | 104 | 13:00 | 156 | Shahmirpur | 32 | 02:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 55 | 00:00 | 157 | Shariatpur | 52 | 19:30
26 | Bhangura | 30 | 07:00 | 92 | Lalmonirhat | 44 | 08:00 | 158 | Sherpur | 138 | 19:00
27 | Bheramara(GK) | 38 | 13:00 | 93 | MI_Cement | 15.4 | 13:00 | 159 | Shikalbaha | 28 | 12:00
28 | Bhulta | 230 | 00:00 | 94 | Madanganj | 18 | 00:00 | 160 | Shitalakhya | 50.5 | 00:00
29 | Bog-Sherpur | 58 | 09:00 | 95 | Madaripur | 66 | 13:00 | 161 | Sholosohor | 31 | 12:00
30 | Bogura | 102 | 09:00 | 96 | Madartek | 63.91 | 13:00 | 162 | Shyampur | 146 | 09:00
31 | Borhanuddin | 54 | 20:00 | 97 | Madunaghat | 40 | 13:00 | 163 | Siddhirganj | 89 | 00:00
32 | Brahmanbaria | 111 | 13:00 | 98 | Magura | 43 | 19:00 | 164 | Sirajganj | 76 | 08:00
33 | Cantonment | 90 | 13:00 | 99 | Mahasthangarh | 60 | 08:00 | 165 | Sonargaon | 79 | 01:00
34 | Chandpur | 43 | 00:00 | 100 | Manikganj | 94 | 00:00 | 166 | Sreemongol | 44 | 18:00
35 | Chandraghona | 27 | 18:30 | 101 | Maniknagar | 46 | 13:00 | 167 | Sreepur | 73 | 00:00
36 | Chapai | 73.3 | 12:00 | 102 | Matarbari | 39 | 13:00 | 168 | Srinagar | 34.35 | 13:00
37 | Charsaidpur | 41 | 00:00 | 103 | Matuail | 46 | 00:00 | 169 | Sunamganj | 38 | 18:30
38 | Chauddagram | 52 | 13:00 | 104 | Millgate | 57 | 00:00 | 170 | Sylhet | 28 | 23:00
39 | Chhatak | 21 | 18:00 | 105 | Mirpur | 107 | 12:00 | 171 | Sylhet-132 | 83 | 13:00
40 | Chowmuhani | 140 | 13:00 | 106 | Mirsorai | 7 | 00:00 | 172 | TK | 16.3 | 18:00
41 | Chuadanga | 71 | 13:00 | 107 | Mirzapur | 39 | 07:00 | 173 | Tangail | 166 | 07:00
42 | Coxsbazar | 116 | 13:00 | 108 | Mithapukur | 52 | 08:00 | 174 | Thakurgaon | 79 | 12:00
43 | Cumilla(N) | 145 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 116 | 12:00
44 | Cumilla(S) | 97 | 13:00 | 110 | Mogbazar | 81.5 | 13:00 | 176 | Ullahpara | 24 | 07:00
45 | Daudkandi | 84 | 20:00 | 111 | Mongla | 25 | 09:00 | 177 | Ullon | 39 | 12:00
46 | Dhaka | 14 | 00:00 | 112 | Motijheel | 24 | 13:00 | 178 | Uttara | 59 | 13:00
47 | Dhamrai | 82 | 08:00 | 113 | Muktagacha | 31 | 13:00 | 179 | UttaraNew | 35 | 13:00
48 | Dhanmondi | 85 | 12:00 | 114 | Munshiganj | 60 | 00:00 | 180 | Zigatola | 60 | 12:00
49 | Dohazari | 92 | 13:00 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 96 | 00:00 | 116 | Mymensingh | 171 | 12:00
51 | Fatullah | 62 | 00:00 | 117 | Naogaon | 108 | 09:00
52 | Fenchuganj | 30 | 13:00 | 118 | Narail | 39 | 19:00
53 | Feni | 82 | 13:00 | 119 | Narinda | 47 | 12:00
54 | GPH | 11 | 03:00 | 120 | Narshingdi | 151 | 00:00
55 | Ghatail | 56 | 13:00 | 121 | Natore | 102 | 09:00
56 | Ghorashal | 10 | 00:00 | 122 | Nawabganj | 33.6 | 13:00
57 | Ghorashal-230 | 58 | 00:00 | 123 | Netrakona | 139 | 09:00
58 | Goalpara | 24 | 13:00 | 124 | New | 56 | 00:00
59 | Gollamari | 54 | 13:00 | 125 | Niamatpur | 91 | 08:00
60 | Gopalganj | 77 | 19:00 | 126 | Noapara | 28 | 19:00
61 | Gulshan | 60 | 12:00 | 127 | PHP | 9 | 14:00
62 | Halishahar | 33 | 22:00 | 128 | Pabna | 52 | 13:00
63 | HaripurSBU | 172 | 03:00 | 129 | Palashbari | 102 | 08:00
64 | Hasnabad | 80 | 00:00 | 130 | Panchagarh | 39 | 09:00
65 | Hathazari | 56 | 13:00 | 131 | Patuakhali | 50.7 | 19:30
66 | Ishurdi | 57 | 13:00 | 132 | Payra | 20 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 10006.32 | 0 |  | 10006.32
1:00 | 9254.56 | 20 |  | 9275.56
2:00 | 8797.72 | 0 |  | 8797.72
3:00 | 8686.32 | 10 |  | 8696.32
4:00 | 8530.41 | 11 |  | 8541.41
5:00 | 8391.74 | 0 |  | 8391.74
6:00 | 8246.95 | 0 |  | 8246.95
7:00 | 8713.17 | 19 |  | 8733.03
8:00 | 9332.38 | 35 |  | 9369.38
9:00 | 9384.49 | 40 |  | 9426.49
10:00 | 9294.27 | 0 |  | 9294.27
11:00 | 9515.61 | 25 |  | 9541.61
12:00 | 10176.42 | 30 |  | 10207.77
13:00 | 10562.25 | 45 |  | 10609.25
14:00 | 9147.37 | 0 |  | 9147.37
15:00 | 8790.07 | 0 |  | 8790.07
16:00 | 8679.94 | 0 |  | 8679.94
17:00 | 8701.18 | 0 |  | 8701.18
18:00 | 9150.5 | 0 |  | 9150.5
19:00 | 9865.5 | 0 |  | 9865.5
19:30 | 9666.5 | 0 |  | 9666.5
20:00 | 9569.5 | 0 |  | 9569.5
21:00 | 9218.05 | 0 |  | 9218.05
22:00 | 8920.01 | 0 |  | 8920.01
23:00 | 8574.68 | 0 |  | 8574.68
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 14-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2439 | 1929.5 | 925 | 0 | 60 | 756.82 | 40 | 2775 | 0 | 176 | 895 | 0 | 0 | 10 | 0 | DAILY ENERGY CURVE
00:30 | 2443 | 1942 | 925 | 0 | 58 | 756.94 | 40 | 2747 | 0 | 142.5 | 571 | 0 | 0 | 5 | 10 | 14-02-2025
01:00 | 2447 | 1954.5 | 925 | 0 | 56 | 757.06 | 40 | 2719 | 0 | 109 | 247 | 0 | 0 | 0 | 20
01:30 | 2470.5 | 1974 | 925 | 0 | 56 | 756.14 | 40 | 2550 | 0 | 80.5 | 172.5 | 0 | 0 | 1.5 | 10 | Energy Generated | 223.2312 |  | MKWHr
02:00 | 2494 | 1993.5 | 925 | 0 | 56 | 755.22 | 40 | 2381 | 0 | 52 | 98 | 0 | 0 | 3 | 0 | Energy not Served | 0.235 |  | MKWHr
02:30 | 2482.5 | 1994.5 | 924.5 | 0 | 56.5 | 756.02 | 40 | 2365 | 0 | 52 | 67 | 0 | 0 | 4 | 5 | Total Energy Requirement | 223.4662 |  | MKWHr
03:00 | 2471 | 1995.5 | 924 | 0 | 57 | 756.82 | 40 | 2349 | 0 | 52 | 36 | 0 | 0 | 5 | 10
03:30 | 2486 | 1992.5 | 830 | 0 | 54.5 | 760.365 | 40 | 2350 | 0 | 52 | 40.5 | 0 | 0 | 2.5 | 10.5
04:00 | 2501 | 1989.5 | 736 | 0 | 52 | 763.91 | 40 | 2351 | 0 | 52 | 45 | 0 | 0 | 0 | 11
04:30 | 2471 | 1875 | 736 | 0 | 52 | 764.075 | 40 | 2349.5 | 0 | 68 | 105 | 0 | 0 | 0.5 | 5.5
05:00 | 2441 | 1760.5 | 736 | 0 | 52 | 764.24 | 40 | 2348 | 0 | 84 | 165 | 0 | 0 | 1 | 0
05:30 | 2327 | 1786 | 736 | 0 | 51 | 713.845 | 40 | 2262 | 0 | 84 | 319 | 0 | 0 | 0.5 | 0
06:00 | 2213 | 1811.5 | 736 | 0 | 50 | 663.45 | 40 | 2176 | 0 | 84 | 473 | 0 | 0 | 0 | 0
06:30 | 2262 | 1810.75 | 783 | 0 | 47 | 706.945 | 40 | 2219 | 11.165 | 84 | 515.7 | 0 | 0 | 0.5 | 9.5
07:00 | 2311 | 1810 | 830 | 0 | 44 | 750.44 | 40 | 2262 | 22.33 | 84 | 558.4 | 0 | 0 | 1 | 19
07:30 | 2436 | 1837 | 877.5 | 0 | 45 | 751.72 | 40 | 2273 | 98.355 | 92 | 571.7 | 0 | 0 | 0.5 | 27
08:00 | 2561 | 1864 | 925 | 0 | 46 | 753 | 40 | 2284 | 174.38 | 100 | 585 | 0 | 0 | 0 | 35
08:30 | 2546.5 | 1813 | 901.5 | 0 | 49 | 755.535 | 40 | 2279.5 | 269.9 | 84 | 619.5 | 0 | 0 | 0 | 37.5
09:00 | 2532 | 1762 | 878 | 0 | 52 | 758.07 | 40 | 2275 | 365.42 | 68 | 654 | 0 | 0 | 0 | 40
09:30 | 2491.5 | 1796.75 | 900.5 | 0 | 53 | 757.12 | 40 | 2247.5 | 446.51 | 59 | 547.5 | 0 | 0 | 0 | 20
10:00 | 2451 | 1831.5 | 923 | 0 | 54 | 756.17 | 40 | 2220 | 527.6 | 50 | 441 | 0 | 0 | 0 | 0
10:30 | 2456.5 | 1864.25 | 923.5 | 0 | 54 | 756.72 | 40 | 2252 | 570.97 | 50 | 437 | 0 | 0 | 0 | 12.5
11:00 | 2462 | 1897 | 924 | 0 | 54 | 757.27 | 40 | 2284 | 614.34 | 50 | 433 | 0 | 0 | 0 | 25
11:30 | 2564 | 1917.5 | 924 | 0 | 56 | 757.805 | 40 | 2316 | 633.71 | 116 | 521 | 0 | 0 | 0 | 27.5
12:00 | 2666 | 1938 | 924 | 0 | 58 | 758.34 | 40 | 2348 | 653.08 | 182 | 609 | 0 | 0 | 0 | 30
12:30 | 2669 | 1902 | 924.5 | 0 | 60 | 757.67 | 40 | 2337.5 | 650.165 | 197.5 | 830 | 0 | 0 | 1 | 37.5
13:00 | 2672 | 1866 | 925 | 0 | 62 | 757 | 40 | 2327 | 647.25 | 213 | 1051 | 0 | 0 | 2 | 45
13:30 | 2504 | 1861.25 | 925 | 0 | 58 | 728.5 | 40 | 2198 | 607.06 | 202 | 726.5 | 0 | 0 | 4.5 | 22.5
14:00 | 2336 | 1856.5 | 925 | 0 | 54 | 700 | 40 | 2069 | 566.87 | 191 | 402 | 0 | 0 | 7 | 0
14:30 | 2355 | 1880 | 925 | 0 | 51 | 684 | 40 | 2080 | 503.22 | 165 | 279 | 0 | 0 | 6.5 | 0
15:00 | 2374 | 1903.5 | 925 | 0 | 48 | 668 | 40 | 2091 | 439.57 | 139 | 156 | 0 | 0 | 6 | 0
15:30 | 2430.5 | 1930 | 884.5 | 0 | 49 | 664 | 40 | 2094 | 350.005 | 139 | 147.5 | 0 | 0 | 6.5 | 0
16:00 | 2487 | 1956.5 | 844 | 0 | 50 | 660 | 40 | 2097 | 260.44 | 139 | 139 | 0 | 0 | 7 | 0
16:30 | 2523 | 1948.5 | 790 | 0 | 48 | 659.5 | 40 | 2179 | 167.56 | 147 | 183 | 0 | 0 | 5 | 0
17:00 | 2559 | 1940.5 | 736 | 0 | 46 | 659 | 40 | 2261 | 74.68 | 155 | 227 | 0 | 0 | 3 | 0
17:30 | 2628.5 | 1791.5 | 829 | 0 | 49 | 659 | 40 | 2267 | 37.84 | 220.5 | 402 | 0 | 0 | 1.5 | 0
18:00 | 2698 | 1642.5 | 922 | 0 | 52 | 659 | 40 | 2273 | 1 | 286 | 577 | 0 | 0 | 0 | 0
18:30 | 2756 | 1783.5 | 900 | 0 | 52 | 711.5 | 40 | 2296.5 | 0.5 | 283 | 685 | 0 | 0 | 0 | 0
19:00 | 2814 | 1924.5 | 878 | 0 | 52 | 764 | 40 | 2320 | 0 | 280 | 793 | 0 | 0 | 0 | 0
19:30 | 2765 | 2043.5 | 878 | 0 | 52 | 759 | 40 | 2355 | 0 | 159 | 615 | 0 | 0 | 0 | 0
20:00 | 2719 | 1984.5 | 878 | 0 | 50 | 759 | 40 | 2355 | 0 | 161 | 623 | 0 | 0 | 0 | 0
20:30 | 2722.5 | 1949.5 | 901 | 0 | 51 | 759.775 | 40 | 2323 | 0 | 100.5 | 546.5 | 0 | 0 | 0 | 0
21:00 | 2726 | 1914.5 | 924 | 0 | 52 | 760.55 | 40 | 2291 | 0 | 40 | 470 | 0 | 0 | 0 | 0
21:30 | 2733.5 | 1905 | 924.5 | 0 | 52 | 760.53 | 40 | 2292 | 0 | 36.5 | 325 | 0 | 0 | 0 | 0
22:00 | 2741 | 1895.5 | 925 | 0 | 52 | 760.51 | 40 | 2293 | 0 | 33 | 180 | 0 | 0 | 0 | 0
22:30 | 2751 | 1864 | 925 | 0 | 51 | 760.345 | 40 | 2210.5 | 0 | 16.5 | 129 | 0 | 0 | 0 | 0
23:00 | 2761 | 1832.5 | 925 | 0 | 50 | 760.18 | 40 | 2128 | 0 | 0 | 78 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5400 | 4606.32 | 10006.32 | DAILY GENERATION CURVE
00:30 | 5116.5 | 4513.94 | 9630.44
01:00 | 4833 | 4421.56 | 9254.56 | 14-02-2025
01:30 | 4815 | 4211.14 | 9026.14
02:00 | 4797 | 4000.72 | 8797.72
02:30 | 4760 | 3982.02 | 8742.02
03:00 | 4723 | 3963.32 | 8686.32
03:30 | 4735 | 3873.365 | 8608.365
04:00 | 4747 | 3783.41 | 8530.41
04:30 | 4693.5 | 3767.575 | 8461.075
05:00 | 4640 | 3751.74 | 8391.74
05:30 | 4699.5 | 3619.845 | 8319.345
06:00 | 4759 | 3487.95 | 8246.95
06:30 | 4841.515 | 3638.545 | 8480.06
07:00 | 4924.03 | 3789.14 | 8713.17
07:30 | 5037.485 | 3985.29 | 9022.775
08:00 | 5150.94 | 4181.44 | 9332.38
08:30 | 5157.245 | 4201.19 | 9358.435
09:00 | 5163.55 | 4220.94 | 9384.49
09:30 | 5104.615 | 4234.765 | 9339.38
10:00 | 5045.68 | 4248.59 | 9294.27
10:30 | 5068.805 | 4336.135 | 9404.94
11:00 | 5091.93 | 4423.68 | 9515.61
11:30 | 5278.055 | 4567.96 | 9846.015
12:00 | 5464.18 | 4712.24 | 10176.42
12:30 | 5681.49 | 4687.845 | 10369.335
13:00 | 5898.8 | 4663.45 | 10562.25
13:30 | 5410.05 | 4444.76 | 9854.81
14:00 | 4921.3 | 4226.07 | 9147.37
14:30 | 4832.45 | 4136.27 | 8968.72
15:00 | 4743.6 | 4046.47 | 8790.07
15:30 | 4774.135 | 3960.87 | 8735.005
16:00 | 4804.67 | 3875.27 | 8679.94
16:30 | 4899.185 | 3791.375 | 8690.56
17:00 | 4993.7 | 3707.48 | 8701.18
17:30 | 5062.85 | 3862.99 | 8925.84
18:00 | 5132 | 4018.5 | 9150.5
18:30 | 5413 | 4095 | 9508
19:00 | 5694 | 4171.5 | 9865.5
19:30 | 5641 | 4025.5 | 9666.5
20:00 | 5534 | 4035.5 | 9569.5
20:30 | 5376.5 | 4017.275 | 9393.775 |  | Executive Engineer
21:00 | 5219 | 3999.05 | 9218.05 |  | Network Operation Division
21:30 | 5100.5 | 3968.53 | 9069.03
22:00 | 4982 | 3938.01 | 8920.01
22:30 | 4898.5 | 3848.845 | 8747.345
23:00 | 4815 | 3759.68 | 8574.68

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 05:00 | 390 | 11:00 | Payra | 426 | 23:00 | 416 | 00:00
Ashuganj | 410 | 0:00 | 392 | 12:00 | Rahanpur | 416 | 05:00 | 403 | 08:00
Bhulta | 412 | 22:00 | 393 | 11:00 | Rampal | 419 | 23:00 | 400 | 11:00
Bibiana | 413 | 23:00 | 401 | 11:00
BIPTC | 407 | 04:00 | 388 | 12:00
Bogura | 415 | 05:00 | 400 | 08:00
Gopalganj | 421 | 23:00 | 405 | 11:00
Kaliakoir | 404 | 23:00 | 388 | 10:00
Madunaghat | 406 | 06:00 | 397 | 12:00
Meghnaghat | 407 | 23:00 | 391 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 23:00 | 226 | 11:00 | Keranigonj | 237 | 23:00 | 225 | 11:00
AKSML | 232 | 07:00 | 226 | 01:00 | Khulna(S) | 243 | 05:00 | 230 | 12:00
Aminbazar | 238 | 23:00 | 226 | 12:00 | Madunaghat | 234 | 08:00 | 227 | 11:00
Ashuganj | 244 | 20:00 | 235 | 01:00 | Madunaghat-400 | 234 | 06:00 | 31 | 20:00
Ashuganj-400 | 240 | 03:00 | 224 | 12:00 | Maniknagar | 238 | 00:00 | 226 | 11:00
Baghabari | 240 | 20:00 | 232 | 12:00 | Meghnaghat | 242 | 18:30 | 235 | 00:00
Barapukuria | 228 | 06:00 | 218 | 08:00 | Meghnaghat-400 | 239 | 23:00 | 229 | 01:00
Barapukuria-230 | 228 | 06:00 | 218 | 08:00 | Mirsorai | 234 | 05:00 | 225 | 01:00
Barishal | 246 | 23:00 | 238 | 13:00 | Rajshahi | 241 | 17:00 | 232 | 09:00
Bheramara | 240 | 05:00 | 230 | 12:00 | Rampal | 241 | 05:00 | 230 | 09:00
Bhulta | 239 | 23:00 | 227 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 239 | 05:00 | 230 | 01:00 | Rampura | 238 | 22:00 | 227 | 11:00
BIPTC | 242 | 05:00 | 231 | 13:00 | Shikalbaha | 232 | 06:00 | 226 | 01:00
Bogura | 241 | 05:00 | 232 | 08:00 | Shyampur | 237 | 23:00 | 226 | 11:00
Bogura-400 | 240 | 05:00 | 230 | 08:00 | Siddhirganj | 240 | 22:00 | 227 | 12:00
Borhanuddin | 249 | 23:00 | 244 | 12:00 | Sirajgonj | 245 | 21:00 | 238 | 09:00
BSRM | 233 | 05:00 | 225 | 01:00 | Sreepur | 241 | 20:00 | 233 | 11:00
Cumilla(N) | 236 | 20:00 | 227 | 11:00 | Tongi | 234 | 23:00 | 223 | 11:00
Faridpur | 247 | 23:00 | 237 | 12:00
Fenchuganj | 242 | 07:00 | 231 | 00:00
Ghorashal | 240 | 04:00 | 230 | 00:00
Ghorashal-230 | 238 | 20:00 | 227 | 11:00
Gopalganj | 246 | 23:00 | 237 | 11:00
GPH | 233 | 05:00 | 226 | 01:00
Haripur | 238 | 20:00 | 228 | 00:00
Hasnabad | 237 | 20:00 | 226 | 10:00
Hathazari | 236 | 04:00 | 229 | 11:00
Ishurdi | 242 | 23:00 | 233 | 12:00
Jhenaidah | 240 | 05:00 | 228 | 13:00
Kaliakoir | 235 | 22:00 | 224 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 22:00 | 126 | 13:00 | Magura | 139 | 03:00 | 131 | 12:00
Agargaon | 138 | 23:00 | 130 | 12:00 | Mahasthangarh | 137 | 05:00 | 128 | 08:00
Agrabad | 135 | 08:00 | 128 | 01:00 | Manikganj | 140 | 23:00 | 135 | 01:00
AKS | 132 | 04:00 | 128 | 01:00 | Maniknagar | 136 | 20:00 | 128 | 11:00
Aminbazar | 137 | 19:30 | 128 | 11:00 | Matarbari | 125 | 07:00 | 117 | 22:00
Amnura | 147 | 16:00 | 131 | 08:00 | Matuail | 137 | 20:00 | 129 | 00:00
Ashuganj | 141 | 05:00 | 139 | 11:00 | Millgate | 139 | 23:00 | 130 | 11:00
Bagerhat | 137 | 06:00 | 131 | 08:00 | Mirpur | 136 | 19:30 | 126 | 12:00
Bajitpur | 138 | 22:00 | 133 | 08:00 | Mirzapur | 139 | 23:00 | 130 | 01:00
Bakulia | 136 | 08:00 | 129 | 11:00 | Mithapukur | 135 | 06:00 | 124 | 09:00
Banani | 136 | 23:00 | 127 | 12:00 | MI_Cement | 138 | 20:00 | 130 | 01:00
Bangabhaban | 136 | 22:00 | 129 | 11:00 | Modern | 0 | 00:00 | 0 | 00:00
Barapukuria | 138 | 06:00 | 129 | 08:00 | Mogbazar | 136 | 23:00 | 129 | 11:00
Barguna | 141 | 05:00 | 138 | 00:00 | Mongla | 138 | 21:00 | 131 | 11:00
Barishal | 136 | 23:00 | 131 | 11:00 | Motijheel | 136 | 20:00 | 129 | 11:00
Barishal-230 | 138 | 05:00 | 132 | 11:00 | Muktagacha | 134 | 20:00 | 117 | 01:00
Baroaulia | 135 | 09:00 | 130 | 11:00 | Munshiganj | 137 | 20:00 | 129 | 00:00
Baroirhat | 132 | 09:00 | 125 | 12:00 | Muradnagar | 136 | 19:00 | 129 | 11:00
Bashundhara | 138 | 21:00 | 128 | 00:00 | Mymensingh | 134 | 22:00 | 115 | 01:00
BashundharaCement | 137 | 20:00 | 129 | 00:00 | Naogaon | 136 | 05:00 | 126 | 08:00
Beanibazar | 136 | 05:00 | 131 | 12:00 | Narail | 138 | 05:00 | 130 | 12:00
Benapole | 137 | 04:00 | 126 | 13:00 | Narinda | 136 | 20:00 | 128 | 11:00
Bhaluka | 130 | 04:00 | 121 | 09:00 | Narshingdi | 136 | 22:00 | 125 | 00:00
Bhandaria | 134 | 17:00 | 127 | 13:00 | Natore | 138 | 00:00 | 133 | 08:00
Bhangura | 139 | 05:00 | 133 | 07:00 | Nawabganj | 142 | 20:00 | 134 | 11:00
Bheramara | 140 | 05:00 | 135 | 08:00 | Netrakona | 126 | 21:00 | 115 | 09:00
Bheramara(GK) | 139 | 02:00 | 130 | 01:00 | New | 139 | 20:00 | 131 | 11:00
Bhulta | 133 | 20:00 | 124 | 00:00 | Niamatpur | 140 | 04:00 | 134 | 08:00
Bog-Sherpur | 137 | 05:00 | 130 | 08:00 | Noapara | 138 | 22:00 | 130 | 07:00
Bogura | 137 | 04:00 | 132 | 09:00 | Pabna | 137 | 05:00 | 129 | 08:00
Bogura-230 | 138 | 05:00 | 131 | 08:00 | Palashbari | 132 | 03:00 | 119 | 08:00
Brahmanbaria | 139 | 23:00 | 131 | 00:00 | Panchagarh | 139 | 05:00 | 124 | 09:00
Cantonment | 137 | 05:00 | 130 | 11:00 | Patuakhali | 140 | 06:00 | 135 | 01:00
Chandpur | 135 | 09:00 | 120 | 11:00 | Payra | 140 | 05:00 | 136 | 01:00
Chandraghona | 135 | 06:00 | 131 | 02:00 | PHP | 132 | 09:00 | 13 | 08:00
Chapai | 138 | 03:00 | 131 | 09:00 | Postogola | 140 | 19:00 | 133 | 11:00
Charsaidpur | 138 | 20:00 | 130 | 00:00 | Purbachal | 136 | 23:00 | 128 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 133 | 08:00 | 125 | 11:00 | Purbasadipur | 138 | 22:00 | 121 | 09:00
Chhatak | 135 | 05:00 | 130 | 12:00 | Rahanpur | 141 | 23:00 | 136 | 08:00
Chowmuhani | 130 | 09:00 | 122 | 12:00 | Rahanpur-400 | 141 | 05:00 | 136 | 08:00
Chuadanga | 139 | 05:00 | 129 | 12:00 | Rahim | 136 | 21:00 | 129 | 00:00
Coxsbazar | 125 | 08:00 | 117 | 12:00 | Rajbari | 137 | 23:00 | 131 | 11:00
Cumilla(N) | 137 | 06:00 | 130 | 11:00 | Rajendrapur | 138 | 23:00 | 130 | 12:00
Cumilla(S) | 135 | 05:00 | 129 | 02:00 | Rajshahi | 139 | 17:00 | 135 | 08:00
Daudkandi | 135 | 19:00 | 127 | 01:00 | Rajshahi-230 | 139 | 06:00 | 126 | 12:00
Dhaka | 136 | 23:00 | 128 | 11:00 | Ramganj | 131 | 00:00 | 119 | 11:00
Dhamrai | 136 | 23:00 | 129 | 00:00 | Rampur | 134 | 06:00 | 129 | 02:00
Dhanmondi | 137 | 20:00 | 130 | 00:00 | Rampura | 135 | 22:00 | 127 | 12:00
Dohazari | 131 | 04:00 | 125 | 12:00 | Rangamati | 134 | 06:00 | 130 | 11:00
Faridpur | 136 | 06:00 | 131 | 13:00 | Rangpur | 134 | 02:00 | 122 | 09:00
Fatullah | 140 | 23:00 | 132 | 00:00 | Ruppur | 141 | 17:00 | 136 | 08:00
Fenchuganj | 141 | 20:00 | 130 | 00:00 | Saidpur | 138 | 17:00 | 124 | 09:00
Feni | 131 | 09:00 | 122 | 11:00 | Satkhira | 138 | 23:00 | 128 | 13:00
Ghatail | 132 | 20:00 | 120 | 01:00 | Satmasjid | 138 | 23:00 | 130 | 11:00
Ghorashal | 144 | 23:00 | 138 | 00:00 | Savar | 136 | 21:00 | 125 | 12:00
Goalpara | 142 | 05:00 | 133 | 12:00 | SevenRings | 143 | 21:00 | 136 | 11:00
Gollamari | 140 | 05:00 | 132 | 12:00 | ShahCement | 138 | 20:00 | 130 | 00:00
Gopalganj | 138 | 05:00 | 132 | 11:00 | Shahjadpur | 142 | 03:00 | 136 | 08:00
Gopalganj-400 | 139 | 22:00 | 134 | 01:00 | Shahjibazar | 140 | 20:00 | 134 | 00:00
Gulshan | 136 | 00:00 | 127 | 12:00 | Shahmirpur | 136 | 09:00 | 129 | 15:00
Halishahar | 137 | 06:00 | 129 | 15:00 | Shariatpur | 138 | 23:00 | 132 | 11:00
Haripur | 136 | 20:00 | 129 | 01:00 | Sherpur | 130 | 20:00 | 107 | 01:00
HaripurSBU | 136 | 21:00 | 129 | 01:00 | Shikalbaha | 125 | 07:00 | 118 | 15:00
Hasnabad | 140 | 19:30 | 133 | 00:00 | Shikalbaha-230 | 135 | 07:00 | 130 | 01:00
Hathazari | 136 | 04:00 | 133 | 11:00 | Shitalakhya | 138 | 20:00 | 130 | 01:00
Ishurdi | 142 | 05:00 | 137 | 08:00 | Sholosohor | 134 | 05:00 | 130 | 01:00
Jaldhaka | 133 | 04:00 | 120 | 08:00 | Shyampur | 139 | 20:00 | 130 | 11:00
Jamalpur | 135 | 20:00 | 111 | 01:00 | Shyampur-230 | 139 | 23:00 | 131 | 12:00
Jashore | 138 | 02:00 | 128 | 13:00 | Siddhirganj | 137 | 20:00 | 130 | 00:00
Jhenaidah | 140 | 03:00 | 132 | 12:00 | Sirajganj | 137 | 02:00 | 130 | 08:00
Jhenaidah-230 | 141 | 05:00 | 132 | 13:00 | Sonargaon | 136 | 20:00 | 127 | 01:00
Joydebpur | 140 | 22:00 | 132 | 10:00 | Sreemongol | 139 | 22:00 | 134 | 00:00
Joypurhat | 136 | 05:00 | 124 | 08:00 | Sreepur | 131 | 20:00 | 125 | 11:00
Juldah | 137 | 13:00 | 129 | 15:00 | Srinagar | 142 | 20:00 | 135 | 11:00
Kabirpur | 143 | 20:00 | 126 | 11:00 | SSM | 139 | 06:00 | 132 | 12:00
Kachua | 135 | 09:00 | 125 | 11:00 | Sunamganj | 135 | 05:00 | 130 | 11:00
Kaliakoir | 142 | 13:00 | 131 | 12:00 | Sylhet | 138 | 07:00 | 131 | 13:00
Kallyanpur | 135 | 05:00 | 129 | 12:00 | Sylhet-132 | 138 | 05:00 | 132 | 12:00
Kalurghat | 134 | 06:00 | 130 | 02:00 | Tangail | 134 | 22:00 | 125 | 07:00
Kamrangirchar | 142 | 19:30 | 128 | 11:00 | Thakurgaon | 137 | 05:00 | 121 | 09:00
Kaptai | N/A | N/A | N/A | N/A | TK | 135 | 04:00 | 131 | 14:00
Kazla | 136 | 23:00 | 128 | 12:00 | Tongi | 139 | 21:00 | 131 | 12:00
Keranigonj | 142 | 20:00 | 14 | 18:00 | Ullahpara | 139 | 23:00 | 134 | 07:00
Khagrachori | 134 | 06:00 | 129 | 11:00 | Ullon | 135 | 23:00 | 128 | 11:00
Khulna | 138 | 23:00 | 131 | 11:00 | Uttara | 135 | 06:00 | 126 | 12:00
Khulna(S) | 141 | 05:00 | 133 | 12:00 | UttaraNew | 139 | 22:00 | 130 | 00:00
Khulshi | 134 | 07:00 | 128 | 02:00 | Zigatola | 142 | 19:00 | 135 | 11:00
Kishoreganj | 133 | 02:00 | 128 | 07:00
Kodda | 141 | 22:00 | 131 | 11:00
KSRM | 136 | 08:00 | 129 | 15:00
Kulaura | 139 | 07:00 | 135 | 02:00
Kurigram | 133 | 05:00 | 24 | 10:00
Kushtia | 140 | 23:00 | 134 | 12:00
Lalbag | 143 | 20:00 | 135 | 11:00
Lalmonirhat | 132 | 00:00 | 121 | 15:00
Madanganj | 137 | 20:00 | 129 | 00:00
Madaripur | 138 | 05:00 | 132 | 13:00
Madartek | 135 | 20:00 | 128 | 10:00
Madunaghat | 135 | 13:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division