## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8146.22 | 0 |  | 8146.22
1:00 | 7532.54 | 0 |  | 7532.54
2:00 | 7148.86 | 0 |  | 7148.86
3:00 | 6988.5 | 0 |  | 6988.5
4:00 | 6952.5 | 0 |  | 6952.5
5:00 | 6920.62 | 0 |  | 6920.62
6:00 | 6935.57 | 0 |  | 6935.57
7:00 | 7281.05 | 0 |  | 7281.05
8:00 | 8110.45 | 0 |  | 8110.45
9:00 | 8295.72 | 0 |  | 8295.72
10:00 | 8239.39 | 0 |  | 8239.39
11:00 | 8550.84 | 0 |  | 8550.84
12:00 | 9057.02 | 0 |  | 9057.02
13:00 | 9614.49 | 0 |  | 9614.49
14:00 | 9575.63 | 0 |  | 9575.63
15:00 | 8989.1 | 0 |  | 8989.1
16:00 | 8595.96 | 0 |  | 8595.96
17:00 | 8751.79 | 0 |  | 8751.79
18:00 | 9781.69 | 0 |  | 9781.69
19:00 | 10318.89 | 0 |  | 10318.89
19:30 | 10170.89 | 0 |  | 10170.89
20:00 | 10078.09 | 0 |  | 10078.09
21:00 | 10074.69 | 0 |  | 10074.69
22:00 | 9730.62 | 0 |  | 9730.62
23:00 | 9288.67 | 0 |  | 9288.67
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 15-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2765 | 1829.5 | 924 | 0 | 46 | 627.72 | 40 | 1896 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2759.5 | 1768.5 | 831 | 0 | 45 | 575.88 | 40 | 1810.5 | 0 | 0 | 9 | 0 | 0 | 0 | 0
01:00 | 2754 | 1707.5 | 738 | 0 | 44 | 524.04 | 40 | 1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2760 | 1631 | 737 | 0 | 43 | 477.7 | 40 | 1652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 205.1053 |  | MKWHr
02:00 | 2766 | 1554.5 | 736 | 0 | 42 | 431.36 | 40 | 1579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2768 | 1494.5 | 736 | 0 | 41 | 429.18 | 40 | 1560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 205.1053 |  | MKWHr
03:00 | 2770 | 1434.5 | 736 | 0 | 40 | 427 | 40 | 1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2735.5 | 1447.5 | 736 | 0 | 40 | 429.5 | 40 | 1540.5 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
04:00 | 2701 | 1460.5 | 736 | 0 | 40 | 432 | 40 | 1540 | 0 | 0 | 0 | 0 | 0 | 3 | 0
04:30 | 2714 | 1480 | 689 | 0 | 40 | 429.06 | 40 | 1541.5 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:00 | 2727 | 1499.5 | 642 | 0 | 40 | 426.12 | 40 | 1543 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 2725 | 1464 | 688.5 | 0 | 39 | 426.095 | 40 | 1541.5 | 0 | 0 | 2.5 | 0 | 0 | 1.5 | 0
06:00 | 2723 | 1428.5 | 735 | 0 | 38 | 426.07 | 40 | 1540 | 0 | 0 | 5 | 0 | 0 | 0 | 0
06:30 | 2761.5 | 1510.5 | 735 | 0 | 38 | 423.37 | 40 | 1580.5 | 10.44 | 0.5 | 8.5 | 0 | 0 | 0 | 0
07:00 | 2800 | 1592.5 | 735 | 0 | 38 | 420.67 | 40 | 1621 | 20.88 | 1 | 12 | 0 | 0 | 0 | 0
07:30 | 2838 | 1645 | 807 | 0 | 40 | 495.035 | 40 | 1686.5 | 94.715 | 9 | 40.5 | 0 | 0 | 0 | 0
08:00 | 2876 | 1697.5 | 879 | 0 | 42 | 569.4 | 40 | 1752 | 168.55 | 17 | 69 | 0 | 0 | 0 | 0
08:30 | 2909.5 | 1661.5 | 879 | 0 | 43 | 566.035 | 40 | 1765.5 | 259.55 | 8.5 | 70.5 | 0 | 0 | 0 | 0
09:00 | 2943 | 1625.5 | 879 | 0 | 44 | 562.67 | 40 | 1779 | 350.55 | 0 | 72 | 0 | 0 | 0 | 0
09:30 | 2886 | 1647 | 901.5 | 0 | 46 | 520.095 | 40 | 1731 | 423.96 | 0 | 72 | 0 | 0 | 0 | 0
10:00 | 2829 | 1668.5 | 924 | 0 | 48 | 477.52 | 40 | 1683 | 497.37 | 0 | 72 | 0 | 0 | 0 | 0
10:30 | 2872.5 | 1704 | 924 | 0 | 49 | 470.74 | 40 | 1713 | 549.375 | 0 | 72.5 | 0 | 0 | 0 | 0
11:00 | 2916 | 1739.5 | 924 | 0 | 50 | 463.96 | 40 | 1743 | 601.38 | 0 | 73 | 0 | 0 | 0 | 0
11:30 | 2970.5 | 1762.25 | 924 | 0 | 52 | 532.105 | 40 | 1824.5 | 619.075 | 0 | 79 | 0 | 0 | 0.5 | 0
12:00 | 3025 | 1785 | 924 | 0 | 54 | 600.25 | 40 | 1906 | 636.77 | 0 | 85 | 0 | 0 | 1 | 0
12:30 | 3056 | 1778.75 | 924 | 0 | 55 | 678.815 | 40 | 2007.5 | 621.69 | 0 | 173 | 0 | 0 | 1 | 0
13:00 | 3087 | 1772.5 | 924 | 0 | 56 | 757.38 | 40 | 2109 | 606.61 | 0 | 261 | 0 | 0 | 1 | 0
13:30 | 3081.5 | 1783 | 923.5 | 0 | 56 | 756.34 | 40 | 2115 | 554.22 | 0 | 283 | 0 | 0 | 2.5 | 0
14:00 | 3076 | 1793.5 | 923 | 0 | 56 | 755.3 | 40 | 2121 | 501.83 | 0 | 305 | 0 | 0 | 4 | 0
14:30 | 3023.5 | 1758.5 | 924 | 0 | 54 | 755.04 | 40 | 2101 | 444.325 | 0 | 177.5 | 0 | 0 | 4.5 | 0
15:00 | 2971 | 1723.5 | 925 | 0 | 52 | 754.78 | 40 | 2081 | 386.82 | 0 | 50 | 0 | 0 | 5 | 0
15:30 | 2983.5 | 1740.75 | 925 | 0 | 52 | 727.8 | 40 | 1963 | 305.48 | 0 | 50 | 0 | 0 | 5 | 0
16:00 | 2996 | 1758 | 925 | 0 | 52 | 700.82 | 40 | 1845 | 224.14 | 0 | 50 | 0 | 0 | 5 | 0
16:30 | 3017.5 | 1783.25 | 925 | 0 | 52 | 688.185 | 40 | 1902.5 | 143.94 | 0 | 116.5 | 0 | 0 | 5 | 0
17:00 | 3039 | 1808.5 | 925 | 0 | 52 | 675.55 | 40 | 1960 | 63.74 | 0 | 183 | 0 | 0 | 5 | 0
17:30 | 3028.5 | 1798.25 | 925 | 0 | 54 | 715.12 | 40 | 2047 | 32.37 | 93 | 526 | 0 | 0 | 7.5 | 0
18:00 | 3018 | 1788 | 925 | 0 | 56 | 754.69 | 40 | 2134 | 1 | 186 | 869 | 0 | 0 | 10 | 0
18:30 | 3022 | 1844.5 | 901.5 | 0 | 56 | 755.29 | 40 | 2161 | 0.5 | 178.5 | 1082.5 | 0 | 0 | 8.5 | 0
19:00 | 3026 | 1901 | 878 | 0 | 56 | 755.89 | 40 | 2188 | 0 | 171 | 1296 | 0 | 0 | 7 | 0
19:30 | 3061 | 1914.5 | 878 | 0 | 56 | 752.39 | 40 | 2189 | 0 | 157 | 1117 | 0 | 0 | 6 | 0
20:00 | 3120 | 1923 | 879 | 0 | 58 | 754.09 | 40 | 2188 | 0 | 107 | 1004 | 0 | 0 | 5 | 0
20:30 | 3128.5 | 1931.75 | 902 | 0 | 58 | 754.64 | 40 | 2188 | 0 | 98.5 | 970.5 | 0 | 0 | 4.5 | 0
21:00 | 3137 | 1940.5 | 925 | 0 | 58 | 755.19 | 40 | 2188 | 0 | 90 | 937 | 0 | 0 | 4 | 0
21:30 | 3128 | 1925.5 | 924.5 | 0 | 57 | 754.155 | 40 | 2188.5 | 0 | 66 | 817 | 0 | 0 | 2 | 0
22:00 | 3119 | 1910.5 | 924 | 0 | 56 | 753.12 | 40 | 2189 | 0 | 42 | 697 | 0 | 0 | 0 | 0
22:30 | 3084 | 1923.25 | 924.5 | 0 | 55 | 753.895 | 40 | 2188.5 | 0 | 21 | 519.5 | 0 | 0 | 0 | 0
23:00 | 3049 | 1936 | 925 | 0 | 54 | 754.67 | 40 | 2188 | 0 | 0 | 342 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4623 | 3523.22 | 8146.22 | DAILY GENERATION CURVE
00:30 | 4468 | 3371.38 | 7839.38
01:00 | 4313 | 3219.54 | 7532.54 | 15-02-2025
01:30 | 4162 | 3178.7 | 7340.7
02:00 | 4011 | 3137.86 | 7148.86
02:30 | 3951 | 3117.68 | 7068.68
03:00 | 3891 | 3097.5 | 6988.5
03:30 | 3852.5 | 3118 | 6970.5
04:00 | 3814 | 3138.5 | 6952.5
04:30 | 3832 | 3104.56 | 6936.56
05:00 | 3850 | 3070.62 | 6920.62
05:30 | 3817.5 | 3110.595 | 6928.095
06:00 | 3785 | 3150.57 | 6935.57
06:30 | 3920.265 | 3188.045 | 7108.31
07:00 | 4055.53 | 3225.52 | 7281.05
07:30 | 4245.74 | 3450.01 | 7695.75
08:00 | 4435.95 | 3674.5 | 8110.45
08:30 | 4426.555 | 3776.53 | 8203.085
09:00 | 4417.16 | 3878.56 | 8295.72
09:30 | 4410.465 | 3857.09 | 8267.555
10:00 | 4403.77 | 3835.62 | 8239.39
10:30 | 4509.125 | 3885.99 | 8395.115
11:00 | 4614.48 | 3936.36 | 8550.84
11:30 | 4758.105 | 4045.825 | 8803.93
12:00 | 4901.73 | 4155.29 | 9057.02
12:30 | 5037.725 | 4298.03 | 9335.755
13:00 | 5173.72 | 4440.77 | 9614.49
13:30 | 5161.41 | 4433.65 | 9595.06
14:00 | 5149.1 | 4426.53 | 9575.63
14:30 | 5003.07 | 4279.295 | 9282.365
15:00 | 4857.04 | 4132.06 | 8989.1
15:30 | 4813.55 | 3978.98 | 8792.53
16:00 | 4770.06 | 3825.9 | 8595.96
16:30 | 4829.31 | 3844.565 | 8673.875
17:00 | 4888.56 | 3863.23 | 8751.79
17:30 | 5206.03 | 4060.71 | 9266.74
18:00 | 5523.5 | 4258.19 | 9781.69
18:30 | 5771.5 | 4278.79 | 10050.29
19:00 | 6019.5 | 4299.39 | 10318.89
19:30 | 5833 | 4337.89 | 10170.89
20:00 | 5729.5 | 4348.59 | 10078.09
20:30 | 5700.75 | 4375.64 | 10076.39 |  | Executive Engineer
21:00 | 5672 | 4402.69 | 10074.69 |  | Network Operation Division
21:30 | 5571.5 | 4331.155 | 9902.655
22:00 | 5471 | 4259.62 | 9730.62
22:30 | 5339.75 | 4169.895 | 9509.645
23:00 | 5208.5 | 4080.17 | 9288.67

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9057.02 | MW | 12:00 Hr. | Energy Generated |  |  | 205.1053 |  | MKWHr.
| Day Peak Demand |  |  | 9057.02 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10318.89 | MW | 19:00 Hr. | Energy Demand |  |  | 205.1053 |  | MKWHr.
| Evening Peak Demand |  |  | 10318.89 | MW | 19:00 Hr. | Maximum Temperature |  |  | 29.1 |  | °C
| Minimum Generation of the Day |  |  | 6920.62 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 871.95 |  | MMCFD
| Maximum Generation of the Day |  |  | 10318.89 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.3986 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.7306 | 0 | 1.5492 | 0 | 0 | 0.20492 | 0 | 0 | 31.4847 | Gas | 110.4322 | Gas | 399563152.4306
| Chattogram Zone |  |  | 6.1504 | 23.4964 | 1.536 | 0 | 0.95952 | 0.11856 | 0 | 0.04992 | 32.3107 | Coal | 45.3928 | Coal | 320824508.5567
| Cumilla Zone |  |  | 18.6318 | 0 | 1.4272 | 0 | 0 | 0.34667 | 1.1664 | 0 | 21.5721 | HFO | 7.5731 | HFO | 137523491.04
| Mymensingh Zone |  |  | 3.001 | 0 | 1.1364 | 0 | 0 | 0.32388 | 0 | 0 | 4.4612 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 22.5872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5872 | Hydro | 0.95952 | Hydro | 95952
| Khulna Zone |  |  | 8.5922 | 0 | 0 | 0 | 0 | 0.57816 | 20.7607 | 0 | 29.9311 | Solar | 4.0816 | Solar | 64332198.882
| Barishal Zone |  |  | 7.9911 | 18.3725 | 0.4056 | 0 | 0 | 0.003393 | 0 | 0 | 26.7725 | Import | 36.6162 | Import | 184164422.55
| Rajshahi Zone |  |  | 13.7479 | 0 | 0.47775 | 0 | 0 | 1.1448 | 14.6891 | 0 | 30.0596 | Wind | 0.04992 | Wind | 778752
| Rangpur Zone |  |  | 0 | 3.524 | 1.041 | 0 | 0 | 1.3612 | 0 | 0 | 5.9262
| Total |  |  | 110.4322 | 45.3928 | 7.5731 | 0 | 0.95952 | 4.0816 | 36.6162 | 0.04992 | 205.1053
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 399563152.4306 |  | Hydro | 95952
|  |  |  | Coal | 320824508.5567 |  | Solar | 64332198.882
|  |  |  | HFO | 137523491.04 |  | Import | 184164422.55
|  |  |  | HSD | 0 |  | Wind | 778752
[5 empty] | Total: | 110,72,82,477 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.7607 | Peak Hr Flow | 878.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8872181.899 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.6891 | Peak Hr Flow | 755.89 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 520 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.1664 | Peak Hr Flow | 56.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 742 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.6162 | Peak Hr Flow | 1689.89 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3288
|  |  |  | Chattogram |  | 0 |  | 1078
|  |  |  | Cumilla |  | 0 |  | 893
|  |  |  | Mymensingh |  | 0 |  | 944
|  |  |  | Sylhet |  | 0 |  | 358
|  |  |  | Khulna |  | 0 |  | 1205
|  |  |  | Barishal |  | 0 |  | 308
|  |  |  | Rajshahi |  | 0 |  | 1072
|  |  |  | Rangpur |  | 0 |  | 753
|  |  |  | Total |  | 0 |  | 9899
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 225MW CCPP Unit-3 GT |  |  | 141
|  | 7 | Sirajgonj 225MW CCPP Unit-3 ST |  |  | 79
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1012 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1678.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 14:38 | Chowmuhani 132/33kV S/S TR1-415T HT Scheduled S/D Due to 33 kv Tr-01 Bus and Loop | [7 empty] | 25.0MW load
|  |  | Maintenance Work | [7 empty] | interrup.
| 08:15 | 14:38 | Chowmuhani 132/33kV S/S TR1 Scheduled S/D Due to 33 kv Tr-01 Bus and Loop Maintenance | [7 empty] | 15.0MW load
|  |  | Work | [7 empty] | interrup.
| 08:35 |  | Meghnaghat CCPP 450MW GT2 was shutdown at 08:35 hrs due to HRSG maintenance.
| 08:42 | 15:44 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-02 Scheduled S/D Due to Yearly
maintenance
| 08:43 | 14:05 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Maintenance by PBS. | [7 empty] | 10.0MW load
interrup.
| 08:43 | 14:03 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Maintenance by PBS. | [7 empty] | 10.0MW load
interrup.
| 08:43 | 15:45 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to line
shutdown for annual maintenance work
| 08:45 |  | Baghabari-Shahjadpur 132 kV Ckt-2 Scheduled S/D from Shahjadpur 132/33kV end Due to
Piling work go on
| 08:46 | 09:50 | Palashbari 132/33kV S/S TR2-404T LT Scheduled S/D Due to 33kV Bus maintenance | [7 empty] | 30.0MW load
interrup.
| 08:46 | 09:46 | Palashbari 132/33kV S/S TR2-404T HT Scheduled S/D Due to 33kV Bus maintenance | [7 empty] | 30.0MW load
interrup.
| 08:47 | 17:00 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project work.
| 08:48 | 16:03 | BSRM 230/33kV S/S AKSML Ckt Scheduled S/D Due to For Deadline Checking, S/D taken by
Baraulia SS.
| 08:59 | 16:01 | GPH 230/33kV S/S BSRM CKT-1 Scheduled S/D Due to annual maintenance
|  | 09:25 | Coxsbazar 132/33kV S/S Main Bus is restored.
| 09:30 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 09:30 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- GT-synchronized at
09:30 hrs.
| 09:58 | 10:34 | Faridpur 132/33kV S/S Bus-B Scheduled S/D Due to Red hot
|  | 10:04 | Keranigonj 230/132/33kV S/S TR-1 HT is restored.
|  | 10:04 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
| 10:14 | 11:38 | Haripur 230/132kV S/S 132KV Bhulta-2 Tripped showing Siprotec: General Trip, Zone-2,
R-phase Trip, Y-phase Trip, A/R Off/BLK. relays Due to Trip
| 10:18 | 10:41 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Tripped showing Siprotec: General | [7 empty] | 150.0MW load
|  |  | Trip, OC/EF/EFCOM, A/R Off/BLK. relays Due to Overload. | [7 empty] | interrup.
| 10:37 | 18:03 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Interlock work
| 10:37 | 18:05 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Interlock work
| 11:12 | 13:10 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Scheduled S/D Due to oil temperature meter | [7 empty] | 20.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 11:36 |  | Barapukuria-3 was shutdown at 11:36 hrs due to feed pump maintenance.
|  | 11:36 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 11:36 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
| 11:36 |  | Ashuganj 450 MW CCPP(South), FGMO is ON with remarks:-
| 11:58 | 12:58 | Sholosohor 132/33kV S/S Sholoshahar-Madunaghat Ckt-1 Tripped showing 86.1 and 86.2
relays.
| 11:58 | 12:57 | Khulshi-Madunaghat 132kV Ckt-1 Tripped from Madunaghat 132/33kV end showing REL670
relays Due to General Trip, Zone1, 67N Trip, R-Phase fault
| 12:00 |  | Day peak Generation is 9054 MW
| 12:02 |  | Siddhirganj GT1 was sync. at 12:02 hrs.
| 12:27 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- ST synchronized at
12:27 hrs.
| 12:27 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 13:07 | 18:10 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Interlocking work
|  | 13:19 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
| 14:34 | 17:40 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Mirsorai 230/33kV end Due to
Annual Maintenance
| 15:41 | 17:30 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Forced S/D Due to RED HOT at other
end.
|  | 16:23 | Keranigonj 230/132/33kV S/S TR-2 HT is restored.
|  | 16:24 | Keranigonj 230/132/33kV S/S TR-2 LT is restored.
|  | 16:30 | Aminbazar 400/230/132kV S/S Gopalganj-1 is restored.
|  | 16:32 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 is restored.
| 19:00 |  | Evening Peak Generation: 10317 MW.
| 19:45 |  | Ghorashal Unit-5 was sync.
| 05:00 |  | Minimum generation 7474 MW
| 05:59 | 06:26 | Goalpara 132/33kV S/S T-5 LT Tripped showing Dir OC, EF relays Due to Tripped due to REB
33KV feeder fault
| 06:50 |  | Bogura 132/33kV S/S Transformer-4 LT Project Work S/D Due to 33 kV Busbar up-gradation | [7 empty] | 25.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:50 |  | Bogura 132/33kV S/S Transformer-4 HT Project Work S/D Due to 33 kV Busbar up-gradation | [7 empty] | 25.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:50 |  | Bogura 132/33kV S/S Transformer-3 LT Project Work S/D Due to 33 kV Busbar up-gradation | [7 empty] | 25.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:50 |  | Bogura 132/33kV S/S Transformer-3 HT Project Work S/D Due to 33 kV Busbar up-gradation | [7 empty] | 25.0MW load
|  |  | work. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 3630844 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 126000 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9525600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 6161000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6968582 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 39 | 85122 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 204000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 260280 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 38880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 113997 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 264393 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10.5 | 273600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 417240 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 14 | 288720 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 648200 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Under Maintenance
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 32 | 75168 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 78720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 620640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204919 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 138 | 1486818.18 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 12000 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 1727.5 | 31484723.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 92880 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 158400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 959520 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5200432 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 570399 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 32 | 70560 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 71040 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 949920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 90327 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 153054 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 70080 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 268473 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 83636 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 11459999 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 7 | 49920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 577 | 12036363.64 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1890 | 32310683.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 185 | 4605000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 305 | 7550000 | HGPI Maintenance Work is going on.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 793008 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 553440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 3813818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 919550 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 240807 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 424800 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 56 | 1166400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 397000 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 199080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 105 | 562560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 346673 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1144 | 21572136
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 153 | 3000960 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 153600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 740400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 309880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 86880 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 155520 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 262 | 4461240
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 29 | 708000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3635673 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 553392 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 57600 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 614112 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1343040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 218000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 543408 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7237500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7676500 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 996 | 22587225
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 878 | 20760727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 385 | 8592192 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 578160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1263 | 29931079
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 132512 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2763000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 12481454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5095570 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 405600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5891000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3393 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1340 | 26772529.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 197 | 5117791 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 385 | 8557672 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 72486 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 44083 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 433664 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755.89 | 14689091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 393000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 716850 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1441.39 | 30059557
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1645964 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 1878000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 526204 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35218.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 514749 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 163945 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1162080 | -
Rangpur Area Total |  |  |  |  | 950 | 255 | 5926160.32
Eastern Grid Total |  |  |  |  | 16856.242 | 6019.5 | 112416007.82
Western Grid Total |  |  |  |  | 10294.5 | 4299.39 | 92689325.87
National Grid Total |  |  |  |  | 27150.742 | 10318.89 | 205105333.69
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-02-2025 | during | 16-02-2025 | during | 16-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 240 | 230 | 240 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 402 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 285 | 300 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 39 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 210 | 210 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 12 | 10.5 | 22.5 | 22.5 | 22.5 | 22.5 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 8 | 14 | 25 | 25 | 25 | 25 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 32.5 | 32 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 32 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 54 | 17 | 54 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 83 | 138 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1322.5 | 1727.5 | 4578.87 | 4572.87 | 3529.58 | 3523.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 223 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 32 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 34 | 34 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.91 | 0 | 3.91 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 540 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 1 | 7 | 0 | 6 | 0 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 577 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1437 | 1890 | 2943.77 | 2973.86 | 2828.77 | 2858.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 185 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 305 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 33 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 175 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 40 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 70 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 68 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 56 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 105 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 899 | 1144 | 2095.53 | 2035.53 | 1864.2 | 1804.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-02-2025 | during | 16-02-2025 | during | 16-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 139 | 153 | 210 | 210 | 150 | 150 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 59 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.23 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 261.23 | 262 | 653.4 | 601.5 | 593.4 | 541.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 29 | 29 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 330 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 25 | 35 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 982 | 996 | 1387 | 1387 | 1018 | 1018
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 878 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 394 | 385 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 86.71 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234.2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1404.71 | 1263 | 3588.2 | 3498.2 | 2144 | 2054
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 622 | 622 | 622 | 602 | 602 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 12 | 54 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 280 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1086.59 | 1340 | 1556.12 | 1555.12 | 1533 | 1532
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 214 | 197 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 395 | 385 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 32 | 32 | 32 | 32 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.15 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 600.25 | 755.89 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.09 | 0 | 60 | 0 | 60 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1379.99 | 1441.39 | 2273.54 | 2108.24 | 2011.76 | 1846.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 70 | 70 | 70 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 183 | 0 | 180.91 | 0 | 180.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 284 | 255 | 546.51 | 332 | 541.51 | 327
System Total |  |  |  |  | 27884.66 | 27150.742 | 9057.02 | 10318.89 | 19622.94 | 19064.32 | 16064.22 | 15505.6
Forecast Scenario (16-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8900 |  | 0 |  | 8900
|  |  |  | 1:00 | 8350 |  | 0 |  | 8350
|  |  |  | 2:00 | 8000 |  | 0 |  | 8000
|  |  |  | 3:00 | 7700 |  | 0 |  | 7700
|  |  |  | 4:00 | 7450 |  | 0 |  | 7450
|  |  |  | 5:00 | 7460 |  | 0 |  | 7460
|  |  |  | 6:00 | 7850 |  | 0 |  | 7850
|  |  |  | 7:00 | 8970 |  | 0 |  | 8970
|  |  |  | 8:00 | 9920 |  | 0 |  | 9920
|  |  |  | 9:00 | 10400 |  | 0 |  | 10400
|  |  |  | 10:00 | 10330 |  | 0 |  | 10330
|  |  |  | 11:00 | 10420 |  | 0 |  | 10420
|  |  |  | 12:00 | 10810 |  | 0 |  | 10810
|  |  |  | 13:00 | 11080 |  | 0 |  | 11080
|  |  |  | 14:00 | 10650 |  | 0 |  | 10650
|  |  |  | 15:00 | 10150 |  | 0 |  | 10150
|  |  |  | 16:00 | 9780 |  | 0 |  | 9780
|  |  |  | 17:00 | 9820 |  | 0 |  | 9820
|  |  |  | 18:00 | 10650 |  | 0 |  | 10650
|  |  |  | 18:30 | 10980 |  | 0 |  | 10980
|  |  |  | 19:00 | 11370 |  | 0 |  | 11370
|  |  |  | 19:30 | 11070 |  | 0 |  | 11070
|  |  |  | 20:00 | 10960 |  | 0 |  | 10960
|  |  |  | 21:00 | 10690 |  | 0 |  | 10690
|  |  |  | 22:00 | 10310 |  | 0 |  | 10310
|  |  |  | 23:00 | 9680 |  | 0 |  | 9680
Probable Maximum Temperature: |  |  | 29.00°C
Probable Maximum Demand at Day Peak: |  |  | 10810.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11370.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11370.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 231.70 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:34 hrs on 16-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6561.04 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3337.9 | MW
i) Dhaka area |  |  | 3287.54 |  | MW | i) Khulna area |  |  |  | 1204.8 | MW
ii) Chattogram area |  |  | 1078.5 |  | MW | ii) Barishal area |  |  |  | 308.5 | MW
iii) Cumilla area |  |  | 893 |  | MW | iii) Rajshahi area |  |  |  | 1071.6 | MW
iv) Mymensingh area |  |  | 944 |  | MW | iv) Rangpur area |  |  |  | 753 | MW
v) Sylhet area |  |  | 358 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9898.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 58 | 18:30 | 133 | Postogola | 29 | 13:00
2 | AKSML | 25 | 18:00 | 68 | Jamalpur | 106 | 18:00 | 134 | Purbachal | 13 | 12:00
3 | Aftabnagar | 22 | 13:00 | 69 | Jashore | 103 | 19:00 | 135 | Purbasadipur | 121 | 13:00
4 | Agargaon | 66 | 13:00 | 70 | Jhenaidah | 96 | 18:30 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 60 | 19:00 | 71 | Joydebpur | 107 | 20:00 | 137 | Rahim | 24 | 10:00
6 | Amnura | 51 | 13:00 | 72 | Joypurhat | 56 | 09:00 | 138 | Rajbari | 54 | 19:00
7 | Ashuganj | 69 | 23:00 | 73 | Juldah | 11 | 00:00 | 139 | Rajendrapur | 84 | 13:00
8 | BSRM | 200 | 19:00 | 74 | KSRM | 13 | 18:00 | 140 | Rajshahi | 70 | 19:00
9 | Bagerhat | 64 | 18:30 | 75 | Kabirpur | 155 | 21:00 | 141 | Rajshahi-230 | 66 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 51 | 14:00 | 142 | Ramganj | 84 | 20:00
11 | Bakulia | 61 | 18:30 | 77 | Kallyanpur | 69 | 13:00 | 143 | Rampur | 26 | 00:00
12 | Banani | 16 | 18:30 | 78 | Kalurghat | 20 | 18:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 3 | 12:00 | 79 | Kamrangirchar | 37.6 | 22:00 | 145 | Rangpur | 104 | 14:00
14 | Barapukuria | 59 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 3 | 10:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 72 | 22:00 | 147 | SSM | 0 | 00:00
16 | Barishal | 66 | 13:00 | 82 | Keranigonj | 45 | 21:00 | 148 | Saidpur | 93 | 14:00
17 | Barishal-230 | 70 | 19:00 | 83 | Khagrachori | 24 | 18:30 | 149 | Satkhira | 91 | 18:30
18 | Baroaulia | 37 | 21:00 | 84 | Khulna | 52 | 19:00 | 150 | Satmasjid | 64 | 13:00
19 | Baroirhat | 37 | 18:30 | 85 | Khulshi | 132 | 14:00 | 151 | Savar | 104 | 21:00
20 | Bashundhara | 120 | 13:00 | 86 | Kishoreganj | 110 | 13:00 | 152 | SevenRings | 15.16 | 08:00
21 | BashundharaCement | 7 | 11:00 | 87 | Kodda | 111 | 20:00 | 153 | ShahCement | 31 | 18:00
22 | Beanibazar | 42 | 18:00 | 88 | Kulaura | 27 | 18:30 | 154 | Shahjadpur | 58 | 13:00
23 | Benapole | 48 | 08:00 | 89 | Kurigram | 60 | 18:00 | 155 | Shahjibazar | 85 | 21:00
24 | Bhaluka | 86 | 10:00 | 90 | Kushtia | 98 | 18:30 | 156 | Shahmirpur | 26 | 18:00
25 | Bhandaria | 42 | 18:30 | 91 | Lalbag | 42 | 23:00 | 157 | Shariatpur | 58 | 19:00
26 | Bhangura | 32 | 18:30 | 92 | Lalmonirhat | 50 | 18:30 | 158 | Sherpur | 144 | 08:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | MI_Cement | 16.8 | 12:00 | 159 | Shikalbaha | 15 | 18:30
28 | Bhulta | 198 | 13:00 | 94 | Madanganj | 18 | 12:00 | 160 | Shitalakhya | 40.8 | 21:00
29 | Bog-Sherpur | 62 | 08:00 | 95 | Madaripur | 68 | 18:30 | 161 | Sholosohor | 27 | 21:00
30 | Bogura | 113 | 13:00 | 96 | Madartek | 58.86 | 13:00 | 162 | Shyampur | 130 | 13:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madunaghat | 36 | 18:00 | 163 | Siddhirganj | 69 | 23:00
32 | Brahmanbaria | 102 | 18:00 | 98 | Magura | 44 | 18:30 | 164 | Sirajganj | 78 | 12:00
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 62 | 09:00 | 165 | Sonargaon | 69 | 21:00
34 | Chandpur | 44 | 18:00 | 100 | Manikganj | 89 | 22:00 | 166 | Sreemongol | 39 | 18:00
35 | Chandraghona | 27 | 18:30 | 101 | Maniknagar | 34 | 13:00 | 167 | Sreepur | 64 | 18:30
36 | Chapai | 63 | 07:00 | 102 | Matarbari | 36 | 18:30 | 168 | Srinagar | 29.97 | 14:00
37 | Charsaidpur | 41 | 05:00 | 103 | Matuail | 41 | 23:00 | 169 | Sunamganj | 42 | 18:30
38 | Chauddagram | 44 | 13:00 | 104 | Millgate | 47 | 12:00 | 170 | Sylhet | 22 | 18:00
39 | Chhatak | 22 | 18:00 | 105 | Mirpur | 85.5 | 18:30 | 171 | Sylhet-132 | 74 | 18:30
40 | Chowmuhani | 149 | 18:00 | 106 | Mirsorai | 8 | 12:00 | 172 | TK | 21 | 18:30
41 | Chuadanga | 68 | 13:00 | 107 | Mirzapur | 40 | 14:00 | 173 | Tangail | 156 | 08:00
42 | Coxsbazar | 119 | 12:00 | 108 | Mithapukur | 48 | 08:00 | 174 | Thakurgaon | 77 | 13:00
43 | Cumilla(N) | 131 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 77 | 12:00
44 | Cumilla(S) | 91 | 18:30 | 110 | Mogbazar | 79.2 | 14:00 | 176 | Ullahpara | 25 | 08:00
45 | Daudkandi | 84 | 19:30 | 111 | Mongla | 23 | 23:00 | 177 | Ullon | 34 | 14:00
46 | Dhaka | 16 | 18:00 | 112 | Motijheel | 20 | 13:00 | 178 | Uttara | 55 | 18:30
47 | Dhamrai | 86 | 18:00 | 113 | Muktagacha | 30 | 14:00 | 179 | UttaraNew | 30 | 13:00
48 | Dhanmondi | 66 | 19:00 | 114 | Munshiganj | 70 | 20:00 | 180 | Zigatola | 52 | 14:00
49 | Dohazari | 76 | 18:30 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 102 | 17:00 | 116 | Mymensingh | 165 | 14:00
51 | Fatullah | 46 | 23:00 | 117 | Naogaon | 102 | 09:00
52 | Fenchuganj | 25 | 18:00 | 118 | Narail | 44 | 18:30
53 | Feni | 82 | 18:00 | 119 | Narinda | 40 | 13:00
54 | GPH | 15 | 02:00 | 120 | Narshingdi | 148 | 19:30
55 | Ghatail | 52 | 18:00 | 121 | Natore | 116 | 18:30
56 | Ghorashal | 11 | 20:00 | 122 | Nawabganj | 31.6 | 13:00
57 | Ghorashal-230 | 51 | 18:00 | 123 | Netrakona | 137 | 18:00
58 | Goalpara | 20 | 13:00 | 124 | New | 46.1 | 22:00
59 | Gollamari | 58 | 13:00 | 125 | Niamatpur | 89 | 09:00
60 | Gopalganj | 73.6 | 18:30 | 126 | Noapara | 32 | 18:30
61 | Gulshan | 58 | 18:00 | 127 | PHP | 8 | 01:00
62 | Halishahar | 33 | 15:00 | 128 | Pabna | 60 | 18:30
63 | HaripurSBU | 156 | 23:00 | 129 | Palashbari | 94 | 13:00
64 | Hasnabad | 87 | 19:00 | 130 | Panchagarh | 42 | 18:30
65 | Hathazari | 55 | 13:00 | 131 | Patuakhali | 57.5 | 19:00
66 | Ishurdi | 56 | 19:00 | 132 | Payra | 20 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 416 | 06:00 | 398 | 13:00 | Payra | 427 | 06:00 | 418 | 13:00
Ashuganj | 418 | 6:00 | 400 | 13:00 | Rahanpur | 419 | 03:00 | 401 | 13:00
Bhulta | 416 | 06:00 | 399 | 13:00 | Rampal | 420 | 06:00 | 397 | 13:00
Bibiana | 413 | 00:00 | 403 | 15:00
BIPTC | 406 | 04:00 | 387 | 11:00
Bogura | 418 | 03:00 | 398 | 12:00
Gopalganj | 422 | 06:00 | 405 | 13:00
Kaliakoir | 406 | 04:00 | 393 | 13:00
Madunaghat | 409 | 07:00 | 400 | 13:00
Meghnaghat | 412 | 06:00 | 397 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 06:00 | 230 | 13:00 | Keranigonj | 238 | 03:00 | 230 | 13:00
AKSML | 235 | 18:00 | 226 | 13:00 | Khulna(S) | 244 | 05:00 | 230 | 13:00
Aminbazar | 238 | 00:00 | 230 | 13:00 | Madunaghat | 235 | 18:00 | 229 | 12:00
Ashuganj | 246 | 06:00 | 236 | 13:00 | Madunaghat-400 | 235 | 07:00 | 229 | 14:00
Ashuganj-400 | 246 | 06:00 | 236 | 13:00 | Maniknagar | 241 | 06:00 | 231 | 13:00
Baghabari | 243 | 03:00 | 233 | 12:00 | Meghnaghat | 243 | 00:00 | 239 | 09:00
Barapukuria | 229 | 05:00 | 210 | 12:00 | Meghnaghat-400 | 242 | 06:00 | 233 | 13:00
Barapukuria-230 | 229 | 05:00 | 210 | 12:00 | Mirsorai | 237 | 06:00 | 227 | 13:00
Barishal | 247 | 06:00 | 239 | 14:00 | Rajshahi | 242 | 05:00 | 231 | 13:00
Bheramara | 242 | 05:00 | 230 | 13:00 | Rampal | 242 | 06:00 | 228 | 13:00
Bhulta | 242 | 06:00 | 232 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 240 | 05:00 | 232 | 14:00 | Rampura | 242 | 06:00 | 232 | 13:00
BIPTC | 244 | 05:00 | 232 | 13:00 | Shikalbaha | 234 | 18:00 | 225 | 14:00
Bogura | 243 | 03:00 | 230 | 12:00 | Shyampur | 240 | 06:00 | 230 | 13:00
Bogura-400 | 241 | 03:00 | 228 | 12:00 | Siddhirganj | 241 | 00:00 | 234 | 12:00
Borhanuddin | 249 | 00:00 | 245 | 18:30 | Sirajgonj | 247 | 05:00 | 240 | 12:00
BSRM | 237 | 06:00 | 227 | 13:00 | Sreepur | 243 | 00:00 | 231 | 13:00
Cumilla(N) | 238 | 06:00 | 230 | 13:00 | Tongi | 237 | 03:00 | 228 | 13:00
Faridpur | 248 | 06:00 | 238 | 13:00
Fenchuganj | 242 | 00:00 | 233 | 19:00
Ghorashal | 240 | 00:00 | 240 | 00:00
Ghorashal-230 | 240 | 01:00 | 232 | 13:00
Gopalganj | 247 | 06:00 | 237 | 13:00
GPH | 237 | 06:00 | 227 | 13:00
Haripur | 240 | 00:00 | 231 | 13:00
Hasnabad | 241 | 06:00 | 231 | 14:00
Hathazari | 236 | 06:00 | 230 | 12:00
Ishurdi | 245 | 05:00 | 234 | 13:00
Jhenaidah | 242 | 05:00 | 228 | 14:00
Kaliakoir | 236 | 02:00 | 228 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 00:00 | 131 | 13:00 | Magura | 141 | 04:00 | 131 | 13:00
Agargaon | 140 | 06:00 | 133 | 13:00 | Mahasthangarh | 137 | 00:00 | 127 | 12:00
Agrabad | 135 | 06:00 | 122 | 01:00 | Manikganj | 141 | 01:00 | 136 | 00:00
AKS | 133 | 19:00 | 127 | 15:00 | Maniknagar | 138 | 04:00 | 132 | 13:00
Aminbazar | 138 | 00:00 | 131 | 13:00 | Matarbari | 130 | 09:00 | 111 | 11:00
Amnura | 142 | 20:00 | 129 | 13:00 | Matuail | 139.5 | 06:00 | 133 | 13:00
Ashuganj | 143 | 00:00 | 140 | 12:00 | Millgate | 140 | 01:00 | 133 | 13:00
Bagerhat | 140 | 05:00 | 130 | 13:00 | Mirpur | 137 | 00:00 | 131 | 12:00
Bajitpur | 139 | 02:00 | 133 | 12:00 | Mirzapur | 139 | 02:00 | 123 | 18:30
Bakulia | 136 | 06:00 | 129 | 12:00 | Mithapukur | 138 | 19:30 | 120 | 12:00
Banani | 138 | 00:00 | 131 | 13:00 | MI_Cement | 140 | 06:00 | 134 | 13:00
Bangabhaban | 138 | 03:00 | 132 | 13:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 138 | 05:00 | 125 | 12:00 | Mogbazar | 138 | 01:00 | 133 | 08:00
Barguna | 141 | 18:00 | 138 | 11:00 | Mongla | 140 | 05:00 | 130 | 13:00
Barishal | 137 | 02:00 | 132 | 12:00 | Motijheel | 138 | 03:00 | 132 | 13:00
Barishal-230 | 138 | 06:00 | 132 | 18:30 | Muktagacha | 132 | 01:00 | 127 | 09:00
Baroaulia | 135 | 19:00 | 130 | 12:00 | Munshiganj | 138 | 05:00 | 133 | 13:00
Baroirhat | 135 | 06:00 | 126 | 16:00 | Muradnagar | 139 | 06:00 | 132 | 13:00
Bashundhara | 140 | 05:00 | 131 | 13:00 | Mymensingh | 133 | 20:00 | 117 | 12:00
BashundharaCement | 138 | 05:00 | 132 | 13:00 | Naogaon | 136 | 00:00 | 125 | 12:00
Beanibazar | 138 | 06:00 | 133 | 18:30 | Narail | 140 | 01:00 | 131 | 12:00
Benapole | 139 | 05:00 | 127 | 13:00 | Narinda | 138 | 04:00 | 132 | 13:00
Bhaluka | 129 | 00:00 | 121 | 12:00 | Narshingdi | 137 | 00:00 | 127 | 16:00
Bhandaria | 135 | 05:00 | 126 | 18:30 | Natore | 139 | 00:00 | 132 | 13:00
Bhangura | 139 | 00:00 | 132 | 12:00 | Nawabganj | 142 | 06:00 | 134 | 13:00
Bheramara | 140 | 00:00 | 135 | 13:00 | Netrakona | 127 | 03:00 | 116 | 07:00
Bheramara(GK) | 140 | 00:00 | 136 | 12:00 | New | 140 | 00:00 | 134 | 13:00
Bhulta | 134 | 00:00 | 129 | 13:00 | Niamatpur | 141 | 05:00 | 133 | 13:00
Bog-Sherpur | 138 | 02:00 | 128 | 12:00 | Noapara | 141 | 05:00 | 130 | 13:00
Bogura | 139 | 05:00 | 130 | 12:00 | Pabna | 138 | 00:00 | 128 | 13:00
Bogura-230 | 139 | 03:00 | 130 | 13:00 | Palashbari | 133 | 00:00 | 120 | 12:00
Brahmanbaria | 139 | 00:00 | 135 | 15:00 | Panchagarh | 143 | 19:30 | 118 | 09:00
Cantonment | 139 | 05:00 | 133 | 13:00 | Patuakhali | 140 | 18:00 | 136 | 13:00
Chandpur | 137 | 19:30 | 122 | 16:00 | Payra | 141 | 06:00 | 137 | 09:00
Chandraghona | 137 | 04:00 | 131 | 13:00 | PHP | 134 | 06:00 | 124 | 15:00
Chapai | 138 | 00:00 | 130 | 13:00 | Postogola | 141 | 00:00 | 136 | 12:00
Charsaidpur | 140 | 03:00 | 134 | 12:00 | Purbachal | 137 | 01:00 | 131 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 136 | 06:00 | 127 | 14:00 | Purbasadipur | 135 | 19:00 | 116 | 12:00
Chhatak | 136 | 05:00 | 131 | 18:00 | Rahanpur | 142 | 01:00 | 135 | 13:00
Chowmuhani | 132 | 22:00 | 122 | 14:00 | Rahanpur-400 | 142 | 01:00 | 136 | 08:00
Chuadanga | 141 | 01:00 | 130 | 13:00 | Rahim | 136 | 00:00 | 131 | 14:00
Coxsbazar | 122 | 02:00 | 104 | 11:00 | Rajbari | 137 | 05:00 | 131 | 13:00
Cumilla(N) | 138 | 04:00 | 132 | 15:00 | Rajendrapur | 140 | 06:00 | 132 | 13:00
Cumilla(S) | 139 | 06:00 | 128 | 10:00 | Rajshahi | 141 | 04:00 | 133 | 13:00
Daudkandi | 137 | 05:00 | 129 | 13:00 | Rajshahi-230 | 140 | 05:00 | 125 | 13:00
Dhaka | 137 | 00:00 | 131 | 13:00 | Ramganj | 134 | 22:00 | 120 | 16:00
Dhamrai | 136 | 00:00 | 132 | 14:00 | Rampur | 135 | 06:00 | 128 | 15:00
Dhanmondi | 139 | 06:00 | 131.6 | 13:00 | Rampura | 138 | 06:00 | 131 | 13:00
Dohazari | 139 | 07:00 | 125 | 00:00 | Rangamati | 136 | 06:00 | 130 | 13:00
Faridpur | 137 | 00:00 | 132 | 12:00 | Rangpur | 135 | 20:00 | 120 | 12:00
Fatullah | 141 | 06:00 | 135 | 12:00 | Ruppur | 142 | 05:00 | 136 | 18:00
Fenchuganj | 141 | 00:00 | 138 | 04:00 | Saidpur | 136 | 19:30 | 119 | 09:00
Feni | 133 | 19:30 | 125 | 14:00 | Satkhira | 140 | 06:00 | 129 | 13:00
Ghatail | 134 | 00:00 | 126 | 07:00 | Satmasjid | 139 | 06:00 | 133 | 13:00
Ghorashal | 144 | 01:00 | 139 | 13:00 | Savar | 139 | 09:00 | 131 | 13:00
Goalpara | 141 | 06:00 | 131 | 18:30 | SevenRings | 145 | 00:00 | 139 | 13:00
Gollamari | 142 | 06:00 | 132 | 13:00 | ShahCement | 140 | 03:00 | 134 | 12:00
Gopalganj | 139 | 05:00 | 132 | 13:00 | Shahjadpur | 142 | 00:00 | 136 | 12:00
Gopalganj-400 | 140 | 06:00 | 134 | 13:00 | Shahjibazar | 141 | 00:00 | 137 | 16:00
Gulshan | 136 | 00:00 | 130 | 13:00 | Shahmirpur | 135 | 18:00 | 130 | 12:00
Halishahar | 136 | 18:00 | 130 | 10:00 | Shariatpur | 139 | 06:00 | 132 | 13:00
Haripur | 136 | 00:00 | 133 | 13:00 | Sherpur | 125 | 16:00 | 114 | 07:00
HaripurSBU | 137 | 05:00 | 123 | 18:30 | Shikalbaha | 124 | 06:00 | 117 | 01:00
Hasnabad | 141 | 01:00 | 135 | 13:00 | Shikalbaha-230 | 136 | 08:00 | 130 | 11:00
Hathazari | 137 | 19:30 | 133 | 12:00 | Shitalakhya | 140 | 06:00 | 134 | 13:00
Ishurdi | 142 | 00:00 | 137 | 12:00 | Sholosohor | 136 | 06:00 | 131 | 12:00
Jaldhaka | 134 | 19:30 | 116 | 12:00 | Shyampur | 140 | 01:00 | 135 | 13:00
Jamalpur | 131 | 10:00 | 119 | 07:00 | Shyampur-230 | 141 | 06:00 | 134 | 13:00
Jashore | 139 | 03:00 | 129 | 13:00 | Siddhirganj | 139 | 06:00 | 133 | 12:00
Jhenaidah | 141 | 01:00 | 132 | 13:00 | Sirajganj | 138 | 03:00 | 129 | 12:00
Jhenaidah-230 | 142 | 05:00 | 133 | 13:00 | Sonargaon | 138 | 04:00 | 131 | 13:00
Joydebpur | 142 | 05:00 | 134 | 13:00 | Sreemongol | 140 | 00:00 | 136 | 13:00
Joypurhat | 135 | 00:00 | 122 | 13:00 | Sreepur | 132 | 00:00 | 124 | 13:00
Juldah | 136 | 05:00 | 130 | 11:00 | Srinagar | 142 | 06:00 | 135 | 13:00
Kabirpur | 143 | 00:00 | 132 | 13:00 | SSM | 140 | 08:00 | 133 | 14:00
Kachua | 137 | 22:00 | 124 | 15:00 | Sunamganj | 136 | 00:00 | 129 | 18:00
Kaliakoir | 145 | 10:00 | 133 | 13:00 | Sylhet | 137 | 00:00 | 133 | 18:00
Kallyanpur | 135 | 00:00 | 130 | 13:00 | Sylhet-132 | 139 | 06:00 | 135 | 11:00
Kalurghat | 135 | 18:00 | 131 | 13:00 | Tangail | 135 | 03:00 | 128 | 07:00
Kamrangirchar | 142 | 06:00 | 129 | 13:00 | Thakurgaon | 141 | 19:30 | 115 | 09:00
Kaptai | 137 | 4:00 | 124 | 12:00 | TK | 136 | 05:00 | 131 | 12:00
Kazla | 137 | 01:00 | 132 | 14:00 | Tongi | 139 | 00:00 | 135 | 12:00
Keranigonj | 141 | 06:00 | 135 | 13:00 | Ullahpara | 141 | 02:00 | 124 | 05:00
Khagrachori | 136 | 06:00 | 129 | 13:00 | Ullon | 137 | 06:00 | 131 | 14:00
Khulna | 138 | 00:00 | 131 | 13:00 | Uttara | 138 | 06:00 | 130 | 13:00
Khulna(S) | 142 | 06:00 | 133 | 13:00 | UttaraNew | 141 | 06:00 | 133 | 13:00
Khulshi | 135 | 06:00 | 129 | 11:00 | Zigatola | 141 | 00:00 | 135 | 13:00
Kishoreganj | 135 | 00:00 | 127 | 13:00
Kodda | 140 | 00:00 | 132 | 12:00
KSRM | 136 | 06:00 | 131 | 14:00
Kulaura | 140 | 00:00 | 137 | 12:00
Kurigram | 135 | 19:30 | 118 | 09:00
Kushtia | 141 | 01:00 | 135 | 13:00
Lalbag | 142 | 06:00 | 135 | 13:00
Lalmonirhat | 131 | 19:30 | 120 | 15:00
Madanganj | 138 | 05:00 | 132 | 13:00
Madaripur | 137 | 04:00 | 133 | 18:30
Madartek | 138 | 06:00 | 131 | 13:00
Madunaghat | 136 | 07:00 | 131 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-02-2025 | [28 empty] | Date: | 15-02-2025 | [28 empty] | Date: | 15-02-2025 | [28 empty] | Date: | 15-02-2025 | [28 empty] | Date: | 15-02-2025 | [19 empty] | Date: | 15-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [19 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 250 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 575 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 440 | 0 | 51 | 0 | 199 | 0 | 0 | 360 | 29 | 182 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 275 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 18 | 75 | 0 | 0 | 0 | 4623 | 924 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 161 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 220 | 0 | 0 | 450 | 0 | 3523.22 | 8146.22 | 90.44
01:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 360 | 293 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 457 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 128 | 0 | 0 | 360 | 29 | 182 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 31 | 30 | 0 | 10 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 4313 | 738 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 158 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 220 | 0 | 0 | 440 | 0 | 3219.54 | 7532.54 | 90.43
02:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 360 | 302 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 372 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 340 | 0 | 5 | 0 | 78 | 0 | 0 | 360 | 20 | 197 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 290 | 320 | 0 | 5 | 30 | 0 | 2 | 120 | 22 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 4011 | 736 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 156 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 220 | 0 | 0 | 440 | 0 | 3137.86 | 7148.86 | 90.43
03:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 320 | 269 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 373 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 303 | 0 | 5 | 0 | 78 | 0 | 0 | 360 | 5 | 182 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 300 | 320 | 0 | 5 | 30 | 0 | 2 | 120 | 22 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 3891 | 736 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 154 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 440 | 0 | 3097.5 | 6988.5 | 90.42
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 320 | 291 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 374 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 78 | 0 | 0 | 300 | 5 | 195 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 305 | 320 | 0 | 5 | 30 | 0 | 2 | 120 | 22 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 3814 | 736 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 154 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 440 | 0 | 3138.5 | 6952.5 | 90.42
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 320 | 298 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 374 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 303 | 0 | 5 | 0 | 78 | 0 | 0 | 300 | 5 | 182 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 315 | 320 | 0 | 5 | 30 | 0 | 2 | 140 | 22 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 3850 | 642 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 2.5 | 154 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 440 | 0 | 3070.62 | 6920.62 | 90.41
06:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 320 | 264 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 370 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 303 | 0 | 5 | 0 | 78 | 0 | 0 | 300 | 5 | 182 | 33 | 0 | 0 | 0 | 0 | 16 | 0 | 38 | 0 | 0 | 0 | 285 | 320 | 0 | 5 | 30 | 0 | 2 | 140 | 22 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 5 | 108 | 0 | 0 | 0 | 3785 | 735 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 155 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 440 | 0 | 3150.57 | 6935.57 | 90.41
07:00 | 0 | 1 | 0 | 0 | 0 | 230 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 300 | 300 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 1 | 0 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 452 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 303 | 0 | 8 | 0 | 125 | 0 | 0 | 330 | 5 | 202 | 33 | 0 | 0 | 0 | 0 | 16 | 0 | 38 | 0 | 4 | 0 | 300 | 320 | 0 | 5 | 30 | 0 | 2 | 140 | 22 | 0 | 41 | 20 | 0 | 0 | 0 | 0 | 3 | 9 | 118 | 0 | 1.53 | 0 | 4055.53 | 735 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 420.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.87 | 184 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.16 | 2.5 | 154 | 72 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 0.02 | 0 | 200 | 5 | 100 | 220 | 0 | 0 | 440 | 0 | 3225.52 | 7281.05 | 90.4
08:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 300 | 290 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 12 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 42 | 452 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 182 | 0 | 0 | 360 | 14 | 182 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 42 | 0 | 23 | 0 | 300 | 320 | 0 | 5 | 30 | 0 | 2 | 140 | 22 | 0 | 41 | 20 | 0 | 0 | 0 | 0 | 57 | 9 | 126 | 1 | 13.95 | 3 | 4435.95 | 879 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.28 | 0 | 0 | 569.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 17.08 | 192 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 1.43 | 2.5 | 155 | 70 | 0 | 6 | 0 | 0 | 0 | 0.8 | 46 | 0.01 | 0 | 200 | 4 | 100 | 220 | 0 | 0 | 475 | 0 | 3674.5 | 8110.45 | 90.4
09:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 225 | 300 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 452 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 172 | 0 | 0 | 360 | 28 | 194 | 33 | 0 | 0 | 0 | 0 | 5 | 0 | 44 | 0 | 43 | 0 | 300 | 320 | 0 | 5 | 30 | 0 | 2 | 140 | 22 | 0 | 41 | 20 | 0 | 0 | 0 | 0 | 57 | 9 | 134 | 1 | 28.16 | 6 | 4417.16 | 879 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.32 | 0 | 0 | 562.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 34.49 | 201 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 2.95 | 2.5 | 157 | 70 | 0 | 16 | 0 | 0 | 0 | 2.6 | 98 | 0.03 | 0 | 200 | 3 | 100 | 220 | 0 | 0 | 500 | 0 | 3878.56 | 8295.72 | 90.39
10:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 225 | 288 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 24 | 0 | 12 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 42 | 453 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 400 | 0 | 40 | 0 | 177 | 0 | 0 | 270 | 29 | 183 | 32 | 0 | 0 | 0 | 0 | 13 | 0 | 48 | 0 | 58 | 0 | 290 | 320 | 0 | 5 | 30 | 0 | 2 | 140 | 23 | 0 | 41 | 20 | 0 | 0 | 0 | 0 | 57 | 9 | 135 | 2 | 38.77 | 6 | 4403.77 | 924 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.72 | 0 | 0 | 477.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 46.93 | 200 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 4.18 | 2.5 | 160 | 70 | 0 | 24 | 0 | 0 | 0 | 4.3 | 141 | 0.47 | 0 | 200 | 3 | 100 | 220 | 0 | 0 | 400 | 0 | 3835.62 | 8239.39 | 90.39
11:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 225 | 292 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29 | 0 | 12 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 42 | 506 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 400 | 17 | 40 | 0 | 177 | 0 | 0 | 275 | 29 | 189 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 50 | 0 | 66 | 0 | 300 | 320 | 0 | 10 | 29 | 0 | 2 | 163 | 23 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 134 | 2 | 44.48 | 6 | 4614.48 | 924 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.65 | 0 | 0 | 463.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 54.44 | 203 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 5.06 | 2.5 | 167 | 70 | 0 | 25 | 0 | 0 | 0 | 5.2 | 170 | 0.55 | 0 | 200 | 3 | 130 | 220 | 0 | 0 | 400 | 0 | 3936.36 | 8550.84 | 90.38
12:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 225 | 285 | 0 | 0 | 0 | 32.5 | 0 | 0 | 0 | 30 | 0 | 12 | 15 | 0 | 83 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 34 | 576 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 540 | 16 | 40 | 0 | 175 | 0 | 0 | 300 | 29 | 183 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 54 | 0 | 68 | 0 | 305 | 320 | 0 | 25 | 29 | 0 | 2 | 163 | 24 | 0 | 84 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 139 | 2 | 47.23 | 6 | 4901.73 | 924 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.71 | 0 | 0 | 600.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 60.09 | 214 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 5.15 | 2.5 | 0 | 70 | 0 | 25 | 0 | 0 | 0 | 6 | 183 | 0.59 | 0 | 280 | 4 | 130 | 220 | 0 | 0 | 440 | 12 | 4155.29 | 9057.02 | 90.38
13:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 225 | 290 | 0 | 0 | 17 | 32 | 0 | 38 | 0 | 29 | 0 | 12 | 22 | 0 | 100 | 12 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 28 | 575 | 0 | 0 | 6 | 0 | 10 | 223 | 0 | 0 | 0 | 612 | 18 | 43 | 0 | 182 | 0 | 0 | 305 | 29 | 183 | 33 | 14 | 0 | 12 | 5 | 17 | 0 | 56 | 0 | 66 | 0 | 290 | 320 | 0 | 28 | 29 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 140 | 2 | 47.72 | 6 | 5173.72 | 924 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.25 | 0 | 0 | 757.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 58.79 | 214 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 5.16 | 2.5 | 0 | 70 | 30 | 25 | 30 | 0 | 0 | 6.1 | 157 | 0.59 | 0 | 307 | 3 | 130 | 180 | 0 | 0 | 545 | 17 | 4440.77 | 9614.49 | 90.37
14:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 225 | 280 | 0 | 0 | 17 | 32 | 0 | 38 | 0 | 26 | 0 | 12 | 22 | 0 | 110 | 17 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 28 | 577 | 0 | 0 | 17 | 0 | 17 | 223 | 0 | 0 | 0 | 612 | 16 | 43 | 0 | 184 | 0 | 0 | 300 | 29 | 182 | 33 | 16 | 0 | 17 | 9 | 17 | 0 | 56 | 0 | 9 | 0 | 305 | 320 | 0 | 31 | 29 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 134 | 1 | 39.1 | 6 | 5149.1 | 923 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.15 | 0 | 0 | 755.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 50.36 | 214 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 4.54 | 2.5 | 0 | 70 | 35 | 22 | 35 | 0 | 0 | 5.2 | 159 | 0.48 | 0 | 307 | 4 | 130 | 180 | 0 | 0 | 555 | 17 | 4426.53 | 9575.63 | 90.37
15:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 256 | 0 | 0 | 0 | 32 | 0 | 39 | 0 | 21 | 0 | 12 | 22 | 0 | 129 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 28 | 577 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 612 | 13 | 43 | 0 | 184 | 0 | 0 | 275 | 29 | 182 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 280 | 320 | 0 | 35 | 29 | 0 | 2 | 120 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 35 | 9 | 133 | 2 | 30.04 | 6 | 4857.04 | 925 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.26 | 0 | 0 | 754.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 38.6 | 214 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 3.53 | 2.5 | 0 | 71 | 0 | 21 | 0 | 0 | 0 | 4 | 122 | 0.39 | 0 | 271 | 4 | 130 | 180 | 0 | 0 | 550 | 0 | 4132.06 | 8989.1 | 90.36
16:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 290 | 0 | 0 | 0 | 32 | 0 | 40 | 0 | 14 | 0 | 12.5 | 22 | 0 | 118 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 500 | 8 | 43 | 0 | 185 | 0 | 0 | 280 | 29 | 187 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 29 | 0 | 2 | 120 | 23 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 35 | 9 | 144 | 1 | 15.56 | 6 | 4770.06 | 925 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.45 | 0 | 0 | 700.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 23.01 | 214 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 2.19 | 2.5 | 0 | 70 | 0 | 11 | 0 | 0 | 0 | 1.7 | 65 | 0.23 | 0 | 200 | 3 | 130 | 180 | 0 | 0 | 500 | 0 | 3825.9 | 8595.96 | 90.36
17:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 225 | 265 | 0 | 0 | 5 | 32 | 0 | 0 | 0 | 5 | 0 | 12 | 22 | 0 | 118 | 1 | 15 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 3 | 0 | 40 | 0 | 33 | 575 | 12 | 0 | 2 | 0 | 1 | 223 | 0 | 0 | 0 | 555 | 2 | 51 | 1 | 185 | 0 | 0 | 300 | 29 | 183 | 33 | 1 | 0 | 1 | 1 | 17 | 0 | 52 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 29 | 0 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 18 | 0 | 1 | 35 | 9 | 147 | 0 | 4.56 | 6 | 4888.56 | 925 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.95 | 0 | 0 | 675.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 6.08 | 214 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0.47 | 2.5 | 0 | 70 | 32 | 3 | 10 | 0 | 0 | 0.6 | 18 | 0.08 | 0 | 250 | 5 | 130 | 180 | 0 | 0 | 510 | 30 | 3863.23 | 8751.79 | 90.35
18:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 20 | 0 | 0 | 17 | 32 | 0 | 15 | 25 | 100 | 14 | 0 | 225 | 253 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 17 | 10.5 | 22 | 0 | 115 | 33 | 30 | 0 | 0 | 10 | 0 | 30 | 0 | 25 | 38 | 0 | 40 | 18 | 34 | 575 | 51 | 0 | 18 | 0 | 30 | 222 | 0 | 0 | 0 | 612 | 0 | 51 | 32 | 197 | 0 | 0 | 300 | 29 | 182 | 33 | 35 | 0 | 26 | 21 | 17 | 0 | 56 | 0 | 0 | 0 | 275 | 320 | 0 | 35 | 29 | 0 | 2 | 163 | 0 | 0 | 85 | 30 | 0 | 18 | 0 | 20 | 58 | 9 | 148 | 0 | 0 | 6 | 5523.5 | 925 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 754.69 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 2.5 | 0 | 70 | 90 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 120 | 220 | 0 | 0 | 570 | 54 | 4258.19 | 9781.69 | 90.35
19:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 35 | 0 | 0 | 32 | 32 | 0 | 39 | 55 | 108 | 14 | 0 | 225 | 300 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 138 | 35 | 45 | 0 | 0 | 7 | 0 | 32 | 0 | 36 | 38 | 0 | 40 | 34 | 34 | 577 | 53 | 0 | 19 | 0 | 105 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 197 | 0 | 0 | 305 | 29 | 185 | 33 | 105 | 0 | 68 | 28 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 29 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 153 | 0 | 0 | 6 | 6019.5 | 878 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.89 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 5.5 | 0 | 70 | 95 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 54 | 4299.39 | 10318.89 | 90.34
19:30 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 40 | 55 | 108 | 14 | 0 | 225 | 300 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 137 | 35 | 0 | 0 | 0 | 6 | 0 | 32 | 0 | 0 | 0 | 0 | 40 | 34 | 34 | 578 | 0 | 0 | 19 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 197 | 0 | 0 | 310 | 29 | 186 | 33 | 115 | 0 | 68 | 28 | 17 | 0 | 56 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 59 | 9 | 153 | 0 | 0 | 6 | 5833 | 878 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752.39 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 5.5 | 0 | 70 | 95 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 54 | 4337.89 | 10170.89
20:00 | 0 | 17 | 0 | 0 | 0 | 230 | 20 | 0 | 401 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 108 | 14 | 0 | 225 | 300 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 159 | 35 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 34 | 577 | 0 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 197 | 0 | 0 | 320 | 29 | 190 | 33 | 115 | 0 | 68 | 28 | 17 | 0 | 58 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 35 | 9 | 170 | 0 | 0 | 6 | 5729.5 | 879 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.09 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 5.5 | 0 | 70 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 54 | 4348.59 | 10078.09 | 90.34
21:00 | 0 | 0 | 0 | 0 | 0 | 230 | 20 | 0 | 401 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 14 | 0 | 225 | 302 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 150 | 35 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 34 | 577 | 0 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 20 | 197 | 0 | 0 | 320 | 29 | 188 | 33 | 115 | 0 | 68 | 29 | 17 | 0 | 58 | 0 | 0 | 0 | 315 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 18 | 0 | 35 | 16 | 9 | 182 | 0 | 0 | 6 | 5672 | 925 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.19 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 5.5 | 0 | 70 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 54 | 4402.69 | 10074.69 | 90.33
22:00 | 0 | 0 | 0 | 0 | 0 | 230 | 30 | 0 | 401 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 225 | 286 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 158 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 578 | 0 | 0 | 19 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 305 | 29 | 182 | 33 | 96 | 0 | 68 | 29 | 17 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 5471 | 924 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 8 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 5.5 | 0 | 70 | 55 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 54 | 4259.62 | 9730.62 | 90.33
23:00 | 0 | 0 | 0 | 0 | 0 | 230 | 30 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 14 | 0 | 225 | 302 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 161 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 576 | 0 | 0 | 19 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 199 | 0 | 0 | 290 | 28 | 192 | 33 | 0 | 0 | 34 | 26 | 17 | 0 | 54 | 0 | 0 | 0 | 300 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 5208.5 | 925 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 5.5 | 0 | 71 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 54 | 4080.17 | 9288.67 | 90.32
Total KWH | 0 | 78720 | 0 | 0 | 0 | 3630844 | 126000 | 0 | 9525600 | 0 | 0 | 260280 | 0 | 0 | 75168 | 38880 | 0 | 85122 | 113997 | 620640 | 288720 | 0 | 6161000 | 6968582 | 0 | 0 | 264393 | 648200 | 0 | 204000 | 0 | 204919 | 12000 | 273600 | 417240 | 0 | 1486818.18 | 268473 | 90327 | 0 | 0 | 49920 | 0 | 70560 | 0 | 71040 | 70080 | 25680 | 959520 | 153054 | 949920 | 12036363.64 | 83636 | 0 | 158400 | 0 | 570399 | 5200432 | 0 | 0 | 0 | 11459999 | 92880 | 919550 | 240807 | 3813818 | 0 | 0 | 7550000 | 553440 | 4605000 | 793008 | 562560 | 0 | 424800 | 199080 | 397000 | 0 | 1166400 | 0 | 346673 | 0 | 7237500 | 7676500 | 0 | 553392 | 708000 | 0 | 57600 | 3635673 | 543408 | 0 | 1343040 | 614112 | 0 | 218000 | 0 | 155520 | 740400 | 153600 | 3000960 | 14000 | 309880 | 86880 | 112416007.82 | 20760727 | 8592192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578160 | 0 | 0 | 14689091 | 0 | 0 | 0 | 0 | 0 | 0 | 433664 | 0 | 0 | 44083 | 716850 | 0 | 393000 | 5117791 | 0 | 0 | 0 | 0 | 0 | 8557672 | 0 | 34920 | 72486 | 1878000 | 1645964 | 514749 | 163945 | 526204 | 0 | 0 | 35218.32 | 1162080 | 3393 | 0 | 5891000 | 132512 | 2763000 | 5095570 | 0 | 0 | 12481454.55 | 405600 | 92689325.87 | 205105333.69