## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-02-2025 | during | 17-02-2025 | during | 17-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | Unit-2 shut down for leak repairing
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 33 | 53.97 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 130 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 17 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 20.5 | 22.5 | 22.5 | 22.5 | 22.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 14 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 17 | 25 | 25 | 25 | 25 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 0 | 0 | line SD
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 45 | 109 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 70 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 72 | 162 | 162 | 17 | 17 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 17 | 54 | 17 | 54 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 584 | 584 | 584 | 600 | 600 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1724 | 2163.5 | 4565.87 | 4572.87 | 2504.62 | 2511.62
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 223 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 61 | 71 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 48 | 79 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 85 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 7 | 10 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.21 | 0 | 4.21 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 103 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 31 | 75 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 20 | 145 | 145 | 145 | 35 | 35 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 3 | 20 | 3 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 576 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1757 | 2356 | 2833.07 | 2868.86 | 2642.07 | 2677.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 305 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 29 | 32 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 195 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 103 | 139 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 2 | 31 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 40 | 163 | 163 | 45 | 45 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 155 | 174 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 70 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 27 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 115 | 115 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1300 | 1413 | 2105.53 | 2035.53 | 1700.2 | 1630.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-02-2025 | during | 17-02-2025 | during | 17-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 110 | 102 | 210 | 210 | 70 | 70 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 58 | 200 | 200 | 50 | 50 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.3 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 6 | 6 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 35 | 38 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 258.3 | 213 | 653.4 | 601.5 | 241.4 | 189.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 35 | 35 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 82 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 15 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 335 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1015 | 1001 | 1027 | 1027 | 998 | 998
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 873 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 408 | 385 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87.35 | 0 | 83 | 0 | 83 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234.2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1419.35 | 1258 | 3581.2 | 3498.2 | 1571 | 1488
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 600 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1283.59 | 1414 | 1556.12 | 1555.12 | 1553 | 1552
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 25 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 6 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 22 | 33 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 384 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 30 | 30 | 32 | 32 | 32 | 32 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 16 | 44 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 90 | 90 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 58 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.08 | 0 | 5.55 | 0 | 5.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 761 | 760 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.67 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1619.25 | 1649.5 | 2276.79 | 2116.24 | 1925.01 | 1764.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 70 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 68 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 173 | 0 | 165.15 | 0 | 165.15 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 442.8 | 272 | 532.75 | 332 | 532.75 | 332
System Total |  |  |  |  | 27884.66 | 27150.742 | 10819.29 | 11740 | 19131.73 | 18607.32 | 13668.05 | 13143.64
Forecast Scenario (17-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9300 |  | 0 |  | 9300
|  |  |  | 1:00 | 8600 |  | 0 |  | 8600
|  |  |  | 2:00 | 8180 |  | 0 |  | 8180
|  |  |  | 3:00 | 7900 |  | 0 |  | 7900
|  |  |  | 4:00 | 7750 |  | 0 |  | 7750
|  |  |  | 5:00 | 7530 |  | 0 |  | 7530
|  |  |  | 6:00 | 7990 |  | 0 |  | 7990
|  |  |  | 7:00 | 8990 |  | 0 |  | 8990
|  |  |  | 8:00 | 9880 |  | 0 |  | 9880
|  |  |  | 9:00 | 10850 |  | 0 |  | 10850
|  |  |  | 10:00 | 10800 |  | 0 |  | 10800
|  |  |  | 11:00 | 10850 |  | 0 |  | 10850
|  |  |  | 12:00 | 11300 |  | 0 |  | 11300
|  |  |  | 13:00 | 11800 |  | 0 |  | 11800
|  |  |  | 14:00 | 11300 |  | 0 |  | 11300
|  |  |  | 15:00 | 10620 |  | 0 |  | 10620
|  |  |  | 16:00 | 10010 |  | 0 |  | 10010
|  |  |  | 17:00 | 10000 |  | 0 |  | 10000
|  |  |  | 18:00 | 10820 |  | 0 |  | 10820
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11700 |  | 0 |  | 11700
|  |  |  | 19:30 | 11300 |  | 0 |  | 11300
|  |  |  | 20:00 | 11130 |  | 0 |  | 11130
|  |  |  | 21:00 | 10900 |  | 0 |  | 10900
|  |  |  | 22:00 | 10500 |  | 0 |  | 10500
|  |  |  | 23:00 | 9900 |  | 0 |  | 9900
Probable Maximum Temperature: |  |  | 31.50°C
Probable Maximum Demand at Day Peak: |  |  | 11300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 238.60 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:41 hrs on 17-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-02-2025 | [28 empty] | Date: | 16-02-2025 | [28 empty] | Date: | 16-02-2025 | [28 empty] | Date: | 16-02-2025 | [28 empty] | Date: | 16-02-2025 | [19 empty] | Date: | 16-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [19 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 200 | 40 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 294 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 576 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 575 | 0 | 51 | 0 | 199 | 0 | 0 | 275 | 29 | 182 | 33 | 0 | 0 | 0 | 9 | 17 | 0 | 52 | 0 | 0 | 0 | 280 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 4964.5 | 925 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 2.5 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3796.19 | 8760.69 | 90.32
01:00 | 0 | 0 | 0 | 0 | 0 | 160 | 60 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 294 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 577 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 199 | 0 | 0 | 275 | 29 | 182 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 23 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 4885.5 | 924 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 446.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 2.5 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 130 | 220 | 0 | 0 | 550 | 0 | 3431.46 | 8316.96 | 90.31
02:00 | 0 | 0 | 0 | 0 | 0 | 160 | 100 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 285 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 505 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 199 | 0 | 0 | 275 | 29 | 182 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 23 | 0 | 41 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 4696.5 | 925 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 2.5 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 0 | 500 | 0 | 3302.9 | 7999.4 | 90.31
03:00 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 285 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 506 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 199 | 0 | 0 | 290 | 29 | 193 | 33 | 0 | 0 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 23 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 4596.5 | 762 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 2.5 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 0 | 450 | 0 | 3099.65 | 7696.15 | 90.3
04:00 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 283 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 506 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 158 | 0 | 0 | 280 | 24 | 189 | 30 | 0 | 30 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 300 | 320 | 0 | 5 | 30 | 0 | 2 | 120 | 22 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 4496.5 | 736 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 2.5 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 0 | 400 | 0 | 3019.4 | 7515.9 | 90.3
05:00 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 282 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 504 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 158 | 0 | 0 | 275 | 5 | 184 | 30 | 0 | 40 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 305 | 320 | 0 | 5 | 30 | 0 | 2 | 120 | 22 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 4453.5 | 736 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 2.5 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 130 | 220 | 0 | 0 | 400 | 0 | 3021.86 | 7475.36 | 90.29
06:00 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 312 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 580 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 390 | 0 | 5 | 0 | 158 | 0 | 0 | 320 | 5 | 210 | 30 | 0 | 40 | 0 | 0 | 15 | 0 | 46 | 0 | 0 | 0 | 310 | 320 | 0 | 5 | 30 | 0 | 2 | 120 | 22 | 0 | 5 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 4706.5 | 736 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 2.5 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 6 | 130 | 220 | 0 | 0 | 400 | 0 | 3208.71 | 7915.21 | 90.29
07:00 | 0 | 1 | 0 | 0 | 0 | 160 | 110 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 225 | 295 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 1 | 0 | 14 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 574 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 535 | 2 | 9 | 0 | 195 | 0 | 0 | 310 | 5 | 203 | 30 | 0 | 45 | 0 | 0 | 17 | 0 | 48 | 0 | 4 | 0 | 325 | 320 | 0 | 12 | 30 | 0 | 2 | 120 | 22 | 0 | 42 | 30 | 0 | 18 | 0 | 0 | 3 | 2 | 192 | 0 | 1.93 | 0 | 5125.93 | 924 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.75 | 0 | 0 | 722.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.66 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.16 | 2.5 | 0 | 72 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0.03 | 0 | 307 | 6 | 132 | 220 | 0 | 0 | 440 | 0 | 3817.58 | 8943.51 | 90.28
08:00 | 0 | 17 | 0 | 0 | 0 | 160 | 110 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 27 | 32 | 0 | 0 | 1.5 | 23 | 17 | 0 | 225 | 288 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 9 | 0 | 11 | 22 | 0 | 500 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 3 | 13 | 576 | 0 | 0 | 9 | 0 | 20 | 226 | 0 | 0 | 0 | 612 | 8 | 43 | 17 | 195 | 0 | 0 | 375 | 21 | 182 | 30 | 0 | 45 | 14 | 1 | 17 | 0 | 60 | 0 | 21 | 0 | 295 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 9 | 56 | 171 | 1 | 13.09 | 0 | 5629.59 | 878 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.76 | 0 | 0 | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 27 | 0 | 14.05 | 180 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 1.2 | 2.5 | 0 | 70 | 70 | 6 | 35 | 0 | 0 | 1.2 | 38 | 0.14 | 0 | 307 | 5 | 132 | 180 | 0 | 0 | 600 | 90 | 4100.85 | 9730.44 | 90.28
09:00 | 0 | 35 | 0 | 0 | 0 | 160 | 110 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 0 | 0 | 17 | 35 | 17 | 0 | 225 | 308 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 17 | 0 | 18 | 14 | 0 | 500 | 35 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 3 | 40 | 17 | 9 | 576 | 0 | 0 | 20 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 13 | 43 | 50 | 197 | 0 | 0 | 345 | 28 | 203 | 30 | 0 | 45 | 51 | 9 | 17 | 0 | 64 | 0 | 41 | 0 | 320 | 320 | 0 | 36 | 30 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 0 | 0 | 9 | 56 | 158 | 1 | 25.94 | 0 | 6013.94 | 878 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.71 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 55 | 0 | 29.95 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.65 | 2.5 | 0 | 70 | 75 | 15 | 49 | 0 | 0 | 1.9 | 89 | 0.3 | 0 | 307 | 4 | 132 | 220 | 0 | 0 | 600 | 17 | 4295.01 | 10308.95 | 90.27
10:00 | 0 | 35 | 0 | 0 | 0 | 160 | 110 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 0 | 12 | 33.7 | 35 | 17 | 0 | 225 | 125 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 24 | 0 | 21 | 14 | 0 | 500 | 35 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 6 | 3 | 40 | 17 | 7 | 576 | 0 | 0 | 32 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 17 | 43 | 50 | 199 | 0 | 0 | 310 | 29 | 182 | 30 | 0 | 45 | 51 | 9 | 17 | 0 | 68 | 0 | 54 | 0 | 300 | 320 | 0 | 36 | 30 | 0 | 2 | 163 | 22 | 0 | 82 | 30 | 0 | 0 | 0 | 9 | 9 | 56 | 144 | 2 | 36.04 | 0 | 5844.74 | 878 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.93 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 75 | 0 | 44.4 | 214 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 3.58 | 2.5 | 0 | 70 | 94 | 22 | 53 | 0 | 0 | 4.4 | 132 | 0.47 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 600 | 0 | 4433.28 | 10278.02 | 90.27
11:00 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 34 | 32 | 0 | 30 | 35 | 54 | 17 | 0 | 225 | 50 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 28 | 0 | 21 | 14 | 0 | 500 | 35 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 12 | 4 | 40 | 17 | 7 | 576 | 0 | 0 | 33 | 0 | 51 | 224 | 0 | 0 | 0 | 612 | 19 | 43 | 58 | 197 | 0 | 0 | 320 | 29 | 189 | 29 | 0 | 40 | 60 | 9 | 17 | 0 | 70 | 0 | 62 | 0 | 285 | 320 | 0 | 36 | 30 | 0 | 2 | 120 | 15 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 138 | 2 | 44.35 | 0 | 5798.35 | 926 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.23 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16 | 91 | 26 | 52.79 | 214 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 4.8 | 2.5 | 0 | 70 | 95 | 28 | 49 | 0 | 0 | 5.3 | 162 | 0.57 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 600 | 0 | 4500.19 | 10298.54 | 90.27
12:00 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 45 | 32 | 0 | 35 | 35 | 54 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 29 | 0 | 20 | 14 | 0 | 500 | 35 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 12 | 38 | 4 | 40 | 31 | 7 | 576 | 20 | 0 | 33 | 0 | 61 | 220 | 0 | 0 | 0 | 612 | 20 | 43 | 103 | 195 | 0 | 0 | 340 | 29 | 200 | 29 | 0 | 40 | 155 | 9 | 17 | 0 | 74 | 0 | 64 | 2 | 335 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 15 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 110 | 2 | 46.3 | 0 | 6054.3 | 924 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.35 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 99 | 30 | 55.67 | 214 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.08 | 2.5 | 0 | 70 | 95 | 31 | 68 | 0 | 0 | 5.8 | 173 | 0.59 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 622 | 0 | 4764.99 | 10819.29 | 90.27
13:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 406 | 0 | 0 | 17 | 0 | 0 | 85 | 64 | 0 | 55 | 17 | 54 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 0 | 20 | 14 | 0 | 500 | 35 | 45 | 0 | 0 | 1 | 0 | 46 | 0 | 72 | 76 | 4 | 40 | 83 | 11 | 575 | 35 | 0 | 33 | 0 | 87 | 222 | 0 | 0 | 0 | 612 | 19 | 43 | 127 | 197 | 0 | 0 | 310 | 28 | 183 | 32 | 12 | 40 | 182 | 9 | 17 | 0 | 72 | 16 | 61 | 35 | 310 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 106 | 2 | 44.06 | 4 | 6430.06 | 921 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.71 | 0 | 0 | 762 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 25 | 22 | 8 | 98 | 30 | 54.58 | 214 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 5.14 | 2.5 | 0 | 70 | 95 | 31 | 100 | 0 | 0 | 5.7 | 163 | 0.6 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 0 | 4820.23 | 11250.29 | 90.26
14:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 80 | 64 | 0 | 55 | 17 | 54 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 25 | 0 | 20 | 14 | 0 | 400 | 35 | 15 | 9 | 0 | 12 | 0 | 45 | 0 | 36 | 100 | 3 | 80 | 101 | 8 | 577 | 35 | 0 | 33 | 0 | 96 | 222 | 0 | 0 | 0 | 612 | 17 | 43 | 120 | 195 | 0 | 0 | 305 | 29 | 192 | 32 | 17 | 40 | 189 | 9 | 17 | 0 | 74 | 16 | 54 | 38 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 57 | 103 | 2 | 36.42 | 6 | 6295.42 | 921 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.88 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 35 | 4 | 0 | 35 | 22 | 8 | 87 | 30 | 45.39 | 170 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 4.25 | 2.5 | 0 | 70 | 95 | 25 | 49 | 0 | 0 | 5.1 | 146 | 0.51 | 0 | 307 | 5 | 85 | 180 | 0 | 0 | 622 | 0 | 4463.63 | 10759.05 | 90.26
15:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 65 | 32 | 0 | 55 | 17 | 54 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 18 | 0 | 19.5 | 22 | 0 | 530 | 35 | 15 | 12 | 0 | 8 | 0 | 48 | 0 | 36 | 100 | 2 | 40 | 110 | 3 | 578 | 35 | 0 | 33 | 0 | 105 | 222 | 0 | 0 | 0 | 612 | 14 | 43 | 122 | 192 | 0 | 0 | 305 | 29 | 184 | 31 | 17 | 40 | 200 | 9 | 17 | 0 | 74 | 0 | 0 | 47 | 300 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 57 | 102 | 1 | 26.56 | 6 | 6287.06 | 920 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.19 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 25 | 8 | 67 | 30 | 33.64 | 170 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 3.08 | 2.5 | 0 | 70 | 95 | 20 | 34 | 0 | 0 | 2.2 | 108 | 0.39 | 0 | 307 | 5 | 100 | 180 | 0 | 0 | 622 | 0 | 4336 | 10623.06 | 90.26
16:00 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 4 | 0 | 50 | 16 | 0 | 30 | 17 | 54 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 11 | 10 | 19.5 | 22 | 0 | 584 | 35 | 15 | 12 | 0 | 9 | 0 | 69 | 0 | 12 | 50 | 1 | 40 | 68 | 3 | 577 | 17 | 0 | 40 | 0 | 105 | 223 | 0 | 0 | 0 | 612 | 9 | 51 | 80 | 192 | 0 | 0 | 320 | 29 | 195 | 28 | 17 | 40 | 200 | 9 | 17 | 0 | 72 | 0 | 0 | 47 | 305 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 57 | 102 | 1 | 14.36 | 6 | 6143.86 | 920 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.21 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 21 | 8 | 39 | 30 | 19.73 | 170 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 1.81 | 2.5 | 0 | 70 | 95 | 11 | 34 | 0 | 0 | 2 | 63 | 0.23 | 0 | 307 | 4 | 100 | 180 | 0 | 0 | 620 | 24 | 4256.48 | 10400.34 | 90.25
17:00 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 53 | 0 | 50 | 16 | 0 | 30 | 17 | 54 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 4 | 17 | 20 | 22 | 0 | 584 | 35 | 15 | 12 | 0 | 0 | 0 | 74 | 0 | 12 | 12 | 0 | 40 | 51 | 6 | 578 | 17 | 0 | 19 | 0 | 51 | 223 | 0 | 0 | 0 | 612 | 3 | 51 | 80 | 192 | 0 | 0 | 310 | 29 | 184 | 31 | 31 | 40 | 136 | 9 | 17 | 0 | 68 | 0 | 0 | 47 | 300 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 102 | 0 | 4.18 | 6 | 5969.18 | 920 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.24 | 0 | 0 | 760 | 0 | 0 | 32 | 0 | 0 | 4 | 90 | 0 | 21 | 8 | 12 | 30 | 5.34 | 170 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 2.5 | 0 | 70 | 55 | 3 | 34 | 0 | 0 | 0.8 | 19 | 0.08 | 0 | 307 | 4 | 100 | 220 | 0 | 0 | 600 | 150 | 4289.96 | 10259.14 | 90.25
18:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 396 | 0 | 0 | 17 | 54 | 0 | 58 | 98 | 0 | 34 | 0 | 72 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 500 | 35 | 15 | 17 | 0 | 4 | 51 | 77 | 0 | 48 | 100 | 0 | 40 | 51 | 11 | 576 | 53 | 0 | 20 | 4 | 51 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 95 | 195 | 0 | 0 | 320 | 29 | 196 | 31 | 63 | 40 | 136 | 18 | 17 | 0 | 74 | 16 | 0 | 47 | 305 | 320 | 0 | 35 | 30 | 0 | 2 | 120 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 58 | 102 | 0 | 0 | 6 | 6356.5 | 921 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 758 | 0 | 0 | 25 | 0 | 10 | 5 | 90 | 0 | 28 | 16 | 0 | 30 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 2.5 | 0 | 71 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 130 | 220 | 0 | 0 | 600 | 150 | 4408.5 | 10765 | 90.25
19:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 33 | 54 | 0 | 109 | 130 | 0 | 55 | 35 | 72 | 17 | 0 | 225 | 0 | 0 | 0 | 55 | 32 | 0 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 584 | 35 | 103 | 45 | 0 | 0 | 85 | 79 | 0 | 100 | 100 | 0 | 40 | 75 | 10 | 576 | 145 | 0 | 40 | 17 | 71 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 139 | 185 | 0 | 0 | 305 | 29 | 182 | 32 | 115 | 40 | 174 | 27 | 17 | 0 | 70 | 16 | 0 | 31 | 315 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 38 | 9 | 58 | 102 | 0 | 0 | 6 | 7146.5 | 873 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 25 | 0 | 58 | 6 | 90 | 0 | 33 | 44 | 0 | 30 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 5.5 | 0 | 70 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 600 | 150 | 4593.5 | 11740 | 90.24
19:30 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 80 | 133 | 0 | 15 | 35 | 72 | 17 | 0 | 225 | 0 | 0 | 0 | 55 | 32 | 0 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 584 | 35 | 100 | 12 | 0 | 0 | 85 | 79 | 0 | 50 | 50 | 0 | 40 | 85 | 10 | 575 | 145 | 0 | 40 | 25 | 51 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 185 | 0 | 0 | 305 | 29 | 182 | 32 | 115 | 40 | 100 | 29 | 17 | 0 | 68 | 0 | 0 | 31 | 260 | 312 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 82 | 30 | 0 | 0 | 0 | 54.5 | 19 | 58 | 103 | 0 | 0 | 6 | 6727.5 | 872 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 25 | 0 | 95 | 6 | 50 | 0 | 33 | 52 | 0 | 30 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 5.5 | 0 | 70 | 74 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 610 | 150 | 4552.5 | 11280 | 90.24
20:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 87 | 82 | 0 | 15 | 35 | 72 | 17 | 0 | 225 | 0 | 0 | 0 | 55 | 32 | 0 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 607 | 35 | 100 | 19 | 0 | 0 | 85 | 79 | 0 | 50 | 50 | 0 | 40 | 51 | 18 | 576 | 145 | 0 | 40 | 25 | 51 | 223 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 195 | 0 | 0 | 315 | 29 | 191 | 33 | 68 | 40 | 100 | 28 | 17 | 0 | 68 | 0 | 0 | 32 | 280 | 320 | 0 | 32 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 54.5 | 9 | 58 | 102 | 0 | 0 | 6 | 6688.5 | 873 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 25 | 0 | 110 | 6 | 50 | 0 | 35 | 52 | 0 | 30 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 5.5 | 0 | 70 | 74 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 150 | 4502.5 | 11191 | 90.24
21:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 35 | 54 | 0 | 78 | 32 | 0 | 0 | 0 | 72 | 17 | 0 | 225 | 0 | 0 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 591 | 35 | 100 | 12 | 0 | 0 | 83 | 79 | 0 | 50 | 50 | 0 | 40 | 51 | 9 | 576 | 145 | 0 | 40 | 25 | 51 | 228 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 195 | 0 | 0 | 320 | 29 | 192 | 33 | 68 | 40 | 100 | 29 | 17 | 0 | 66 | 0 | 0 | 32 | 310 | 320 | 0 | 32 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 102 | 0 | 0 | 6 | 6496 | 919 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.18 | 0 | 0 | 25 | 0 | 113 | 12 | 50 | 0 | 33 | 52 | 0 | 30 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 2.5 | 0 | 70 | 74 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 622 | 150 | 4550.68 | 11046.68 | 90.24
22:00 | 0 | 70 | 0 | 0 | 0 | 238 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 78 | 32 | 0 | 0 | 0 | 35 | 17 | 0 | 225 | 0 | 0 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 592 | 35 | 100 | 10 | 0 | 0 | 84 | 79 | 0 | 50 | 50 | 0 | 40 | 51 | 23 | 577 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 195 | 0 | 0 | 270 | 29 | 182 | 33 | 68 | 40 | 100 | 29 | 17 | 0 | 62 | 0 | 0 | 31 | 300 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 70 | 0 | 0 | 6 | 6146 | 919 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.78 | 0 | 0 | 25 | 0 | 113 | 13 | 50 | 0 | 33 | 52 | 0 | 30 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 2.5 | 0 | 70 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 150 | 4411.28 | 10557.28 | 90.24
23:00 | 0 | 70 | 0 | 0 | 0 | 218 | 0 | 0 | 400 | 0 | 0 | 0 | 54 | 0 | 78 | 16 | 0 | 0 | 0 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 592 | 35 | 100 | 0 | 0 | 0 | 84 | 79 | 0 | 50 | 50 | 0 | 40 | 51 | 29 | 363 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 195 | 0 | 0 | 270 | 29 | 184 | 33 | 0 | 40 | 100 | 29 | 17 | 0 | 60 | 0 | 0 | 32 | 290 | 320 | 0 | 35 | 30 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 74 | 0 | 0 | 6 | 5748 | 924 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 113 | 14 | 50 | 0 | 32 | 52 | 0 | 30 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 2.5 | 0 | 70 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 560 | 150 | 4328.5 | 10076.5 | 90.23
Total KWH | 0 | 858240 | 0 | 0 | 0 | 4797031 | 1023750 | 0 | 9583200 | 0 | 0 | 260280 | 438840 | 0 | 1076832 | 708960 | 0 | 430387 | 268385 | 809280 | 387720 | 0 | 5306500 | 3018269 | 0 | 0 | 265013 | 786000 | 0 | 0 | 0 | 192875 | 73200 | 423600 | 480600 | 0 | 11354090.91 | 593400 | 720109 | 151680 | 0 | 30720 | 480631 | 927321 | 0 | 572160 | 759360 | 26641 | 961500 | 1004470 | 504480 | 13163636.36 | 622255 | 0 | 468960 | 95234.4 | 1126581 | 5331269 | 0 | 0 | 0 | 13101817 | 138510 | 977718 | 1391330 | 4549818 | 0 | 0 | 7486000 | 610080 | 4677000 | 744480 | 571200 | 752970 | 2170080 | 283080 | 401660 | 0 | 1453440 | 57202 | 342282 | 424752 | 7373500 | 7749300 | 0 | 730584 | 716000 | 0 | 54864 | 3558518 | 536904 | 0 | 1606080 | 718656 | 0 | 180000 | 0 | 411120 | 164400 | 952800 | 3167040 | 13050 | 293090 | 71760 | 138514545.67 | 21280000 | 8758656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545760 | 0 | 0 | 16330909 | 0 | 0 | 156680 | 0 | 782112 | 80428 | 566560 | 79488 | 260673 | 395525 | 668040 | 317108 | 359252 | 4679455 | 0 | 0 | 0 | 0 | 0 | 8594472 | 0 | 30000 | 68706 | 0 | 1585745 | 1271809 | 194654 | 920793 | 0 | 0 | 35471.16 | 1101600 | 3849 | 0 | 6545000 | 141055 | 2933000 | 5234300 | 0 | 0 | 13661090.91 | 1334400 | 98916591.07 | 237431136.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10819.29 | MW | 12:00 Hr. | Energy Generated |  |  | 237.4311 |  | MKWHr.
| Day Peak Demand |  |  | 10878.29 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.241 |  | MKWHr.
| Evening Peak Generation |  |  | 11740 | MW | 19:00 Hr. | Energy Demand |  |  | 237.6721 |  | MKWHr.
| Evening Peak Demand |  |  | 11740 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 7475.36 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 873.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 11740 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.3013 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.1608 | 0 | 5.1894 | 0 | 0 | 0.19287 | 0 | 0 | 42.5431 | Gas | 119.9973 | Gas | 429967603.3947
| Chattogram Zone |  |  | 5.8357 | 26.2655 | 7.5222 | 0 | 0.9615 | 0.16515 | 0 | 0.03072 | 40.7807 | Coal | 48.0573 | Coal | 333062837.1726
| Cumilla Zone |  |  | 20.1997 | 0 | 4.8976 | 0 | 0 | 0.34228 | 1.4534 | 0 | 26.8931 | HFO | 25.3749 | HFO | 468918578.528
| Mymensingh Zone |  |  | 3.167 | 0 | 1.6001 | 0 | 0 | 0.30614 | 0 | 0 | 5.0733 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.2244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2244 | Hydro | 0.9615 | Hydro | 96150
| Khulna Zone |  |  | 8.7587 | 0 | 0 | 0 | 0 | 0.54576 | 21.28 | 0 | 30.5844 | Solar | 3.9451 | Solar | 64496092.4376
| Barishal Zone |  |  | 8.3084 | 20.2061 | 1.3344 | 0 | 0 | 0.003849 | 0 | 0 | 29.8527 | Import | 39.0643 | Import | 199129179.51
| Rajshahi Zone |  |  | 13.3426 | 0 | 2.6386 | 0 | 0 | 1.0573 | 16.3309 | 0 | 33.3694 | Wind | 0.03072 | Wind | 449740.8
| Rangpur Zone |  |  | 0 | 1.5857 | 2.1926 | 0 | 0 | 1.3317 | 0 | 0 | 5.1101
| Total |  |  | 119.9973 | 48.0573 | 25.3749 | 0 | 0.9615 | 3.9451 | 39.0643 | 0.03072 | 237.4311
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 429967603.3947 |  | Hydro | 96150
|  |  |  | Coal | 333062837.1726 |  | Solar | 64496092.4376
|  |  |  | HFO | 468918578.528 |  | Import | 199129179.51
|  |  |  | HSD | 0 |  | Wind | 449740.8
[5 empty] | Total: | 149,61,20,181 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.28 | Peak Hr Flow | 873.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9004545.527 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.3309 | Peak Hr Flow | 760.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 512 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4534 | Peak Hr Flow | 70.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 770 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.0643 | Peak Hr Flow | 1703.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4154
|  |  |  | Chattogram |  | 0 |  | 1188
|  |  |  | Cumilla |  | 0 |  | 957
|  |  |  | Mymensingh |  | 0 |  | 1010
|  |  |  | Sylhet |  | 0 |  | 399
|  |  |  | Khulna |  | 0 |  | 1294
|  |  |  | Barishal |  | 0 |  | 314
|  |  |  | Rajshahi |  | 0 |  | 1125
|  |  |  | Rangpur |  | 0 |  | 786
|  |  |  | Total |  | 0 |  | 11227
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 225MW CCPP Unit-3 GT |  |  | 141
|  | 7 | Sirajgonj 225MW CCPP Unit-3 ST |  |  | 79
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1012 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1678.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:16 | 16:37 | Bibiyana-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
|  | 08:20 | Bogura 132/33kV S/S Transformer-4 LT is restored.
|  | 08:20 | Bogura 132/33kV S/S Transformer-4 HT is restored.
| 08:24 | 16:51 | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ghorashal 230kV end Due to Insulator
disk cleaning work requsition by Dhamrai 132/33kV S/S. and from Ishurdi 230/132kVend.
| 08:33 | 15:40 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
Maintenance work
| 08:38 | 15:39 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-02 Scheduled S/D Due to yearly
maintenance.
| 09:00 | 13:27 | Agrabad 132/33kV S/S MTR-01 (406T) HT Scheduled S/D Due to Relay Test by SPMD,Ctg
| 09:01 | 15:08 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 Project Work S/D
| 09:06 | 17:16 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance and from Bibiana 400/230kV end Due to For AM
| 09:27 |  | GPH 230/33kV S/S BSRM CKT-1 Scheduled S/D Due to annual maintenance
| 09:36 | 16:48 | BSRM 230/33kV S/S AKSML Ckt Scheduled S/D Due to Annual Line Maintenance
| 09:37 | 19:53 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Interlock update work
| 09:38 | 19:52 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Interlock update work.
|  | 09:40 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt is restored.
| 09:55 | 15:09 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-02 Scheduled S/D Due to yearly
maintenance.
| 10:03 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
| 10:03 |  | Meghnaghat CCPP(Summit) GT-1 Shutdown with remarks:- NLDC asked for CCPP Shutdown.
| 10:05 |  | Meghnaghat CCPP(Summit) GT-1 Ready with remarks:- None
| 10:28 | 11:10 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 10:29 | 11:09 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 10:40 | 12:13 | Bheramara P/S-Ishurdi 132 kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end Due to G to
G project work and from Bheramara 230/132kV end Due to Project work
| 10:50 | 11:29 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 10:58 |  | Meghnaghat CCPP(Summit) ST Shutdown with remarks:- NLDC asked for CCPP Shutdown.
| 10:58 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- ST
| 10:59 |  | Meghnaghat CCPP(Summit) ST Ready with remarks:- None
| 11:09 |  | Meghnaghat CCPP(Summit) GT-2 Shutdown with remarks:- NLDC asked for CCPP Shutdown.
| 11:09 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
| 11:10 | 11:53 | Tangail 132/33kV S/S Tr-2 LT Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 11:11 | 11:52 | Tangail 132/33kV S/S Tr-2 HT Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 11:11 |  | Meghnaghat CCPP(Summit) GT-2 Ready with remarks:- None
| 11:15 | 18:56 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to for dead line
checking and from Sylhet 132/33kV end Due to dead line checking of chhatak end
| 11:15 | 16:03 | Aminbazar-Manikgonj PP 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Relay test
| 11:31 | 12:16 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 11:44 | 16:46 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to Colour work
| 11:44 | 16:48 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to Colour work
| 11:50 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:- NLDC asked for CCPP shutdown.
| 12:19 | 13:28 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 12:20 | 13:27 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 12:24 | 13:25 | Mymensingh RPCL-Tangail 132kV Ckt-1 Forced S/D from Ghatail 132/33kV end Due to As per
direction of NLDC(Reporting)
| 12:25 | 13:24 | Tangail 132/33kV S/S RPCL-1 Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 13:41 | 14:04 | Tangail 132/33kV S/S RPCL-2 Scheduled S/D Due to Realy Setting (SPMD) | [7 empty] | 25.0MW load
interrup.
| 13:42 | 14:05 | Mymensingh RPCL-Tangail 132kV Ckt-2 Forced S/D from Ghatail 132/33kV end Due to As per
direction of NLDC
| 14:15 | 18:25 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Mirsorai 230/33kV end Due to
Annual Maintenance
| 16:14 | 17:24 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
SPMD work
|  | 16:27 | Ishurdi-Pabna 132kV ckt is restored.
|  | 18:01 | Bogura 132/33kV S/S Transformer-3 HT is restored.
|  | 18:03 | Bogura 132/33kV S/S Transformer-3 LT is restored.
| 19:00 |  | Evening Peak Gen. 11740 MW
| 21:30 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:- At 19:27
| 05:00 |  | Minimum Generation: 8061 MW.
| 07:02 |  | Amtoli-RNPL Ckt-1 S/D.
| 07:13 |  | Bogura 132/33kV S/S Transformer-4 LT Project Work S/D Due to 33 kv bus upgrading work.
| 07:14 |  | Bogura 132/33kV S/S Transformer-4 HT Project Work S/D Due to 33 KV Bus Upgrading Work.
| 07:49 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ghorashal 230kV end Due to Insulator
Disc cleaning and from Ishurdi 230/132kV end Due to dhamrai disc cleaning work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 4797031 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 1023750 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9583200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5306500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 3018269 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 430387 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33 | 260280 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 130 | 708960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 268385 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 265013 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 423600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 480600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 387720 | Unschedule maintenance
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 786000 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 109 | 1076832 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 858240 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 809280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 192875 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 438840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 584 | 11354090.91 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 73200 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2163.5 | 42543052.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 95234.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138510 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 468960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 961500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5331269 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 71 | 1126581 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 79 | 927321 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 480631 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 572160 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 504480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 151680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 103 | 720109 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 75 | 1004470 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 759360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 593400 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 145 | 622255 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13101817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 30720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 576 | 13163636.36 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2356 | 40780734.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4677000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 305 | 7486000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 32 | 744480 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 610080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4549818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 977718 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 139 | 1391330 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 31 | 424752 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 752970 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 174 | 2170080 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 70 | 1453440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 57202 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 401660 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 283080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 571200 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 342282 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1413 | 26893092
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 102 | 3167040 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 952800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 164400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 293090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 71760 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 38 | 411120 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 213 | 5073260
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3558518 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 730584 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 54864 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718656 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1606080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 180000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 536904 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7373500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | schedule outage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7749300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1001 | 23224406
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 873 | 21280000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 385 | 8758656 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 545760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1258 | 30584416
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 141055 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2933000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 13661090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5234300 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1334400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6545000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3849 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1414 | 29852694.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 25 | 156680 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 6 | 80428 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 33 | 260673 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 214 | 4679455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Shutdown due to 4th Minor Inspection of GT
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 384 | 8594472 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 317108 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 68706 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 44 | 395525 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 566560 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 58 | 782112 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 79488 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 760 | 16330909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 359252 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 668040 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1649.5 | 33369408
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1585745 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 920793 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35471.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1271809 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 194654 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1101600 | -
Rangpur Area Total |  |  |  |  | 950 | 272 | 5110072.16
Eastern Grid Total |  |  |  |  | 16856.242 | 7146.5 | 138514545.67
Western Grid Total |  |  |  |  | 10294.5 | 4593.5 | 98916591.07
National Grid Total |  |  |  |  | 27150.742 | 11740 | 237431136.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7708.97 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3519.4 | MW
i) Dhaka area |  |  | 4154.47 |  | MW | i) Khulna area |  |  |  | 1294.5 | MW
ii) Chattogram area |  |  | 1188.5 |  | MW | ii) Barishal area |  |  |  | 313.5 | MW
iii) Cumilla area |  |  | 957 |  | MW | iii) Rajshahi area |  |  |  | 1125.4 | MW
iv) Mymensingh area |  |  | 1010 |  | MW | iv) Rangpur area |  |  |  | 786 | MW
v) Sylhet area |  |  | 399 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11228.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 19:00 | 133 | Postogola | 42 | 13:00
2 | AKSML | 106 | 23:00 | 68 | Jamalpur | 107 | 18:30 | 134 | Purbachal | 14 | 18:30
3 | Aftabnagar | 26 | 14:00 | 69 | Jashore | 105 | 19:00 | 135 | Purbasadipur | 117 | 09:00
4 | Agargaon | 76 | 14:00 | 70 | Jhenaidah | 98 | 18:30 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 72 | 18:00 | 71 | Joydebpur | 145 | 12:00 | 137 | Rahim | 28 | 10:00
6 | Amnura | 51 | 08:00 | 72 | Joypurhat | 56 | 08:00 | 138 | Rajbari | 56 | 18:30
7 | Ashuganj | 74 | 14:00 | 73 | Juldah | 11 | 19:30 | 139 | Rajendrapur | 110 | 18:30
8 | BSRM | 201 | 00:00 | 74 | KSRM | 32 | 17:00 | 140 | Rajshahi | 80 | 21:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 218 | 19:00 | 141 | Rajshahi-230 | 74 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 55 | 18:00 | 142 | Ramganj | 86 | 18:30
11 | Bakulia | 76 | 18:30 | 77 | Kallyanpur | 75 | 12:00 | 143 | Rampur | 29 | 18:00
12 | Banani | 20 | 12:00 | 78 | Kalurghat | 32 | 13:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 10 | 10:00 | 79 | Kamrangirchar | 56.4 | 13:00 | 145 | Rangpur | 110 | 13:00
14 | Barapukuria | 61 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 4.8 | 15:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 67 | 00:00 | 147 | SSM | 15 | 00:00
16 | Barishal | 87 | 13:00 | 82 | Keranigonj | 61 | 19:00 | 148 | Saidpur | 103 | 09:00
17 | Barishal-230 | 64 | 18:30 | 83 | Khagrachori | 26 | 18:30 | 149 | Satkhira | 101 | 19:00
18 | Baroaulia | 43 | 19:00 | 84 | Khulna | 65 | 19:00 | 150 | Satmasjid | 76 | 13:00
19 | Baroirhat | 40 | 18:30 | 85 | Khulshi | 148 | 19:00 | 151 | Savar | 180 | 16:00
20 | Bashundhara | 136 | 13:00 | 86 | Kishoreganj | 117 | 18:30 | 152 | SevenRings | 15.26 | 09:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 174 | 18:00 | 153 | ShahCement | 30 | 00:00
22 | Beanibazar | 45 | 18:30 | 88 | Kulaura | 28 | 19:00 | 154 | Shahjadpur | 62 | 18:00
23 | Benapole | 50 | 08:00 | 89 | Kurigram | 59 | 13:00 | 155 | Shahjibazar | 95 | 18:30
24 | Bhaluka | 110 | 08:00 | 90 | Kushtia | 107 | 18:30 | 156 | Shahmirpur | 36 | 18:00
25 | Bhandaria | 36 | 21:00 | 91 | Lalbag | 60 | 19:00 | 157 | Shariatpur | 54 | 20:00
26 | Bhangura | 34 | 18:30 | 92 | Lalmonirhat | 50 | 18:30 | 158 | Sherpur | 136 | 18:30
27 | Bheramara(GK) | 42 | 18:30 | 93 | MI_Cement | 16.1 | 02:00 | 159 | Shikalbaha | 16 | 18:30
28 | Bhulta | 212 | 19:00 | 94 | Madanganj | 20 | 12:00 | 160 | Shitalakhya | 62.7 | 13:00
29 | Bog-Sherpur | 70 | 08:00 | 95 | Madaripur | 69 | 19:30 | 161 | Sholosohor | 33 | 15:00
30 | Bogura | 108 | 19:00 | 96 | Madartek | 61.12 | 19:30 | 162 | Shyampur | 146 | 11:00
31 | Borhanuddin | 55 | 21:00 | 97 | Madunaghat | 37 | 21:00 | 163 | Siddhirganj | 106 | 12:00
32 | Brahmanbaria | 109 | 21:00 | 98 | Magura | 47 | 18:30 | 164 | Sirajganj | 90 | 08:00
33 | Cantonment | 94 | 13:00 | 99 | Mahasthangarh | 72 | 13:00 | 165 | Sonargaon | 84 | 12:00
34 | Chandpur | 47 | 21:00 | 100 | Manikganj | 105 | 19:00 | 166 | Sreemongol | 44 | 18:00
35 | Chandraghona | 27 | 18:30 | 101 | Maniknagar | 50 | 13:00 | 167 | Sreepur | 90 | 16:00
36 | Chapai | 76 | 11:00 | 102 | Matarbari | 41 | 18:30 | 168 | Srinagar | 31.2 | 19:30
37 | Charsaidpur | 42 | 19:00 | 103 | Matuail | 60 | 12:00 | 169 | Sunamganj | 40 | 19:30
38 | Chauddagram | 46 | 13:00 | 104 | Millgate | 63 | 16:00 | 170 | Sylhet | 24 | 18:30
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 111 | 19:30 | 171 | Sylhet-132 | 84 | 18:00
40 | Chowmuhani | 157 | 18:30 | 106 | Mirsorai | 9 | 19:00 | 172 | TK | 21.5 | 18:00
41 | Chuadanga | 73 | 18:30 | 107 | Mirzapur | 37 | 19:30 | 173 | Tangail | 175 | 08:00
42 | Coxsbazar | 116 | 18:00 | 108 | Mithapukur | 52 | 18:30 | 174 | Thakurgaon | 80 | 19:00
43 | Cumilla(N) | 137 | 14:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 101 | 12:00
44 | Cumilla(S) | 112 | 14:00 | 110 | Mogbazar | 97.7 | 13:00 | 176 | Ullahpara | 27 | 08:00
45 | Daudkandi | 95 | 19:00 | 111 | Mongla | 38 | 19:00 | 177 | Ullon | 37 | 13:00
46 | Dhaka | 32 | 13:00 | 112 | Motijheel | 28 | 13:00 | 178 | Uttara | 63 | 14:00
47 | Dhamrai | 98 | 18:30 | 113 | Muktagacha | 31 | 14:00 | 179 | UttaraNew | 33 | 13:00
48 | Dhanmondi | 107 | 13:00 | 114 | Munshiganj | 69 | 14:00 | 180 | Zigatola | 60 | 13:00
49 | Dohazari | 74 | 19:00 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 107 | 18:30 | 116 | Mymensingh | 165 | 14:00
51 | Fatullah | 74 | 12:00 | 117 | Naogaon | 112 | 13:00
52 | Fenchuganj | 25 | 18:30 | 118 | Narail | 42 | 18:30
53 | Feni | 86 | 18:30 | 119 | Narinda | 62 | 13:00
54 | GPH | 15 | 12:00 | 120 | Narshingdi | 161 | 19:00
55 | Ghatail | 60 | 08:00 | 121 | Natore | 114 | 08:00
56 | Ghorashal | 13 | 14:00 | 122 | Nawabganj | 28.8 | 14:00
57 | Ghorashal-230 | 68 | 19:00 | 123 | Netrakona | 140 | 08:00
58 | Goalpara | 26 | 13:00 | 124 | New | 65.3 | 12:00
59 | Gollamari | 58 | 13:00 | 125 | Niamatpur | 90 | 13:00
60 | Gopalganj | 82.5 | 19:00 | 126 | Noapara | 40 | 13:00
61 | Gulshan | 84 | 13:00 | 127 | PHP | 9 | 19:30
62 | Halishahar | 59.5 | 15:00 | 128 | Pabna | 69 | 18:30
63 | HaripurSBU | 158 | 01:00 | 129 | Palashbari | 110 | 08:00
64 | Hasnabad | 85 | 19:30 | 130 | Panchagarh | 42 | 18:30
65 | Hathazari | 55 | 19:00 | 131 | Patuakhali | 51 | 22:00
66 | Ishurdi | 61 | 18:30 | 132 | Payra | 20 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8760.69 | 0 |  | 8760.69
1:00 | 8316.96 | 0 |  | 8316.96
2:00 | 7999.4 | 0 |  | 7999.4
3:00 | 7696.15 | 0 |  | 7696.15
4:00 | 7515.9 | 0 |  | 7515.9
5:00 | 7475.36 | 0 |  | 7475.36
6:00 | 7915.21 | 0 |  | 7915.21
7:00 | 8943.51 | 0 |  | 8943.51
8:00 | 9730.44 | 0 |  | 9730.44
9:00 | 10308.95 | 10 |  | 10318.95
10:00 | 10278.02 | 15 |  | 10294.02
11:00 | 10298.54 | 72 |  | 10373.54
12:00 | 10819.29 | 56 |  | 10878.29
13:00 | 11250.29 | 46 |  | 11298.29
14:00 | 10759.05 | 42 |  | 10803.05
15:00 | 10623.06 | 0 |  | 10623.06
16:00 | 10400.34 | 0 |  | 10400.34
17:00 | 10259.14 | 0 |  | 10259.14
18:00 | 10765 | 0 |  | 10765
19:00 | 11740 | 0 |  | 11740
19:30 | 11280 | 0 |  | 11280
20:00 | 11191 | 0 |  | 11191
21:00 | 11046.68 | 0 |  | 11046.68
22:00 | 10557.28 | 0 |  | 10557.28
23:00 | 10076.5 | 0 |  | 10076.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4964.5 | 3796.19 | 8760.69 | DAILY GENERATION CURVE
00:30 | 4925 | 3613.825 | 8538.825
01:00 | 4885.5 | 3431.46 | 8316.96 | 16-02-2025
01:30 | 4791 | 3367.18 | 8158.18
02:00 | 4696.5 | 3302.9 | 7999.4
02:30 | 4646.5 | 3201.275 | 7847.775
03:00 | 4596.5 | 3099.65 | 7696.15
03:30 | 4546.5 | 3059.525 | 7606.025
04:00 | 4496.5 | 3019.4 | 7515.9
04:30 | 4475 | 3020.63 | 7495.63
05:00 | 4453.5 | 3021.86 | 7475.36
05:30 | 4580 | 3115.285 | 7695.285
06:00 | 4706.5 | 3208.71 | 7915.21
06:30 | 4916.215 | 3513.145 | 8429.36
07:00 | 5125.93 | 3817.58 | 8943.51
07:30 | 5377.76 | 3959.215 | 9336.975
08:00 | 5629.59 | 4100.85 | 9730.44
08:30 | 5821.765 | 4197.93 | 10019.695
09:00 | 6013.94 | 4295.01 | 10308.95
09:30 | 5929.34 | 4364.145 | 10293.485
10:00 | 5844.74 | 4433.28 | 10278.02
10:30 | 5821.545 | 4466.735 | 10288.28
11:00 | 5798.35 | 4500.19 | 10298.54
11:30 | 5926.325 | 4632.59 | 10558.915
12:00 | 6054.3 | 4764.99 | 10819.29
12:30 | 6242.18 | 4792.61 | 11034.79
13:00 | 6430.06 | 4820.23 | 11250.29
13:30 | 6362.74 | 4641.93 | 11004.67
14:00 | 6295.42 | 4463.63 | 10759.05
14:30 | 6291.24 | 4399.815 | 10691.055
15:00 | 6287.06 | 4336 | 10623.06
15:30 | 6215.46 | 4296.24 | 10511.7
16:00 | 6143.86 | 4256.48 | 10400.34
16:30 | 6056.52 | 4273.22 | 10329.74
17:00 | 5969.18 | 4289.96 | 10259.14
17:30 | 6162.84 | 4349.23 | 10512.07
18:00 | 6356.5 | 4408.5 | 10765
18:30 | 6751.5 | 4501 | 11252.5
19:00 | 7146.5 | 4593.5 | 11740
19:30 | 6727.5 | 4552.5 | 11280
20:00 | 6688.5 | 4502.5 | 11191
20:30 | 6592.25 | 4526.59 | 11118.84 |  | Executive Engineer
21:00 | 6496 | 4550.68 | 11046.68 |  | Network Operation Division
21:30 | 6321 | 4480.98 | 10801.98
22:00 | 6146 | 4411.28 | 10557.28
22:30 | 5947 | 4369.89 | 10316.89
23:00 | 5748 | 4328.5 | 10076.5

## En-Curve
QF-LDC-12
Date | 16-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2941 | 2009 | 925 | 0 | 52 | 633.69 | 40 | 2151 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2937 | 2018 | 924.5 | 0 | 50 | 540.325 | 40 | 2024.5 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 16-02-2025
01:00 | 2933 | 2027 | 924 | 0 | 48 | 446.96 | 40 | 1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2953 | 1998 | 924.5 | 0 | 47 | 434.18 | 40 | 1761.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 237.4311 |  | MKWHr
02:00 | 2973 | 1969 | 925 | 0 | 46 | 421.4 | 40 | 1625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0.241 |  | MKWHr
02:30 | 3000 | 1950 | 843.5 | 0 | 45 | 418.775 | 40 | 1550.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 237.6721 |  | MKWHr
03:00 | 3027 | 1931 | 762 | 0 | 44 | 416.15 | 40 | 1476 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 3030 | 1873.5 | 749 | 0 | 44 | 417.025 | 40 | 1452.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 3033 | 1816 | 736 | 0 | 44 | 417.9 | 40 | 1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 3022 | 1808 | 736 | 0 | 44 | 417.63 | 40 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 3011 | 1800 | 736 | 0 | 44 | 417.36 | 40 | 1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 3060 | 1818 | 736 | 0 | 45 | 465.285 | 40 | 1531 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 3109 | 1836 | 736 | 0 | 46 | 513.21 | 40 | 1635 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 3122 | 1976.75 | 830 | 0 | 47 | 617.845 | 40 | 1781.5 | 11.265 | 0.5 | 2.5 | 0 | 0 | 0 | 0
07:00 | 3135 | 2117.5 | 924 | 0 | 48 | 722.48 | 40 | 1928 | 22.53 | 1 | 5 | 0 | 0 | 0 | 0
07:30 | 3105 | 2124.5 | 901 | 0 | 54 | 744.24 | 40 | 2046.5 | 89.985 | 25 | 206.75 | 0 | 0 | 0 | 0
08:00 | 3075 | 2131.5 | 878 | 0 | 60 | 766 | 40 | 2165 | 157.44 | 49 | 408.5 | 0 | 0 | 0 | 0
08:30 | 3115 | 2197.5 | 878 | 0 | 62 | 761.5 | 40 | 2165 | 239.945 | 77.5 | 483.25 | 0 | 0 | 0 | 5
09:00 | 3155 | 2263.5 | 878 | 0 | 64 | 757 | 40 | 2165 | 322.45 | 106 | 558 | 0 | 0 | 0 | 10
09:30 | 3115 | 2162.5 | 878 | 0 | 66 | 758 | 40 | 2165 | 400.635 | 110.5 | 597.85 | 0 | 0 | 0 | 12.5
10:00 | 3075 | 2061.5 | 878 | 0 | 68 | 759 | 40 | 2165 | 478.82 | 115 | 637.7 | 0 | 0 | 0 | 15
10:30 | 3011.5 | 1991.5 | 902 | 0 | 69 | 759.5 | 40 | 2165 | 527.93 | 133 | 688.85 | 0 | 0 | 0 | 43.5
11:00 | 2948 | 1921.5 | 926 | 0 | 70 | 760 | 40 | 2165 | 577.04 | 151 | 740 | 0 | 0 | 0 | 72
11:30 | 3033.5 | 1941 | 925 | 0 | 72 | 760.5 | 40 | 2176 | 599.915 | 160 | 851 | 0 | 0 | 0 | 64
12:00 | 3119 | 1960.5 | 924 | 0 | 74 | 761 | 40 | 2187 | 622.79 | 169 | 962 | 0 | 0 | 0 | 56
12:30 | 3087 | 1955 | 922.5 | 0 | 73 | 761.5 | 40 | 2186.5 | 613.29 | 209 | 1186.5 | 0 | 0 | 0.5 | 51
13:00 | 3055 | 1949.5 | 921 | 0 | 72 | 762 | 40 | 2186 | 603.79 | 249 | 1411 | 0 | 0 | 1 | 46
13:30 | 2945 | 1846.5 | 921 | 0 | 73 | 761 | 60 | 2187 | 565.67 | 252 | 1387 | 0 | 0 | 6.5 | 44
14:00 | 2835 | 1743.5 | 921 | 0 | 74 | 760 | 80 | 2188 | 527.55 | 255 | 1363 | 0 | 0 | 12 | 42
14:30 | 2836 | 1813.25 | 920.5 | 0 | 74 | 758.5 | 60 | 2188.5 | 441.805 | 266.5 | 1322 | 0 | 0 | 10 | 21
15:00 | 2837 | 1883 | 920 | 0 | 74 | 757 | 40 | 2189 | 356.06 | 278 | 1281 | 0 | 0 | 8 | 0
15:30 | 2854 | 1916 | 920 | 0 | 73 | 759 | 40 | 2187.5 | 283.2 | 280 | 1190.5 | 0 | 0 | 8.5 | 0
16:00 | 2871 | 1949 | 920 | 0 | 72 | 761 | 40 | 2186 | 210.34 | 282 | 1100 | 0 | 0 | 9 | 0
16:30 | 2850.5 | 1968.25 | 920 | 0 | 70 | 760.5 | 40 | 2176.5 | 137.49 | 324 | 1078 | 0 | 0 | 4.5 | 0
17:00 | 2830 | 1987.5 | 920 | 0 | 68 | 760 | 40 | 2167 | 64.64 | 366 | 1056 | 0 | 0 | 0 | 0
17:30 | 2924.5 | 1953.25 | 920.5 | 0 | 71 | 759 | 40 | 2138 | 32.82 | 452 | 1219 | 0 | 0 | 2 | 0
18:00 | 3019 | 1919 | 921 | 0 | 74 | 758 | 40 | 2109 | 1 | 538 | 1382 | 0 | 0 | 4 | 0
18:30 | 3014.5 | 1982.5 | 897 | 0 | 72 | 759 | 40 | 2137 | 0.5 | 567 | 1781 | 0 | 0 | 2 | 0
19:00 | 3010 | 2046 | 873 | 0 | 70 | 760 | 40 | 2165 | 0 | 596 | 2180 | 0 | 0 | 0 | 0
19:30 | 2998 | 1991.5 | 872 | 0 | 68 | 753 | 40 | 2174 | 0 | 559 | 1824.5 | 0 | 0 | 0 | 0
20:00 | 2976 | 2052.5 | 873 | 0 | 68 | 756 | 40 | 2187 | 0 | 511 | 1727.5 | 0 | 0 | 0 | 0
20:30 | 2981 | 2054.5 | 896 | 0 | 67 | 755.59 | 40 | 2187 | 0 | 478.5 | 1659.25 | 0 | 0 | 0 | 0
21:00 | 2986 | 2056.5 | 919 | 0 | 66 | 755.18 | 40 | 2187 | 0 | 446 | 1591 | 0 | 0 | 0 | 0
21:30 | 2892 | 2059 | 919 | 0 | 64 | 755.98 | 40 | 2187.5 | 0 | 446.5 | 1438 | 0 | 0 | 0 | 0
22:00 | 2798 | 2061.5 | 919 | 0 | 62 | 756.78 | 40 | 2188 | 0 | 447 | 1285 | 0 | 0 | 0 | 0
22:30 | 2787.5 | 2060 | 921.5 | 0 | 61 | 758.89 | 40 | 2050 | 0 | 427 | 1211 | 0 | 0 | 0 | 0
23:00 | 2777 | 2058.5 | 924 | 0 | 60 | 761 | 40 | 1912 | 0 | 407 | 1137 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 413 | 05:00 | 389 | 12:00 | Payra | 424 | 03:00 | 412 | 11:00
Ashuganj | 418 | 6:00 | 400 | 13:00 | Rahanpur | 417 | 04:00 | 397 | 09:00
Bhulta | 412 | 04:00 | 386 | 12:00 | Rampal | 414 | 04:00 | 388 | 12:00
Bibiana | 410 | 19:00 | 399 | 13:00
BIPTC | 406 | 04:00 | 390 | 11:00
Bogura | 415 | 04:00 | 392 | 09:00
Gopalganj | 416 | 05:00 | 396 | 16:00
Kaliakoir | 404 | 05:00 | 383 | 15:00
Madunaghat | 408 | 20:00 | 401 | 12:00
Meghnaghat | 408 | 04:00 | 390 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 02:00 | 223 | 12:00 | Keranigonj | 237 | 05:00 | 222 | 12:00
AKSML | 238 | 19:30 | 227 | 12:00 | Khulna(S) | 240 | 02:00 | 224 | 12:00
Aminbazar | 236 | 01:00 | 222 | 12:00 | Madunaghat | 236 | 19:00 | 229 | 10:00
Ashuganj | 242 | 01:00 | 232 | 12:00 | Madunaghat-400 | 237 | 20:00 | 229 | 12:00
Ashuganj-400 | 246 | 06:00 | 236 | 13:00 | Maniknagar | 236 | 04:00 | 223 | 12:00
Baghabari | 240 | 04:00 | 229 | 12:00 | Meghnaghat | 242 | 00:00 | 232 | 16:00
Barapukuria | 233 | 15:00 | 210 | 07:00 | Meghnaghat-400 | 239 | 04:00 | 225 | 12:00
Barapukuria-230 | 233 | 15:00 | 210 | 07:00 | Mirsorai | 241 | 19:30 | 225 | 16:00
Barishal | 245 | 04:00 | 235 | 12:00 | Rajshahi | 242 | 03:00 | 228 | 12:00
Bheramara | 240 | 04:00 | 227 | 12:00 | Rampal | 239 | 04:00 | 221 | 13:00
Bhulta | 239 | 04:00 | 225 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 236 | 04:00 | 228 | 16:00 | Rampura | 239 | 05:00 | 222 | 12:00
BIPTC | 242 | 03:00 | 228 | 12:00 | Shikalbaha | 239 | 19:00 | 227 | 10:00
Bogura | 241 | 04:00 | 227 | 08:00 | Shyampur | 238 | 05:00 | 222 | 12:00
Bogura-400 | 239 | 04:00 | 226 | 09:00 | Siddhirganj | 260 | 17:00 | 225 | 12:00
Borhanuddin | 248 | 00:00 | 239 | 15:00 | Sirajgonj | 246 | 03:00 | 237 | 09:00
BSRM | 238 | 19:30 | 225 | 12:00 | Sreepur | 242 | 04:00 | 228 | 12:00
Cumilla(N) | 234 | 01:00 | 226 | 12:00 | Tongi | 232 | 00:00 | 220 | 12:00
Faridpur | 245 | 05:00 | 232 | 12:00
Fenchuganj | 241 | 03:00 | 233 | 15:00
Ghorashal | 240 | 00:00 | 230 | 14:00
Ghorashal-230 | 239 | 03:00 | 224 | 12:00
Gopalganj | 244 | 05:00 | 232 | 12:00
GPH | 237 | 19:00 | 227 | 11:00
Haripur | 237 | 04:00 | 224 | 12:00
Hasnabad | 237 | 02:00 | 223 | 12:00
Hathazari | 239 | 19:00 | 230 | 11:00
Ishurdi | 242 | 04:00 | 230 | 12:00
Jhenaidah | 240 | 04:00 | 223 | 12:00
Kaliakoir | 236 | 05:00 | 220 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 124 | 13:00 | Magura | 139 | 04:00 | 128 | 12:00
Agargaon | 138 | 04:00 | 129 | 12:00 | Mahasthangarh | 136 | 03:00 | 126 | 08:00
Agrabad | 137 | 19:00 | 129 | 11:00 | Manikganj | 139 | 00:00 | 132 | 15:00
AKS | 133 | 18:00 | 128 | 00:00 | Maniknagar | 136 | 04:00 | 126 | 12:00
Aminbazar | 135 | 01:00 | 128 | 14:00 | Matarbari | 126 | 23:00 | 120 | 07:00
Amnura | 142 | 19:00 | 128 | 08:00 | Matuail | 136 | 02:00 | 127.6 | 12:00
Ashuganj | 142 | 00:00 | 138 | 11:00 | Millgate | 139 | 03:00 | 128 | 12:00
Bagerhat | 139 | 05:00 | 125 | 12:00 | Mirpur | 134 | 01:00 | 125 | 15:00
Bajitpur | 137 | 00:00 | 132 | 11:00 | Mirzapur | 140 | 04:00 | 130 | 16:00
Bakulia | 138 | 19:00 | 130 | 11:00 | Mithapukur | 134 | 19:30 | 120 | 07:00
Banani | 136 | 02:00 | 125 | 12:00 | MI_Cement | 137.4 | 04:00 | 129 | 12:00
Bangabhaban | 135 | 01:00 | 126 | 12:00 | Modern | 0 | 00:00 | 0 | 00:00
Barapukuria | 134 | 03:00 | 123 | 07:00 | Mogbazar | 137 | 05:00 | 126 | 12:00
Barguna | 140 | 07:00 | 131 | 12:00 | Mongla | 136 | 05:00 | 125 | 12:00
Barishal | 135 | 01:00 | 130 | 12:00 | Motijheel | 135 | 01:00 | 126 | 12:00
Barishal-230 | 137 | 04:00 | 130 | 12:00 | Muktagacha | 136 | 03:00 | 124 | 08:00
Baroaulia | 137 | 19:00 | 131 | 00:00 | Munshiganj | 137 | 04:00 | 128 | 12:00
Baroirhat | 134 | 19:00 | 127 | 12:00 | Muradnagar | 137 | 05:00 | 128 | 12:00
Bashundhara | 138 | 02:00 | 125 | 12:00 | Mymensingh | 133 | 05:00 | 115 | 08:00
BashundharaCement | 135 | 01:00 | 127 | 12:00 | Naogaon | 135 | 03:00 | 122 | 08:00
Beanibazar | 137 | 01:00 | 130 | 12:00 | Narail | 140 | 03:00 | 127 | 12:00
Benapole | 138 | 04:00 | 123 | 12:00 | Narinda | 136 | 04:00 | 126 | 12:00
Bhaluka | 128 | 01:00 | 119 | 09:00 | Narshingdi | 131 | 00:00 | 123 | 11:00
Bhandaria | 134 | 05:00 | 127 | 12:00 | Natore | 139 | 23:00 | 131 | 08:00
Bhangura | 137 | 00:00 | 130 | 07:00 | Nawabganj | 138 | 04:00 | 129 | 12:00
Bheramara | 139 | 03:00 | 134 | 12:00 | Netrakona | 126 | 00:00 | 112 | 12:00
Bheramara(GK) | 140 | 04:00 | 135 | 12:00 | New | 139 | 05:00 | 128 | 12:00
Bhulta | 131 | 04:00 | 124 | 12:00 | Niamatpur | 139 | 19:30 | 132 | 07:00
Bog-Sherpur | 137 | 05:00 | 126 | 09:00 | Noapara | 140 | 03:00 | 127 | 12:00
Bogura | 138 | 23:00 | 128 | 09:00 | Pabna | 138 | 22:00 | 126 | 12:00
Bogura-230 | 138 | 23:00 | 128 | 08:00 | Palashbari | 133 | 03:00 | 116 | 08:00
Brahmanbaria | 137 | 01:00 | 130 | 12:00 | Panchagarh | 136 | 19:00 | 119 | 07:00
Cantonment | 138 | 04:00 | 128 | 12:00 | Patuakhali | 138 | 17:00 | 132 | 11:00
Chandpur | 141 | 18:00 | 125 | 00:00 | Payra | 139 | 04:00 | 133 | 12:00
Chandraghona | 137 | 19:00 | 132 | 12:00 | PHP | 133 | 19:30 | 126 | 12:00
Chapai | 138 | 01:00 | 128 | 13:00 | Postogola | 139 | 01:00 | 131 | 12:00
Charsaidpur | 137 | 02:00 | 129 | 12:00 | Purbachal | 136 | 01:00 | 125 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 134 | 22:00 | 127 | 12:00 | Purbasadipur | 133 | 19:30 | 116 | 07:00
Chhatak | 136 | 01:00 | 126 | 12:00 | Rahanpur | 142 | 00:00 | 134 | 12:00
Chowmuhani | 131 | 18:30 | 124 | 00:00 | Rahanpur-400 | 142 | 05:00 | 134 | 08:00
Chuadanga | 138 | 04:00 | 126 | 12:00 | Rahim | 135 | 02:00 | 127 | 12:00
Coxsbazar | 125 | 00:00 | 119 | 18:00 | Rajbari | 160 | 11:00 | 129 | 12:00
Cumilla(N) | 137 | 19:00 | 131 | 12:00 | Rajendrapur | 138 | 02:00 | 126 | 12:00
Cumilla(S) | 136 | 04:00 | 127 | 09:00 | Rajshahi | 140 | 19:30 | 133 | 07:00
Daudkandi | 133 | 02:00 | 125 | 12:00 | Rajshahi-230 | 139 | 03:00 | 125 | 09:00
Dhaka | 136 | 03:00 | 125 | 12:00 | Ramganj | 134 | 19:00 | 124 | 00:00
Dhamrai | 136 | 02:00 | 125 | 12:00 | Rampur | 138 | 19:00 | 129 | 11:00
Dhanmondi | 135.5 | 03:00 | 128 | 12:00 | Rampura | 136 | 04:00 | 125 | 12:00
Dohazari | 134 | 19:00 | 127 | 11:00 | Rangamati | 136 | 19:00 | 131 | 11:00
Faridpur | 135 | 03:00 | 130 | 10:00 | Rangpur | 133 | 13:00 | 117 | 07:00
Fatullah | 139 | 05:00 | 129 | 12:00 | Ruppur | 141 | 04:00 | 136 | 09:00
Fenchuganj | 140 | 00:00 | 134 | 15:00 | Saidpur | 132 | 23:00 | 117 | 07:00
Feni | 132 | 22:00 | 127 | 12:00 | Satkhira | 139 | 02:00 | 125 | 18:30
Ghatail | 136 | 04:00 | 124 | 07:00 | Satmasjid | 138 | 05:00 | 127 | 13:00
Ghorashal | 142 | 00:00 | 136 | 12:00 | Savar | 134 | 03:00 | 125 | 12:00
Goalpara | 140 | 04:00 | 128 | 13:00 | SevenRings | 144 | 05:00 | 135 | 12:00
Gollamari | 139 | 04:00 | 132 | 12:00 | ShahCement | 137 | 02:00 | 129 | 12:00
Gopalganj | 138 | 04:00 | 130 | 12:00 | Shahjadpur | 141 | 23:00 | 134 | 11:00
Gopalganj-400 | 138 | 03:00 | 132 | 10:00 | Shahjibazar | 140 | 01:00 | 133 | 12:00
Gulshan | 134 | 01:00 | 124 | 15:00 | Shahmirpur | 139 | 18:30 | 130 | 11:00
Halishahar | 138 | 19:00 | 131 | 00:00 | Shariatpur | 138 | 05:00 | 132 | 09:00
Haripur | 135 | 01:00 | 127 | 12:00 | Sherpur | 129 | 04:00 | 113 | 07:00
HaripurSBU | 136 | 04:00 | 127 | 12:00 | Shikalbaha | 127 | 19:00 | 120 | 00:00
Hasnabad | 138 | 00:00 | 131 | 12:00 | Shikalbaha-230 | 138 | 19:00 | 130 | 11:00
Hathazari | 139 | 19:00 | 132 | 11:00 | Shitalakhya | 137.4 | 04:00 | 129 | 12:00
Ishurdi | 141 | 03:00 | 135 | 12:00 | Sholosohor | 137 | 19:00 | 131 | 11:00
Jaldhaka | 130 | 14:00 | 114 | 07:00 | Shyampur | 137 | 00:00 | 132 | 13:00
Jamalpur | 132 | 04:00 | 117 | 07:00 | Shyampur-230 | 138 | 04:00 | 129 | 12:00
Jashore | 137 | 03:00 | 125 | 12:00 | Siddhirganj | 135 | 04:00 | 128 | 12:00
Jhenaidah | 139 | 05:00 | 127 | 18:00 | Sirajganj | 138 | 02:00 | 126 | 08:00
Jhenaidah-230 | 140 | 03:00 | 129 | 12:00 | Sonargaon | 135 | 01:00 | 127 | 11:00
Joydebpur | 140 | 02:00 | 130 | 11:00 | Sreemongol | 138 | 00:00 | 132 | 12:00
Joypurhat | 135 | 03:00 | 120 | 08:00 | Sreepur | 132 | 05:00 | 123 | 12:00
Juldah | 140 | 19:00 | 130 | 11:00 | Srinagar | 139 | 04:00 | 128 | 12:00
Kabirpur | 143 | 19:30 | 125 | 12:00 | SSM | 140 | 18:30 | 130 | 18:00
Kachua | 137 | 18:00 | 128 | 00:00 | Sunamganj | 136 | 03:00 | 126 | 14:00
Kaliakoir | 145 | 03:00 | 128 | 12:00 | Sylhet | 137 | 02:00 | 130 | 11:00
Kallyanpur | 135 | 02:00 | 126 | 12:00 | Sylhet-132 | 138 | 01:00 | 131 | 12:00
Kalurghat | 136 | 18:30 | 131 | 10:00 | Tangail | 134 | 05:00 | 124 | 12:00
Kamrangirchar | 138 | 01:00 | 125 | 15:00 | Thakurgaon | 136 | 13:00 | 116 | 07:00
Kaptai | 137 | 4:00 | 124 | 12:00 | TK | 137 | 19:00 | 131 | 12:00
Kazla | 136 | 03:00 | 126 | 12:00 | Tongi | 138 | 04:00 | 130 | 16:00
Keranigonj | 139 | 04:00 | 129 | 12:00 | Ullahpara | 140 | 03:00 | 129 | 08:00
Khagrachori | 135 | 19:00 | 130 | 11:00 | Ullon | 135 | 02:00 | 125 | 12:00
Khulna | 137 | 04:00 | 127 | 12:00 | Uttara | 135 | 02:00 | 125 | 15:00
Khulna(S) | 140 | 04:00 | 129 | 12:00 | UttaraNew | 138 | 01:00 | 127 | 12:00
Khulshi | 136 | 19:00 | 129 | 11:00 | Zigatola | 139 | 04:00 | 129 | 13:00
Kishoreganj | 134 | 02:00 | 127 | 08:00
Kodda | 140 | 02:00 | 128 | 11:00
KSRM | 138 | 19:00 | 131 | 12:00
Kulaura | 140 | 03:00 | 134 | 12:00
Kurigram | 131 | 04:00 | 113 | 07:00
Kushtia | 140 | 02:00 | 132 | 12:00
Lalbag | 139 | 04:00 | 129 | 12:00
Lalmonirhat | 130 | 11:00 | 112 | 07:00
Madanganj | 135 | 01:00 | 127 | 12:00
Madaripur | 136 | 17:00 | 133 | 10:00
Madartek | 135 | 04:00 | 125 | 12:00
Madunaghat | 138 | 19:00 | 132 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division