## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-02-2025 | during | 20-02-2025 | during | 20-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 250 | 50 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 408 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | Unit-2 shut down for leak repairing
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 18 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 98 | 130 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19 | 18.5 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 8 | 16 | 25 | 25 | 25 | 25 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 20 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 152 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 133 | 124 | 149 | 149 | 113 | 113 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 72 | 162 | 162 | 35 | 35 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 550 | 320 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 2076 | 2466.5 | 4851.87 | 4623.87 | 2788.79 | 2853.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 3 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 47 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 226 | 222 | 222 | 222 | 222 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 33 | 79 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 68 | 85 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 89 | 100 | 100 | 100 | 90 | 90 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 5 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 51 | 50 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.99 | 0 | 3.99 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 100 | 300 | 300 | 50 | 50 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 29 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 68 | 75 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 75 | 100 | 100 | 100 | 50 | 50 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 37 | 122 | 116 | 116 | 53 | 53 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 36 | 145 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 5 | 25 | 5 | 25 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 577 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2075 | 2520 | 3445.85 | 3482.86 | 3072.85 | 3109.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 190 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 295 | 300 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 192 | 192 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 78 | 100 | 150 | 150 | 107 | 107 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 42 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 50 | 163 | 163 | 40 | 40 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 178 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 84 | 76 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 95 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1413.2 | 1534.2 | 2001.53 | 1931.53 | 1692.03 | 1622.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-02-2025 | during | 20-02-2025 | during | 20-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 28 | 210 | 210 | 30 | 30 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 112 | 59 | 115 | 115 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.29 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 17 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 202.29 | 137 | 648.4 | 601.5 | 222.4 | 175.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 29 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 38 | 45 | 45 | 45 | 45 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 30 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 23 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1024 | 1038 | 1082 | 1082 | 1044 | 1044
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 25 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 165 | 158 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 53.21 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234.2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1142.21 | 1060 | 3589.2 | 3504.2 | 1369.02 | 1284.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 78 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 136 | 136 | 136 | 136 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 622 | 622 | 622 | 602 | 602 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 137 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.38 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1357.38 | 1533 | 1556.12 | 1555.12 | 1536.12 | 1535.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 28 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 9 | 30 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 200 | 200 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 161 | 147 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 24 | 32 | 32 | 32 | 32 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 8 | 8 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.77 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 762.05 | 757 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.36 | 0 | 52 | 0 | 52 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 77 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1694.68 | 1761.5 | 2279.84 | 2127.24 | 2133.85 | 1981.25
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 94 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 100 | 0 | 103 | 0 | 103 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 136.8 | 200 | 400.6 | 262 | 366.62 | 228.02
System Total |  |  |  |  | 27884.66 | 27150.742 | 11121.56 | 12250.2 | 19855.41 | 19170.32 | 14225.68 | 13833.59
Forecast Scenario (20-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10300 |  | 0 |  | 10300
|  |  |  | 1:00 | 9660 |  | 0 |  | 9660
|  |  |  | 2:00 | 9050 |  | 0 |  | 9050
|  |  |  | 3:00 | 8850 |  | 0 |  | 8850
|  |  |  | 4:00 | 8620 |  | 0 |  | 8620
|  |  |  | 5:00 | 8580 |  | 0 |  | 8580
|  |  |  | 6:00 | 8760 |  | 0 |  | 8760
|  |  |  | 7:00 | 9970 |  | 0 |  | 9970
|  |  |  | 8:00 | 10890 |  | 0 |  | 10890
|  |  |  | 9:00 | 10880 |  | 0 |  | 10880
|  |  |  | 10:00 | 10870 |  | 0 |  | 10870
|  |  |  | 11:00 | 11130 |  | 0 |  | 11130
|  |  |  | 12:00 | 11190 |  | 0 |  | 11190
|  |  |  | 13:00 | 11660 |  | 0 |  | 11660
|  |  |  | 14:00 | 11310 |  | 0 |  | 11310
|  |  |  | 15:00 | 11000 |  | 0 |  | 11000
|  |  |  | 16:00 | 10900 |  | 0 |  | 10900
|  |  |  | 17:00 | 10700 |  | 0 |  | 10700
|  |  |  | 18:00 | 10600 |  | 0 |  | 10600
|  |  |  | 18:30 | 10900 |  | 0 |  | 10900
|  |  |  | 19:00 | 12200 |  | 0 |  | 12200
|  |  |  | 19:30 | 12000 |  | 0 |  | 12000
|  |  |  | 20:00 | 11700 |  | 0 |  | 11700
|  |  |  | 21:00 | 11500 |  | 0 |  | 11500
|  |  |  | 22:00 | 11300 |  | 0 |  | 11300
|  |  |  | 23:00 | 10700 |  | 0 |  | 10700
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 11190.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11908.78 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 251.81692 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:41 hrs on 20-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-02-2025 | [28 empty] | Date: | 19-02-2025 | [28 empty] | Date: | 19-02-2025 | [28 empty] | Date: | 19-02-2025 | [28 empty] | Date: | 19-02-2025 | [18 empty] | Date: | 19-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 70 | 82 | 145 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 35 | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 584 | 35 | 51 | 0 | 0 | 0 | 0 | 80 | 0 | 100 | 0 | 0 | 40 | 110 | 24 | 572 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 117 | 197 | 0 | 0 | 270 | 29 | 215 | 36 | 0 | 40 | 155 | 9 | 18 | 0 | 62 | 0 | 0 | 0 | 285 | 320 | 0 | 35 | 30 | 30 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 30 | 0 | 0 | 6 | 6146 | 924 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 113 | 7 | 91 | 70 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 17 | 4157.5 | 10303.5 | 90.06
01:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 27 | 48 | 0 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 19.5 | 22 | 0 | 584 | 17 | 51 | 0 | 0 | 0 | 0 | 40 | 0 | 100 | 0 | 0 | 40 | 110 | 30 | 576 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 197 | 0 | 0 | 270 | 29 | 223 | 36 | 0 | 40 | 155 | 9 | 18 | 0 | 60 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 30 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 32 | 0 | 0 | 6 | 5813.5 | 923 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 7 | 0 | 380 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3851.5 | 9665 | 90.06
02:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 520 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 24 | 576 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 270 | 29 | 225 | 36 | 0 | 40 | 51 | 9 | 18 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 30 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 6 | 5385 | 926 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 9 | 0 | 340 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 180 | 0 | 0 | 622 | 0 | 3664.5 | 9049.5 | 90.06
03:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 361 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 520 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 27 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 270 | 29 | 225 | 36 | 0 | 40 | 17 | 9 | 18 | 0 | 56 | 0 | 0 | 0 | 310 | 320 | 0 | 35 | 30 | 30 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 6 | 5274 | 925 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 3 | 0 | 340 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 180 | 0 | 0 | 622 | 0 | 3583.5 | 8857.5 | 90.05
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 480 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 68 | 24 | 577 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 275 | 29 | 225 | 36 | 0 | 40 | 17 | 9 | 18 | 0 | 54 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 30 | 30 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 0 | 5112 | 925 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 1 | 0 | 300 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 180 | 0 | 0 | 622 | 0 | 3507.5 | 8619.5 | 90.05
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 440 | 0 | 15 | 0 | 0 | 8 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 68 | 24 | 574 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 270 | 29 | 224 | 36 | 0 | 40 | 17 | 9 | 18 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 0 | 35 | 30 | 30 | 2 | 120 | 23 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 0 | 5042 | 926 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 27 | 0 | 300 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 180 | 0 | 0 | 622 | 0 | 3537.5 | 8579.5 | 90.05
06:00 | 0 | 5 | 0 | 0 | 0 | 230 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 0 | 0 | 17 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 440 | 6 | 16 | 0 | 0 | 11 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 90 | 34 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 197 | 0 | 0 | 270 | 29 | 182 | 33 | 0 | 40 | 41 | 9 | 12 | 0 | 54 | 0 | 0 | 0 | 285 | 320 | 0 | 35 | 30 | 30 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 2 | 5147.5 | 926 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 80 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 65 | 0 | 250 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 100 | 180 | 0 | 0 | 622 | 0 | 3618.5 | 8766 | 90.04
07:00 | 0 | 34 | 0 | 0 | 0 | 238 | 0 | 0 | 339 | 0 | 0 | 0 | 15 | 0 | 35 | 115 | 45 | 0 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1 | 0 | 20.5 | 22 | 0 | 500 | 35 | 16 | 0 | 0 | 6 | 0 | 0 | 1 | 100 | 53 | 0 | 40 | 110 | 33 | 577 | 36 | 0 | 0 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 2 | 43 | 37 | 197 | 0 | 0 | 320 | 29 | 182 | 33 | 0 | 40 | 188 | 9 | 12 | 0 | 58 | 0 | 1 | 0 | 295 | 320 | 0 | 35 | 30 | 30 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 34 | 0 | 0.92 | 6 | 5865.42 | 925 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 0 | 0 | 757 | 0 | 0 | 0 | 113 | 0 | 0 | 90 | 0 | 0 | 3 | 0 | 2.02 | 124 | 0 | 0 | 0 | 103 | 0 | 250 | 0 | 0.11 | 2.5 | 0 | 0 | 45 | 1 | 95 | 0 | 0 | 0.2 | 7 | 0.01 | 64 | 307 | 6 | 130 | 220 | 0 | 0 | 622 | 17 | 4043.06 | 9908.48 | 90.04
08:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 18 | 0 | 95 | 116 | 214 | 28 | 0 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 17 | 29 | 0 | 0 | 0 | 7 | 0 | 20.5 | 22 | 0 | 584 | 35 | 50 | 1 | 0 | 11 | 84 | 2 | 38 | 100 | 100 | 1 | 40 | 110 | 5 | 576 | 36 | 0 | 20 | 20 | 105 | 226 | 0 | 0 | 0 | 612 | 7 | 43 | 112 | 197 | 0 | 0 | 310 | 29 | 182 | 36 | 0 | 40 | 191 | 9 | 12 | 70 | 68 | 52.2 | 5 | 0 | 290 | 320 | 0 | 35 | 30 | 30 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 18 | 9 | 56 | 28 | 1 | 5.63 | 6 | 6751.33 | 879 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.74 | 0 | 0 | 755.22 | 0 | 0 | 0 | 113 | 0 | 0 | 95 | 0 | 0 | 24 | 0 | 14.67 | 0 | 0 | 0 | 0 | 120 | 0 | 250 | 0 | 1.23 | 2.5 | 0 | 0 | 73 | 9 | 99 | 0 | 0 | 1.4 | 45 | 0.07 | 106 | 307 | 5 | 127 | 220 | 0 | 0 | 610 | 17 | 4038.83 | 10790.16 | 90.04
09:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 18 | 0 | 114 | 116 | 300 | 55 | 0.8 | 17 | 8 | 0 | 225 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 14 | 0 | 20 | 22 | 0 | 485 | 35 | 50 | 24 | 0 | 4 | 84 | 24 | 44 | 100 | 98 | 1 | 40 | 110 | 2 | 575 | 36 | 0 | 38 | 0 | 105 | 227 | 0 | 0 | 0 | 612 | 12 | 43 | 115 | 197 | 0 | 0 | 270 | 29 | 182 | 36 | 0 | 40 | 182 | 9 | 12 | 70 | 66 | 52.2 | 10 | 0 | 285 | 320 | 0 | 35 | 30 | 30 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 35 | 9 | 56 | 26 | 1 | 8.86 | 6 | 6748.86 | 878 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.48 | 0 | 0 | 758.65 | 0 | 0 | 0 | 113 | 0 | 0 | 95 | 0 | 0 | 46 | 0 | 29.08 | 0 | 0 | 0 | 0 | 126 | 0 | 250 | 0 | 1.61 | 2.5 | 0 | 0 | 38 | 15 | 75 | 0 | 0 | 0 | 92 | 0.17 | 110 | 307 | 5 | 127 | 220 | 0 | 0 | 560 | 17 | 4061.49 | 10810.35 | 90.03
10:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 0 | 18 | 0 | 116 | 116 | 245 | 15 | 17 | 35 | 8 | 0 | 225 | 0 | 0 | 0 | 35 | 16 | 8 | 0 | 0 | 20 | 17 | 19 | 22 | 0 | 450 | 35 | 50 | 50 | 0 | 3 | 84 | 26 | 17 | 100 | 50 | 3 | 40 | 110 | 2 | 576 | 36 | 0 | 19 | 4 | 105 | 227 | 0 | 0 | 0 | 612 | 16 | 43 | 117 | 195 | 0 | 0 | 265 | 29 | 184 | 36 | 0 | 40 | 190 | 9 | 9 | 17 | 74 | 24 | 22 | 23 | 280 | 320 | 0 | 32 | 30 | 20 | 2 | 163 | 20 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 27 | 9 | 11 | 2 | 26.66 | 6 | 6590.66 | 926 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 756.71 | 0 | 0 | 0 | 113 | 0 | 0 | 50 | 0 | 0 | 69 | 0 | 43.33 | 0 | 0 | 0 | 0 | 153 | 0 | 250 | 0 | 3.86 | 2.5 | 0 | 0 | 75 | 24 | 91 | 0 | 0 | 4 | 100 | 0.34 | 110 | 307 | 5 | 127 | 220 | 0 | 0 | 560 | 17 | 4186.55 | 10777.21 | 90.03
11:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 407 | 0 | 0 | 17 | 18 | 0 | 131 | 116 | 145 | 15 | 17 | 35 | 8 | 0 | 225 | 0 | 0 | 0 | 35 | 16 | 1 | 0 | 0 | 26 | 17 | 19 | 22 | 0 | 500 | 35 | 52 | 51 | 0 | 0 | 84 | 31 | 17 | 100 | 75 | 3 | 40 | 110 | 2 | 575 | 36 | 0 | 19 | 0 | 105 | 223 | 0 | 0 | 0 | 612 | 18 | 43 | 60 | 195 | 0 | 0 | 270 | 29 | 183 | 32 | 0 | 40 | 200 | 9 | 12 | 52 | 76 | 43 | 55 | 31 | 290 | 320 | 0 | 32 | 28 | 20 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 93 | 9 | 11 | 2 | 41.62 | 6 | 6742.62 | 926 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.21 | 0 | 0 | 760.04 | 0 | 0 | 0 | 113 | 0 | 0 | 50 | 0 | 0 | 69 | 0 | 52.94 | 0 | 0 | 0 | 0 | 160 | 0 | 320 | 0 | 4.61 | 2.5 | 0 | 0 | 95 | 30 | 91 | 0 | 0 | 5.2 | 100 | 0.5 | 64 | 307 | 5 | 132 | 220 | 0 | 0 | 600 | 17 | 4313 | 11055.62 | 90.03
12:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 408 | 0 | 0 | 17 | 18 | 0 | 133 | 98 | 152 | 15 | 17 | 35 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 16 | 18 | 0 | 0 | 26 | 17 | 19 | 22 | 0 | 550 | 37 | 15 | 51 | 0 | 0 | 68 | 33 | 0 | 89 | 75 | 4 | 40 | 68 | 2 | 577 | 36 | 0 | 19 | 3 | 105 | 222 | 0 | 0 | 0 | 612 | 19 | 43 | 78 | 192 | 0 | 0 | 295 | 29 | 190 | 35 | 0 | 40 | 200 | 9 | 12 | 52 | 84 | 52.2 | 60 | 42 | 320 | 320 | 0 | 32 | 29 | 20 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 112 | 9 | 11 | 2 | 45.29 | 6 | 6790.49 | 924 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.21 | 0 | 0 | 762.05 | 0 | 0 | 0 | 113 | 0 | 0 | 95 | 9 | 0 | 77 | 0 | 56.36 | 0 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 4.77 | 2.5 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 5.8 | 100 | 0.38 | 78 | 307 | 5 | 130 | 220 | 0 | 0 | 600 | 17 | 4331.07 | 11121.56 | 90.02
13:00 | 0 | 52 | 0 | 0 | 0 | 223 | 0 | 0 | 410 | 0 | 0 | 17 | 18 | 0 | 131 | 112 | 258 | 37 | 17 | 35 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 15 | 33 | 0 | 0 | 26 | 17 | 19.5 | 22 | 0 | 350 | 106 | 50 | 49 | 0 | 2 | 85 | 50 | 0 | 89 | 76 | 2 | 40 | 72 | 3 | 577 | 36 | 0 | 27 | 8 | 105 | 222 | 0 | 0 | 0 | 612 | 19 | 43 | 112 | 190 | 0 | 0 | 295 | 29 | 191 | 35 | 13 | 40 | 200 | 9 | 12 | 80 | 84 | 52.2 | 39 | 46 | 300 | 297 | 0 | 34 | 29 | 20 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 27 | 115 | 9 | 10 | 2 | 46.02 | 6 | 6923.72 | 926 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.17 | 0 | 0 | 758.01 | 0 | 0 | 0 | 113 | 4 | 48 | 95 | 16 | 0 | 87 | 0 | 55 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 0 | 4.97 | 2.5 | 0 | 0 | 90 | 32 | 95 | 0 | 0 | 5.5 | 99 | 0.41 | 110 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 35 | 4657.56 | 11581.28 | 90.02
14:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 367 | 0 | 0 | 17 | 18 | 0 | 131 | 112 | 298 | 55 | 17 | 35 | 8 | 0 | 225 | 0 | 0 | 0 | 0 | 5 | 26 | 0 | 0 | 22 | 0 | 19.5 | 22 | 0 | 350 | 122 | 15 | 49 | 0 | 2 | 85 | 78 | 0 | 89 | 76 | 1 | 40 | 68 | 2 | 577 | 36 | 0 | 37 | 8 | 68 | 223 | 0 | 0 | 0 | 612 | 17 | 43 | 112 | 190 | 0 | 0 | 280 | 29 | 190 | 35 | 34 | 40 | 200 | 9 | 12 | 98 | 76 | 52.2 | 21 | 46 | 285 | 320 | 0 | 34 | 29 | 40 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 115 | 9 | 11 | 2 | 38.29 | 6 | 6866.99 | 927 | 160 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.95 | 0 | 0 | 757.89 | 0 | 0 | 0 | 113 | 7 | 49 | 95 | 16 | 0 | 76 | 0 | 49.55 | 0 | 0 | 0 | 0 | 152 | 0 | 320 | 0 | 4.63 | 2.5 | 0 | 0 | 95 | 27 | 93 | 0 | 0 | 5.1 | 95 | 0.46 | 110 | 250 | 3 | 100 | 180 | 0 | 0 | 560 | 54 | 4355.08 | 11222.07 | 90.02
15:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 378 | 0 | 0 | 17 | 18 | 0 | 131 | 96 | 195 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 15 | 94 | 0 | 0 | 18 | 0 | 19 | 22 | 0 | 350 | 122 | 15 | 50 | 0 | 2 | 84 | 78 | 0 | 24 | 24 | 2 | 40 | 34 | 3 | 578 | 17 | 0 | 40 | 8 | 34 | 223 | 0 | 0 | 0 | 612 | 13 | 43 | 113 | 190 | 0 | 0 | 300 | 29 | 202 | 35 | 34 | 50 | 155 | 9 | 12 | 52 | 80 | 52.2 | 38 | 46 | 315 | 320 | 0 | 34 | 29 | 38 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 58 | 9 | 11 | 1 | 28.85 | 6 | 6572.05 | 926 | 153 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 37.99 | 0 | 0 | 752 | 0 | 0 | 0 | 113 | 23 | 49 | 95 | 23 | 0 | 60 | 0 | 37.56 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 3.49 | 2.5 | 0 | 0 | 54 | 20 | 99 | 0 | 0 | 3.2 | 102 | 0.31 | 110 | 250 | 4 | 130 | 220 | 0 | 0 | 560 | 54 | 4459.05 | 11031.1 | 90.02
16:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 17 | 18 | 0 | 124 | 105 | 145 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 15 | 123 | 0 | 0 | 11 | 0 | 18.8 | 22 | 0 | 450 | 122 | 15 | 50 | 0 | 2 | 83 | 78 | 0 | 24 | 24 | 1 | 40 | 34 | 2 | 578 | 17 | 0 | 45 | 8 | 34 | 225 | 0 | 0 | 0 | 612 | 8 | 43 | 50 | 190 | 0 | 0 | 310 | 29 | 194 | 32 | 34 | 50 | 100 | 9 | 12 | 52 | 80 | 43 | 27 | 46 | 310 | 320 | 0 | 34 | 29 | 38 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 58 | 19 | 17 | 1 | 16.96 | 1 | 6569.76 | 926 | 153 | 0 | 9 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 2.55 | 0 | 0 | 760 | 0 | 0 | 0 | 50 | 22 | 49 | 50 | 23 | 0 | 33 | 24 | 22.79 | 0 | 0 | 0 | 0 | 149 | 0 | 414 | 0 | 2.05 | 2.5 | 0 | 0 | 54 | 11 | 49 | 0 | 0 | 2 | 61 | 0.07 | 64 | 307 | 5 | 130 | 220 | 0 | 0 | 560 | 54 | 4228.96 | 10798.72 | 90.01
17:00 | 0 | 52 | 0 | 0 | 0 | 180 | 0 | 0 | 361 | 0 | 0 | 17 | 21 | 0 | 124 | 128 | 145 | 55 | 17 | 54 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 20 | 322 | 0 | 0 | 3 | 0 | 18.8 | 22 | 0 | 400 | 122 | 15 | 51 | 0 | 0 | 84 | 78 | 0 | 24 | 24 | 0 | 40 | 34 | 4 | 576 | 17 | 0 | 47 | 1 | 34 | 225 | 0 | 0 | 0 | 612 | 2 | 51 | 50 | 192 | 0 | 0 | 310 | 29 | 186 | 35 | 34 | 50 | 100 | 9 | 12 | 52 | 74 | 43 | 4 | 46 | 305 | 320 | 0 | 34 | 29 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 59 | 19 | 18 | 0 | 5.11 | 6 | 6577.91 | 926 | 153 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 3.74 | 0 | 0 | 758 | 0 | 50 | 0 | 50 | 22 | 49 | 50 | 23 | 0 | 11 | 24 | 6.24 | 0 | 0 | 0 | 0 | 147 | 0 | 360 | 0 | 0.66 | 2.5 | 0 | 0 | 54 | 3 | 49 | 0 | 0 | 0.7 | 17 | 0.07 | 64 | 307 | 5 | 130 | 220 | 0 | 0 | 500 | 137 | 4177.91 | 10755.82 | 90.01
18:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 351 | 0 | 0 | 17 | 54 | 0 | 124 | 130 | 172 | 55 | 17 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 17 | 20 | 328 | 0 | 0 | 0 | 0 | 18.5 | 22 | 0 | 320 | 122 | 30 | 50 | 0 | 0 | 84 | 78 | 0.48 | 92 | 65 | 0 | 40 | 35 | 2 | 575 | 54 | 0 | 47 | 25 | 53 | 225 | 0 | 0 | 0 | 612 | 0 | 51 | 73 | 192 | 0 | 0 | 285 | 29 | 182 | 35 | 49 | 50 | 117 | 9 | 18 | 100 | 84 | 52.2 | 0 | 46 | 295 | 320 | 0 | 30 | 30 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 59 | 19 | 26 | 0 | 0 | 6 | 6940.18 | 925 | 153 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 50 | 0 | 70 | 30 | 90 | 90 | 27 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 320 | 0 | 0 | 2.5 | 0 | 0 | 94 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 90 | 307 | 6 | 100 | 220 | 0 | 0 | 520 | 137 | 4280.5 | 11220.68 | 90
19:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 124 | 130 | 300 | 55 | 17 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 17 | 20 | 328 | 0 | 0 | 0 | 12 | 18.5 | 22 | 0 | 320 | 122 | 100 | 50 | 0 | 0 | 85 | 79 | 29 | 100 | 100 | 0 | 40 | 75 | 5 | 575 | 145 | 0 | 47 | 25 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 192 | 0 | 0 | 300 | 29 | 188 | 35 | 95 | 50 | 178 | 9 | 18 | 114 | 76 | 52.2 | 0 | 47 | 315 | 320 | 0 | 30 | 30 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 28 | 0 | 0 | 6 | 7695.7 | 877 | 158 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 50 | 0 | 113 | 28 | 90 | 95 | 30 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 94 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 137 | 4554.5 | 12250.2 | 90
19:30 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 17 | 54 | 0 | 124 | 132 | 245 | 15 | 17 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 35 | 20 | 280 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 320 | 108 | 115 | 50 | 0 | 0 | 85 | 72 | 17 | 100 | 50 | 0 | 40 | 110 | 2 | 575 | 145 | 0 | 19 | 25 | 105 | 226 | 0 | 0 | 0 | 617 | 0 | 51 | 113 | 194 | 0 | 0 | 320 | 29 | 198 | 35 | 95 | 50 | 200 | 9 | 18 | 70 | 76 | 26 | 0 | 24 | 310 | 320 | 0 | 34 | 30 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 59 | 9 | 30 | 0 | 0 | 6 | 7479 | 877 | 158 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 50 | 0 | 113 | 23 | 90 | 95 | 27 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 180 | 0 | 0 | 622 | 137 | 4526.5 | 12005.5
20:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 395 | 0 | 0 | 17 | 54 | 0 | 124 | 131 | 195 | 0 | 17 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 35 | 19 | 280 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 320 | 90 | 116 | 51 | 0 | 0 | 85 | 80 | 17 | 100 | 50 | 0 | 40 | 110 | 9 | 575 | 145 | 0 | 19 | 25 | 105 | 226 | 0 | 0 | 0 | 613 | 0 | 51 | 113 | 195 | 0 | 0 | 305 | 29 | 182 | 36 | 94 | 50 | 200 | 9 | 18 | 56 | 68 | 25 | 0 | 24 | 295 | 320 | 0 | 34 | 30 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 42 | 59 | 9 | 29 | 0 | 0 | 6 | 7293 | 877 | 157 | 0 | 25 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 50 | 0 | 113 | 23 | 90 | 113 | 35 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 180 | 0 | 0 | 622 | 137 | 4563.5 | 11856.5 | 90
21:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 18 | 0 | 129 | 131 | 195 | 0 | 17 | 54 | 16 | 0 | 225 | 0 | 0 | 0 | 35 | 19 | 280 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 320 | 72 | 123 | 51 | 0 | 0 | 85 | 80 | 17 | 100 | 50 | 0 | 40 | 110 | 3 | 576 | 90 | 0 | 19 | 25 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 112 | 195 | 0 | 0 | 305 | 29 | 183 | 36 | 91 | 50 | 200 | 9 | 18 | 0 | 66 | 25 | 0 | 24 | 300 | 320 | 0 | 35 | 30 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 59 | 9 | 29 | 0 | 0 | 6 | 7030 | 923 | 162 | 0 | 25 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759.42 | 0 | 50 | 0 | 113 | 28 | 90 | 113 | 30 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 94 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 130 | 180 | 0 | 0 | 622 | 137 | 4632.92 | 11662.92 | 89.99
22:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 18 | 0 | 123 | 98 | 145 | 0 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 35 | 19 | 280 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 320 | 58 | 51 | 45 | 0 | 0 | 85 | 80 | 0 | 100 | 50 | 0 | 40 | 110 | 18 | 577 | 0 | 0 | 18 | 0 | 105 | 226 | 0 | 0 | 0 | 613 | 0 | 51 | 112 | 195 | 0 | 0 | 345 | 29 | 208 | 36 | 51 | 50 | 200 | 9 | 18 | 0 | 60 | 0 | 0 | 24 | 295 | 320 | 0 | 35 | 0 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 59 | 9 | 29 | 0 | 0 | 6 | 6673 | 923 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.02 | 0 | 50 | 0 | 113 | 23 | 90 | 50 | 30 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 54 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 130 | 180 | 0 | 0 | 622 | 137 | 4447.52 | 11120.52 | 89.99
23:00 | 0 | 70 | 0 | 0 | 0 | 231 | 0 | 0 | 350 | 0 | 0 | 17 | 18 | 0 | 113 | 98 | 145 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 53 | 51 | 0 | 0 | 0 | 85 | 80 | 0 | 100 | 50 | 0 | 40 | 110 | 22 | 575 | 0 | 0 | 0 | 0 | 105 | 228 | 0 | 0 | 0 | 612 | 0 | 51 | 107 | 195 | 0 | 0 | 320 | 29 | 191 | 36 | 0 | 40 | 155 | 9 | 18 | 0 | 60 | 0 | 0 | 24 | 315 | 320 | 0 | 11 | 0 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 59 | 9 | 26 | 0 | 0 | 6 | 6356 | 923 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763.19 | 0 | 50 | 0 | 113 | 18 | 90 | 50 | 30 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 52 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 180 | 0 | 0 | 622 | 137 | 4453.69 | 10809.69 | 89.99
Total KWH | 0 | 1147200 | 0 | 0 | 0 | 5416219 | 0 | 0 | 9126000 | 0 | 0 | 26100 | 506880 | 0 | 2132352 | 2007840 | 3786720 | 529496 | 264628 | 799200 | 270720 | 0 | 5386000 | 0 | 0 | 0 | 265739 | 510000 | 2531674 | 0 | 0 | 172594 | 129600 | 440400 | 529200 | 0 | 10426363.64 | 1430182 | 998618 | 685440 | 0 | 49440 | 1347114 | 1060608 | 247149 | 2091840 | 1092480 | 17520 | 961560 | 2248970 | 304800 | 13810909.09 | 725964 | 0 | 481920 | 198847.8 | 2280763 | 5316625 | 0 | 0 | 0 | 14732730 | 133515 | 1082858 | 1889668 | 4666909 | 0 | 0 | 7172000 | 697440 | 4826000 | 850320 | 556800 | 1026180 | 3610080 | 215880 | 345810 | 831060 | 1626240 | 621965 | 271191 | 515328 | 7263500 | 7673400 | 0 | 765576 | 626000 | 756240 | 58080 | 3511472.72 | 559008 | 0 | 2046720 | 718464 | 0 | 0 | 0 | 411480 | 1147200 | 465600 | 562560 | 12900 | 263470 | 131760 | 154401080.25 | 22196363 | 3790080 | 0 | 156480 | 104832 | 0 | 0 | 0 | 0 | 0 | 0 | 343440 | 0 | 0 | 18174437 | 0 | 378594 | 0 | 2417088 | 220060 | 803712 | 1515168 | 255668 | 48778 | 560740 | 196888 | 369744 | 972273 | 0 | 0 | 0 | 2932264 | 0 | 8612872.7 | 0 | 32820 | 78120 | 0 | 0 | 1171762 | 198393 | 1611955 | 0 | 0 | 33455.88 | 792000 | 3001 | 1788576 | 7265000 | 142171 | 2902000 | 4864950 | 0 | 0 | 14542545.45 | 1332000 | 100808231.03 | 255209311.28

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11121.56 | MW | 12:00 Hr. | Energy Generated |  |  | 255.2093 |  | MKWHr.
| Day Peak Demand |  |  | 11193.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.145 |  | MKWHr.
| Evening Peak Generation |  |  | 12250.2 | MW | 19:00 Hr. | Energy Demand |  |  | 256.3543 |  | MKWHr.
| Evening Peak Demand |  |  | 12312.9 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30.4 |  | °C
| Minimum Generation of the Day |  |  | 8579.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 858.8 |  | MMCFD
| Maximum Generation of the Day |  |  | 12250.2 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 7.4786 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.6366 | 0 | 11.5958 | 0 | 0 | 0.17259 | 0 | 0 | 46.4049 | Gas | 109.7613 | Gas | 395204817.1662
| Chattogram Zone |  |  | 5.6214 | 28.5436 | 14.8899 | 0 | 0.96156 | 0.15104 | 0 | 0.04944 | 50.217 | Coal | 50.3512 | Coal | 339386840.3267
| Cumilla Zone |  |  | 20.6675 | 0 | 8.2408 | 0 | 0 | 0.27119 | 1.6262 | 0 | 30.8057 | HFO | 48.884 | HFO | 903446824.296
| Mymensingh Zone |  |  | 0.56256 | 0 | 2.156 | 0 | 0 | 0.27637 | 0 | 0 | 2.995 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.9785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9785 | Hydro | 0.96156 | Hydro | 96156
| Khulna Zone |  |  | 3.7901 | 0 | 0.26131 | 0 | 0 | 0.34344 | 22.1964 | 0 | 26.5912 | Solar | 3.2048 | Solar | 52122159.8868
| Barishal Zone |  |  | 7.9091 | 21.8075 | 3.1206 | 0 | 0 | 0.003001 | 0 | 0 | 32.8402 | Import | 41.997 | Import | 217618505.25
| Rajshahi Zone |  |  | 12.5955 | 0 | 5.836 | 0 | 0 | 0.9633 | 18.1744 | 0 | 37.5692 | Wind | 0.04944 | Wind | 723801.6
| Rangpur Zone |  |  | 0 | 0 | 2.7837 | 0 | 0 | 1.0238 | 0 | 0 | 3.8076
| Total |  |  | 109.7613 | 50.3512 | 48.884 | 0 | 0.96156 | 3.2048 | 41.997 | 0.04944 | 255.2093
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 395204817.1662 |  | Hydro | 96156
|  |  |  | Coal | 339386840.3267 |  | Solar | 52122159.8868
|  |  |  | HFO | 903446824.296 |  | Import | 217618505.25
|  |  |  | HSD | 0 |  | Wind | 723801.6
[5 empty] | Total: | 190,85,99,104 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1964 | Peak Hr Flow | 877.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6888045000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.1744 | Peak Hr Flow | 757.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 440 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6262 | Peak Hr Flow | 76.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 811 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.997 | Peak Hr Flow | 1710.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4523
|  |  |  | Chattogram |  | 0 |  | 1293
|  |  |  | Cumilla |  | 0 |  | 983
|  |  |  | Mymensingh |  | 60 |  | 1000
|  |  |  | Sylhet |  | 0 |  | 412
|  |  |  | Khulna |  | 0 |  | 1279
|  |  |  | Barishal |  | 0 |  | 328
|  |  |  | Rajshahi |  | 0 |  | 1171
|  |  |  | Rangpur |  | 0 |  | 812
|  |  |  | Total |  | 60 |  | 11801
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 660 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1326.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 09:31 | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to DS maintenance
| 08:29 | 15:25 | Ghorasal- Ishwardi 230 kV Ckt-2 Scheduled S/D from Ghorashal 230kV end Due to
Requisition form Dhamrai Grid for Disc cleaning work and from Ishurdi 230/132kVend.
| 08:36 | 09:10 | Ramganj 132/33kV S/S 132 Kv Bus- A Scheduled S/D Due to 132kV Main Bus-1 DS maintenance
of 132kV Desh Energy Ckt-2
| 08:38 | 17:18 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end. and
from Narshingdi 132/33kV end Due to Maintenance
| 08:52 | 19:16 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual dead line checking & disx cleaning and from Meghnaghat 400/230kV end Due to
Aminbazar ckt-2 shutdown by NLDC
| 09:12 | 09:35 | Ramganj 132/33kV S/S 132 Kv Bus-B Scheduled S/D Due to 132kV Main Bus-2 DS maintenance of
132kV Desh Energy Ckt-2
| 09:20 | 17:27 | Madunaghat 400/230kV S/S ATR-2 7106T HT Scheduled S/D Due to Project work
| 09:20 | 17:28 | Madunaghat 400/230kV S/S ATR-2 7106T LT Scheduled S/D Due to Project Work
| 09:20 | 12:10 | Hathazari-Kaptai 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to annual
maintenance
| 09:20 | 13:13 | GPH-Hathazari 230kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to Red hot
maintenance
| 09:22 | 13:13 | GPH 230/33kV S/S HATHAZARI Forced S/D Due to finding red hot, in hathajari line. R and Y
phase
| 09:27 | 15:17 | Baghabari 230/132kV S/S T-2 Bank LT Scheduled S/D Due to Relay replace
| 09:27 | 15:15 | Baghabari 230/132kV S/S T-2 Bank HT Scheduled S/D Due to Relay replace
| 09:34 |  | Siddirganj 335MW CCPP GT was sync.
| 09:37 | 16:30 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual maintenance
| 09:44 |  | Hathazari 230/132/33kV S/S MT-04 HT Scheduled S/D Due to oil leakage maintenance
| 09:44 |  | Hathazari 230/132/33kV S/S MT-04 LT Scheduled S/D Due to oil leakage maintenance
| 10:04 | 18:58 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to Dead Line
checking for Chhatak end
| 10:10 |  | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to T-2, 132 kv CSE installation & XLPE
cable Termination. With T-2 33KV CB Change.
| 10:11 | 18:06 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Project Work S/D Due to Line check
| 10:13 | 18:10 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Project Work S/D Due to Line check
| 10:23 | 13:56 | Savar 132/33kV S/S T-4 LT Scheduled S/D Due to interlock checkup
| 10:23 | 13:56 | Savar 132/33kV S/S T-4 HT Scheduled S/D Due to Interlock checkup
| 10:35 | 13:12 | Bogura 132/33kV S/S 132KV Bus-A Project Work S/D Due to Due to T-1 132kv Bus A loop
Connection.
|  | 11:01 | Madunaghat 132/33kV S/S TR-1(507T) LT is restored.
| 11:29 | 13:05 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to PBS 33 kv barpa feeder ds red hot | [7 empty] | 45.0MW load
|  |  | maintenance near 33 kv bus | [7 empty] | interrup.
| 11:30 | 13:06 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to PBS 33 kv barpa feeder ds red hot | [7 empty] | 45.0MW load
|  |  | maintenance near 33 kv bus | [7 empty] | interrup.
| 11:48 | 12:19 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing 50/51 OC Relay relays Due to Due over | [7 empty] | 27.0MW load
|  |  | current | [7 empty] | interrup.
| 11:48 | 12:19 | Jaldhaka 132/33kV S/S 416T-2 LT Tripped showing 50/51 OC relay relays Due to Due over | [7 empty] | 27.0MW load
|  |  | current | [7 empty] | interrup.
| 11:51 |  | Siddirganj 335MW CCPP ST was sync.
| 12:00 |  | Day Peak Generation: 11118 MW
| 12:15 | 13:54 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
maintenance
| 12:43 | 13:21 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing distance
protection 21/1 z1, AN relays Due to distance 21/z1 PI 1 (dist/def)
| 12:56 | 17:15 | Bogura-Sirajganj 230 kV Ckt-1 Project Work S/D from Bogura 230/132kV end Due to Project
work
| 13:11 | 17:18 | Bogura-Sirajganj 230 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to Project
work and from Sirajgonj 230 end Due to Removing Cradle Guard at Span
| 13:12 | 17:16 | Bogura-Sirajganj 230 kV Ckt-1 Project Work S/D from Sirajgonj 230 end Due to Removing
cradle guard at span
|  | 14:10 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 14:11 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
|  | 14:17 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 14:18 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
| 15:10 | 16:05 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Tr-3 Transformer Oil Leakage
Maintenance Work.
| 15:10 | 16:05 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Tr-3 Oil Leakage Maintenance Work.
| 19:00 |  | Evening Peak Gen. 12250 MW
| 07:47 |  | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to Copper bar change
| 07:47 |  | Bhandaria 132/33kV S/S Transformer-1 HT Project Work S/D Due to Copper ber change
| 07:47 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Shutdown instructed by NLDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 5416219 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9126000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5386000 | Unit-2 shut down for leak repairing
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 529496 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 2531674 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 26100 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 130 | 2007840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 264628 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 265739 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.5 | 440400 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 529200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16 | 270720 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 510000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | line SD
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 3786720 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 124 | 2132352 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1147200 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 799200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 172594 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 506880 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 10426363.64 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 12 | 129600 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2466.5 | 46404925.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 198847.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133515 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 481920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 961560 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5316625 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2280763 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 79 | 1060608 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 1347114 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2091840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 304800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 685440 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 17520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 998618 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 29 | 247149 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 75 | 2248970 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1092480 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 122 | 1430182 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 145 | 725964 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14732730 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 49440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 13810909.09 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2520 | 50216994.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4826000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 300 | 7172000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 850320 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 697440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 192 | 4666909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1082858 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 1889668 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 47 | 515328 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1026180 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 178 | 3610080 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1626240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 621965 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 345810 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 831060 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 215880 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 556800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 271191 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1534.2 | 30805729
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 28 | 562560 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 465600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1147200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 263470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 131760 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 411480 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 137 | 2994970
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 626000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 756240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3511472.72 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 30 | 765576 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58080 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718464 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2046720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 559008 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7263500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7673400 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1038 | 23978460.72
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 22196363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 25 | 156480 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 104832 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 158 | 3790080 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 343440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1060 | 26591195
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1788576 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 142171 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2902000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14542545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4864950 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1332000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7265000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3001 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1533 | 32840243.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 378594 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 28 | 220060 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 30 | 255668 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 972273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 147 | 2932264 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8612872.7 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 24 | 196888 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 78120 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 48778 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 803712 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2417088 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1515168 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 757 | 18174437 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 369744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 560740 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1761.5 | 37569226.7
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1611955 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33455.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 1171762 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 198393 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 792000 | -
Rangpur Area Total |  |  |  |  | 950 | 200 | 3807565.88
Eastern Grid Total |  |  |  |  | 16856.242 | 7695.7 | 154401080.25
Western Grid Total |  |  |  |  | 10294.5 | 4554.5 | 100808231.03
National Grid Total |  |  |  |  | 27150.742 | 12250.2 | 255209311.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8151.16 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3590.1 | MW
i) Dhaka area |  |  | 4522.86 |  | MW | i) Khulna area |  |  |  | 1279.2 | MW
ii) Chattogram area |  |  | 1293.3 |  | MW | ii) Barishal area |  |  |  | 327.5 | MW
iii) Cumilla area |  |  | 983 |  | MW | iii) Rajshahi area |  |  |  | 1171.4 | MW
iv) Mymensingh area |  |  | 940 |  | MW | iv) Rangpur area |  |  |  | 812 | MW
v) Sylhet area |  |  | 412 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11741.26 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 58 | 18:30 | 133 | Postogola | 43 | 18:30
2 | AKSML | 111 | 01:00 | 68 | Jamalpur | 90 | 00:00 | 134 | Purbachal | 15 | 14:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 122 | 13:00 | 135 | Purbasadipur | 126 | 13:00
4 | Agargaon | 87 | 13:00 | 70 | Jhenaidah | 101 | 08:00 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 80 | 19:00 | 71 | Joydebpur | 150 | 18:30 | 137 | Rahim | 40 | 15:00
6 | Amnura | 57 | 10:00 | 72 | Joypurhat | 61 | 08:00 | 138 | Rajbari | 56 | 19:00
7 | Ashuganj | 73 | 15:00 | 73 | Juldah | 17 | 10:00 | 139 | Rajendrapur | 118 | 19:00
8 | BSRM | 200 | 22:00 | 74 | KSRM | 30 | 09:00 | 140 | Rajshahi | 82 | 20:00
9 | Bagerhat | 65 | 19:00 | 75 | Kabirpur | 247 | 16:00 | 141 | Rajshahi-230 | 62 | 13:00
10 | Bajitpur | 21 | 23:00 | 76 | Kachua | 58 | 18:30 | 142 | Ramganj | 84 | 23:00
11 | Bakulia | 80 | 18:30 | 77 | Kallyanpur | 81 | 12:00 | 143 | Rampur | 31 | 18:00
12 | Banani | 24.4 | 13:00 | 78 | Kalurghat | 34 | 10:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 11 | 10:00 | 79 | Kamrangirchar | 62.8 | 19:00 | 145 | Rangpur | 115 | 18:30
14 | Barapukuria | 59 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 5.4 | 16:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 96 | 17:00 | 147 | SSM | 17 | 00:00
16 | Barishal | 77 | 12:00 | 82 | Keranigonj | 66 | 18:30 | 148 | Saidpur | 105 | 10:00
17 | Barishal-230 | 78 | 19:00 | 83 | Khagrachori | 22 | 18:30 | 149 | Satkhira | 98 | 08:00
18 | Baroaulia | 66 | 11:00 | 84 | Khulna | 72 | 13:00 | 150 | Satmasjid | 88 | 13:00
19 | Baroirhat | 44 | 13:00 | 85 | Khulshi | 163 | 12:00 | 151 | Savar | 188 | 16:00
20 | Bashundhara | 140 | 12:00 | 86 | Kishoreganj | 97 | 11:00 | 152 | SevenRings | 19.13 | 04:00
21 | BashundharaCement | 7 | 08:00 | 87 | Kodda | 204 | 18:30 | 153 | ShahCement | 35 | 00:00
22 | Beanibazar | 46 | 18:30 | 88 | Kulaura | 28 | 18:30 | 154 | Shahjadpur | 69 | 19:00
23 | Benapole | 48 | 08:00 | 89 | Kurigram | 64 | 08:00 | 155 | Shahjibazar | 95 | 19:00
24 | Bhaluka | 110 | 19:00 | 90 | Kushtia | 106 | 18:30 | 156 | Shahmirpur | 46 | 14:00
25 | Bhandaria | 41 | 19:30 | 91 | Lalbag | 61 | 19:00 | 157 | Shariatpur | 56 | 21:00
26 | Bhangura | 32 | 08:00 | 92 | Lalmonirhat | 50 | 18:30 | 158 | Sherpur | 120 | 00:00
27 | Bheramara(GK) | 42 | 18:30 | 93 | MI_Cement | 17.3 | 13:00 | 159 | Shikalbaha | 23 | 18:30
28 | Bhulta | 259 | 20:00 | 94 | Madanganj | 29 | 12:00 | 160 | Shitalakhya | 69.8 | 13:00
29 | Bog-Sherpur | 72 | 08:00 | 95 | Madaripur | 72 | 21:00 | 161 | Sholosohor | 36 | 11:00
30 | Bogura | 119 | 19:30 | 96 | Madartek | 69.56 | 18:30 | 162 | Shyampur | 154 | 23:00
31 | Borhanuddin | 57 | 21:00 | 97 | Madunaghat | 38 | 18:00 | 163 | Siddhirganj | 120 | 12:00
32 | Brahmanbaria | 115 | 18:30 | 98 | Magura | 48 | 18:30 | 164 | Sirajganj | 94 | 19:00
33 | Cantonment | 106 | 13:00 | 99 | Mahasthangarh | 58 | 08:00 | 165 | Sonargaon | 85 | 06:00
34 | Chandpur | 48 | 19:30 | 100 | Manikganj | 109 | 19:00 | 166 | Sreemongol | 46 | 18:00
35 | Chandraghona | 25 | 18:30 | 101 | Maniknagar | 58 | 12:00 | 167 | Sreepur | 102 | 18:30
36 | Chapai | 71 | 08:00 | 102 | Matarbari | 45 | 18:30 | 168 | Srinagar | 31.4 | 14:00
37 | Charsaidpur | 39 | 00:00 | 103 | Matuail | 64 | 14:00 | 169 | Sunamganj | 42 | 18:30
38 | Chauddagram | 56 | 14:00 | 104 | Millgate | 77 | 12:00 | 170 | Sylhet | 26 | 12:00
39 | Chhatak | 25 | 18:30 | 105 | Mirpur | 111 | 18:30 | 171 | Sylhet-132 | 87 | 18:00
40 | Chowmuhani | 157 | 18:30 | 106 | Mirsorai | 9 | 13:00 | 172 | TK | 22 | 18:00
41 | Chuadanga | 76 | 18:30 | 107 | Mirzapur | 41 | 16:00 | 173 | Tangail | 160 | 15:00
42 | Coxsbazar | 114 | 19:30 | 108 | Mithapukur | 56 | 08:00 | 174 | Thakurgaon | 79 | 08:00
43 | Cumilla(N) | 158 | 12:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 102 | 15:00
44 | Cumilla(S) | 116 | 12:00 | 110 | Mogbazar | 111.3 | 15:00 | 176 | Ullahpara | 29 | 07:00
45 | Daudkandi | 101 | 20:00 | 111 | Mongla | 41 | 12:00 | 177 | Ullon | 39 | 13:00
46 | Dhaka | 38 | 13:00 | 112 | Motijheel | 34 | 18:00 | 178 | Uttara | 69 | 13:00
47 | Dhamrai | 110 | 11:00 | 113 | Muktagacha | 29 | 15:00 | 179 | UttaraNew | 37 | 13:00
48 | Dhanmondi | 115.4 | 13:00 | 114 | Munshiganj | 71 | 21:00 | 180 | Zigatola | 66 | 13:00
49 | Dohazari | 71 | 18:30 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 111 | 18:30 | 116 | Mymensingh | 175 | 13:00
51 | Fatullah | 78 | 10:00 | 117 | Naogaon | 114 | 08:00
52 | Fenchuganj | 30 | 18:30 | 118 | Narail | 44 | 08:00
53 | Feni | 82 | 19:00 | 119 | Narinda | 72 | 13:00
54 | GPH | 92 | 19:00 | 120 | Narshingdi | 142 | 19:00
55 | Ghatail | 52 | 17:00 | 121 | Natore | 112 | 13:00
56 | Ghorashal | 14 | 19:30 | 122 | Nawabganj | 31.8 | 13:00
57 | Ghorashal-230 | 68 | 18:00 | 123 | Netrakona | 138 | 07:00
58 | Goalpara | 24 | 13:00 | 124 | New | 78 | 12:00
59 | Gollamari | 60 | 13:00 | 125 | Niamatpur | 96 | 08:00
60 | Gopalganj | 79.2 | 19:00 | 126 | Noapara | 37 | 18:30
61 | Gulshan | 94 | 13:00 | 127 | PHP | 9 | 07:00
62 | Halishahar | 59.5 | 11:00 | 128 | Pabna | 78 | 19:00
63 | HaripurSBU | 170 | 01:00 | 129 | Palashbari | 108 | 08:00
64 | Hasnabad | 82 | 18:00 | 130 | Panchagarh | 47 | 18:30
65 | Hathazari | 63 | 13:00 | 131 | Patuakhali | 54 | 19:30
66 | Ishurdi | 63 | 19:00 | 132 | Payra | 22 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 10303.5 | 0 |  | 10303.5
1:00 | 9665 | 0 |  | 9665
2:00 | 9049.5 | 0 |  | 9049.5
3:00 | 8857.5 | 0 |  | 8857.5
4:00 | 8619.5 | 0 |  | 8619.5
5:00 | 8579.5 | 0 |  | 8579.5
6:00 | 8766 | 0 |  | 8766
7:00 | 9908.48 | 61 |  | 9972.23
8:00 | 10790.16 | 99 |  | 10893.16
9:00 | 10810.35 | 75 |  | 10888.35
10:00 | 10777.21 | 93 |  | 10874.21
11:00 | 11055.62 | 74 |  | 11132.62
12:00 | 11121.56 | 69 |  | 11193.67
13:00 | 11581.28 | 76 |  | 11660.7
14:00 | 11222.07 | 90 |  | 11316.07
15:00 | 11031.1 | 90 |  | 11125.1
16:00 | 10798.72 | 60 |  | 10861.72
17:00 | 10755.82 | 70 |  | 10828.97
18:00 | 11220.68 | 80 |  | 11304.68
19:00 | 12250.2 | 60 |  | 12312.9
19:30 | 12005.5 | 60 |  | 12068.5
20:00 | 11856.5 | 50 |  | 11908.5
21:00 | 11662.92 | 50 |  | 11714.92
22:00 | 11120.52 | 48 |  | 11170.52
23:00 | 10809.69 | 0 |  | 10809.69
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6146 | 4157.5 | 10303.5 | DAILY GENERATION CURVE
00:30 | 5979.75 | 4004.5 | 9984.25
01:00 | 5813.5 | 3851.5 | 9665 | 19-02-2025
01:30 | 5599.25 | 3758 | 9357.25
02:00 | 5385 | 3664.5 | 9049.5
02:30 | 5329.5 | 3624 | 8953.5
03:00 | 5274 | 3583.5 | 8857.5
03:30 | 5193 | 3545.5 | 8738.5
04:00 | 5112 | 3507.5 | 8619.5
04:30 | 5077 | 3522.5 | 8599.5
05:00 | 5042 | 3537.5 | 8579.5
05:30 | 5094.75 | 3578 | 8672.75
06:00 | 5147.5 | 3618.5 | 8766
06:30 | 5506.46 | 3830.78 | 9337.24
07:00 | 5865.42 | 4043.06 | 9908.48
07:30 | 6308.375 | 4040.945 | 10349.32
08:00 | 6751.33 | 4038.83 | 10790.16
08:30 | 6750.095 | 4050.16 | 10800.255
09:00 | 6748.86 | 4061.49 | 10810.35
09:30 | 6669.76 | 4124.02 | 10793.78
10:00 | 6590.66 | 4186.55 | 10777.21
10:30 | 6666.64 | 4249.775 | 10916.415
11:00 | 6742.62 | 4313 | 11055.62
11:30 | 6766.555 | 4322.035 | 11088.59
12:00 | 6790.49 | 4331.07 | 11121.56
12:30 | 6857.105 | 4494.315 | 11351.42
13:00 | 6923.72 | 4657.56 | 11581.28
13:30 | 6895.355 | 4506.32 | 11401.675
14:00 | 6866.99 | 4355.08 | 11222.07
14:30 | 6719.52 | 4407.065 | 11126.585
15:00 | 6572.05 | 4459.05 | 11031.1
15:30 | 6570.905 | 4344.005 | 10914.91
16:00 | 6569.76 | 4228.96 | 10798.72
16:30 | 6573.835 | 4203.435 | 10777.27
17:00 | 6577.91 | 4177.91 | 10755.82
17:30 | 6759.045 | 4229.205 | 10988.25
18:00 | 6940.18 | 4280.5 | 11220.68
18:30 | 7317.94 | 4417.5 | 11735.44
19:00 | 7695.7 | 4554.5 | 12250.2
19:30 | 7479 | 4526.5 | 12005.5
20:00 | 7293 | 4563.5 | 11856.5
20:30 | 7161.5 | 4598.21 | 11759.71 |  | Executive Engineer
21:00 | 7030 | 4632.92 | 11662.92 |  | Network Operation Division
21:30 | 6851.5 | 4540.22 | 11391.72
22:00 | 6673 | 4447.52 | 11120.52
22:30 | 6514.5 | 4450.605 | 10965.105
23:00 | 6356 | 4453.69 | 10809.69

## En-Curve
QF-LDC-12
Date | 19-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2697 | 1979.5 | 924 | 0 | 62 | 758 | 40 | 2113 | 0 | 310 | 1420 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2684 | 2008.25 | 923.5 | 0 | 61 | 757 | 40 | 2115 | 0 | 224 | 1171.5 | 0 | 0 | 0 | 0 | 19-02-2025
01:00 | 2671 | 2037 | 923 | 0 | 60 | 756 | 40 | 2117 | 0 | 138 | 923 | 0 | 0 | 0 | 0
01:30 | 2647 | 1982.25 | 924.5 | 0 | 58 | 756 | 40 | 2117 | 0 | 85.5 | 747 | 0 | 0 | 0 | 0 | Energy Generated | 255.2093 |  | MKWHr
02:00 | 2623 | 1927.5 | 926 | 0 | 56 | 756 | 40 | 2117 | 0 | 33 | 571 | 0 | 0 | 0 | 0 | Energy not Served | 1.145 |  | MKWHr
02:30 | 2585 | 1917.5 | 925.5 | 0 | 56 | 755.5 | 40 | 2116.5 | 0 | 25 | 532.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 256.3543 |  | MKWHr
03:00 | 2547 | 1907.5 | 925 | 0 | 56 | 755 | 40 | 2116 | 0 | 17 | 494 | 0 | 0 | 0 | 0
03:30 | 2522.5 | 1883.5 | 925 | 0 | 55 | 756 | 40 | 2117 | 0 | 8.5 | 431 | 0 | 0 | 0 | 0
04:00 | 2498 | 1859.5 | 925 | 0 | 54 | 757 | 40 | 2118 | 0 | 0 | 368 | 0 | 0 | 0 | 0
04:30 | 2504.5 | 1831 | 925.5 | 0 | 54 | 756 | 40 | 2116.5 | 0 | 0 | 368 | 0 | 0 | 4 | 0
05:00 | 2511 | 1802.5 | 926 | 0 | 54 | 755 | 40 | 2115 | 0 | 0 | 368 | 0 | 0 | 8 | 0
05:30 | 2474.5 | 1803.25 | 926 | 0 | 54 | 755 | 40 | 2115.5 | 0 | 26.5 | 468.5 | 0 | 0 | 9.5 | 0
06:00 | 2438 | 1804 | 926 | 0 | 54 | 755 | 40 | 2116 | 0 | 53 | 569 | 0 | 0 | 11 | 0
06:30 | 2512.5 | 1877.5 | 925.5 | 0 | 56 | 756 | 40 | 2117 | 10.24 | 101 | 933 | 0 | 0 | 8.5 | 30.5
07:00 | 2587 | 1951 | 925 | 0 | 58 | 757 | 40 | 2118 | 20.48 | 149 | 1297 | 0 | 0 | 6 | 61
07:30 | 2553 | 1975.5 | 902 | 0 | 63 | 756.11 | 40 | 2111.5 | 74.61 | 201.5 | 1663.6 | 0 | 0 | 8.5 | 80
08:00 | 2519 | 2000 | 879 | 0 | 68 | 755.22 | 40 | 2105 | 128.74 | 254 | 2030.2 | 0 | 0 | 11 | 99
08:30 | 2502 | 1918.25 | 878.5 | 0 | 67 | 756.935 | 40 | 2079.5 | 198.47 | 265 | 2087.1 | 0 | 0 | 7.5 | 87
09:00 | 2485 | 1836.5 | 878 | 0 | 66 | 758.65 | 40 | 2054 | 268.2 | 276 | 2144 | 0 | 0 | 4 | 75
09:30 | 2490 | 1832 | 902 | 0 | 70 | 757.68 | 40 | 2054.5 | 310.6 | 297 | 2036.5 | 0 | 0 | 3.5 | 84
10:00 | 2495 | 1827.5 | 926 | 0 | 74 | 756.71 | 40 | 2055 | 353 | 318 | 1929 | 0 | 0 | 3 | 93
10:30 | 2533 | 1860.5 | 926 | 0 | 75 | 758.375 | 40 | 2074.5 | 392.54 | 324.5 | 1930.5 | 0 | 0 | 1.5 | 83.5
11:00 | 2571 | 1893.5 | 926 | 0 | 76 | 760.04 | 40 | 2094 | 432.08 | 331 | 1932 | 0 | 0 | 0 | 74
11:30 | 2644.5 | 1932 | 925 | 0 | 80 | 761.045 | 40 | 2095 | 458.445 | 325 | 1827.6 | 0 | 0 | 0 | 71.5
12:00 | 2718 | 1970.5 | 924 | 0 | 84 | 762.05 | 40 | 2096 | 484.81 | 319 | 1723.2 | 0 | 0 | 0 | 69
12:30 | 2705 | 1860.75 | 925 | 0 | 84 | 760.03 | 40 | 2107 | 486.44 | 374.5 | 2007.7 | 0 | 0 | 1 | 72.5
13:00 | 2692 | 1751 | 926 | 0 | 84 | 758.01 | 40 | 2118 | 488.07 | 430 | 2292.2 | 0 | 0 | 2 | 76
13:30 | 2622.5 | 1696 | 926.5 | 0 | 80 | 757.95 | 40 | 2058.5 | 445.525 | 442 | 2330.7 | 0 | 0 | 2 | 83
14:00 | 2553 | 1641 | 927 | 0 | 76 | 757.89 | 40 | 1999 | 402.98 | 454 | 2369.2 | 0 | 0 | 2 | 90
14:30 | 2671.5 | 1685.75 | 926.5 | 0 | 78 | 754.945 | 40 | 1999.5 | 384.19 | 457.5 | 2126.7 | 0 | 0 | 2 | 90
15:00 | 2790 | 1730.5 | 926 | 0 | 80 | 752 | 40 | 2000 | 365.4 | 461 | 1884.2 | 0 | 0 | 2 | 90
15:30 | 2819.5 | 1799.4 | 926 | 0 | 80 | 756 | 40 | 2028.5 | 282.41 | 486 | 1695.1 | 0 | 0 | 2 | 75
16:00 | 2849 | 1868.3 | 926 | 0 | 80 | 760 | 40 | 2057 | 199.42 | 511 | 1506 | 0 | 0 | 2 | 60
16:30 | 2871.5 | 1828.3 | 926 | 0 | 77 | 759 | 40 | 2026 | 127.97 | 561 | 1559.5 | 0 | 0 | 1 | 65
17:00 | 2894 | 1788.3 | 926 | 0 | 74 | 758 | 40 | 1995 | 56.52 | 611 | 1613 | 0 | 0 | 0 | 70
17:30 | 2872 | 1743.65 | 925.5 | 0 | 79 | 756.5 | 40 | 2004.5 | 28.26 | 635.5 | 1903.34 | 0 | 0 | 0 | 75
18:00 | 2850 | 1699 | 925 | 0 | 84 | 755 | 40 | 2014 | 0 | 660 | 2193.68 | 0 | 0 | 0 | 80
18:30 | 2951.5 | 1734 | 901 | 0 | 80 | 756 | 40 | 2065 | 0 | 665 | 2542.94 | 0 | 0 | 0 | 70
19:00 | 3053 | 1769 | 877 | 0 | 76 | 757 | 40 | 2116 | 0 | 670 | 2892.2 | 0 | 0 | 0 | 60
19:30 | 3040 | 1727.5 | 877 | 0 | 76 | 755 | 40 | 2121 | 0 | 654 | 2715 | 0 | 0 | 0 | 60
20:00 | 2999 | 1676.5 | 877 | 0 | 68 | 756 | 40 | 2117 | 0 | 680 | 2643 | 0 | 0 | 0 | 50
20:30 | 2979 | 1677 | 900 | 0 | 67 | 757.71 | 40 | 2117 | 0 | 689 | 2533 | 0 | 0 | 0 | 50
21:00 | 2959 | 1677.5 | 923 | 0 | 66 | 759.42 | 40 | 2117 | 0 | 698 | 2423 | 0 | 0 | 0 | 50
21:30 | 2976.5 | 1681 | 923 | 0 | 63 | 758.72 | 40 | 2118 | 0 | 644.5 | 2187 | 0 | 0 | 0 | 49
22:00 | 2994 | 1684.5 | 923 | 0 | 60 | 758.02 | 40 | 2119 | 0 | 591 | 1951 | 0 | 0 | 0 | 48
22:30 | 2970 | 1685 | 923 | 0 | 60 | 760.605 | 40 | 2117.5 | 0 | 580 | 1829 | 0 | 0 | 0 | 24
23:00 | 2946 | 1685.5 | 923 | 0 | 60 | 763.19 | 40 | 2116 | 0 | 569 | 1707 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 05:00 | 388 | 12:00 | Payra | 419 | 19:00 | 411 | 12:00
Ashuganj | 407 | 5:00 | 382 | 12:00 | Rahanpur | 415 | 00:00 | 398 | 08:00
Bhulta | 403 | 06:00 | 388 | 12:00 | Rampal | 407 | 05:00 | 391 | 12:00
Bibiana | 405 | 23:00 | 401 | 18:00
BIPTC | 402 | 04:00 | 391 | 13:00
Bogura | 414 | 23:00 | 392 | 17:00
Gopalganj | 407 | 05:00 | 394 | 12:00
Kaliakoir | 397 | 08:00 | 292 | 03:00
Madunaghat | 408 | 08:00 | 400 | 16:00
Meghnaghat | 396 | 02:00 | 385 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 08:00 | 222 | 12:00 | Keranigonj | 231 | 06:00 | 221 | 12:00
AKSML | 237 | 08:00 | 229 | 17:00 | Khulna(S) | 238 | 05:00 | 225 | 12:00
Aminbazar | 232 | 04:00 | 223 | 12:00 | Madunaghat | 237 | 20:00 | 231 | 15:00
Ashuganj | 242 | 07:00 | 234 | 12:00 | Madunaghat-400 | 237 | 09:00 | 232 | 16:00
Ashuganj-400 | 235 | 5:00 | 226 | 12:00 | Maniknagar | 232 | 05:00 | 223 | 12:00
Baghabari | 239 | 00:00 | 230 | 12:00 | Meghnaghat | 240 | 00:00 | 231 | 12:00
Barapukuria | 230 | 23:00 | 212 | 17:00 | Meghnaghat-400 | 236 | 08:00 | 227 | 12:00
Barapukuria-230 | 228 | 22:00 | 214 | 16:00 | Mirsorai | 239 | 20:00 | 229 | 01:00
Barishal | 242 | 01:00 | 235 | 12:00 | Rajshahi | 238 | 00:00 | 226 | 12:00
Bheramara | 237 | 05:00 | 226 | 12:00 | Rampal | 234 | 04:00 | 223 | 12:00
Bhulta | 233 | 05:00 | 224 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 20:00 | 230 | 18:00 | Rampura | 234 | 08:00 | 223 | 12:00
BIPTC | 239 | 02:00 | 226 | 12:00 | Shikalbaha | 237 | 19:00 | 231 | 15:00
Bogura | 241 | 00:00 | 226 | 16:00 | Shyampur | 232 | 05:00 | 223 | 12:00
Bogura-400 | 239 | 00:00 | 225 | 16:00 | Siddhirganj | 234 | 03:00 | 226 | 12:00
Borhanuddin | 244 | 01:00 | 241 | 11:00 | Sirajgonj | 245 | 00:00 | 238 | 08:00
BSRM | 238 | 20:00 | 229 | 15:00 | Sreepur | 237 | 05:00 | 228 | 12:00
Cumilla(N) | 236 | 08:00 | 228 | 12:00 | Tongi | 233 | 07:00 | 222 | 15:00
Faridpur | 240 | 04:00 | 232 | 12:00
Fenchuganj | 240 | 09:00 | 234 | 01:00
Ghorashal | 235 | 00:00 | 235 | 00:00
Ghorashal-230 | 235 | 08:00 | 225 | 15:00
Gopalganj | 239 | 05:00 | 232 | 12:00
GPH | 237 | 20:00 | 230 | 12:00
Haripur | 235 | 08:00 | 225 | 12:00
Hasnabad | 234 | 07:00 | 222 | 12:00
Hathazari | 240 | 08:00 | 233 | 12:00
Ishurdi | 240 | 06:00 | 228 | 12:00
Jhenaidah | 237 | 06:00 | 224 | 18:30
Kaliakoir | 230 | 08:00 | 223 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 06:00 | 125 | 12:00 | Magura | 138 | 04:00 | 128 | 12:00
Agargaon | 134 | 05:00 | 127 | 12:00 | Mahasthangarh | 137 | 00:00 | 126 | 17:00
Agrabad | 137 | 09:00 | 132 | 12:00 | Manikganj | 138 | 13:00 | 132 | 15:00
AKS | 136 | 08:00 | 131 | 01:00 | Maniknagar | 133 | 07:00 | 125 | 12:00
Aminbazar | 134 | 05:00 | 126 | 12:00 | Matarbari | 131 | 09:00 | 120 | 18:00
Amnura | 142 | 00:00 | 126 | 09:00 | Matuail | 133 | 07:00 | 127 | 12:00
Ashuganj | 142 | 07:00 | 138 | 12:00 | Millgate | 136 | 08:00 | 127 | 15:00
Bagerhat | 135 | 05:00 | 125 | 12:00 | Mirpur | 133 | 06:00 | 124 | 12:00
Bajitpur | 136 | 00:00 | 132 | 12:00 | Mirzapur | 135 | 00:00 | 125 | 15:00
Bakulia | 164 | 22:00 | 133 | 15:00 | Mithapukur | 137 | 19:30 | 121 | 08:00
Banani | 132 | 03:00 | 124 | 12:00 | MI_Cement | 134.5 | 08:00 | 128 | 12:00
Bangabhaban | 133 | 08:00 | 125 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 138 | 23:00 | 127 | 08:00 | Mogbazar | 133 | 04:00 | 125 | 12:00
Barguna | 138 | 20:00 | 133 | 11:00 | Mongla | 135 | 05:00 | 125 | 12:00
Barishal | 137 | 21:00 | 133 | 04:00 | Motijheel | 133 | 08:00 | 125 | 12:00
Barishal-230 | 137 | 23:00 | 132 | 12:00 | Muktagacha | 131 | 00:00 | 120 | 15:00
Baroaulia | 137 | 08:00 | 133 | 12:00 | Munshiganj | 133 | 05:00 | 127 | 12:00
Baroirhat | 136 | 09:00 | 130 | 03:00 | Muradnagar | 137 | 08:00 | 131 | 12:00
Bashundhara | 135 | 08:00 | 125 | 12:00 | Mymensingh | 130 | 00:00 | 115 | 18:30
BashundharaCement | 134 | 08:00 | 127 | 12:00 | Naogaon | 136 | 04:00 | 125 | 08:00
Beanibazar | 136 | 04:00 | 129 | 18:30 | Narail | 138 | 06:00 | 127 | 12:00
Benapole | 135 | 04:00 | 123 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhaluka | 128 | 00:00 | 118 | 18:30 | Narshingdi | 135 | 07:00 | 121 | 12:00
Bhandaria | 135 | 13:00 | 130 | 04:00 | Natore | 137 | 00:00 | 130 | 17:00
Bhangura | 137 | 23:00 | 130 | 12:00 | Nawabganj | 135 | 05:00 | 128 | 12:00
Bheramara | 138 | 00:00 | 132 | 16:00 | Netrakona | 126 | 00:00 | 114 | 18:30
Bheramara(GK) | 139 | 02:00 | 132 | 12:00 | New | 138 | 07:00 | 129 | 15:00
Bhulta | 128 | 02:00 | 121 | 11:00 | Niamatpur | 140 | 03:00 | 133 | 08:00
Bog-Sherpur | 138 | 00:00 | 126 | 09:00 | Noapara | 137 | 03:00 | 126 | 12:00
Bogura | 139 | 00:00 | 128 | 17:00 | Pabna | 139 | 02:00 | 132 | 12:00
Bogura-230 | 139 | 00:00 | 129 | 16:00 | Palashbari | 133 | 00:00 | 119 | 08:00
Brahmanbaria | 138 | 07:00 | 130 | 12:00 | Panchagarh | 143 | 21:00 | 121 | 08:00
Cantonment | 134 | 04:00 | 127 | 12:00 | Patuakhali | 139 | 23:00 | 132 | 11:00
Chandpur | 140 | 19:00 | 133 | 03:00 | Payra | 137 | 20:00 | 131 | 12:00
Chandraghona | 137 | 08:00 | 133 | 12:00 | PHP | 135 | 08:00 | 129 | 03:00
Chapai | 137 | 00:00 | 130 | 12:00 | Postogola | 137 | 08:00 | 130 | 12:00
Charsaidpur | 134 | 05:00 | 129 | 11:00 | Purbachal | 133 | 04:00 | 125 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 137 | 08:00 | 131 | 00:00 | Purbasadipur | 135 | 19:30 | 122 | 07:00
Chhatak | 134 | 04:00 | 125 | 18:30 | Rahanpur | 141 | 05:00 | 134 | 12:00
Chowmuhani | 133 | 18:30 | 128 | 00:00 | Rahanpur-400 | 141 | 00:00 | 134 | 08:00
Chuadanga | 136 | 01:00 | 126 | 12:00 | Rahim | 133 | 06:00 | 127 | 12:00
Coxsbazar | 129 | 10:00 | 120 | 18:00 | Rajbari | 134 | 05:00 | 128 | 12:00
Cumilla(N) | 138 | 08:00 | 133 | 12:00 | Rajendrapur | 135 | 08:00 | 129 | 03:00
Cumilla(S) | 137 | 08:00 | 127 | 10:00 | Rajshahi | 138 | 00:00 | 131 | 12:00
Daudkandi | 133 | 03:00 | 129 | 12:00 | Rajshahi-230 | 138 | 00:00 | 125 | 12:00
Dhaka | 132 | 03:00 | 125 | 12:00 | Ramganj | 136 | 08:00 | 130 | 03:00
Dhamrai | 132 | 02:00 | 125 | 15:00 | Rampur | 137 | 19:00 | 132 | 15:00
Dhanmondi | 134 | 04:00 | 125 | 12:00 | Rampura | 132 | 05:00 | 124 | 12:00
Dohazari | 136 | 09:00 | 129 | 00:00 | Rangamati | 136 | 08:00 | 132 | 12:00
Faridpur | 135 | 05:00 | 131 | 12:00 | Rangpur | 135 | 19:30 | 116 | 08:00
Fatullah | 136 | 08:00 | 129 | 12:00 | Ruppur | 140 | 02:00 | 133 | 12:00
Fenchuganj | 139 | 06:00 | 134 | 15:00 | Saidpur | 135 | 19:30 | 120 | 08:00
Feni | 135 | 19:00 | 130 | 00:00 | Satkhira | 136 | 05:00 | 126 | 12:00
Ghatail | 131 | 00:00 | 116 | 15:00 | Satmasjid | 134 | 04:00 | 127 | 12:00
Ghorashal | 142 | 08:00 | 137 | 01:00 | Savar | 132 | 05:00 | 126 | 11:00
Goalpara | 137 | 06:00 | 129 | 12:00 | SevenRings | 141 | 07:00 | 135 | 16:00
Gollamari | 138 | 06:00 | 129 | 12:00 | ShahCement | 134 | 05:00 | 129 | 11:00
Gopalganj | 137 | 05:00 | 131 | 12:00 | Shahjadpur | 142 | 00:00 | 134 | 15:00
Gopalganj-400 | 139 | 05:00 | 134 | 12:00 | Shahjibazar | 138 | 02:00 | 133 | 12:00
Gulshan | 132 | 04:00 | 124 | 12:00 | Shahmirpur | 139 | 09:00 | 133 | 14:00
Halishahar | 137 | 08:00 | 132 | 22:00 | Shariatpur | 136 | 01:00 | 133 | 12:00
Haripur | 135 | 08:00 | 128 | 11:00 | Sherpur | 126 | 00:00 | 113 | 15:00
HaripurSBU | 135 | 08:00 | 128 | 11:00 | Shikalbaha | 128 | 09:00 | 121 | 15:00
Hasnabad | 136 | 06:00 | 132 | 04:00 | Shikalbaha-230 | 139 | 09:00 | 133 | 15:00
Hathazari | 140 | 08:00 | 135 | 07:00 | Shitalakhya | 134.5 | 08:00 | 128 | 12:00
Ishurdi | 141 | 05:00 | 134 | 12:00 | Sholosohor | 137 | 08:00 | 133 | 03:00
Jaldhaka | 133 | 19:30 | 105 | 08:00 | Shyampur | 135 | 08:00 | 129 | 12:00
Jamalpur | 129 | 00:00 | 119 | 15:00 | Shyampur-230 | 135 | 05:00 | 129 | 12:00
Jashore | 135 | 03:00 | 125 | 12:00 | Siddhirganj | 134 | 05:00 | 128 | 11:00
Jhenaidah | 138 | 01:00 | 128 | 12:00 | Sirajganj | 137 | 00:00 | 126 | 17:00
Jhenaidah-230 | 139 | 05:00 | 129 | 12:00 | Sonargaon | 131 | 21:00 | 125 | 09:00
Joydebpur | 138 | 22:00 | 132 | 09:00 | Sreemongol | 139 | 08:00 | 133 | 12:00
Joypurhat | 135 | 00:00 | 123 | 08:00 | Sreepur | 129 | 02:00 | 123 | 12:00
Juldah | 140 | 09:00 | 134 | 00:00 | Srinagar | 135 | 05:00 | 129 | 12:00
Kabirpur | 140 | 02:00 | 125 | 15:00 | SSM | 140 | 03:00 | 138 | 12:00
Kachua | 138 | 09:00 | 132 | 03:00 | Sunamganj | 134 | 06:00 | 126 | 18:30
Kaliakoir | 141 | 00:00 | 128 | 15:00 | Sylhet | 136 | 07:00 | 130 | 15:00
Kallyanpur | 131 | 03:00 | 125 | 12:00 | Sylhet-132 | 136 | 06:00 | 131 | 12:00
Kalurghat | 136 | 08:00 | 133 | 03:00 | Tangail | 130 | 00:00 | 123 | 10:00
Kamrangirchar | 135 | 04:00 | 123 | 12:00 | Thakurgaon | 142 | 21:00 | 120 | 08:00
Kaptai | N/A | N/A | N/A | N/A | TK | 139 | 08:00 | 134 | 02:00
Kazla | 132 | 05:00 | 125 | 12:00 | Tongi | 138 | 07:00 | 130 | 15:00
Keranigonj | 135 | 05:00 | 129 | 12:00 | Ullahpara | 138 | 00:00 | 128 | 17:00
Khagrachori | 136 | 09:00 | 132 | 01:00 | Ullon | 131 | 01:00 | 124 | 12:00
Khulna | 136 | 05:00 | 128 | 12:00 | Uttara | 133 | 06:00 | 124 | 12:00
Khulna(S) | 138 | 05:00 | 129 | 12:00 | UttaraNew | 134 | 00:00 | 126 | 16:00
Khulshi | 137 | 08:00 | 131 | 12:00 | Zigatola | 135 | 04:00 | 129 | 13:00
Kishoreganj | 133 | 00:00 | 128 | 11:00
Kodda | 139 | 08:00 | 130 | 03:00
KSRM | 138 | 08:00 | 133 | 12:00
Kulaura | 139 | 07:00 | 135 | 12:00
Kurigram | 135 | 20:00 | 116 | 08:00
Kushtia | 139 | 01:00 | 131 | 12:00
Lalbag | 135 | 05:00 | 128 | 12:00
Lalmonirhat | 133 | 19:30 | 116 | 08:00
Madanganj | 134 | 08:00 | 127 | 12:00
Madaripur | 136 | 00:00 | 133 | 12:00
Madartek | 132 | 05:00 | 125 | 12:00
Madunaghat | 137 | 13:00 | 133 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division