## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-02-2025 | during | 21-02-2025 | during | 21-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 140 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 110 | 30 | 80 | 30 | 80 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 340 | 302 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 270 | 335 | 335 | 300 | 300 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 82 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 17 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 0 | 17 | Liquid fuel shortage
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 18 | 18 | 22.5 | 22.5 | 22.5 | 22.5 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 20 | 17 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 275 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 109 | 114 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 72 | 162 | 162 | 35 | 72 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 54 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 290 | 280 | 584 | 584 | 320 | 320 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 25 | 35 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 2105 | 2277 | 4863.87 | 4886.87 | 2906.79 | 2983.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 41 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 225 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 79 | 78 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 74 | 84 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 18 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 22 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.86 | 0 | 3.86 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 51 | 300 | 300 | 50 | 50 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 2 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 108 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 926 | 1038 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 1 | 3 | 8 | 3 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2465 | 2810.36 | 3443.72 | 3468.86 | 3193.72 | 3218.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 221 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 295 | 305 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 194 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 107 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 31 | 46 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 35 | 35 | 163 | 163 | 40 | 40 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 80 | 80 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 20.83 | 20.83 | 18 | 18 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 50 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 2 | 9 | 9 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 92 | 115 | 115 | 0 | 95 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1253 | 1479.2 | 1999.53 | 1931.53 | 1695.2 | 1722.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-02-2025 | during | 21-02-2025 | during | 21-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 18 | 210 | 210 | 35 | 35 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 60 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.87 | 0 | 44 | 0 | 44 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 130.87 | 126 | 647.5 | 601.5 | 472.5 | 426.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 28 | 34 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 346 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 990 | 968 | 1050 | 1050 | 1008 | 1008
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 35 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 160 | 155 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 77.29 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1161.29 | 1066 | 2931.1 | 2841.1 | 1308.02 | 1218.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 128 | 130 | 67 | 67 | 67 | 67 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 600 | 622 | 622 | 602 | 602 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 137 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1387.59 | 1511 | 1487.12 | 1486.12 | 1464 | 1463
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 37 | 41 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 23 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 30 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 157 | 153 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 30 | 30 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 88 | 88 | 50 | 90 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.95 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 760 | 754.79 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 37.06 | 0 | 52 | 0 | 52 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 24 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1691.51 | 1775.29 | 2271.89 | 2119.24 | 1844.11 | 1731.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 107 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 80 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 101 | 0 | 101 | 0 | 101 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 327 | 208 | 398.6 | 262 | 364.62 | 228.02
System Total |  |  |  |  | 27884.66 | 27150.742 | 11511.26 | 12220.85 | 19093.33 | 18647.22 | 14256.96 | 13999.85
Forecast Scenario (21-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10300 |  | 0 |  | 10300
|  |  |  | 1:00 | 9570 |  | 0 |  | 9570
|  |  |  | 2:00 | 9090 |  | 0 |  | 9090
|  |  |  | 3:00 | 8990 |  | 0 |  | 8990
|  |  |  | 4:00 | 8840 |  | 0 |  | 8840
|  |  |  | 5:00 | 8690 |  | 0 |  | 8690
|  |  |  | 6:00 | 8540 |  | 0 |  | 8540
|  |  |  | 7:00 | 9030 |  | 0 |  | 9030
|  |  |  | 8:00 | 9660 |  | 0 |  | 9660
|  |  |  | 9:00 | 9720 |  | 0 |  | 9720
|  |  |  | 10:00 | 9590 |  | 0 |  | 9590
|  |  |  | 11:00 | 9840 |  | 0 |  | 9840
|  |  |  | 12:00 | 10500 |  | 0 |  | 10500
|  |  |  | 13:00 | 10900 |  | 0 |  | 10900
|  |  |  | 14:00 | 9440 |  | 0 |  | 9440
|  |  |  | 15:00 | 9090 |  | 0 |  | 9090
|  |  |  | 16:00 | 8980 |  | 0 |  | 8980
|  |  |  | 17:00 | 9000 |  | 0 |  | 9000
|  |  |  | 18:00 | 9450 |  | 0 |  | 9450
|  |  |  | 18:30 | 9800 |  | 0 |  | 9800
|  |  |  | 19:00 | 10160 |  | 0 |  | 10160
|  |  |  | 19:30 | 9960 |  | 0 |  | 9960
|  |  |  | 20:00 | 9870 |  | 0 |  | 9870
|  |  |  | 21:00 | 9510 |  | 0 |  | 9510
|  |  |  | 22:00 | 9220 |  | 0 |  | 9220
|  |  |  | 23:00 | 8870 |  | 0 |  | 8870
Probable Maximum Temperature: |  |  | 30.20°C
Probable Maximum Demand at Day Peak: |  |  | 10500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10160.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10160.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.85 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:04 hrs on 21-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-02-2025 | [28 empty] | Date: | 20-02-2025 | [28 empty] | Date: | 20-02-2025 | [28 empty] | Date: | 20-02-2025 | [28 empty] | Date: | 20-02-2025 | [18 empty] | Date: | 20-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 18 | 0 | 73 | 32 | 95 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 37 | 52 | 0 | 0 | 0 | 51 | 80 | 0 | 100 | 24 | 0 | 40 | 110 | 10 | 576 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 108 | 195 | 0 | 0 | 305 | 29 | 185 | 36 | 0 | 40 | 155 | 0 | 18 | 0 | 58 | 0 | 0 | 24 | 290 | 320 | 0 | 11 | 0 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 59 | 9 | 28 | 0 | 0 | 6 | 6055 | 924 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.63 | 0 | 0 | 0 | 113 | 6 | 80 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 7 | 130 | 180 | 0 | 0 | 622 | 137 | 4131.13 | 10186.13 | 89.98
01:00 | 0 | 50 | 0 | 0 | 0 | 232 | 0 | 0 | 350 | 0 | 0 | 17 | 18 | 0 | 33 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 35 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 0 | 40 | 110 | 24 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 108 | 195 | 0 | 0 | 305 | 29 | 184 | 36 | 0 | 40 | 155 | 0 | 18 | 0 | 54 | 0 | 0 | 0 | 300 | 320 | 0 | 32 | 0 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 19 | 9 | 32 | 0 | 0 | 6 | 5709 | 923 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.72 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0.48 | 64 | 307 | 7 | 130 | 180 | 0 | 0 | 622 | 90 | 3986.7 | 9695.7 | 89.98
02:00 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 350 | 0 | 0 | 17 | 18 | 0 | 23 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 40 | 110 | 23 | 577 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 20 | 195 | 0 | 0 | 305 | 29 | 184 | 36 | 0 | 40 | 51 | 0 | 18 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 0 | 32 | 0 | 38 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 19 | 9 | 32 | 0 | 0 | 6 | 5385 | 923 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.6 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 370 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 130 | 180 | 0 | 0 | 622 | 0 | 3721.1 | 9106.1 | 89.97
03:00 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 40 | 110 | 25 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 195 | 0 | 0 | 305 | 29 | 183 | 36 | 0 | 40 | 0 | 0 | 18 | 0 | 50 | 0 | 0 | 0 | 295 | 320 | 0 | 32 | 0 | 38 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 5175 | 923 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 370 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 5 | 100 | 180 | 0 | 0 | 622 | 0 | 3579 | 8754 | 89.97
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 34 | 17 | 578 | 0 | 0 | 0 | 0 | 34 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 185 | 0 | 0 | 335 | 29 | 199 | 36 | 0 | 40 | 0 | 0 | 18 | 0 | 50 | 0 | 0 | 0 | 290 | 320 | 0 | 32 | 0 | 38 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 5004 | 924 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 370 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 100 | 180 | 0 | 0 | 622 | 0 | 3529.53 | 8533.53 | 89.97
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 34 | 30 | 575 | 0 | 0 | 0 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 187 | 0 | 0 | 305 | 29 | 184 | 36 | 0 | 40 | 0 | 0 | 18 | 0 | 50 | 0 | 0 | 0 | 295 | 320 | 0 | 32 | 0 | 38 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 2 | 2 | 34 | 0 | 0 | 0 | 4985 | 923 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 370 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 100 | 180 | 0 | 0 | 622 | 0 | 3536.25 | 8521.25 | 89.96
06:00 | 0 | 5 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 16 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 320 | 1 | 30 | 0 | 0 | 6 | 0 | 0 | 0 | 45 | 0 | 0 | 40 | 34 | 32 | 577 | 0 | 0 | 0 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 187 | 0 | 0 | 320 | 29 | 226 | 36 | 0 | 40 | 1 | 0 | 18 | 0 | 50 | 0 | 0 | 0 | 310 | 320 | 0 | 32 | 0 | 38 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 34 | 0 | 0 | 2 | 5261 | 923 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 340 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 4 | 100 | 220 | 0 | 0 | 622 | 0 | 3583.76 | 8844.76 | 89.96
07:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 356 | 0 | 0 | 17 | 0 | 0 | 19 | 48 | 8 | 0 | 1 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 16 | 300 | 0 | 0 | 1 | 0 | 20 | 0 | 0 | 320 | 26 | 32 | 0 | 0 | 2 | 0 | 0 | 0 | 89 | 35 | 0 | 40 | 64 | 35 | 577 | 8 | 0 | 0 | 0 | 69 | 228 | 0 | 0 | 0 | 612 | 1 | 51 | 0 | 187 | 0 | 0 | 360 | 22 | 225 | 36 | 0 | 40 | 40 | 0 | 3 | 0 | 54 | 0 | 4 | 0 | 320 | 320 | 0 | 33 | 0 | 38 | 2 | 163 | 17 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 34 | 0 | 1.48 | 6 | 5598.48 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 0 | 0 | 760.29 | 0 | 0 | 0 | 36 | 0 | 0 | 35 | 0 | 0 | 3 | 0 | 2.13 | 0 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 0.16 | 2.5 | 0 | 0 | 10 | 1 | 81 | 0 | 0 | 0.2 | 7 | 0.03 | 29 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 72 | 4010.47 | 9608.95 | 89.96
08:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 385 | 0 | 0 | 0 | 18 | 0 | 40 | 98 | 77 | 4 | 16 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 17 | 16 | 300 | 0 | 0 | 5 | 0 | 18.5 | 15 | 0 | 320 | 35 | 50 | 0 | 0 | 5 | 0 | 0 | 28 | 100 | 100 | 1 | 40 | 103 | 5 | 578 | 36 | 0 | 13 | 3 | 105 | 226 | 0 | 0 | 0 | 612 | 3 | 51 | 20 | 187 | 0 | 0 | 315 | 10 | 228 | 36 | 0 | 45 | 158 | 0 | 18 | 58 | 64 | 16 | 21 | 0 | 315 | 320 | 0 | 33 | 0 | 38 | 2 | 163 | 17 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 29 | 1 | 11.7 | 6 | 6255.2 | 904 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.66 | 0 | 0 | 758.75 | 0 | 0 | 0 | 109 | 0 | 0 | 100 | 0 | 0 | 22 | 0 | 11.88 | 0 | 0 | 0 | 0 | 167 | 0 | 414 | 0 | 1.01 | 2.5 | 0 | 0 | 90 | 7 | 90 | 0 | 0 | 1.2 | 44 | 0.14 | 110 | 307 | 5 | 130 | 220 | 0 | 0 | 622 | 17 | 4333.14 | 10588.34 | 89.96
09:00 | 0 | 52 | 0 | 0 | 0 | 200 | 0 | 0 | 383 | 0 | 0 | 0 | 18 | 0 | 59 | 81 | 270 | 15 | 17 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 17 | 23 | 300 | 0 | 0 | 12 | 7 | 18 | 15 | 0 | 320 | 35 | 50 | 14 | 0 | 4 | 51 | 35 | 34 | 89 | 50 | 2 | 40 | 110 | 2 | 576 | 36 | 0 | 32 | 17 | 105 | 226 | 0 | 0 | 0 | 612 | 12 | 51 | 40 | 187 | 0 | 0 | 295 | 10 | 226 | 33 | 0 | 40 | 200 | 0 | 18 | 34 | 70 | 34 | 39 | 0 | 300 | 320 | 0 | 33 | 0 | 38 | 2 | 120 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 26 | 1 | 24.27 | 6 | 6513.27 | 877 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.63 | 0 | 0 | 758 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 38 | 0 | 25.74 | 0 | 0 | 0 | 0 | 165 | 0 | 390 | 0 | 2.27 | 2.5 | 0 | 0 | 95 | 16 | 99 | 0 | 0 | 2.8 | 91 | 0.29 | 110 | 307 | 5 | 130 | 220 | 0 | 0 | 610 | 17 | 4387.23 | 10900.5 | 89.95
10:00 | 0 | 52 | 0 | 0 | 0 | 200 | 0 | 0 | 370 | 0 | 0 | 0 | 18 | 0 | 88 | 64 | 265 | 30 | 17 | 35 | 15 | 0 | 225 | 0 | 0 | 0 | 35 | 22 | 270 | 0 | 0 | 22 | 17 | 18 | 15 | 0 | 320 | 35 | 52 | 0 | 0 | 3 | 51 | 79 | 0 | 89 | 50 | 3 | 40 | 110 | 2 | 576 | 0 | 0 | 0 | 17 | 105 | 225 | 0 | 0 | 0 | 689 | 15 | 51 | 0 | 187 | 0 | 0 | 310 | 8 | 223 | 33 | 0 | 40 | 200 | 4 | 18 | 0 | 74 | 0 | 54 | 31 | 290 | 320 | 0 | 33 | 0 | 38 | 2 | 120 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 11 | 1 | 34.35 | 6 | 6497.35 | 923 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.59 | 0 | 0 | 756 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 47 | 0 | 37.14 | 0 | 0 | 0 | 0 | 164 | 0 | 390 | 0 | 3.34 | 2.5 | 0 | 0 | 54 | 23 | 107 | 0 | 0 | 4.5 | 100 | 0.41 | 110 | 307 | 5 | 130 | 220 | 0 | 0 | 600 | 17 | 4455.48 | 10952.83 | 89.95
11:00 | 0 | 52 | 0 | 0 | 0 | 191 | 0 | 0 | 340 | 0 | 0 | 0 | 15 | 0 | 93 | 64 | 265 | 34 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 22 | 270 | 0 | 0 | 22 | 17 | 18 | 10 | 0 | 290 | 35 | 52 | 0 | 0 | 0 | 51 | 79 | 0 | 89 | 50 | 4 | 40 | 110 | 2 | 576 | 0 | 0 | 0 | 17 | 105 | 226 | 0 | 0 | 0 | 862 | 18 | 51 | 0 | 183 | 0 | 0 | 275 | 5 | 223 | 33 | 0 | 35 | 200 | 9 | 18 | 0 | 74 | 0 | 64 | 31 | 295 | 320 | 0 | 29 | 0 | 38 | 2 | 120 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 11 | 2 | 41.21 | 6 | 6547.21 | 922 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.17 | 0 | 0 | 759 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 28 | 0 | 26.91 | 0 | 0 | 0 | 0 | 161 | 0 | 390 | 0 | 0 | 2.5 | 0 | 0 | 54 | 29 | 107 | 0 | 0 | 5.7 | 100 | 0.49 | 110 | 307 | 5 | 130 | 220 | 0 | 0 | 600 | 17 | 4437.77 | 10984.98 | 89.95
12:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 340 | 0 | 0 | 0 | 18 | 0 | 109 | 82 | 275 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 20 | 270 | 0 | 0 | 13 | 25 | 18 | 15 | 0 | 290 | 35 | 52 | 0 | 0 | 0 | 74 | 79 | 2 | 100 | 88 | 4 | 40 | 110 | 0 | 576 | 17 | 0 | 1 | 17 | 105 | 221 | 0 | 0 | 0 | 926 | 18 | 43 | 1 | 182 | 0 | 0 | 295 | 5 | 221 | 34 | 0 | 35 | 200 | 9 | 18 | 17 | 80 | 16 | 66 | 31 | 310 | 346 | 0 | 28 | 0 | 38 | 2 | 163 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 60 | 11 | 2 | 42.87 | 6 | 6943.87 | 924 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.29 | 0 | 0 | 760 | 0 | 37 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 24 | 30 | 37.06 | 0 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 3.95 | 2.5 | 0 | 0 | 80 | 33 | 107 | 0 | 0 | 6 | 101 | 0.59 | 110 | 307 | 5 | 128 | 220 | 0 | 0 | 600 | 17 | 4567.39 | 11511.26 | 89.94
13:00 | 0 | 52 | 0 | 0 | 0 | 195 | 0 | 0 | 336 | 0 | 0 | 0 | 18 | 0 | 128 | 95 | 297 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 18 | 250 | 0 | 0 | 12 | 35 | 18 | 15 | 0 | 310 | 35 | 69 | 21 | 0 | 0 | 85 | 78 | 51.35 | 100 | 88 | 4 | 40 | 110 | 0 | 577 | 36 | 0 | 19 | 17 | 105 | 222 | 0 | 0 | 0 | 939 | 18 | 51 | 22 | 180 | 0 | 0 | 345 | 8 | 220 | 35 | 16 | 35 | 200 | 0 | 18 | 70 | 82 | 52 | 63 | 31 | 310 | 320 | 0 | 33 | 0 | 38 | 2 | 163 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 68 | 11 | 2 | 30.35 | 6 | 7264.7 | 924 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.04 | 0 | 0 | 761 | 0 | 51 | 0 | 113 | 4 | 0 | 113 | 0 | 0 | 19 | 30 | 21.45 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 0 | 2.17 | 2.5 | 0 | 0 | 95 | 31 | 107 | 0 | 0 | 5.8 | 102 | 0.48 | 110 | 307 | 5 | 128 | 220 | 0 | 0 | 622 | 17 | 4530.44 | 11795.14 | 89.94
14:00 | 0 | 52 | 0 | 0 | 0 | 236 | 0 | 0 | 320 | 0 | 0 | 0 | 18 | 0 | 128 | 110 | 300 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 18 | 250 | 0 | 0 | 14 | 35 | 18 | 15 | 0 | 280 | 35 | 52 | 25 | 0 | 0 | 82 | 78 | 54.36 | 100 | 88 | 3 | 40 | 110 | 3 | 523 | 36 | 0 | 40 | 17 | 105 | 220 | 0 | 0 | 0 | 944 | 15 | 51 | 40 | 180 | 0 | 0 | 300 | 15 | 222 | 35 | 34 | 35 | 180 | 0 | 18 | 21 | 86 | 52 | 56 | 37 | 280 | 320 | 0 | 33 | 0 | 38 | 2 | 120 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 11 | 2 | 35.29 | 6 | 7091.65 | 924 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 0 | 0 | 759.03 | 0 | 51 | 0 | 113 | 7 | 0 | 70 | 10 | 0 | 24 | 30 | 35.36 | 0 | 0 | 0 | 0 | 153 | 0 | 320 | 0 | 3.02 | 2.5 | 0 | 0 | 74 | 28 | 107 | 0 | 0 | 5.2 | 100 | 0.26 | 110 | 307 | 6 | 100 | 220 | 0 | 0 | 560 | 17 | 4296.12 | 11387.77 | 89.94
15:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 0 | 0 | 0 | 18 | 0 | 103 | 93 | 300 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 18 | 250 | 0 | 0 | 7 | 35 | 18 | 15 | 0 | 280 | 35 | 52 | 22 | 0 | 2 | 79 | 78 | 17 | 100 | 88 | 2 | 40 | 110 | 6 | 521 | 17 | 0 | 19 | 17 | 105 | 218 | 0 | 0 | 0 | 976 | 12 | 51 | 40 | 182 | 0 | 0 | 300 | 15 | 219 | 35 | 34 | 35 | 155 | 0 | 18 | 17 | 82 | 16 | 35 | 37 | 290 | 320 | 0 | 31 | 0 | 38 | 2 | 120 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 11 | 1 | 24.34 | 6 | 6887.34 | 923 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.42 | 0 | 0 | 759.3 | 0 | 50 | 0 | 113 | 7 | 0 | 70 | 20 | 0 | 20 | 30 | 20.19 | 0 | 0 | 0 | 0 | 151 | 0 | 320 | 0 | 1.29 | 2.5 | 0 | 0 | 35 | 21 | 107 | 0 | 0 | 3.9 | 103 | 0.07 | 110 | 307 | 5 | 122 | 180 | 0 | 0 | 550 | 17 | 4203.67 | 11091.01 | 89.93
16:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 0 | 0 | 0 | 10 | 0 | 114 | 108 | 245 | 55 | 17 | 35 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 18 | 250 | 0 | 0 | 4 | 35 | 18 | 17 | 0 | 280 | 35 | 51 | 0 | 0 | 6 | 69 | 77 | 17 | 100 | 24 | 2 | 40 | 110 | 6 | 522 | 17 | 0 | 19 | 17 | 105 | 218 | 0 | 0 | 0 | 1023 | 7 | 43 | 40 | 182 | 0 | 0 | 300 | 15 | 222 | 29 | 34 | 35 | 155 | 0 | 18 | 17 | 80 | 16 | 11 | 37 | 295 | 320 | 0 | 31 | 0 | 38 | 2 | 120 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 11 | 0 | 10.23 | 6 | 6759.23 | 923 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 759.26 | 0 | 50 | 0 | 113 | 7 | 50 | 70 | 21 | 0 | 35 | 30 | 12.2 | 0 | 0 | 0 | 0 | 151 | 0 | 320 | 0 | 0.93 | 2.5 | 0 | 0 | 35 | 13 | 110 | 0 | 0 | 2.6 | 61 | 0.04 | 110 | 307 | 5 | 125 | 180 | 0 | 0 | 550 | 17 | 4212.53 | 10971.76 | 89.93
17:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 304 | 0 | 0 | 0 | 21 | 0 | 114 | 92 | 195 | 55 | 17 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 3 | 35 | 18 | 22 | 0 | 280 | 35 | 51 | 14 | 0 | 3 | 83 | 77 | 17 | 100 | 24 | 0 | 40 | 110 | 15 | 520 | 17 | 0 | 19 | 17 | 105 | 225 | 0 | 0 | 0 | 1032 | 2 | 51 | 40 | 187 | 0 | 0 | 300 | 20 | 183 | 32 | 34 | 35 | 155 | 0 | 18 | 17 | 80 | 16 | 5 | 39 | 290 | 320 | 0 | 34 | 0 | 38 | 2 | 120 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 11 | 0 | 4.27 | 6 | 6759.27 | 922 | 150 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 758.18 | 0 | 50 | 0 | 113 | 7 | 50 | 35 | 21 | 0 | 11 | 30 | 4.34 | 0 | 0 | 0 | 0 | 151 | 0 | 320 | 0 | 0.49 | 2.5 | 0 | 0 | 35 | 4 | 113 | 0 | 0 | 0.8 | 17 | 0.01 | 48 | 307 | 5 | 125 | 180 | 0 | 0 | 550 | 17 | 4036.32 | 10795.59 | 89.93
18:00 | 0 | 70 | 0 | 30 | 0 | 200 | 0 | 0 | 300 | 0 | 0 | 0 | 54 | 0 | 115 | 107 | 278 | 55 | 19 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 17 | 17 | 270 | 0 | 0 | 0 | 35 | 18 | 22 | 0 | 280 | 35 | 51 | 24 | 0 | 5 | 83 | 77 | 54.36 | 100 | 88 | 0 | 40 | 110 | 18 | 575 | 72 | 0 | 22 | 25 | 105 | 226 | 0 | 0 | 0 | 1037 | 0 | 51 | 56 | 192 | 0 | 0 | 270 | 29 | 182 | 32 | 44 | 35 | 167 | 0 | 3 | 17 | 86 | 25 | 0 | 45 | 285 | 320 | 0 | 34 | 0 | 38 | 2 | 120 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 11 | 9 | 58 | 11 | 0 | 0 | 6 | 7186.36 | 924 | 152 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.2 | 0 | 50 | 0 | 113 | 20 | 89 | 100 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 250 | 0 | 0 | 2.5 | 0 | 0 | 81 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 6 | 100 | 180 | 0 | 0 | 520 | 137 | 4218.7 | 11405.06 | 89.93
19:00 | 0 | 70 | 0 | 110 | 0 | 140 | 0 | 0 | 302 | 0 | 0 | 0 | 54 | 0 | 114 | 127 | 300 | 15 | 35 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 55 | 17 | 270 | 0 | 0 | 0 | 35 | 18 | 22 | 0 | 280 | 35 | 51 | 22 | 0 | 1 | 84 | 78 | 54.36 | 100 | 100 | 0 | 40 | 110 | 18 | 575 | 108 | 0 | 41 | 25 | 105 | 225 | 0 | 0 | 0 | 1038 | 0 | 51 | 107 | 194 | 0 | 0 | 305 | 29 | 183 | 35 | 92 | 35 | 200 | 2 | 18 | 50 | 80 | 52.2 | 0 | 46 | 300 | 320 | 0 | 34 | 0 | 38 | 2 | 163 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 35 | 9 | 58 | 18 | 0 | 0 | 6 | 7660.56 | 876 | 155 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.79 | 0 | 41 | 0 | 113 | 23 | 90 | 113 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 220 | 0 | 0 | 600 | 137 | 4560.29 | 12220.85 | 89.92
19:30 | 0 | 70 | 0 | 0 | 0 | 220 | 0 | 0 | 302 | 0 | 0 | 17 | 54 | 0 | 105 | 127 | 300 | 0 | 35 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 55 | 17 | 270 | 0 | 0 | 0 | 35 | 18 | 22 | 0 | 280 | 35 | 51 | 0 | 0 | 0 | 34 | 78 | 17 | 100 | 50 | 0 | 40 | 110 | 21 | 575 | 53 | 0 | 19 | 8 | 105 | 225 | 0 | 0 | 0 | 1038 | 0 | 51 | 126 | 195 | 0 | 0 | 305 | 29 | 189 | 35 | 94 | 35 | 200 | 9 | 18 | 0 | 78 | 16 | 0 | 46 | 305 | 320 | 0 | 34 | 0 | 38 | 2 | 163 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 17 | 9 | 58 | 19 | 0 | 0 | 6 | 7307 | 877 | 154 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.43 | 0 | 41 | 0 | 113 | 28 | 90 | 113 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 54 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 137 | 4538.93 | 11845.93
20:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 35 | 54 | 0 | 105 | 93 | 300 | 0 | 17 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 55 | 18 | 270 | 0 | 0 | 0 | 17 | 18 | 22 | 0 | 280 | 35 | 51 | 0 | 0 | 0 | 34 | 78 | 0 | 100 | 50 | 0 | 40 | 110 | 6 | 575 | 0 | 0 | 12 | 0 | 105 | 225 | 0 | 0 | 0 | 1038 | 0 | 51 | 127 | 195 | 0 | 0 | 300 | 29 | 183 | 35 | 94 | 35 | 200 | 9 | 18 | 0 | 76 | 0 | 0 | 46 | 295 | 320 | 0 | 34 | 0 | 38 | 2 | 163 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 28 | 0 | 0 | 6 | 7120 | 877 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.43 | 0 | 41 | 0 | 113 | 30 | 90 | 113 | 35 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 54 | 0 | 113 | 15 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 137 | 4532.93 | 11652.93 | 89.92
21:00 | 0 | 70 | 0 | 0 | 0 | 237 | 0 | 0 | 302 | 0 | 0 | 35 | 54 | 0 | 97 | 93 | 225 | 0 | 0 | 72 | 16 | 0 | 225 | 0 | 0 | 0 | 35 | 20 | 270 | 0 | 0 | 0 | 0 | 19.5 | 22 | 0 | 280 | 35 | 51 | 0 | 0 | 0 | 34 | 78 | 0 | 100 | 50 | 0 | 40 | 110 | 23 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 1038 | 0 | 51 | 123 | 195 | 0 | 0 | 300 | 29 | 183 | 35 | 94 | 35 | 200 | 9 | 18 | 0 | 76 | 0 | 0 | 46 | 305 | 320 | 0 | 34 | 0 | 38 | 2 | 163 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 30 | 0 | 0 | 6 | 7007.5 | 877 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.56 | 0 | 41 | 0 | 113 | 28 | 90 | 113 | 28 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 113 | 16 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 130 | 220 | 0 | 0 | 622 | 137 | 4469.06 | 11476.56 | 89.91
22:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 35 | 36 | 0 | 97 | 93 | 95 | 0 | 0 | 54 | 16 | 0 | 225 | 0 | 0 | 0 | 17 | 20 | 270 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 280 | 35 | 51 | 0 | 0 | 0 | 0 | 78 | 0 | 100 | 0 | 0 | 40 | 110 | 25 | 575 | 0 | 0 | 0 | 0 | 105 | 225 | 0 | 0 | 0 | 1037 | 0 | 51 | 122 | 195 | 0 | 0 | 305 | 29 | 182 | 33 | 55 | 35 | 200 | 9 | 18 | 0 | 72 | 0 | 0 | 14 | 290 | 320 | 0 | 35 | 0 | 38 | 2 | 163 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 29 | 0 | 0 | 6 | 6643 | 924 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 113 | 27 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 113 | 16 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 130 | 220 | 0 | 0 | 622 | 150 | 4426.5 | 11069.5 | 89.91
23:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 17 | 0 | 0 | 97 | 93 | 0 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 21 | 270 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 280 | 35 | 51 | 0 | 0 | 0 | 0 | 78 | 0 | 100 | 0 | 0 | 40 | 110 | 30 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 1039 | 0 | 51 | 123 | 195 | 0 | 0 | 300 | 29 | 184 | 33 | 0 | 35 | 200 | 9 | 18 | 0 | 70 | 0 | 0 | 11 | 300 | 320 | 0 | 35 | 0 | 38 | 2 | 120 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 28 | 0 | 0 | 6 | 6352 | 924 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 113 | 12 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 150 | 4277.5 | 10629.5 | 89.91
Total KWH | 0 | 1091520 | 0 | 71900 | 0 | 5312719 | 0 | 0 | 8110800 | 0 | 0 | 494820 | 475200 | 0 | 1854144 | 1654080 | 3882567 | 534884 | 269954 | 792000 | 375480 | 0 | 5414000 | 0 | 0 | 0 | 265164 | 502800 | 6645330 | 0 | 0 | 105961 | 346800 | 441000 | 432000 | 0 | 7297727.27 | 703800 | 1048800 | 16224 | 0 | 44160 | 847821 | 1105872 | 413134 | 2102400 | 952320 | 26402 | 928980 | 2449700 | 377760 | 13578181.82 | 381382 | 0 | 293280 | 213712.2 | 2330945 | 5285828 | 0 | 0 | 0 | 20045453 | 119070 | 1138036 | 1264581 | 4549818 | 0 | 0 | 7564000 | 514560 | 4978000 | 824976 | 559680 | 898800 | 3501600 | 63840 | 396600 | 322620 | 1654080 | 326947 | 417136 | 489472 | 7272500 | 7694800 | 0 | 768744 | 0 | 887768 | 57936 | 3511473 | 506808 | 0 | 2069760 | 0 | 0 | 0 | 0 | 66240 | 232800 | 1120800 | 509760 | 11150 | 267880 | 126720 | 154205960.29 | 21949090 | 3888288 | 0 | 60960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310320 | 0 | 0 | 18173192 | 0 | 469881 | 0 | 2312544 | 163969 | 712720 | 1563744 | 178776 | 27686 | 250470 | 314874 | 247504 | 0 | 0 | 0 | 0 | 3962482 | 0 | 9414109 | 0 | 20100 | 76824 | 0 | 0 | 912453 | 202946 | 1997491 | 40000 | 0 | 38528.28 | 805680 | 2758 | 1743264 | 7244000 | 140501 | 2892000 | 4951770 | 0 | 0 | 14418909.09 | 1286400 | 100774233.37 | 254980193.66

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11511.26 | MW | 12:00 Hr. | Energy Generated |  |  | 254.9802 |  | MKWHr.
| Day Peak Demand |  |  | 11593.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.051 |  | MKWHr.
| Evening Peak Generation |  |  | 12220.85 | MW | 19:00 Hr. | Energy Demand |  |  | 256.0312 |  | MKWHr.
| Evening Peak Demand |  |  | 12316.85 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30.6 |  | °C
| Minimum Generation of the Day |  |  | 8521.25 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 828.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 12220.85 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 7.2309 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.6038 | 0 | 11.6611 | 0 | 0 | 0.10596 | 0 | 0 | 46.3709 | Gas | 109.7377 | Gas | 393788205.9759
| Chattogram Zone |  |  | 5.6636 | 33.6236 | 12.8594 | 0 | 0.92898 | 0.14547 | 0 | 0.04416 | 53.2652 | Coal | 55.2865 | Coal | 372971087.6788
| Cumilla Zone |  |  | 20.8648 | 0 | 6.5287 | 0 | 0 | 0.41714 | 1.6541 | 0 | 29.4647 | HFO | 44.3406 | HFO | 810725534.684
| Mymensingh Zone |  |  | 0.50976 | 0 | 1.5466 | 0 | 0 | 0.27903 | 0 | 0 | 2.3354 | HSD | 0.04 | HSD | 2219600
| Sylhet Zone |  |  | 22.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7698 | Hydro | 0.92898 | Hydro | 92898
| Khulna Zone |  |  | 3.8883 | 0 | 0.06096 | 0 | 0 | 0.31032 | 21.9491 | 0 | 26.2087 | Solar | 2.8259 | Solar | 46088464.0008
| Barishal Zone |  |  | 7.9843 | 21.6629 | 3.0297 | 0 | 0 | 0.002758 | 0 | 0 | 32.6796 | Import | 41.7764 | Import | 217191861.08
| Rajshahi Zone |  |  | 13.4534 | 0 | 5.7442 | 0 | 0 | 0.51807 | 18.1732 | 0 | 37.8889 | Wind | 0.04416 | Wind | 646502.4
| Rangpur Zone |  |  | 0 | 0 | 2.9099 | 0.04 | 0 | 1.0472 | 0 | 0 | 3.9971
| Total |  |  | 109.7377 | 55.2865 | 44.3406 | 0.04 | 0.92898 | 2.8259 | 41.7764 | 0.04416 | 254.9802
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 393788205.9759 |  | Hydro | 92898
|  |  |  | Coal | 372971087.6788 |  | Solar | 46088464.0008
|  |  |  | HFO | 810725534.684 |  | Import | 217191861.08
|  |  |  | HSD | 2219600 |  | Wind | 646502.4
[5 empty] | Total: | 184,37,24,153 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9491 | Peak Hr Flow | 876.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9409945.535 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.1732 | Peak Hr Flow | 754.79 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 486 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6541 | Peak Hr Flow | 80.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 776 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.7764 | Peak Hr Flow | 1710.79 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4522
|  |  |  | Chattogram |  | 0 |  | 1340
|  |  |  | Cumilla |  | 0 |  | 1021
|  |  |  | Mymensingh |  | 92 |  | 1036
|  |  |  | Sylhet |  | 0 |  | 419
|  |  |  | Khulna |  | 0 |  | 1194
|  |  |  | Barishal |  | 0 |  | 302
|  |  |  | Rajshahi |  | 0 |  | 1151
|  |  |  | Rangpur |  | 0 |  | 784
|  |  |  | Total |  | 92 |  | 11769
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:34 | 14:01 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to
Protection Checking by SPMD
| 08:35 | 17:43 | Bogura 132/33kV S/S Transformer-3 HT Project Work S/D Due to T-3 & T-4 Transformer 33 kv | [7 empty] | 15.0MW load
|  |  | bus coupler Isolator change | [7 empty] | interrup.
| 08:35 | 17:43 | Bogura 132/33kV S/S Transformer-3 LT Project Work S/D Due to T-3 & T-4 Transformer 33 kv | [7 empty] | 15.0MW load
|  |  | bus coupler Isolator change | [7 empty] | interrup.
| 08:35 | 17:42 | Bogura 132/33kV S/S Transformer-4 HT Project Work S/D Due to T-3 & T-4 Transformer 33 kv | [7 empty] | 15.0MW load
|  |  | bus coupler Isolator change | [7 empty] | interrup.
| 08:35 | 17:42 | Bogura 132/33kV S/S Transformer-4 LT Project Work S/D Due to T-3 & T-4 Transformer 33 kv | [7 empty] | 15.0MW load
|  |  | bus coupler Isolator change | [7 empty] | interrup.
| 08:45 | 14:56 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Annual maintenance
| 08:45 |  | Madunaghat 400/230kV S/S ATR-3 7206T HT Project Work S/D Due to Hydro Fire fighting
install work
| 08:50 |  | Madunaghat 400/230kV S/S Madunaghat-Old Madunaghat 230kV Ckt.-1 Project Work S/D Due to
Maintenance
| 08:54 | 18:05 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Paininting work and insulator disk cleaning tower no-1/2
| 08:56 | 14:58 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to
Shut down was taken from B.baria grid ss.
| 09:30 | 12:13 | Chandpur 132/33kV S/S 422T HT Scheduled S/D
| 09:30 | 12:14 | Chandpur 132/33kV S/S 422T LT Scheduled S/D
| 09:31 |  | SS Power unit-2 was sync.
| 09:41 | 17:01 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Line Checking
| 09:41 | 17:01 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Line Checking
| 10:11 | 19:26 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Disc cleaning work
| 10:13 | 19:25 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D Due to None
| 10:36 | 18:07 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to dead line
checking
| 11:13 |  | Hasnabad-Postogola 132kV ckt-2 Scheduled S/D from Postogola 132/33kV end Due to Yearly
maintenance
| 11:51 | 13:12 | Bogura-Sirajganj 230 kV Ckt-1 Forced S/D from Bogura 230/132kV end Due to 98 No Tower
Insulator maintenance
| 12:00 |  | Day peak Generation is 11508 MW
| 12:38 |  | Hasnabad-Postogola 132kV ckt-1 Scheduled S/D from Postogola 132/33kV end Due to Yearly
maintenance
|  | 12:50 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 13:03 | 15:19 | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work
| 13:16 | 15:08 | Bogura-Sirajganj 230 kV Ckt-2 Forced S/D from Bogura 230/132kV end Due to 98 No Tower
Insulator maintenance
|  | 14:33 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
| 14:50 | 16:44 | Kishoreganj-Mymensingh 132kV Ckt-1 Project Work S/D from Kishoreganj 132/33kV end Due to
G to G Project worek
|  | 17:51 | Hathazari 230/132/33kV S/S MT-04 LT is restored.
|  | 17:51 | Hathazari 230/132/33kV S/S MT-04 HT is restored.
|  | 17:52 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 17:54 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
| 19:00 |  | Evening Peak Gen. 12219 MW
| 19:00 |  | Evening Peak Generation: 12219 MW.
| 02:59 |  | Meghnaghat CCPP 450 MW GT-1 was sync.
| 02:59 |  | Meghnaghat 450 MW CCPP (MPL) GT-1 Synchronized with remarks:- None
| 03:29 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 03:37 |  | Unique Meghnaghat Power 584 MW CCPP was shut down at 03:37 hours.
| 03:37 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 05:00 |  | Min. Gen. 8634 MW
| 07:17 | 07:28 | Kurigram-Rangpur 132kV Ckt-1 Tripped from Rangpur 132/33kV end showing SPS auxiliary | [7 empty] | 55.0MW load
|  |  | relay relays. | [7 empty] | interrup. Rangpur
132/33kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 140 | 5312719 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 71900 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 302 | 8110800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5414000 | Unit-2 shut down for leak repairing
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 534884 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6645330 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 494820 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 1654080 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 269954 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 265164 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 441000 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 432000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16 | 375480 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 502800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 3882567 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 1854144 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1091520 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 792000 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 105961 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 475200 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 280 | 7297727.27 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 35 | 346800 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2277 | 46370850.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 213712.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119070 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 41 | 293280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 928980 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5285828 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2330945 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 1105872 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 84 | 847821 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2102400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 377760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 22 | 16224 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26402 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 51 | 1048800 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 413134 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2449700 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 952320 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 703800 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 108 | 381382 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1038 | 20045453 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 44160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 13578181.82 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2810.36 | 53265225.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4978000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 305 | 7564000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 824976 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 514560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 194 | 4549818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1138036 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 107 | 1264581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 489472 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 898800 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3501600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1654080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 326947 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 396600 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 50 | 322620 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 2 | 63840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 559680 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 417136 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1479.2 | 29464746
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 509760 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1120800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 232800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 267880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 126720 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 66240 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 126 | 2335350
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 887768 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3511473 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 34 | 768744 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 57936 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2069760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 506808 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7272500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7694800 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 968 | 22769789
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 21949090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 35 | 60960 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 155 | 3888288 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 310320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1066 | 26208658
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1743264 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 140501 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2892000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 14418909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4951770 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1286400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7244000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2758 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1511 | 32679602.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 41 | 469881 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 23 | 163969 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 30 | 178776 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 153 | 3962482 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9414109 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 314874 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 76824 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 27686 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 712720 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2312544 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1563744 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 754.79 | 18173192 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 247504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 250470 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1775.29 | 37888875
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 40000 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1997491 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38528.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 912453 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 202946 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 805680 | -
Rangpur Area Total |  |  |  |  | 950 | 208 | 3997098.28
Eastern Grid Total |  |  |  |  | 16856.242 | 7660.56 | 154205960.29
Western Grid Total |  |  |  |  | 10294.5 | 4560.29 | 100774233.37
National Grid Total |  |  |  |  | 27150.742 | 12220.85 | 254980193.66
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8247 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3431.4 | MW
i) Dhaka area |  |  | 4522.5 |  | MW | i) Khulna area |  |  |  | 1194 | MW
ii) Chattogram area |  |  | 1340.5 |  | MW | ii) Barishal area |  |  |  | 302 | MW
iii) Cumilla area |  |  | 1021 |  | MW | iii) Rajshahi area |  |  |  | 1151.4 | MW
iv) Mymensingh area |  |  | 944 |  | MW | iv) Rangpur area |  |  |  | 784 | MW
v) Sylhet area |  |  | 419 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11678.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 08:00 | 133 | Postogola | 45 | 13:00
2 | AKSML | 125.5 | 06:00 | 68 | Jamalpur | 93 | 09:00 | 134 | Purbachal | 17 | 11:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 104 | 12:00 | 135 | Purbasadipur | 123 | 13:00
4 | Agargaon | 87 | 13:00 | 70 | Jhenaidah | 98 | 07:00 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 78 | 18:00 | 71 | Joydebpur | 145 | 18:30 | 137 | Rahim | 48 | 12:00
6 | Amnura | 60 | 08:00 | 72 | Joypurhat | 59 | 08:00 | 138 | Rajbari | 56 | 18:30
7 | Ashuganj | 84 | 19:00 | 73 | Juldah | 16 | 15:00 | 139 | Rajendrapur | 114 | 18:30
8 | BSRM | 185 | 04:00 | 74 | KSRM | 28 | 21:00 | 140 | Rajshahi | 86 | 13:00
9 | Bagerhat | 61 | 20:00 | 75 | Kabirpur | 263 | 18:30 | 141 | Rajshahi-230 | 54 | 13:00
10 | Bajitpur | 38 | 18:30 | 76 | Kachua | 56 | 20:00 | 142 | Ramganj | 90 | 18:30
11 | Bakulia | 80 | 18:30 | 77 | Kallyanpur | 72 | 18:30 | 143 | Rampur | 33 | 18:30
12 | Banani | 24 | 12:00 | 78 | Kalurghat | 34 | 12:00 | 144 | Rangamati | 13 | 18:00
13 | Bangabhaban | 11 | 10:00 | 79 | Kamrangirchar | 64.2 | 13:00 | 145 | Rangpur | 114 | 18:30
14 | Barapukuria | 62 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 4.6 | 16:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 88 | 18:30 | 147 | SSM | 16 | 01:00
16 | Barishal | 77 | 13:00 | 82 | Keranigonj | 66 | 13:00 | 148 | Saidpur | 115 | 09:00
17 | Barishal-230 | 74 | 18:30 | 83 | Khagrachori | 26 | 18:30 | 149 | Satkhira | 89 | 08:00
18 | Baroaulia | 75 | 12:00 | 84 | Khulna | 72 | 20:00 | 150 | Satmasjid | 84 | 13:00
19 | Baroirhat | 46 | 18:30 | 85 | Khulshi | 157 | 18:30 | 151 | Savar | 208 | 15:00
20 | Bashundhara | 148 | 13:00 | 86 | Kishoreganj | 100 | 18:30 | 152 | SevenRings | 19.8 | 17:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 202 | 18:00 | 153 | ShahCement | 28 | 23:00
22 | Beanibazar | 46 | 18:30 | 88 | Kulaura | 29 | 18:30 | 154 | Shahjadpur | 73 | 07:00
23 | Benapole | 53 | 08:00 | 89 | Kurigram | 64 | 08:00 | 155 | Shahjibazar | 93 | 18:30
24 | Bhaluka | 114 | 10:00 | 90 | Kushtia | 106 | 18:30 | 156 | Shahmirpur | 47 | 15:00
25 | Bhandaria | 54 | 21:00 | 91 | Lalbag | 73 | 13:00 | 157 | Shariatpur | 55 | 18:30
26 | Bhangura | 31 | 19:00 | 92 | Lalmonirhat | 52 | 18:30 | 158 | Sherpur | 122 | 22:00
27 | Bheramara(GK) | 38 | 19:00 | 93 | MI_Cement | 17 | 13:00 | 159 | Shikalbaha | 24 | 18:00
28 | Bhulta | 243 | 19:30 | 94 | Madanganj | 34 | 13:00 | 160 | Shitalakhya | 70.6 | 12:00
29 | Bog-Sherpur | 72 | 08:00 | 95 | Madaripur | 70 | 21:00 | 161 | Sholosohor | 35 | 15:00
30 | Bogura | 121 | 19:00 | 96 | Madartek | 69.01 | 18:30 | 162 | Shyampur | 180 | 09:00
31 | Borhanuddin | 59 | 21:00 | 97 | Madunaghat | 41 | 18:30 | 163 | Siddhirganj | 113 | 12:00
32 | Brahmanbaria | 112 | 20:00 | 98 | Magura | 45 | 19:00 | 164 | Sirajganj | 92 | 08:00
33 | Cantonment | 102 | 13:00 | 99 | Mahasthangarh | 74 | 09:00 | 165 | Sonargaon | 99 | 18:00
34 | Chandpur | 49 | 19:30 | 100 | Manikganj | 109 | 18:30 | 166 | Sreemongol | 53 | 18:00
35 | Chandraghona | 26 | 18:30 | 101 | Maniknagar | 76 | 13:00 | 167 | Sreepur | 99 | 09:00
36 | Chapai | 65 | 07:00 | 102 | Matarbari | 42 | 18:30 | 168 | Srinagar | 31.13 | 21:00
37 | Charsaidpur | 42 | 11:00 | 103 | Matuail | 64 | 17:00 | 169 | Sunamganj | 40 | 18:30
38 | Chauddagram | 50 | 14:00 | 104 | Millgate | 80 | 12:00 | 170 | Sylhet | 26 | 18:00
39 | Chhatak | 26 | 18:30 | 105 | Mirpur | 111 | 18:30 | 171 | Sylhet-132 | 90 | 18:00
40 | Chowmuhani | 153 | 18:00 | 106 | Mirsorai | 9 | 11:00 | 172 | TK | 24.5 | 18:30
41 | Chuadanga | 70 | 08:00 | 107 | Mirzapur | 38 | 13:00 | 173 | Tangail | 152 | 20:00
42 | Coxsbazar | 119 | 18:00 | 108 | Mithapukur | 50 | 08:00 | 174 | Thakurgaon | 77 | 08:00
43 | Cumilla(N) | 150 | 19:30 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 100 | 11:00
44 | Cumilla(S) | 118 | 14:00 | 110 | Mogbazar | 123.7 | 13:00 | 176 | Ullahpara | 28 | 07:00
45 | Daudkandi | 112 | 13:00 | 111 | Mongla | 41 | 11:00 | 177 | Ullon | 34 | 21:00
46 | Dhaka | 38 | 13:00 | 112 | Motijheel | 36 | 13:00 | 178 | Uttara | 71 | 13:00
47 | Dhamrai | 110 | 08:00 | 113 | Muktagacha | 32 | 07:00 | 179 | UttaraNew | 35 | 13:00
48 | Dhanmondi | 117 | 13:00 | 114 | Munshiganj | 72 | 13:00 | 180 | Zigatola | 60 | 13:00
49 | Dohazari | 79 | 19:30 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 108 | 18:30 | 116 | Mymensingh | 167 | 19:00
51 | Fatullah | 77 | 12:00 | 117 | Naogaon | 119 | 09:00
52 | Fenchuganj | 26 | 13:00 | 118 | Narail | 40 | 08:00
53 | Feni | 87 | 18:30 | 119 | Narinda | 71.5 | 13:00
54 | GPH | 101 | 08:00 | 120 | Narshingdi | 146 | 19:30
55 | Ghatail | 46 | 07:00 | 121 | Natore | 109 | 13:00
56 | Ghorashal | 13 | 08:00 | 122 | Nawabganj | 30 | 21:00
57 | Ghorashal-230 | 60 | 21:00 | 123 | Netrakona | 135 | 18:00
58 | Goalpara | 24 | 13:00 | 124 | New | 75.3 | 12:00
59 | Gollamari | 58 | 00:00 | 125 | Niamatpur | 96 | 09:00
60 | Gopalganj | 70.8 | 18:30 | 126 | Noapara | 36 | 19:00
61 | Gulshan | 96 | 13:00 | 127 | PHP | 9 | 13:00
62 | Halishahar | 72 | 15:00 | 128 | Pabna | 76 | 18:30
63 | HaripurSBU | 164 | 01:00 | 129 | Palashbari | 110 | 08:00
64 | Hasnabad | 80 | 14:00 | 130 | Panchagarh | 45 | 18:30
65 | Hathazari | 60 | 19:00 | 131 | Patuakhali | 52.4 | 21:00
66 | Ishurdi | 63 | 19:00 | 132 | Payra | 20 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 10186.13 | 0 |  | 10186.13
1:00 | 9695.7 | 0 |  | 9695.7
2:00 | 9106.1 | 0 |  | 9106.1
3:00 | 8754 | 0 |  | 8754
4:00 | 8533.53 | 0 |  | 8533.53
5:00 | 8521.25 | 0 |  | 8521.25
6:00 | 8844.76 | 0 |  | 8844.76
7:00 | 9608.95 | 70 |  | 9681.95
8:00 | 10588.34 | 70 |  | 10661.34
9:00 | 10900.5 | 65 |  | 10968.5
10:00 | 10952.83 | 67 |  | 11022.83
11:00 | 10984.98 | 65 |  | 11052.98
12:00 | 11511.26 | 78 |  | 11593.26
13:00 | 11795.14 | 65 |  | 11863.14
14:00 | 11387.77 | 72 |  | 11462.77
15:00 | 11091.01 | 64 |  | 11158.01
16:00 | 10971.76 | 63 |  | 11037.76
17:00 | 10795.59 | 64 |  | 10862.59
18:00 | 11405.06 | 111 |  | 11521.06
19:00 | 12220.85 | 92 |  | 12316.85
19:30 | 11845.93 | 86 |  | 11935.93
20:00 | 11652.93 | 70 |  | 11726.08
21:00 | 11476.56 | 20 |  | 11497.46
22:00 | 11069.5 | 15 |  | 11085.5
23:00 | 10629.5 | 0 |  | 10629.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 20-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2920 | 1648.5 | 924 | 0 | 58 | 758.63 | 40 | 2117 | 0 | 343 | 1377 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2922 | 1673 | 923.5 | 0 | 56 | 757.675 | 40 | 2116.5 | 0.24 | 208.5 | 1243.5 | 0 | 0 | 0 | 0 | 20-02-2025
01:00 | 2924 | 1697.5 | 923 | 0 | 54 | 756.72 | 40 | 2116 | 0.48 | 74 | 1110 | 0 | 0 | 0 | 0
01:30 | 2902 | 1691 | 923 | 0 | 54 | 757.16 | 40 | 2117 | 0.24 | 37 | 879.5 | 0 | 0 | 0 | 0 | Energy Generated | 254.9802 |  | MKWHr
02:00 | 2880 | 1684.5 | 923 | 0 | 54 | 757.6 | 40 | 2118 | 0 | 0 | 649 | 0 | 0 | 0 | 0 | Energy not Served | 1.051 |  | MKWHr
02:30 | 2868.5 | 1687.5 | 923 | 0 | 52 | 757.05 | 40 | 2117 | 0 | 0 | 485 | 0 | 0 | 0 | 0 | Total Energy Requirement | 256.0312 |  | MKWHr
03:00 | 2857 | 1690.5 | 923 | 0 | 50 | 756.5 | 40 | 2116 | 0 | 0 | 321 | 0 | 0 | 0 | 0
03:30 | 2884 | 1680 | 923.5 | 0 | 50 | 755.265 | 40 | 2089 | 0 | 0 | 222 | 0 | 0 | 0 | 0
04:00 | 2911 | 1669.5 | 924 | 0 | 50 | 754.03 | 40 | 2062 | 0 | 0 | 123 | 0 | 0 | 0 | 0
04:30 | 2889.5 | 1679.5 | 923.5 | 0 | 50 | 756.39 | 40 | 2060.5 | 0 | 0 | 126.5 | 0 | 0 | 1.5 | 0
05:00 | 2868 | 1689.5 | 923 | 0 | 50 | 758.75 | 40 | 2059 | 0 | 0 | 130 | 0 | 0 | 3 | 0
05:30 | 2884.5 | 1739.5 | 923 | 0 | 50 | 757.505 | 40 | 2060 | 0 | 10.5 | 213.5 | 0 | 0 | 4.5 | 0
06:00 | 2901 | 1789.5 | 923 | 0 | 50 | 756.26 | 40 | 2061 | 0 | 21 | 297 | 0 | 0 | 6 | 0
06:30 | 2994 | 1766 | 923.5 | 0 | 52 | 758.275 | 40 | 2089.5 | 12.08 | 59.5 | 528 | 0 | 0 | 4 | 35
07:00 | 3087 | 1742.5 | 924 | 0 | 54 | 760.29 | 40 | 2118 | 24.16 | 98 | 759 | 0 | 0 | 2 | 70
07:30 | 3080 | 1733.25 | 914 | 0 | 59 | 759.52 | 40 | 2118.5 | 86.875 | 124 | 1180 | 0 | 0 | 3.5 | 70
08:00 | 3073 | 1724 | 904 | 0 | 64 | 758.75 | 40 | 2119 | 149.59 | 150 | 1601 | 0 | 0 | 5 | 70
08:30 | 3009 | 1696.75 | 890.5 | 0 | 67 | 758.375 | 40 | 2112 | 221.295 | 188 | 1757 | 0 | 0 | 4.5 | 67.5
09:00 | 2945 | 1669.5 | 877 | 0 | 70 | 758 | 40 | 2105 | 293 | 226 | 1913 | 0 | 0 | 4 | 65
09:30 | 2918 | 1663 | 900 | 0 | 72 | 757 | 40 | 2138.5 | 349.665 | 260 | 1825 | 0 | 0 | 3.5 | 66
10:00 | 2891 | 1656.5 | 923 | 0 | 74 | 756 | 40 | 2172 | 406.33 | 294 | 1737 | 0 | 0 | 3 | 67
10:30 | 2850 | 1636.5 | 922.5 | 0 | 74 | 757.5 | 40 | 2258.5 | 409.405 | 294 | 1725 | 0 | 0 | 1.5 | 66
11:00 | 2809 | 1616.5 | 922 | 0 | 74 | 759 | 40 | 2345 | 412.48 | 294 | 1713 | 0 | 0 | 0 | 65
11:30 | 2854.5 | 1641 | 923 | 0 | 77 | 759.5 | 40 | 2377 | 420.62 | 352 | 1803.5 | 0 | 0 | 0 | 71.5
12:00 | 2900 | 1665.5 | 924 | 0 | 80 | 760 | 40 | 2409 | 428.76 | 410 | 1894 | 0 | 0 | 0 | 78
12:30 | 2879.5 | 1681.5 | 924 | 0 | 81 | 760.5 | 40 | 2427 | 377.525 | 435.5 | 2046.675 | 0 | 0 | 0 | 71.5
13:00 | 2859 | 1697.5 | 924 | 0 | 82 | 761 | 40 | 2445 | 326.29 | 461 | 2199.35 | 0 | 0 | 0 | 65
13:30 | 2785.5 | 1651.5 | 924 | 0 | 84 | 760.015 | 40 | 2389.5 | 327.585 | 476.5 | 2152.855 | 0 | 0 | 0 | 68.5
14:00 | 2712 | 1605.5 | 924 | 0 | 86 | 759.03 | 40 | 2334 | 328.88 | 492 | 2106.36 | 0 | 0 | 0 | 72
14:30 | 2716 | 1591.5 | 923.5 | 0 | 84 | 759.165 | 40 | 2344 | 292.045 | 486.5 | 2001.68 | 0 | 0 | 1 | 68
15:00 | 2720 | 1577.5 | 923 | 0 | 82 | 759.3 | 40 | 2354 | 255.21 | 481 | 1897 | 0 | 0 | 2 | 64
15:30 | 2718 | 1581 | 923 | 0 | 81 | 759.28 | 40 | 2378 | 209.605 | 508.5 | 1829 | 0 | 0 | 4 | 63.5
16:00 | 2716 | 1584.5 | 923 | 0 | 80 | 759.26 | 40 | 2402 | 164 | 536 | 1761 | 0 | 0 | 6 | 63
16:30 | 2705 | 1599 | 922.5 | 0 | 80 | 758.72 | 40 | 2405.5 | 108.955 | 539.5 | 1720 | 0 | 0 | 4.5 | 63.5
17:00 | 2694 | 1613.5 | 922 | 0 | 80 | 758.18 | 40 | 2409 | 53.91 | 543 | 1679 | 0 | 0 | 3 | 64
17:30 | 2630.5 | 1612.5 | 923 | 0 | 83 | 756.19 | 40 | 2424 | 26.955 | 604 | 1996.18 | 0 | 0 | 4 | 87.5
18:00 | 2567 | 1611.5 | 924 | 0 | 86 | 754.2 | 40 | 2439 | 0 | 665 | 2313.36 | 0 | 0 | 5 | 111
18:30 | 2700 | 1671 | 900 | 0 | 83 | 754.495 | 40 | 2479.5 | 0 | 677 | 2504.96 | 0 | 0 | 3 | 101.5
19:00 | 2833 | 1730.5 | 876 | 0 | 80 | 754.79 | 40 | 2520 | 0 | 689 | 2696.56 | 0 | 0 | 1 | 92
19:30 | 2807 | 1739.5 | 877 | 0 | 78 | 755.43 | 40 | 2542 | 0 | 638 | 2369 | 0 | 0 | 0 | 86
20:00 | 2816 | 1715.5 | 877 | 0 | 76 | 755.43 | 40 | 2542 | 0 | 564 | 2252 | 15 | 0 | 0 | 70
20:30 | 2821 | 1729.75 | 877 | 0 | 76 | 755.495 | 40 | 2542 | 0 | 551 | 2157 | 15.5 | 0 | 0 | 45
21:00 | 2826 | 1744 | 877 | 0 | 76 | 755.56 | 40 | 2542 | 0 | 538 | 2062 | 16 | 0 | 0 | 20
21:30 | 2822.5 | 1737.75 | 900.5 | 0 | 74 | 758.28 | 40 | 2541.5 | 0 | 455 | 1927.5 | 16 | 0 | 0 | 17.5
22:00 | 2819 | 1731.5 | 924 | 0 | 72 | 761 | 40 | 2541 | 0 | 372 | 1793 | 16 | 0 | 0 | 15
22:30 | 2817 | 1717 | 924 | 0 | 71 | 759.5 | 40 | 2542 | 0 | 363 | 1608 | 8 | 0 | 0 | 7.5
23:00 | 2815 | 1702.5 | 924 | 0 | 70 | 758 | 40 | 2543 | 0 | 354 | 1423 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6055 | 4131.13 | 10186.13 | DAILY GENERATION CURVE
00:30 | 5882 | 4058.915 | 9940.915
01:00 | 5709 | 3986.7 | 9695.7 | 20-02-2025
01:30 | 5547 | 3853.9 | 9400.9
02:00 | 5385 | 3721.1 | 9106.1
02:30 | 5280 | 3650.05 | 8930.05
03:00 | 5175 | 3579 | 8754
03:30 | 5089.5 | 3554.265 | 8643.765
04:00 | 5004 | 3529.53 | 8533.53
04:30 | 4994.5 | 3532.89 | 8527.39
05:00 | 4985 | 3536.25 | 8521.25
05:30 | 5123 | 3560.005 | 8683.005
06:00 | 5261 | 3583.76 | 8844.76
06:30 | 5429.74 | 3797.115 | 9226.855
07:00 | 5598.48 | 4010.47 | 9608.95
07:30 | 5926.84 | 4171.805 | 10098.645
08:00 | 6255.2 | 4333.14 | 10588.34
08:30 | 6384.235 | 4360.185 | 10744.42
09:00 | 6513.27 | 4387.23 | 10900.5
09:30 | 6505.31 | 4421.355 | 10926.665
10:00 | 6497.35 | 4455.48 | 10952.83
10:30 | 6522.28 | 4446.625 | 10968.905
11:00 | 6547.21 | 4437.77 | 10984.98
11:30 | 6745.54 | 4502.58 | 11248.12
12:00 | 6943.87 | 4567.39 | 11511.26
12:30 | 7104.285 | 4548.915 | 11653.2
13:00 | 7264.7 | 4530.44 | 11795.14
13:30 | 7178.175 | 4413.28 | 11591.455
14:00 | 7091.65 | 4296.12 | 11387.77
14:30 | 6989.495 | 4249.895 | 11239.39
15:00 | 6887.34 | 4203.67 | 11091.01
15:30 | 6823.285 | 4208.1 | 11031.385
16:00 | 6759.23 | 4212.53 | 10971.76
16:30 | 6759.25 | 4124.425 | 10883.675
17:00 | 6759.27 | 4036.32 | 10795.59
17:30 | 6972.815 | 4127.51 | 11100.325
18:00 | 7186.36 | 4218.7 | 11405.06
18:30 | 7423.46 | 4389.495 | 11812.955
19:00 | 7660.56 | 4560.29 | 12220.85
19:30 | 7307 | 4538.93 | 11845.93
20:00 | 7120 | 4532.93 | 11652.93
20:30 | 7063.75 | 4500.995 | 11564.745 |  | Executive Engineer
21:00 | 7007.5 | 4469.06 | 11476.56 |  | Network Operation Division
21:30 | 6825.25 | 4447.78 | 11273.03
22:00 | 6643 | 4426.5 | 11069.5
22:30 | 6497.5 | 4352 | 10849.5
23:00 | 6352 | 4277.5 | 10629.5

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 402 | 05:00 | 381 | 12:00 | Payra | 423 | 18:00 | 413 | 12:00
Ashuganj | 407 | 5:00 | 382 | 12:00 | Rahanpur | 416 | 18:00 | 396 | 08:00
Bhulta | 403 | 05:00 | 379 | 12:00 | Rampal | 417 | 18:00 | 393 | 12:00
Bibiana | 408 | 20:00 | 395 | 12:00
BIPTC | 403 | 23:00 | 395 | 11:00
Bogura | 419 | 18:00 | 390 | 08:00
Gopalganj | 414 | 18:00 | 396 | 12:00
Kaliakoir | 393 | 19:30 | 380 | 12:00
Madunaghat | 405 | 14:00 | 397 | 12:00
Meghnaghat | 397 | 05:00 | 381 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 05:00 | 217 | 12:00 | Keranigonj | 230 | 05:00 | 215 | 12:00
AKSML | 236 | 00:00 | 228 | 04:00 | Khulna(S) | 240 | 05:00 | 225 | 12:00
Aminbazar | 238 | 19:30 | 218 | 12:00 | Madunaghat | 235 | 08:00 | 230 | 04:00
Ashuganj | 239 | 00:00 | 220 | 11:00 | Madunaghat-400 | 236 | 20:00 | 230 | 04:00
Ashuganj-400 | 241 | 00:00 | 232 | 12:00 | Maniknagar | 234 | 05:00 | 219 | 12:00
Baghabari | 239 | 01:00 | 229 | 11:00 | Meghnaghat | 239 | 04:00 | 230 | 11:00
Barapukuria | 228 | 20:00 | 204 | 08:00 | Meghnaghat-400 | 234 | 05:00 | 223 | 12:00
Barapukuria-230 | 228 | 20:00 | 204 | 08:00 | Mirsorai | 236 | 08:00 | 227 | 04:00
Barishal | 243 | 01:00 | 238 | 10:00 | Rajshahi | 238 | 19:00 | 26 | 08:00
Bheramara | 236 | 00:00 | 224 | 12:00 | Rampal | 238 | 05:00 | 224 | 12:00
Bhulta | 233 | 05:00 | 220 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 19:00 | 226 | 12:00 | Rampura | 232 | 05:00 | 219 | 12:00
BIPTC | 239 | 05:00 | 225 | 12:00 | Shikalbaha | 236 | 09:00 | 229 | 04:00
Bogura | 241 | 18:00 | 226 | 08:00 | Shyampur | 230 | 00:00 | 216 | 12:00
Bogura-400 | 240 | 18:00 | 224 | 08:00 | Siddhirganj | 233 | 00:00 | 226 | 15:00
Borhanuddin | 246 | 19:00 | 241 | 12:00 | Sirajgonj | 244 | 00:00 | 234 | 08:00
BSRM | 234 | 08:00 | 226 | 12:00 | Sreepur | 236 | 21:00 | 223 | 12:00
Cumilla(N) | 233 | 01:00 | 223 | 12:00 | Tongi | 229 | 03:00 | 218 | 11:00
Faridpur | 245 | 18:00 | 234 | 12:00
Fenchuganj | 239 | 04:00 | 231 | 18:00
Ghorashal | 237 | 07:00 | 230 | 15:00
Ghorashal-230 | 232 | 01:00 | 221 | 12:00
Gopalganj | 242 | 18:30 | 232 | 12:00
GPH | 234 | 08:00 | 228 | 04:00
Haripur | 233 | 05:00 | 221 | 12:00
Hasnabad | 232 | 01:00 | 221 | 13:00
Hathazari | 238 | 19:00 | 232 | 10:00
Ishurdi | 238 | 00:00 | 227 | 12:00
Jhenaidah | 237 | 05:00 | 222 | 13:00
Kaliakoir | 229 | 19:30 | 218 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 03:00 | 121 | 12:00 | Magura | 138 | 03:00 | 127 | 12:00
Agargaon | 134 | 05:00 | 124 | 12:00 | Mahasthangarh | 137 | 20:00 | 126 | 08:00
Agrabad | 135 | 08:00 | 130 | 11:00 | Manikganj | 137 | 23:00 | 132 | 12:00
AKS | 133 | 07:00 | 130 | 02:00 | Maniknagar | 130 | 00:00 | 122 | 12:00
Aminbazar | 137 | 19:30 | 124 | 10:00 | Matarbari | 127 | 14:00 | 119 | 19:30
Amnura | 142 | 20:00 | 127 | 08:00 | Matuail | 133 | 02:00 | 125 | 12:00
Ashuganj | 140 | 00:00 | 135 | 12:00 | Millgate | 134 | 20:00 | 125 | 12:00
Bagerhat | 137 | 16:00 | 124 | 12:00 | Mirpur | 136 | 18:00 | 122 | 12:00
Bajitpur | 135 | 00:00 | 128 | 12:00 | Mirzapur | 134 | 00:00 | 129 | 12:00
Bakulia | 136 | 08:00 | 132 | 03:00 | Mithapukur | 138 | 18:00 | 121 | 07:00
Banani | 131 | 01:00 | 121 | 12:00 | MI_Cement | 134 | 03:00 | 125 | 12:00
Bangabhaban | 132 | 02:00 | 122 | 12:00 | Modern | 0 | 00:00 | 0 | 00:00
Barapukuria | 137 | 18:00 | 123 | 07:00 | Mogbazar | 133 | 03:00 | 123 | 12:00
Barguna | 139 | 18:00 | 134 | 03:00 | Mongla | 136 | 15:00 | 125 | 12:00
Barishal | 138 | 18:00 | 133 | 12:00 | Motijheel | 132 | 02:00 | 122 | 12:00
Barishal-230 | 138 | 20:00 | 133 | 12:00 | Muktagacha | 128 | 00:00 | 117 | 12:00
Baroaulia | 136 | 06:00 | 131 | 10:00 | Munshiganj | 133 | 04:00 | 124 | 12:00
Baroirhat | 134 | 08:00 | 127 | 12:00 | Muradnagar | 134 | 00:00 | 127 | 12:00
Bashundhara | 133 | 03:00 | 121 | 12:00 | Mymensingh | 127 | 00:00 | 114 | 12:00
BashundharaCement | 132 | 01:00 | 124 | 12:00 | Naogaon | 136 | 20:00 | 122 | 08:00
Beanibazar | 136 | 02:00 | 128 | 12:00 | Narail | 137 | 03:00 | 127 | 12:00
Benapole | 135 | 16:00 | 123 | 19:30 | Narinda | 130 | 00:00 | 122 | 12:00
Bhaluka | 128 | 03:00 | 118 | 08:00 | Narshingdi | 132 | 03:00 | 118 | 12:00
Bhandaria | 136 | 15:00 | 130 | 12:00 | Natore | 137 | 00:00 | 130 | 08:00
Bhangura | 139 | 02:00 | 130 | 12:00 | Nawabganj | 136 | 20:00 | 123 | 12:00
Bheramara | 138 | 01:00 | 132 | 12:00 | Netrakona | 126 | 00:00 | 112 | 12:00
Bheramara(GK) | 139 | 02:00 | 132 | 12:00 | New | 134 | 00:00 | 125 | 12:00
Bhulta | 127 | 06:00 | 120 | 12:00 | Niamatpur | 140 | 20:00 | 131 | 08:00
Bog-Sherpur | 136 | 01:00 | 127 | 08:00 | Noapara | 137 | 04:00 | 127 | 12:00
Bogura | 138 | 00:00 | 129 | 08:00 | Pabna | 138 | 00:00 | 131 | 08:00
Bogura-230 | 139 | 18:00 | 129 | 08:00 | Palashbari | 132 | 00:00 | 116 | 08:00
Brahmanbaria | 133 | 00:00 | 126 | 12:00 | Panchagarh | 142 | 18:00 | 118 | 07:00
Cantonment | 134 | 05:00 | 124 | 12:00 | Patuakhali | 139 | 00:00 | 132 | 02:00
Chandpur | 138 | 21:00 | 127 | 02:00 | Payra | 138 | 18:00 | 132 | 12:00
Chandraghona | 136 | 08:00 | 132 | 11:00 | PHP | 133 | 08:00 | 125 | 12:00
Chapai | 138 | 01:00 | 128 | 08:00 | Postogola | 136 | 05:00 | 127 | 12:00
Charsaidpur | 133 | 03:00 | 125 | 12:00 | Purbachal | 132 | 04:00 | 121 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 134 | 08:00 | 127 | 11:00 | Purbasadipur | 135 | 18:00 | 120 | 06:00
Chhatak | 133 | 04:00 | 125 | 11:00 | Rahanpur | 140 | 00:00 | 133 | 08:00
Chowmuhani | 130 | 07:00 | 126 | 02:00 | Rahanpur-400 | 141 | 18:00 | 134 | 08:00
Chuadanga | 137 | 00:00 | 127 | 08:00 | Rahim | 133 | 05:00 | 124 | 13:00
Coxsbazar | 125 | 09:00 | 119 | 18:00 | Rajbari | 135 | 05:00 | 130 | 12:00
Cumilla(N) | 136 | 01:00 | 129 | 12:00 | Rajendrapur | 134 | 00:00 | 124 | 13:00
Cumilla(S) | 136 | 08:00 | 127 | 11:00 | Rajshahi | 138 | 01:00 | 130 | 12:00
Daudkandi | 132 | 18:00 | 126 | 11:00 | Rajshahi-230 | 138 | 01:00 | 125 | 08:00
Dhaka | 132 | 00:00 | 122 | 12:00 | Ramganj | 133 | 09:00 | 126 | 05:00
Dhamrai | 131 | 06:00 | 123 | 12:00 | Rampur | 135 | 08:00 | 130 | 11:00
Dhanmondi | 132.5 | 05:00 | 125 | 12:00 | Rampura | 132 | 05:00 | 122 | 12:00
Dohazari | 132 | 17:00 | 128 | 22:00 | Rangamati | 135 | 08:00 | 132 | 06:00
Faridpur | 136 | 04:00 | 130 | 12:00 | Rangpur | 134 | 18:00 | 118 | 07:00
Fatullah | 134 | 03:00 | 126 | 12:00 | Ruppur | 139 | 05:00 | 132 | 12:00
Fenchuganj | 138 | 04:00 | 133 | 12:00 | Saidpur | 135 | 18:00 | 116 | 07:00
Feni | 134 | 08:00 | 126 | 12:00 | Satkhira | 138 | 15:00 | 125 | 12:00
Ghatail | 128 | 00:00 | 119 | 12:00 | Satmasjid | 133 | 03:00 | 124 | 12:00
Ghorashal | 139 | 00:00 | 135 | 11:00 | Savar | 136 | 18:30 | 122 | 11:00
Goalpara | 139 | 05:00 | 129 | 12:00 | SevenRings | 139 | 05:00 | 133 | 12:00
Gollamari | 138 | 18:00 | 129 | 00:00 | ShahCement | 133 | 00:00 | 125 | 12:00
Gopalganj | 139 | 18:00 | 131 | 12:00 | Shahjadpur | 140 | 00:00 | 134 | 11:00
Gopalganj-400 | 141 | 18:00 | 134 | 12:00 | Shahjibazar | 137 | 01:00 | 129 | 12:00
Gulshan | 130 | 00:00 | 121 | 12:00 | Shahmirpur | 137 | 09:00 | 131 | 04:00
Halishahar | 136 | 08:00 | 131 | 11:00 | Shariatpur | 139 | 18:00 | 133 | 12:00
Haripur | 133 | 05:00 | 125 | 12:00 | Sherpur | 125 | 20:00 | 113 | 12:00
HaripurSBU | 132 | 01:00 | 125 | 12:00 | Shikalbaha | 125 | 08:00 | 119 | 04:00
Hasnabad | 136 | 01:00 | 127 | 11:00 | Shikalbaha-230 | 136 | 08:00 | 132 | 00:00
Hathazari | 138 | 19:00 | 134 | 17:00 | Shitalakhya | 134 | 03:00 | 125 | 12:00
Ishurdi | 140 | 00:00 | 133 | 08:00 | Sholosohor | 135 | 08:00 | 132 | 04:00
Jaldhaka | 133 | 14:00 | 113 | 07:00 | Shyampur | 134 | 03:00 | 125 | 12:00
Jamalpur | 128 | 20:00 | 119 | 12:00 | Shyampur-230 | 135 | 05:00 | 125 | 12:00
Jashore | 135 | 02:00 | 125 | 12:00 | Siddhirganj | 133 | 02:00 | 126 | 12:00
Jhenaidah | 137 | 00:00 | 129 | 07:00 | Sirajganj | 136 | 02:00 | 125 | 08:00
Jhenaidah-230 | 139 | 05:00 | 129 | 12:00 | Sonargaon | 131 | 00:00 | 124 | 12:00
Joydebpur | 136 | 23:00 | 126 | 12:00 | Sreemongol | 137 | 03:00 | 129 | 12:00
Joypurhat | 134 | 18:00 | 120 | 08:00 | Sreepur | 128 | 00:00 | 120 | 12:00
Juldah | 138 | 08:00 | 133 | 22:00 | Srinagar | 137 | 20:00 | 124 | 11:00
Kabirpur | 140 | 02:00 | 121 | 12:00 | SSM | 140 | 00:00 | 136 | 13:00
Kachua | 138 | 19:00 | 129 | 05:00 | Sunamganj | 133 | 03:00 | 124 | 13:00
Kaliakoir | 141 | 20:00 | 126 | 12:00 | Sylhet | 135 | 04:00 | 128 | 15:00
Kallyanpur | 132 | 03:00 | 126 | 12:00 | Sylhet-132 | 136 | 04:00 | 128 | 12:00
Kalurghat | 136 | 14:00 | 132 | 12:00 | Tangail | 130 | 00:00 | 124 | 11:00
Kamrangirchar | 137 | 21:00 | 123 | 12:00 | Thakurgaon | 141 | 18:00 | 115 | 07:00
Kaptai | N/A | N/A | N/A | N/A | TK | 136 | 08:00 | 133 | 03:00
Kazla | 131 | 02:00 | 122 | 12:00 | Tongi | 135 | 04:00 | 127 | 11:00
Keranigonj | 137 | 20:00 | 124 | 12:00 | Ullahpara | 137 | 00:00 | 127 | 08:00
Khagrachori | 135 | 09:00 | 130 | 12:00 | Ullon | 131 | 01:00 | 122 | 12:00
Khulna | 137 | 15:00 | 127 | 12:00 | Uttara | 136 | 00:00 | 122 | 12:00
Khulna(S) | 139 | 05:00 | 129 | 12:00 | UttaraNew | 134 | 05:00 | 125 | 12:00
Khulshi | 134 | 08:00 | 130 | 03:00 | Zigatola | 137 | 19:30 | 123 | 12:00
Kishoreganj | 133 | 00:00 | 125 | 12:00
Kodda | 139 | 19:30 | 125 | 12:00
KSRM | 137 | 14:00 | 131 | 04:00
Kulaura | 137 | 00:00 | 132 | 12:00
Kurigram | 132 | 14:00 | 115 | 07:00
Kushtia | 139 | 03:00 | 130 | 12:00
Lalbag | 136 | 21:00 | 124 | 12:00
Lalmonirhat | 133 | 14:00 | 122 | 08:00
Madanganj | 132 | 01:00 | 124 | 12:00
Madaripur | 139 | 18:00 | 133 | 14:00
Madartek | 132 | 05:00 | 122 | 12:00
Madunaghat | 136 | 08:00 | 132 | 04:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division