## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10195.83 | MW | 12:00 Hr. | Energy Generated |  |  | 231.0413 |  | MKWHr.
| Day Peak Demand |  |  | 10195.83 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.233 |  | MKWHr.
| Evening Peak Generation |  |  | 10580.47 | MW | 19:00 Hr. | Energy Demand |  |  | 231.2743 |  | MKWHr.
| Evening Peak Demand |  |  | 10580.47 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.2 |  | °C
| Minimum Generation of the Day |  |  | 8634.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 824.68 |  | MMCFD
| Maximum Generation of the Day |  |  | 10649.13 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.9982 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.0612 | 0 | 2.9247 | 0 | 0 | 0.2063 | 0 | 0 | 36.1922 | Gas | 110.8784 | Gas | 401656593.3888
| Chattogram Zone |  |  | 6.1139 | 35.4855 | 6.1215 | 0 | 0.9855 | 0.13968 | 0 | 0.08592 | 48.932 | Coal | 57.1591 | Coal | 386053180.9694
| Cumilla Zone |  |  | 20.7181 | 0 | 3.007 | 0 | 0 | 0.38076 | 1.4506 | 0 | 25.5564 | HFO | 18.3039 | HFO | 332076651.8
| Mymensingh Zone |  |  | 1.5283 | 0 | 1.3584 | 0 | 0 | 0.26656 | 0 | 0 | 3.1533 | HSD | 0.004 | HSD | 221960
| Sylhet Zone |  |  | 23.7032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7032 | Hydro | 0.9855 | Hydro | 98550
| Khulna Zone |  |  | 4.5242 | 0 | 0 | 0 | 0 | 0.57384 | 21.3185 | 0 | 26.4166 | Solar | 3.6034 | Solar | 58076249.4636
| Barishal Zone |  |  | 7.244 | 21.6736 | 1.0263 | 0 | 0 | 0.003822 | 0 | 0 | 29.9478 | Import | 40.0211 | Import | 206383142.69
| Rajshahi Zone |  |  | 13.9854 | 0 | 2.7193 | 0 | 0 | 1.0195 | 17.252 | 0 | 34.9763 | Wind | 0.08592 | Wind | 1257868.8
| Rangpur Zone |  |  | 0 | 0 | 1.1466 | 0.004 | 0 | 1.0129 | 0 | 0 | 2.1635
| Total |  |  | 110.8784 | 57.1591 | 18.3039 | 0.004 | 0.9855 | 3.6034 | 40.0211 | 0.08592 | 231.0413
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 401656593.3888 |  | Hydro | 98550
|  |  |  | Coal | 386053180.9694 |  | Solar | 58076249.4636
|  |  |  | HFO | 332076651.8 |  | Import | 206383142.69
|  |  |  | HSD | 221960 |  | Wind | 1257868.8
[5 empty] | Total: | 138,58,24,197 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3185 | Peak Hr Flow | 877.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7925454.613 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.252 | Peak Hr Flow | 759.97 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 440 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4506 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 632 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.0211 | Peak Hr Flow | 1702.97 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3506
|  |  |  | Chattogram |  | 0 |  | 1188
|  |  |  | Cumilla |  | 0 |  | 965
|  |  |  | Mymensingh |  | 0 |  | 927
|  |  |  | Sylhet |  | 0 |  | 389
|  |  |  | Khulna |  | 0 |  | 1183
|  |  |  | Barishal |  | 0 |  | 303
|  |  |  | Rajshahi |  | 0 |  | 1123
|  |  |  | Rangpur |  | 0 |  | 749
|  |  |  | Total |  | 0 |  | 10333
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:30 |  | Hathazari 230/132/33kV S/S T-02 LT Project Work S/D
| 08:30 |  | Hathazari 230/132/33kV S/S T-02 HT Project Work S/D
| 08:31 | 15:12 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Project Work S/D Due to Relay
replacement work
| 08:32 | 15:06 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Project Work S/D Due to Relay
replacement work
| 12:00 |  | Day Peak Generation: 10191 MW.
| 14:28 | 14:43 | Barguna 132/33kV S/S Transformer-1 LT Tripped showing Over Current & Earth Fault Relay. | [7 empty] | 5.0MW load
|  |  | relays Due to Over Current & Earth Fault for WZPDCL-2 Bus side D/S Flashing. | [7 empty] | interrup.
| 14:28 | 14:43 | Barguna 132/33kV S/S Transformer-2 LT Tripped showing Over Current & Earth Fault Relay | [7 empty] | 5.0MW load
|  |  | relays Due to Over Current & Earth Fault for WZPDCL-2 Bus side D/S Flashing. | [7 empty] | interrup.
| 19:00 |  | Evening peak Generation is 10578 MW
| 04:02 | 04:20 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Tripped showing Over Current relays Due to Fault
| 04:02 | 04:20 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Tripped showing Over Current relays Due to Fault
| 04:02 | 04:18 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Tripped showing Over Current relays Due to Fault
| 04:02 | 04:18 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Tripped showing Over Current relays Due to Fault
| 05:49 |  | Bagerhat-Mongla 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Mongla 132
kv bus maintenance work
| 05:49 |  | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Same as
monngla-1 line
| 06:48 |  | Coxsbazar 132/33kV S/S Main Bus Project Work S/D Due to CB replacement & new CB | [7 empty] | 88.0MW load
|  |  | commissioning | [7 empty] | interrup.
| 06:51 | 07:31 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to SD taken
by Cox'sBazar
| 06:51 |  | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to SD taken
by Cox'sBazar
| 07:03 |  | Bogura 132/33kV S/S Transformer-2 LT Project Work S/D Due to 33kv Bus Upgrading Work. | [7 empty] | 30.0MW load
interrup.
| 07:05 |  | Bogura 132/33kV S/S Transformer-2 HT Project Work S/D Due to 33kv Bus Upgrading Work. | [7 empty] | 30.0MW load
interrup.
| 07:20 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to 33kV outdoor bus maintenance wok | [7 empty] | 10.0MW load
|  |  | by BPDB | [7 empty] | interrup.
| 07:20 |  | Khulshi 132/33kV S/S 415T (T2) HT Scheduled S/D Due to 33kV outdoor bus maintenance wok | [7 empty] | 10.0MW load
|  |  | by BPDB. | [7 empty] | interrup.
| 07:25 |  | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to Oil centrifusing
| 07:26 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to Oil centrifusing work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 5525469 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9230400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8085500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7393040 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 67680 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 602880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 15 | 76472 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 99113 | Liquid fuel shortage
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15.5 | 344400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 424440 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 15 | 375480 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32.5 | 706100 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | line SD
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 508091 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 41 | 605664 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 420480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 394560 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 206297 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 149760 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 976363.64 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 1631 | 36192189.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115560 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 26880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 985500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5365069 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 86 | 1499599 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 356736 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 98449 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 1431360 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 37 | 748800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 99 | 654873 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 24200 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 70 | 1618360 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 152640 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 258436 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1217 | 26547271 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 85920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 8938181.82 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2459 | 48931955.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4671000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 300 | 7506000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 32 | 767304 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 697440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 4499636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1145858 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 38 | 868145 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 144346 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1015750 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 65 | 1656000 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1450560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 415130 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 4 | 83160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 22 | 255360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 380755 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1039 | 25556444
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 110 | 1528320 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 57 | 1056000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 216000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 254810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 5 | 86400 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 181 | 3153280
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 928680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3861491 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 31 | 730656 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58080 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 102432 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2060160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 519744 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7727500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7714500 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 958 | 23703243
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 21318545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 203 | 4524192 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 573840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1080 | 26416577
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 239136 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 141039 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 60 | 1966000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14539636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5137010 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 135 | 787200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7134000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3822 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1398 | 29947843.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 41 | 50317 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 33153 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 45103 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 176 | 3984036 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9919272 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 230000 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 82098 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 836864 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1185216 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 110 | 338688 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 759.97 | 17252001 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 300752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 691820 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1661.47 | 34976260
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 4000 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 103 | 464044 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37619.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 682516 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 193394 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 781920 | -
Rangpur Area Total |  |  |  |  | 950 | 173 | 2163493.76
Eastern Grid Total |  |  |  |  | 16856.242 | 6268 | 137537112.46
Western Grid Total |  |  |  |  | 10294.5 | 4312.47 | 93504174.12
National Grid Total |  |  |  |  | 27150.742 | 10580.47 | 231041286.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6975.4 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3358.1 | MW
i) Dhaka area |  |  | 3506.4 |  | MW | i) Khulna area |  |  |  | 1182.9 | MW
ii) Chattogram area |  |  | 1188 |  | MW | ii) Barishal area |  |  |  | 303 | MW
iii) Cumilla area |  |  | 965 |  | MW | iii) Rajshahi area |  |  |  | 1123.2 | MW
iv) Mymensingh area |  |  | 927 |  | MW | iv) Rangpur area |  |  |  | 749 | MW
v) Sylhet area |  |  | 389 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10333.5 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 59 | 09:00 | 133 | Postogola | 36 | 00:00
2 | AKSML | 109 | 16:00 | 68 | Jamalpur | 107 | 13:00 | 134 | Purbachal | 19 | 13:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 100 | 13:00 | 135 | Purbasadipur | 128 | 12:00
4 | Agargaon | 76 | 13:00 | 70 | Jhenaidah | 100 | 19:00 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 66 | 21:00 | 71 | Joydebpur | 107 | 00:00 | 137 | Rahim | 41 | 04:00
6 | Amnura | 56 | 12:00 | 72 | Joypurhat | 56 | 08:00 | 138 | Rajbari | 52 | 19:00
7 | Ashuganj | 70 | 00:00 | 73 | Juldah | 16 | 00:00 | 139 | Rajendrapur | 96 | 00:00
8 | BSRM | 204 | 17:00 | 74 | KSRM | 23 | 00:00 | 140 | Rajshahi | 80 | 19:00
9 | Bagerhat | 62 | 19:00 | 75 | Kabirpur | 184 | 00:00 | 141 | Rajshahi-230 | 55 | 13:00
10 | Bajitpur | 41 | 18:30 | 76 | Kachua | 55 | 13:00 | 142 | Ramganj | 90 | 13:00
11 | Bakulia | 68 | 19:00 | 77 | Kallyanpur | 78 | 13:00 | 143 | Rampur | 30 | 22:00
12 | Banani | 16.6 | 18:30 | 78 | Kalurghat | 23 | 00:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 3 | 12:00 | 79 | Kamrangirchar | 52.4 | 00:00 | 145 | Rangpur | 105 | 13:00
14 | Barapukuria | 57 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 4.4 | 12:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 79 | 00:00 | 147 | SSM | 8 | 01:00
16 | Barishal | 70 | 13:00 | 82 | Keranigonj | 56 | 13:00 | 148 | Saidpur | 93 | 12:00
17 | Barishal-230 | 70 | 18:30 | 83 | Khagrachori | 26 | 18:30 | 149 | Satkhira | 89 | 19:00
18 | Baroaulia | 46 | 19:30 | 84 | Khulna | 72 | 20:00 | 150 | Satmasjid | 80 | 13:00
19 | Baroirhat | 43 | 19:00 | 85 | Khulshi | 145 | 19:00 | 151 | Savar | 132 | 00:00
20 | Bashundhara | 131 | 13:00 | 86 | Kishoreganj | 95 | 13:00 | 152 | SevenRings | 17.55 | 04:00
21 | BashundharaCement | 6 | 00:00 | 87 | Kodda | 157 | 00:00 | 153 | ShahCement | 35 | 20:00
22 | Beanibazar | 46 | 18:30 | 88 | Kulaura | 29 | 18:30 | 154 | Shahjadpur | 58 | 18:30
23 | Benapole | 46 | 08:00 | 89 | Kurigram | 60 | 18:30 | 155 | Shahjibazar | 82 | 19:00
24 | Bhaluka | 88 | 09:00 | 90 | Kushtia | 93 | 18:30 | 156 | Shahmirpur | 32 | 00:00
25 | Bhandaria | 36 | 21:00 | 91 | Lalbag | 55 | 00:00 | 157 | Shariatpur | 54 | 13:00
26 | Bhangura | 34 | 13:00 | 92 | Lalmonirhat | 48 | 18:30 | 158 | Sherpur | 146 | 18:30
27 | Bheramara(GK) | 38 | 18:30 | 93 | MI_Cement | 16.2 | 01:00 | 159 | Shikalbaha | 21 | 00:00
28 | Bhulta | 201 | 07:00 | 94 | Madanganj | 30 | 00:00 | 160 | Shitalakhya | 51.9 | 00:00
29 | Bog-Sherpur | 64 | 08:00 | 95 | Madaripur | 68 | 21:00 | 161 | Sholosohor | 29 | 00:00
30 | Bogura | 102 | 19:00 | 96 | Madartek | 64.35 | 12:00 | 162 | Shyampur | 146 | 04:00
31 | Borhanuddin | 56 | 22:00 | 97 | Madunaghat | 35 | 18:30 | 163 | Siddhirganj | 87 | 00:00
32 | Brahmanbaria | 114 | 13:00 | 98 | Magura | 45 | 19:00 | 164 | Sirajganj | 80 | 08:00
33 | Cantonment | 94 | 13:00 | 99 | Mahasthangarh | 56 | 08:00 | 165 | Sonargaon | 79 | 04:00
34 | Chandpur | 46 | 19:00 | 100 | Manikganj | 92 | 00:00 | 166 | Sreemongol | 47 | 19:30
35 | Chandraghona | 26 | 18:30 | 101 | Maniknagar | 56 | 22:00 | 167 | Sreepur | 78 | 00:00
36 | Chapai | 61 | 08:00 | 102 | Matarbari | 37 | 18:30 | 168 | Srinagar | 33.87 | 13:00
37 | Charsaidpur | 39 | 02:00 | 103 | Matuail | 50 | 00:00 | 169 | Sunamganj | 40 | 18:30
38 | Chauddagram | 51 | 18:30 | 104 | Millgate | 57 | 00:00 | 170 | Sylhet | 24 | 19:00
39 | Chhatak | 23 | 12:00 | 105 | Mirpur | 103 | 13:00 | 171 | Sylhet-132 | 80 | 13:00
40 | Chowmuhani | 148 | 18:30 | 106 | Mirsorai | 9 | 18:30 | 172 | TK | 22 | 17:00
41 | Chuadanga | 71 | 18:30 | 107 | Mirzapur | 39 | 12:00 | 173 | Tangail | 162 | 09:00
42 | Coxsbazar | 116 | 19:00 | 108 | Mithapukur | 53 | 08:00 | 174 | Thakurgaon | 80 | 09:00
43 | Cumilla(N) | 158 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 88 | 00:00
44 | Cumilla(S) | 99 | 13:00 | 110 | Mogbazar | 91.4 | 13:00 | 176 | Ullahpara | 26 | 18:00
45 | Daudkandi | 92 | 19:00 | 111 | Mongla | 27 | 00:00 | 177 | Ullon | 38 | 19:00
46 | Dhaka | 18 | 12:00 | 112 | Motijheel | 30 | 12:00 | 178 | Uttara | 64 | 13:00
47 | Dhamrai | 90 | 00:00 | 113 | Muktagacha | 30 | 12:00 | 179 | UttaraNew | 31 | 13:00
48 | Dhanmondi | 83.2 | 19:00 | 114 | Munshiganj | 72 | 13:00 | 180 | Zigatola | 56 | 13:00
49 | Dohazari | 74 | 18:30 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 95 | 00:00 | 116 | Mymensingh | 172 | 13:00
51 | Fatullah | 62 | 00:00 | 117 | Naogaon | 117 | 09:00
52 | Fenchuganj | 28 | 12:00 | 118 | Narail | 42 | 18:30
53 | Feni | 79 | 13:00 | 119 | Narinda | 50 | 13:00
54 | GPH | 91 | 02:00 | 120 | Narshingdi | 135 | 00:00
55 | Ghatail | 54 | 13:00 | 121 | Natore | 110 | 19:00
56 | Ghorashal | 13 | 00:00 | 122 | Nawabganj | 34 | 13:00
57 | Ghorashal-230 | 62 | 02:00 | 123 | Netrakona | 146 | 09:00
58 | Goalpara | 24 | 13:00 | 124 | New | 53.9 | 00:00
59 | Gollamari | 54 | 13:00 | 125 | Niamatpur | 92 | 08:00
60 | Gopalganj | 79.9 | 19:00 | 126 | Noapara | 29 | 19:00
61 | Gulshan | 66 | 12:00 | 127 | PHP | 7 | 02:00
62 | Halishahar | 39 | 13:00 | 128 | Pabna | 68 | 19:00
63 | HaripurSBU | 157 | 01:00 | 129 | Palashbari | 105 | 08:00
64 | Hasnabad | 69 | 14:00 | 130 | Panchagarh | 42 | 18:30
65 | Hathazari | 57 | 18:00 | 131 | Patuakhali | 49 | 21:00
66 | Ishurdi | 54 | 19:00 | 132 | Payra | 22 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 10136.5 | 0 |  | 10136.5
1:00 | 9728 | 0 |  | 9728
2:00 | 9317.5 | 0 |  | 9317.5
3:00 | 8989.5 | 0 |  | 8989.5
4:00 | 8641.5 | 0 |  | 8641.5
5:00 | 8634.5 | 0 |  | 8634.5
6:00 | 8684.5 | 0 |  | 8684.5
7:00 | 9091.88 | 50 |  | 9144.13
8:00 | 9485.18 | 65 |  | 9553.11
9:00 | 9556.67 | 67 |  | 9626.69
10:00 | 9501.35 | 40 |  | 9543.15
11:00 | 9733.27 | 11 |  | 9744.77
12:00 | 10195.83 | 0 |  | 10195.83
13:00 | 10649.13 | 0 |  | 10649.13
14:00 | 9568.86 | 0 |  | 9568.86
15:00 | 9059.67 | 0 |  | 9059.67
16:00 | 8860.47 | 0 |  | 8860.47
17:00 | 8784.76 | 0 |  | 8784.76
18:00 | 9438.61 | 0 |  | 9438.61
19:00 | 10580.47 | 0 |  | 10580.47
19:30 | 10446.55 | 0 |  | 10446.55
20:00 | 10423.63 | 0 |  | 10423.63
21:00 | 10423.01 | 0 |  | 10423.01
22:00 | 10207.73 | 0 |  | 10207.73
23:00 | 9808.68 | 0 |  | 9808.68
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6247 | 3889.5 | 10136.5 | DAILY GENERATION CURVE
00:30 | 6044.75 | 3887.5 | 9932.25
01:00 | 5842.5 | 3885.5 | 9728 | 21-02-2025
01:30 | 5686.25 | 3836.5 | 9522.75
02:00 | 5530 | 3787.5 | 9317.5
02:30 | 5425 | 3728.5 | 9153.5
03:00 | 5320 | 3669.5 | 8989.5
03:30 | 5155.5 | 3660 | 8815.5
04:00 | 4991 | 3650.5 | 8641.5
04:30 | 5016.5 | 3621.5 | 8638
05:00 | 5042 | 3592.5 | 8634.5
05:30 | 5102.5 | 3557 | 8659.5
06:00 | 5163 | 3521.5 | 8684.5
06:30 | 5317.345 | 3570.845 | 8888.19
07:00 | 5471.69 | 3620.19 | 9091.88
07:30 | 5569.075 | 3719.455 | 9288.53
08:00 | 5666.46 | 3818.72 | 9485.18
08:30 | 5655.27 | 3865.655 | 9520.925
09:00 | 5644.08 | 3912.59 | 9556.67
09:30 | 5562.31 | 3966.7 | 9529.01
10:00 | 5480.54 | 4020.81 | 9501.35
10:30 | 5600.045 | 4017.265 | 9617.31
11:00 | 5719.55 | 4013.72 | 9733.27
11:30 | 5819.695 | 4144.855 | 9964.55
12:00 | 5919.84 | 4275.99 | 10195.83
12:30 | 6065.415 | 4357.065 | 10422.48
13:00 | 6210.99 | 4438.14 | 10649.13
13:30 | 5906.26 | 4202.735 | 10108.995
14:00 | 5601.53 | 3967.33 | 9568.86
14:30 | 5454.225 | 3860.04 | 9314.265
15:00 | 5306.92 | 3752.75 | 9059.67
15:30 | 5333.825 | 3626.245 | 8960.07
16:00 | 5360.73 | 3499.74 | 8860.47
16:30 | 5342.81 | 3479.805 | 8822.615
17:00 | 5324.89 | 3459.87 | 8784.76
17:30 | 5548.445 | 3563.24 | 9111.685
18:00 | 5772 | 3666.61 | 9438.61
18:30 | 6020 | 3989.54 | 10009.54
19:00 | 6268 | 4312.47 | 10580.47
19:30 | 6293 | 4153.55 | 10446.55
20:00 | 6288 | 4135.63 | 10423.63
20:30 | 6302.25 | 4121.07 | 10423.32 |  | Executive Engineer
21:00 | 6316.5 | 4106.51 | 10423.01 |  | Network Operation Division
21:30 | 6262.25 | 4053.12 | 10315.37
22:00 | 6208 | 3999.73 | 10207.73
22:30 | 6074.5 | 3933.705 | 10008.205
23:00 | 5941 | 3867.68 | 9808.68

## En-Curve
QF-LDC-12
Date | 21-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2844 | 1688.5 | 924 | 0 | 66 | 754 | 40 | 2544 | 0 | 217 | 1057 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 2839 | 1725.25 | 924 | 0 | 65 | 754.5 | 40 | 2437 | 0 | 210.5 | 936 | 0 | 0 | 1 | 0 | 21-02-2025
01:00 | 2834 | 1762 | 924 | 0 | 64 | 755 | 40 | 2330 | 0 | 204 | 815 | 0 | 0 | 0 | 0
01:30 | 2835.5 | 1757.75 | 924 | 0 | 63 | 756.5 | 40 | 2285 | 0 | 142.5 | 713.5 | 0 | 0 | 5 | 0 | Energy Generated | 231.0413 |  | MKWHr
02:00 | 2837 | 1753.5 | 924 | 0 | 62 | 758 | 40 | 2240 | 0 | 81 | 612 | 0 | 0 | 10 | 0 | Energy not Served | 0.233 |  | MKWHr
02:30 | 2821 | 1763 | 924.5 | 0 | 61 | 760 | 40 | 2240.5 | 0 | 65 | 471 | 0 | 0 | 7.5 | 0 | Total Energy Requirement | 231.2743 |  | MKWHr
03:00 | 2805 | 1772.5 | 925 | 0 | 60 | 762 | 40 | 2241 | 0 | 49 | 330 | 0 | 0 | 5 | 0
03:30 | 2872 | 1633 | 925 | 0 | 59 | 759 | 40 | 2243 | 0 | 49 | 228.5 | 0 | 0 | 7 | 0
04:00 | 2939 | 1493.5 | 925 | 0 | 58 | 756 | 40 | 2245 | 0 | 49 | 127 | 0 | 0 | 9 | 0
04:30 | 2917 | 1510.5 | 925 | 0 | 58 | 756.5 | 40 | 2243.5 | 0 | 49 | 127 | 0 | 0 | 11.5 | 0
05:00 | 2895 | 1527.5 | 925 | 0 | 58 | 757 | 40 | 2242 | 0 | 49 | 127 | 0 | 0 | 14 | 0
05:30 | 2885.5 | 1568.5 | 879 | 0 | 58 | 758.5 | 40 | 2243 | 0 | 49 | 167.5 | 0 | 0 | 10.5 | 0
06:00 | 2876 | 1609.5 | 833 | 0 | 58 | 760 | 40 | 2244 | 0 | 49 | 208 | 0 | 0 | 7 | 0
06:30 | 2868.5 | 1645.5 | 832.5 | 0 | 57 | 760 | 40 | 2244 | 12.19 | 69 | 351.5 | 0 | 0 | 8 | 25
07:00 | 2861 | 1681.5 | 832 | 0 | 56 | 760 | 40 | 2244 | 24.38 | 89 | 495 | 0 | 0 | 9 | 50
07:30 | 2831.5 | 1673 | 855.5 | 0 | 55 | 759.5 | 40 | 2179 | 83.53 | 117.5 | 689 | 0 | 0 | 5 | 57.5
08:00 | 2802 | 1664.5 | 879 | 0 | 54 | 759 | 40 | 2114 | 142.68 | 146 | 883 | 0 | 0 | 1 | 65
08:30 | 2814 | 1664 | 879 | 0 | 54 | 758.5 | 40 | 2097 | 229.425 | 131 | 853.5 | 0 | 0 | 0.5 | 66
09:00 | 2826 | 1663.5 | 879 | 0 | 54 | 758 | 40 | 2080 | 316.17 | 116 | 824 | 0 | 0 | 0 | 67
09:30 | 2839.5 | 1661 | 902 | 0 | 55 | 743 | 40 | 2053 | 376.01 | 108 | 751.5 | 0 | 0 | 0 | 53.5
10:00 | 2853 | 1658.5 | 925 | 0 | 56 | 728 | 40 | 2026 | 435.85 | 100 | 679 | 0 | 0 | 0 | 40
10:30 | 2909 | 1658 | 925.5 | 0 | 57 | 697 | 40 | 2091 | 470.81 | 110 | 659 | 0 | 0 | 0 | 25.5
11:00 | 2965 | 1657.5 | 926 | 0 | 58 | 666 | 40 | 2156 | 505.77 | 120 | 639 | 0 | 0 | 0 | 11
11:30 | 2961 | 1601 | 926 | 0 | 61 | 690 | 40 | 2202 | 515.565 | 169 | 798.985 | 0 | 0 | 0 | 5.5
12:00 | 2957 | 1544.5 | 926 | 0 | 64 | 714 | 40 | 2248 | 525.36 | 218 | 958.97 | 0 | 0 | 0 | 0
12:30 | 2955.5 | 1597 | 926 | 0 | 67 | 735.5 | 40 | 2278.5 | 523.495 | 234.5 | 1064.985 | 0 | 0 | 0 | 0
13:00 | 2954 | 1649.5 | 926 | 0 | 70 | 757 | 40 | 2309 | 521.63 | 251 | 1171 | 0 | 0 | 0 | 0
13:30 | 2928 | 1579.75 | 925.5 | 0 | 67 | 713.5 | 40 | 2266.5 | 494.245 | 228.5 | 860.5 | 0 | 0 | 5.5 | 0
14:00 | 2902 | 1510 | 925 | 0 | 64 | 670 | 40 | 2224 | 466.86 | 206 | 550 | 0 | 0 | 11 | 0
14:30 | 2972.5 | 1523.75 | 889.5 | 0 | 61 | 666.14 | 40 | 2260 | 408.375 | 177 | 308 | 0 | 0 | 8 | 0
15:00 | 3043 | 1537.5 | 854 | 0 | 58 | 662.28 | 40 | 2296 | 349.89 | 148 | 66 | 0 | 0 | 5 | 0
15:30 | 3005.5 | 1546.5 | 794 | 0 | 58 | 660.255 | 40 | 2371.5 | 280.315 | 130.5 | 66 | 0 | 0 | 7.5 | 0
16:00 | 2968 | 1555.5 | 734 | 0 | 58 | 658.23 | 40 | 2447 | 210.74 | 113 | 66 | 0 | 0 | 10 | 0
16:30 | 3000.5 | 1555.5 | 734 | 0 | 57 | 658.145 | 40 | 2452 | 141.97 | 113 | 64 | 0 | 0 | 6.5 | 0
17:00 | 3033 | 1555.5 | 734 | 0 | 56 | 658.06 | 40 | 2457 | 73.2 | 113 | 62 | 0 | 0 | 3 | 0
17:30 | 3077.5 | 1536.5 | 734 | 0 | 60 | 683.585 | 40 | 2534.5 | 37.1 | 161 | 244.5 | 0 | 0 | 3 | 0
18:00 | 3122 | 1517.5 | 734 | 0 | 64 | 709.11 | 40 | 2612 | 1 | 209 | 427 | 0 | 0 | 3 | 0
18:30 | 3092.5 | 1557.5 | 805.5 | 0 | 65 | 734.54 | 40 | 2666.5 | 0.5 | 177.5 | 867 | 0 | 0 | 3 | 0
19:00 | 3063 | 1597.5 | 877 | 0 | 66 | 759.97 | 40 | 2721 | 0 | 146 | 1307 | 0 | 0 | 3 | 0
19:30 | 3135 | 1609 | 876 | 0 | 62 | 754.55 | 40 | 2724 | 0 | 88 | 1155 | 0 | 0 | 3 | 0
20:00 | 3131 | 1607.5 | 877 | 0 | 64 | 757.13 | 40 | 2728 | 0 | 88 | 1129 | 0 | 0 | 2 | 0
20:30 | 3137 | 1619.25 | 901 | 0 | 65 | 758.07 | 40 | 2728 | 0 | 88.5 | 1085.5 | 0 | 0 | 1 | 0
21:00 | 3143 | 1631 | 925 | 0 | 66 | 759.01 | 40 | 2728 | 0 | 89 | 1042 | 0 | 0 | 0 | 0
21:30 | 3163 | 1628.75 | 925 | 0 | 66 | 758.62 | 40 | 2729.5 | 0 | 89 | 915.5 | 0 | 0 | 0 | 0
22:00 | 3183 | 1626.5 | 925 | 0 | 66 | 758.23 | 40 | 2731 | 0 | 89 | 789 | 0 | 0 | 0 | 0
22:30 | 3162.5 | 1602.5 | 925 | 0 | 65 | 757.705 | 40 | 2729.5 | 0 | 65.5 | 660.5 | 0 | 0 | 0 | 0
23:00 | 3142 | 1578.5 | 925 | 0 | 64 | 757.18 | 40 | 2728 | 0 | 42 | 532 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 407 | 06:00 | 392 | 16:00 | Payra | 422 | 09:00 | 415 | 13:00
Ashuganj | 411 | 7:00 | 396 | 0:00 | Rahanpur | 414 | 19:00 | 398 | 08:00
Bhulta | 409 | 07:00 | 395 | 00:00 | Rampal | 414 | 02:00 | 394 | 13:00
Bibiana | 412 | 06:00 | 394 | 15:00
BIPTC | 405 | 06:00 | 394 | 13:00
Bogura | 413 | 19:00 | 392 | 08:00
Gopalganj | 413 | 06:00 | 400 | 13:00
Kaliakoir | 398 | 06:00 | 375 | 13:00
Madunaghat | 411 | 10:00 | 403 | 16:00
Meghnaghat | 404 | 06:00 | 395 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 07:00 | 228 | 00:00 | Keranigonj | 234 | 07:00 | 227 | 00:00
AKSML | 234 | 00:00 | 225 | 15:00 | Khulna(S) | 243 | 06:00 | 229 | 13:00
Aminbazar | 237 | 07:00 | 228 | 00:00 | Madunaghat | 235 | 07:00 | 228 | 15:00
Ashuganj | 241 | 06:00 | 236 | 01:00 | Madunaghat-400 | 236 | 08:00 | 228 | 16:00
Ashuganj-400 | 241 | 06:00 | 236 | 01:00 | Maniknagar | 235 | 07:00 | 229 | 00:00
Baghabari | 239 | 19:00 | 233 | 08:00 | Meghnaghat | 242 | 06:00 | 235 | 00:00
Barapukuria | 228 | 19:00 | 204 | 07:00 | Meghnaghat-400 | 237 | 06:00 | 231 | 00:00
Barapukuria-230 | 228 | 19:00 | 204 | 07:00 | Mirsorai | 233 | 09:00 | 224 | 17:00
Barishal | 243 | 05:00 | 238 | 13:00 | Rajshahi | 239 | 06:00 | 224 | 21:00
Bheramara | 239 | 06:00 | 231 | 12:00 | Rampal | 240 | 06:00 | 226 | 13:00
Bhulta | 237 | 06:00 | 229 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 235 | 05:00 | 227 | 14:00 | Rampura | 235 | 06:00 | 229 | 00:00
BIPTC | 242 | 06:00 | 231 | 13:00 | Shikalbaha | 235 | 09:00 | 225 | 15:00
Bogura | 240 | 19:00 | 226 | 08:00 | Shyampur | 234 | 06:00 | 228 | 00:00
Bogura-400 | 239 | 19:00 | 226 | 08:00 | Siddhirganj | 238 | 07:00 | 232 | 00:00
Borhanuddin | 246 | 00:00 | 242 | 21:00 | Sirajgonj | 245 | 19:00 | 239 | 13:00
BSRM | 232 | 07:00 | 224 | 17:00 | Sreepur | 239 | 06:00 | 234 | 01:00
Cumilla(N) | 235 | 07:00 | 229 | 15:00 | Tongi | 234 | 08:00 | 225 | 01:00
Faridpur | 246 | 06:00 | 224 | 18:00
Fenchuganj | 238 | 05:00 | 231 | 10:00
Ghorashal | 240 | 01:00 | 235 | 00:00
Ghorashal-230 | 236 | 07:00 | 229 | 00:00
Gopalganj | 243 | 06:00 | 235 | 13:00
GPH | 233 | 07:00 | 225 | 17:00
Haripur | 236 | 07:00 | 230 | 00:00
Hasnabad | 234 | 06:00 | 229 | 00:00
Hathazari | 238 | 06:00 | 227 | 17:00
Ishurdi | 242 | 06:00 | 233 | 13:00
Jhenaidah | 240 | 06:00 | 227 | 12:00
Kaliakoir | 238 | 08:00 | 226 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 129 | 15:00 | Magura | 139 | 06:00 | 130 | 13:00
Agargaon | 136 | 07:00 | 130 | 16:00 | Mahasthangarh | 137 | 19:00 | 127 | 08:00
Agrabad | 134 | 06:00 | 128 | 15:00 | Manikganj | 138 | 04:00 | 123 | 09:00
AKS | 133 | 07:00 | 128 | 16:00 | Maniknagar | 134 | 05:00 | 131 | 00:00
Aminbazar | 143 | 07:00 | 136 | 00:00 | Matarbari | 124 | 06:00 | 116 | 18:30
Amnura | 141 | 14:00 | 129 | 08:00 | Matuail | 135 | 09:00 | 131 | 00:00
Ashuganj | 142 | 06:00 | 138 | 00:00 | Millgate | 138 | 08:00 | 132 | 00:00
Bagerhat | 138 | 04:00 | 129 | 13:00 | Mirpur | 140 | 06:00 | 135 | 00:00
Bajitpur | 135 | 05:00 | 130 | 13:00 | Mirzapur | 136 | 06:00 | 128 | 12:00
Bakulia | 135 | 09:00 | 129 | 15:00 | Mithapukur | 137 | 18:30 | 119 | 08:00
Banani | 134 | 06:00 | 129 | 13:00 | MI_Cement | 136 | 06:00 | 131 | 00:00
Bangabhaban | 134 | 06:00 | 130 | 00:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 19:00 | 120 | 08:00 | Mogbazar | 135 | 06:00 | 128 | 10:00
Barguna | 138 | 19:00 | 131 | 15:00 | Mongla | 139 | 06:00 | 130 | 13:00
Barishal | 136 | 08:00 | 132 | 15:00 | Motijheel | 134 | 06:00 | 130 | 00:00
Barishal-230 | 137 | 19:00 | 132 | 13:00 | Muktagacha | 133 | 19:00 | 123 | 12:00
Baroaulia | 133 | 00:00 | 130 | 17:00 | Munshiganj | 135 | 09:00 | 130 | 00:00
Baroirhat | 132 | 09:00 | 123 | 15:00 | Muradnagar | 135 | 07:00 | 130 | 15:00
Bashundhara | 138 | 08:00 | 129 | 00:00 | Mymensingh | 132 | 19:00 | 118 | 13:00
BashundharaCement | 135 | 07:00 | 132 | 00:00 | Naogaon | 135 | 19:00 | 123 | 08:00
Beanibazar | 137 | 06:00 | 130 | 13:00 | Narail | 140 | 06:00 | 129 | 13:00
Benapole | 138 | 06:00 | 124 | 18:30 | Narinda | 134 | 05:00 | 131 | 00:00
Bhaluka | 129 | 04:00 | 121 | 13:00 | Narshingdi | 134 | 08:00 | 127 | 00:00
Bhandaria | 134 | 08:00 | 128 | 23:00 | Natore | 137 | 02:00 | 132 | 08:00
Bhangura | 137 | 01:00 | 133 | 08:00 | Nawabganj | 139 | 06:00 | 133 | 13:00
Bheramara | 139 | 06:00 | 135 | 08:00 | Netrakona | 126 | 01:00 | 116 | 13:00
Bheramara(GK) | 139 | 03:00 | 135 | 12:00 | New | 139 | 08:00 | 132 | 00:00
Bhulta | 132 | 03:00 | 124 | 00:00 | Niamatpur | 138 | 00:00 | 132 | 08:00
Bog-Sherpur | 136 | 02:00 | 128 | 08:00 | Noapara | 139 | 03:00 | 130 | 13:00
Bogura | 137 | 05:00 | 130 | 08:00 | Pabna | 139 | 06:00 | 134 | 17:00
Bogura-230 | 138 | 19:00 | 129 | 08:00 | Palashbari | 131 | 06:00 | 116 | 08:00
Brahmanbaria | 137 | 06:00 | 132 | 00:00 | Panchagarh | 140 | 19:00 | 121 | 07:00
Cantonment | 136 | 07:00 | 131 | 00:00 | Patuakhali | 140 | 19:00 | 131 | 00:00
Chandpur | 139 | 03:00 | 120 | 15:00 | Payra | 138 | 19:00 | 131 | 15:00
Chandraghona | 135 | 07:00 | 131 | 15:00 | PHP | 131 | 08:00 | 122 | 15:00
Chapai | 138 | 02:00 | 131 | 08:00 | Postogola | 139 | 05:00 | 134 | 00:00
Charsaidpur | 135 | 07:00 | 131 | 00:00 | Purbachal | 134 | 07:00 | 129 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 133 | 07:00 | 125 | 15:00 | Purbasadipur | 135 | 19:00 | 116 | 07:00
Chhatak | 136 | 06:00 | 126 | 12:00 | Rahanpur | 139 | 00:00 | 134 | 08:00
Chowmuhani | 130 | 06:00 | 119 | 15:00 | Rahanpur-400 | 140 | 02:00 | 134 | 08:00
Chuadanga | 139 | 06:00 | 129 | 13:00 | Rahim | 134 | 06:00 | 130 | 00:00
Coxsbazar | 123 | 02:00 | 118 | 18:00 | Rajbari | 136 | 06:00 | 131 | 13:00
Cumilla(N) | 137 | 08:00 | 130 | 15:00 | Rajendrapur | 137 | 19:30 | 130 | 16:00
Cumilla(S) | 135 | 07:00 | 128 | 15:00 | Rajshahi | 139 | 03:00 | 134 | 08:00
Daudkandi | 134 | 06:00 | 128 | 18:00 | Rajshahi-230 | 138 | 05:00 | 126 | 08:00
Dhaka | 133 | 08:00 | 129 | 00:00 | Ramganj | 133 | 07:00 | 117 | 15:00
Dhamrai | 136 | 09:00 | 131 | 00:00 | Rampur | 135 | 08:00 | 128 | 16:00
Dhanmondi | 135 | 07:00 | 130 | 13:00 | Rampura | 133 | 03:00 | 129 | 00:00
Dohazari | 131 | 08:00 | 124 | 19:00 | Rangamati | 135 | 03:00 | 129 | 17:00
Faridpur | 136 | 06:00 | 132 | 13:00 | Rangpur | 134 | 19:00 | 115 | 08:00
Fatullah | 137 | 06:00 | 133 | 00:00 | Ruppur | 140 | 04:00 | 136 | 07:00
Fenchuganj | 138 | 04:00 | 133 | 14:00 | Saidpur | 133 | 19:00 | 118 | 08:00
Feni | 131 | 08:00 | 124 | 15:00 | Satkhira | 139 | 06:00 | 129 | 13:00
Ghatail | 131 | 10:00 | 121 | 12:00 | Satmasjid | 136 | 09:00 | 131 | 00:00
Ghorashal | 141 | 19:00 | 138 | 00:00 | Savar | 141 | 08:00 | 134 | 00:00
Goalpara | 141 | 06:00 | 131 | 18:30 | SevenRings | 141 | 08:00 | 137 | 02:00
Gollamari | 139 | 05:00 | 133 | 13:00 | ShahCement | 135 | 07:00 | 131 | 00:00
Gopalganj | 140 | 06:00 | 133 | 13:00 | Shahjadpur | 142 | 03:00 | 136 | 10:00
Gopalganj-400 | 140 | 05:00 | 136 | 13:00 | Shahjibazar | 140 | 06:00 | 135 | 00:00
Gulshan | 133 | 08:00 | 128 | 00:00 | Shahmirpur | 134 | 04:00 | 129 | 15:00
Halishahar | 135 | 06:00 | 128 | 17:00 | Shariatpur | 139 | 04:00 | 134 | 15:00
Haripur | 134 | 06:00 | 131 | 00:00 | Sherpur | 125 | 10:00 | 112 | 13:00
HaripurSBU | 134 | 06:00 | 131 | 00:00 | Shikalbaha | 123 | 01:00 | 118 | 15:00
Hasnabad | 138 | 07:00 | 134 | 00:00 | Shikalbaha-230 | 136 | 08:00 | 129 | 16:00
Hathazari | 138 | 05:00 | 132 | 16:00 | Shitalakhya | 136 | 06:00 | 132 | 00:00
Ishurdi | 141 | 06:00 | 136 | 08:00 | Sholosohor | 134 | 02:00 | 121 | 14:00
Jaldhaka | 133 | 19:00 | 114 | 07:00 | Shyampur | 136 | 07:00 | 133 | 00:00
Jamalpur | 129 | 10:00 | 117 | 12:00 | Shyampur-230 | 136 | 06:00 | 132 | 00:00
Jashore | 137 | 04:00 | 128 | 13:00 | Siddhirganj | 135 | 03:00 | 131 | 00:00
Jhenaidah | 137 | 01:00 | 131 | 13:00 | Sirajganj | 136 | 13:00 | 128 | 08:00
Jhenaidah-230 | 141 | 06:00 | 132 | 13:00 | Sonargaon | 134 | 07:00 | 129 | 00:00
Joydebpur | 136 | 00:00 | 133 | 16:00 | Sreemongol | 138 | 05:00 | 133 | 12:00
Joypurhat | 133 | 03:00 | 121 | 08:00 | Sreepur | 130 | 06:00 | 126 | 10:00
Juldah | 135 | 13:00 | 129 | 15:00 | Srinagar | 140 | 06:00 | 133 | 13:00
Kabirpur | 139 | 09:00 | 130 | 00:00 | SSM | 137 | 00:00 | 132 | 16:00
Kachua | 135 | 01:00 | 123 | 15:00 | Sunamganj | 134 | 06:00 | 126 | 12:00
Kaliakoir | 142 | 06:00 | 131 | 00:00 | Sylhet | 136 | 05:00 | 129 | 13:00
Kallyanpur | 133 | 06:00 | 129 | 00:00 | Sylhet-132 | 135 | 02:00 | 130 | 13:00
Kalurghat | 135 | 06:00 | 131 | 18:00 | Tangail | 132 | 03:00 | 123 | 07:00
Kamrangirchar | 140 | 06:00 | 128 | 00:00 | Thakurgaon | 138 | 19:00 | 117 | 07:00
Kaptai | 136 | 4:00 | 124 | 12:00 | TK | 136 | 09:00 | 130 | 15:00
Kazla | 134 | 08:00 | 129 | 00:00 | Tongi | 140 | 08:00 | 134 | 00:00
Keranigonj | 140 | 06:00 | 133 | 13:00 | Ullahpara | 138 | 02:00 | 131 | 08:00
Khagrachori | 134 | 02:00 | 129 | 15:00 | Ullon | 133 | 03:00 | 129 | 00:00
Khulna | 138 | 06:00 | 131 | 13:00 | Uttara | 142 | 07:00 | 136 | 00:00
Khulna(S) | 141 | 06:00 | 133 | 13:00 | UttaraNew | 138 | 08:00 | 131 | 00:00
Khulshi | 134 | 07:00 | 127 | 15:00 | Zigatola | 140 | 06:00 | 133 | 13:00
Kishoreganj | 133 | 04:00 | 126 | 13:00
Kodda | 138 | 07:00 | 129 | 02:00
KSRM | 137 | 07:00 | 129 | 17:00
Kulaura | 139 | 05:00 | 133 | 18:00
Kurigram | 133 | 19:00 | 113 | 08:00
Kushtia | 140 | 06:00 | 133 | 13:00
Lalbag | 140 | 06:00 | 134 | 12:00
Lalmonirhat | 132 | 14:00 | 115 | 08:00
Madanganj | 135 | 07:00 | 132 | 00:00
Madaripur | 139 | 04:00 | 135 | 15:00
Madartek | 133 | 06:00 | 129 | 00:00
Madunaghat | 135 | 07:00 | 130 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-02-2025 | during | 22-02-2025 | during | 22-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 225 | 230 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 100 | 100 | 100 | 100 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 370 | 450 | 450 | 340 | 340 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 324 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 14 | 15.5 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 13 | 20 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 15 | 15 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 32.5 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 41 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 17 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 17 | 35 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 18 | 18 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1639 | 1631 | 4933.87 | 4906.87 | 2553.79 | 2544.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 222 | 222 | 225 | 222 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 65 | 86 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 32 | 0 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 34 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 75 | 75 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 38 | 37 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.04 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 99 | 300 | 300 | 66 | 66 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 4.97 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 41 | 70 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 21 | 35 | 116 | 116 | 35 | 35 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1119 | 1217 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 3 | 3 | 25 | 3 | 25 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 200 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2013.97 | 2459 | 3443.9 | 3485.86 | 3128.9 | 3170.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 300 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 32 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 184 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 70 | 38 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 40 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 50 | 163 | 163 | 40 | 40 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 65 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 66 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 18 | 20.83 | 20.83 | 18 | 18 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 4 | 9 | 9 | 9 | 9 | Fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 22 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1131 | 1039 | 1996.53 | 1931.53 | 1807.2 | 1742.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-02-2025 | during | 22-02-2025 | during | 22-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 60 | 110 | 210 | 210 | 120 | 120 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 57 | 200 | 200 | 55 | 55 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.87 | 0 | 40.23 | 0 | 40.23 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 5 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 174.87 | 181 | 643.73 | 601.5 | 302.73 | 260.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 26 | 31 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 23 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 341 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 324 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 961 | 958 | 1067.5 | 1067.5 | 978 | 978
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 38 | 38 | 38 | 38 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 185 | 203 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85.21 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1196.21 | 1080 | 2921.1 | 2841.1 | 1468.02 | 1388.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 48 | 16 | 48 | 16 | 48 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 6 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 65 | 60 | 67 | 67 | 67 | 67 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 | 622 | 622 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 190 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 72 | 135 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1276.59 | 1398 | 1392.12 | 1424.12 | 1392.12 | 1424.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 41 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 5 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 163 | 176 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 380 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 32 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 25 | 88 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 110 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.81 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 714 | 759.97 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 40.38 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1539.69 | 1661.47 | 2356.84 | 2196.24 | 1974.06 | 1813.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 33 | 103 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 100 | 0 | 100 | 0 | 100 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 263.5 | 173 | 397.6 | 262 | 363.62 | 228.02
System Total |  |  |  |  | 27884.66 | 27150.742 | 10195.83 | 10580.47 | 19153.19 | 18716.72 | 13968.44 | 13549.97
Forecast Scenario (22-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9370 |  | 0 |  | 9370
|  |  |  | 1:00 | 8800 |  | 0 |  | 8800
|  |  |  | 2:00 | 8340 |  | 0 |  | 8340
|  |  |  | 3:00 | 8050 |  | 0 |  | 8050
|  |  |  | 4:00 | 7810 |  | 0 |  | 7810
|  |  |  | 5:00 | 7700 |  | 0 |  | 7700
|  |  |  | 6:00 | 8080 |  | 0 |  | 8080
|  |  |  | 7:00 | 9110 |  | 0 |  | 9110
|  |  |  | 8:00 | 9880 |  | 0 |  | 9880
|  |  |  | 9:00 | 10000 |  | 0 |  | 10000
|  |  |  | 10:00 | 10300 |  | 0 |  | 10300
|  |  |  | 11:00 | 10500 |  | 0 |  | 10500
|  |  |  | 12:00 | 10800 |  | 0 |  | 10800
|  |  |  | 13:00 | 11200 |  | 0 |  | 11200
|  |  |  | 14:00 | 10700 |  | 0 |  | 10700
|  |  |  | 15:00 | 10400 |  | 0 |  | 10400
|  |  |  | 16:00 | 10200 |  | 0 |  | 10200
|  |  |  | 17:00 | 10200 |  | 0 |  | 10200
|  |  |  | 18:00 | 11100 |  | 0 |  | 11100
|  |  |  | 18:30 | 11600 |  | 0 |  | 11600
|  |  |  | 19:00 | 11900 |  | 0 |  | 11900
|  |  |  | 19:30 | 11700 |  | 0 |  | 11700
|  |  |  | 20:00 | 11500 |  | 0 |  | 11500
|  |  |  | 21:00 | 11400 |  | 0 |  | 11400
|  |  |  | 22:00 | 10800 |  | 0 |  | 10800
|  |  |  | 23:00 | 10300 |  | 0 |  | 10300
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 10800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 238.44 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:16 hrs on 22-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-02-2025 | [28 empty] | Date: | 21-02-2025 | [28 empty] | Date: | 21-02-2025 | [28 empty] | Date: | 21-02-2025 | [28 empty] | Date: | 21-02-2025 | [18 empty] | Date: | 21-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 17 | 0 | 0 | 97 | 93 | 0 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 21 | 270 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 280 | 17 | 52 | 0 | 0 | 2 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 33 | 576 | 0 | 0 | 0 | 0 | 105 | 225 | 0 | 0 | 0 | 1039 | 0 | 51 | 90 | 195 | 0 | 0 | 360 | 29 | 219 | 32 | 0 | 35 | 200 | 0 | 18 | 0 | 66 | 0 | 0 | 0 | 305 | 320 | 0 | 35 | 0 | 38 | 2 | 120 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 29 | 0 | 0 | 6 | 6247 | 924 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 113 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 350 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3889.5 | 10136.5 | 89.9
01:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 97 | 93 | 0 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 25 | 270 | 0 | 0 | 0 | 0 | 17.5 | 15 | 0 | 280 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 33 | 362 | 0 | 0 | 0 | 0 | 93 | 226 | 0 | 0 | 0 | 1039 | 0 | 51 | 0 | 195 | 0 | 0 | 310 | 29 | 194 | 33 | 0 | 35 | 200 | 0 | 18 | 0 | 64 | 0 | 0 | 0 | 320 | 320 | 0 | 35 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 33 | 0 | 0 | 6 | 5842.5 | 924 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 113 | 4 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3885.5 | 9728 | 89.9
02:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 17 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 25 | 270 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 280 | 0 | 52 | 0 | 0 | 10 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 33 | 273 | 0 | 0 | 0 | 0 | 87 | 226 | 0 | 0 | 0 | 1038 | 0 | 51 | 0 | 195 | 0 | 0 | 320 | 29 | 193 | 33 | 0 | 35 | 100 | 0 | 18 | 0 | 62 | 0 | 0 | 0 | 310 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 6 | 5530 | 924 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 622 | 0 | 3787.5 | 9317.5 | 89.9
03:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 15 | 0 | 250 | 0 | 0 | 0 | 0 | 27 | 270 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 33 | 274 | 0 | 0 | 0 | 0 | 70 | 226 | 0 | 0 | 0 | 1038 | 0 | 51 | 0 | 195 | 0 | 0 | 300 | 29 | 186 | 33 | 0 | 39 | 0 | 0 | 18 | 0 | 60 | 0 | 0 | 0 | 305 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 6 | 5320 | 925 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 622 | 0 | 3669.5 | 8989.5 | 89.89
04:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 34 | 33 | 274 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1042 | 0 | 51 | 0 | 195 | 0 | 0 | 310 | 29 | 187 | 33 | 0 | 40 | 0 | 0 | 18 | 0 | 58 | 0 | 0 | 0 | 305 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 6 | 4991 | 925 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 125 | 220 | 0 | 0 | 622 | 0 | 3650.5 | 8641.5 | 89.89
05:00 | 0 | 17 | 0 | 0 | 0 | 228 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 34 | 33 | 276 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1037 | 0 | 51 | 0 | 195 | 0 | 0 | 300 | 29 | 183 | 33 | 0 | 40 | 0 | 0 | 18 | 0 | 58 | 0 | 0 | 0 | 290 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 34 | 0 | 0 | 6 | 5042 | 925 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 350 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 125 | 220 | 0 | 0 | 622 | 0 | 3592.5 | 8634.5 | 89.89
06:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 1 | 17 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 34 | 38 | 275 | 0 | 0 | 0 | 0 | 5 | 227 | 0 | 0 | 0 | 1040 | 0 | 51 | 0 | 195 | 0 | 0 | 300 | 29 | 185 | 33 | 0 | 40 | 1 | 0 | 18 | 0 | 58 | 0 | 0 | 0 | 320 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 56 | 34 | 0 | 0 | 6 | 5163 | 833 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 350 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 125 | 220 | 0 | 0 | 622 | 2 | 3521.5 | 8684.5 | 89.88
07:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 341 | 0 | 0 | 0 | 18 | 0 | 12 | 72 | 30 | 0 | 17 | 17 | 15 | 0 | 420 | 0 | 0 | 0 | 17 | 31 | 335 | 0 | 0 | 1 | 0 | 13 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 0 | 0 | 64 | 0 | 0 | 40 | 34 | 38 | 276 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 1039 | 1 | 51 | 16 | 187 | 0 | 0 | 300 | 29 | 186 | 32 | 0 | 40 | 42 | 0 | 18 | 0 | 56 | 0 | 3 | 0 | 341 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 6 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 56 | 34 | 0 | 1.69 | 4 | 5471.69 | 832 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 0 | 760 | 0 | 0 | 0 | 35 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 1.41 | 0 | 0 | 0 | 0 | 120 | 0 | 414 | 0 | 0.17 | 2.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7 | 0.01 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 622 | 17 | 3620.19 | 9091.88 | 89.88
08:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 377 | 0 | 0 | 0 | 18 | 0 | 33 | 97 | 95 | 0 | 17 | 17 | 15 | 0 | 380 | 0 | 0 | 0 | 17 | 30 | 250 | 0 | 0 | 9 | 0 | 13 | 22 | 0 | 0 | 24 | 50 | 0 | 0 | 1 | 0 | 32 | 0 | 24 | 12 | 1 | 40 | 45 | 42 | 275 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 1039 | 4 | 51 | 50 | 187 | 0 | 0 | 280 | 29 | 190 | 30 | 0 | 40 | 105 | 0 | 18 | 0 | 54 | 0 | 7 | 0 | 341 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 56 | 39 | 0 | 10.46 | 0 | 5666.46 | 879 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.51 | 0 | 0 | 759 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 0 | 0 | 27 | 0 | 11.29 | 0 | 0 | 0 | 0 | 118 | 0 | 414 | 0 | 0.98 | 5.5 | 0 | 0 | 78 | 7 | 0 | 0 | 0 | 1.3 | 41 | 0.14 | 16 | 240 | 5 | 65 | 220 | 0 | 0 | 560 | 81 | 3818.72 | 9485.18 | 89.88
09:00 | 0 | 52 | 0 | 0 | 0 | 235 | 0 | 0 | 373 | 0 | 0 | 0 | 18 | 0 | 46 | 32 | 45 | 0 | 17 | 17 | 15 | 0 | 380 | 0 | 0 | 0 | 17 | 31 | 250 | 0 | 0 | 17 | 0 | 13 | 22 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 12 | 2 | 40 | 68 | 42 | 213 | 0 | 0 | 0 | 0 | 55 | 227 | 0 | 0 | 0 | 1077 | 10 | 51 | 50 | 187 | 0 | 0 | 270 | 29 | 182 | 33 | 0 | 40 | 68 | 0 | 16 | 0 | 54 | 0 | 34 | 0 | 341 | 320 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 62 | 1 | 22.08 | 4 | 5644.08 | 879 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.54 | 0 | 0 | 758 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 54 | 0 | 23.03 | 0 | 0 | 0 | 0 | 128 | 0 | 414 | 0 | 2.13 | 5.5 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 3.1 | 86 | 0.29 | 16 | 240 | 5 | 65 | 220 | 0 | 0 | 550 | 54 | 3912.59 | 9556.67 | 89.87
10:00 | 0 | 52 | 0 | 0 | 0 | 231 | 0 | 0 | 374 | 0 | 0 | 0 | 18 | 0 | 34 | 16 | 45 | 0 | 0 | 17 | 15 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 250 | 0 | 0 | 24 | 0 | 13 | 22 | 0 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 12 | 3 | 40 | 34 | 42 | 156 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 1080 | 14 | 51 | 50 | 187 | 0 | 0 | 270 | 29 | 186 | 31 | 0 | 40 | 34 | 2 | 16 | 0 | 56 | 0 | 51 | 0 | 341 | 320 | 0 | 29 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 63 | 1 | 30.54 | 6 | 5480.54 | 925 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.66 | 0 | 0 | 728 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 81 | 0 | 34.32 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 0 | 3.19 | 2.5 | 0 | 0 | 95 | 22 | 0 | 0 | 0 | 4.7 | 100 | 0.44 | 16 | 240 | 4 | 65 | 220 | 0 | 0 | 550 | 35 | 4020.81 | 9501.35 | 89.87
11:00 | 0 | 34 | 0 | 0 | 0 | 231 | 0 | 0 | 393 | 0 | 0 | 0 | 18 | 0 | 34 | 16 | 45 | 0 | 0 | 17 | 15 | 0 | 380 | 0 | 0 | 0 | 0 | 32 | 280 | 0 | 0 | 30 | 0 | 14 | 22 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 12 | 4 | 40 | 34 | 38 | 155 | 0 | 0 | 0 | 0 | 51 | 222 | 0 | 0 | 0 | 1124 | 17 | 51 | 50 | 187 | 0 | 0 | 300 | 29 | 183 | 32 | 0 | 40 | 34 | 9 | 16 | 0 | 58 | 0 | 59 | 38 | 341 | 397 | 0 | 32 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 60 | 2 | 37.55 | 6 | 5719.55 | 926 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6 | 0 | 0 | 666 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 41.7 | 0 | 0 | 0 | 0 | 159 | 0 | 380 | 0 | 3.77 | 2.5 | 0 | 0 | 95 | 29 | 12 | 0 | 0 | 5.6 | 100 | 0.55 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 570 | 17 | 4013.72 | 9733.27 | 89.87
12:00 | 0 | 34 | 0 | 0 | 0 | 225 | 0 | 0 | 404 | 0 | 0 | 0 | 17 | 0 | 34 | 16 | 95 | 0 | 0 | 17 | 15 | 0 | 360 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 30 | 0 | 14 | 13 | 0 | 0 | 21 | 50 | 0 | 0 | 0 | 34 | 32 | 4.97 | 75 | 50 | 4 | 40 | 41 | 38 | 200 | 0 | 0 | 1 | 0 | 65 | 222 | 0 | 0 | 0 | 1119 | 17 | 51 | 70 | 184 | 0 | 0 | 300 | 29 | 183 | 32 | 0 | 40 | 50 | 9 | 16 | 0 | 64 | 0 | 63 | 40 | 341 | 324 | 0 | 26 | 0 | 39 | 2 | 120 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 60 | 2 | 39.87 | 6 | 5919.84 | 926 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.21 | 0 | 0 | 714 | 0 | 0 | 0 | 35 | 5 | 25 | 35 | 0 | 0 | 104 | 32 | 40.38 | 0 | 0 | 0 | 0 | 163 | 0 | 380 | 0 | 3.81 | 2.5 | 0 | 0 | 95 | 30 | 33 | 0 | 0 | 5.5 | 100 | 0.59 | 16 | 307 | 4 | 65 | 190 | 0 | 0 | 622 | 72 | 4275.99 | 10195.83 | 89.86
13:00 | 0 | 34 | 0 | 0 | 0 | 231 | 0 | 0 | 405 | 0 | 0 | 0 | 18 | 0 | 50 | 7 | 95 | 0 | 0 | 17 | 15 | 0 | 380 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 30 | 0 | 20 | 14 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 34 | 32 | 0 | 88 | 50 | 4 | 40 | 60 | 42 | 253 | 0 | 0 | 15 | 0 | 92 | 222 | 0 | 0 | 0 | 1127 | 16 | 51 | 100 | 180 | 0 | 0 | 305 | 29 | 184 | 32 | 0 | 40 | 116 | 9 | 18 | 0 | 70 | 0 | 53 | 40 | 341 | 320 | 0 | 28 | 0 | 39 | 2 | 163 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 60 | 2 | 39.99 | 6 | 6210.99 | 926 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.68 | 0 | 0 | 757 | 0 | 0 | 0 | 35 | 7 | 51 | 70 | 14 | 0 | 104 | 32 | 47.46 | 0 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 4.32 | 2.5 | 0 | 0 | 74 | 29 | 35 | 0 | 0 | 5.6 | 100 | 0.58 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 622 | 72 | 4438.14 | 10649.13 | 89.85
14:00 | 0 | 17 | 0 | 0 | 0 | 231 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 32 | 0 | 15 | 0 | 0 | 17 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 26 | 0 | 15.5 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 11 | 34 | 32 | 0 | 50 | 0 | 3 | 40 | 51 | 42 | 290 | 0 | 0 | 0 | 0 | 51 | 221 | 0 | 0 | 0 | 1124 | 15 | 51 | 30 | 180 | 0 | 0 | 300 | 29 | 183 | 32 | 0 | 40 | 34 | 9 | 18 | 0 | 64 | 0 | 50 | 15 | 325 | 320 | 0 | 29 | 0 | 40 | 2 | 120 | 23 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 60 | 2 | 34.03 | 6 | 5601.53 | 925 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2 | 0 | 0 | 670 | 0 | 0 | 0 | 35 | 7 | 51 | 0 | 18 | 0 | 88 | 32 | 43.6 | 0 | 0 | 0 | 0 | 157 | 0 | 370 | 0 | 3.68 | 2.5 | 0 | 0 | 35 | 24 | 35 | 0 | 0 | 4.9 | 99 | 0.45 | 16 | 250 | 5 | 65 | 180 | 0 | 0 | 560 | 35 | 3967.33 | 9568.86 | 89.85
15:00 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 15 | 322 | 0 | 0 | 21 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 32 | 0 | 0 | 0 | 1 | 40 | 0 | 42 | 397 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1080 | 12 | 51 | 0 | 180 | 0 | 0 | 340 | 29 | 207 | 32 | 0 | 40 | 0 | 0 | 18 | 0 | 58 | 0 | 32 | 8 | 295 | 320 | 0 | 28 | 0 | 39 | 2 | 163 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 70 | 1 | 22.92 | 0 | 5306.92 | 854 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.41 | 0 | 0 | 662.28 | 0 | 0 | 0 | 0 | 7 | 51 | 0 | 18 | 0 | 66 | 32 | 30.75 | 0 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 2.92 | 2.5 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 3.5 | 87 | 0.39 | 0 | 269 | 5 | 65 | 220 | 0 | 0 | 550 | 0 | 3752.75 | 9059.67 | 89.84
16:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 31 | 323 | 0 | 0 | 14 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 30 | 0 | 0 | 0 | 1 | 40 | 0 | 42 | 510 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1080 | 8 | 51 | 0 | 180 | 0 | 0 | 320 | 29 | 191 | 31 | 0 | 40 | 0 | 0 | 18 | 0 | 58 | 0 | 18 | 0 | 290 | 320 | 0 | 28 | 0 | 39 | 2 | 163 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 70 | 1 | 11.73 | 0 | 5360.73 | 734 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.28 | 0 | 0 | 658.23 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 38 | 32 | 19.47 | 0 | 0 | 0 | 0 | 158 | 0 | 370 | 0 | 1.93 | 2.5 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 2.1 | 49 | 0.23 | 0 | 307 | 5 | 65 | 220 | 0 | 0 | 550 | 0 | 3499.74 | 8860.47 | 89.84
17:00 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 31 | 324 | 0 | 0 | 5 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 30 | 0 | 5 | 0 | 0 | 40 | 0 | 39 | 510 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1080 | 2 | 51 | 0 | 160 | 0 | 0 | 305 | 29 | 197 | 31 | 0 | 40 | 0 | 0 | 18 | 0 | 56 | 0 | 6 | 0 | 310 | 320 | 0 | 31 | 0 | 38 | 2 | 163 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 48 | 84 | 0 | 3.89 | 0 | 5324.89 | 734 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.83 | 0 | 0 | 658.06 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 32 | 5.64 | 0 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0.46 | 2.5 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.3 | 16 | 0.08 | 0 | 307 | 5 | 65 | 220 | 0 | 0 | 560 | 0 | 3459.87 | 8784.76 | 89.83
18:00 | 0 | 25 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 17 | 15 | 0 | 350 | 0 | 0 | 0 | 17 | 33 | 310 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 22 | 30 | 0 | 0 | 3 | 0 | 30 | 0 | 62 | 0 | 0 | 40 | 21 | 36 | 525 | 0 | 0 | 0 | 0 | 29 | 222 | 0 | 0 | 0 | 1180 | 0 | 51 | 1 | 180 | 0 | 0 | 350 | 29 | 210 | 32 | 0 | 50 | 0 | 9 | 18 | 0 | 64 | 0 | 0 | 0 | 290 | 320 | 0 | 34 | 0 | 38 | 2 | 120 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 111 | 0 | 0 | 1 | 5772 | 734 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 709.11 | 0 | 18 | 0 | 1 | 0 | 88 | 10 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 307 | 6 | 60 | 220 | 0 | 0 | 600 | 17 | 3666.61 | 9438.61 | 89.83
19:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 41 | 0 | 45 | 0 | 15 | 35 | 15 | 0 | 370 | 0 | 0 | 0 | 35 | 32.5 | 324 | 0 | 0 | 0 | 0 | 15.5 | 20 | 0 | 0 | 35 | 99 | 0 | 0 | 3 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 70 | 37 | 575 | 0 | 0 | 0 | 0 | 86 | 222 | 0 | 0 | 0 | 1217 | 0 | 51 | 38 | 182 | 0 | 0 | 300 | 29 | 182 | 32 | 22 | 50 | 65 | 4 | 18 | 0 | 66 | 0 | 0 | 0 | 300 | 320 | 0 | 31 | 0 | 39 | 2 | 163 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 110 | 0 | 0 | 5 | 6268 | 877 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759.97 | 0 | 41 | 0 | 70 | 0 | 88 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 70 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 6 | 60 | 220 | 0 | 0 | 622 | 135 | 4312.47 | 10580.47 | 89.82
19:30 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 15 | 0 | 370 | 0 | 0 | 0 | 0 | 32.5 | 329 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 105 | 34 | 575 | 0 | 0 | 0 | 0 | 105 | 222 | 0 | 0 | 0 | 1220 | 0 | 51 | 80 | 192 | 0 | 0 | 335 | 29 | 202 | 32 | 50 | 50 | 155 | 9 | 18 | 0 | 62 | 0 | 0 | 0 | 300 | 320 | 0 | 30 | 0 | 39 | 2 | 163 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 57 | 110 | 0 | 0 | 0 | 6293 | 876 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.55 | 0 | 0 | 0 | 105 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 0 | 0 | 5 | 0 | 0 | 72 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 7 | 60 | 220 | 0 | 0 | 622 | 135 | 4153.55 | 10446.55
20:00 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 35 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 33 | 326 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 105 | 42 | 575 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 192 | 0 | 0 | 320 | 29 | 198 | 32 | 53 | 50 | 155 | 9 | 18 | 0 | 64 | 0 | 0 | 0 | 290 | 320 | 0 | 32 | 0 | 39 | 2 | 163 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 9 | 58 | 110 | 0 | 0 | 0 | 6288 | 877 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.13 | 0 | 0 | 0 | 108 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 7 | 65 | 220 | 0 | 0 | 622 | 135 | 4135.63 | 10423.63 | 89.82
21:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 35 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 32.5 | 328 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 110 | 38 | 575 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 195 | 0 | 0 | 315 | 29 | 189 | 32 | 52 | 50 | 155 | 9 | 18 | 0 | 66 | 0 | 0 | 0 | 310 | 320 | 0 | 31 | 0 | 39 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 110 | 0 | 0 | 0 | 6316.5 | 925 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759.01 | 0 | 0 | 0 | 113 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 5.5 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 622 | 135 | 4106.51 | 10423.01 | 89.81
22:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 33 | 332 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 40 | 108 | 42 | 578 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 194 | 0 | 0 | 295 | 28 | 193 | 32 | 51 | 50 | 120 | 9 | 18 | 0 | 66 | 0 | 0 | 0 | 305 | 320 | 0 | 31 | 0 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 35 | 130 | 0 | 0 | 0 | 6208 | 925 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.23 | 0 | 0 | 0 | 113 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 622 | 0 | 3999.73 | 10207.73 | 89.81
23:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 332 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 40 | 105 | 42 | 575 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 18 | 195 | 0 | 0 | 275 | 29 | 183 | 29 | 51 | 50 | 51 | 9 | 18 | 0 | 64 | 0 | 0 | 0 | 285 | 320 | 0 | 31 | 0 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 0 | 112 | 0 | 0 | 0 | 5941 | 925 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.18 | 0 | 0 | 0 | 50 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 622 | 0 | 3867.68 | 9808.68 | 89.8
Total KWH | 0 | 420480 | 0 | 0 | 0 | 5525469 | 0 | 0 | 9230400 | 0 | 0 | 67680 | 149760 | 0 | 605664 | 602880 | 508091 | 0 | 76472 | 394560 | 375480 | 0 | 8085500 | 0 | 0 | 0 | 99113 | 706100 | 7393040 | 0 | 0 | 206297 | 0 | 344400 | 424440 | 0 | 976363.64 | 258436 | 654873 | 0 | 0 | 85920 | 98449 | 356736 | 24200 | 1431360 | 152640 | 24121 | 985500 | 1618360 | 748800 | 8938181.82 | 0 | 0 | 26880 | 0 | 1499599 | 5365069 | 0 | 0 | 0 | 26547271 | 115560 | 1145858 | 868145 | 4499636 | 0 | 0 | 7506000 | 697440 | 4671000 | 767304 | 255360 | 1015750 | 1656000 | 83160 | 415130 | 0 | 1450560 | 0 | 380755 | 144346 | 7727500 | 7714500 | 0 | 730656 | 0 | 928680 | 58080 | 3861491 | 519744 | 0 | 2060160 | 102432 | 0 | 0 | 0 | 0 | 216000 | 1056000 | 1528320 | 11750 | 254810 | 86400 | 137537112.46 | 21318545 | 4524192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573840 | 0 | 0 | 17252001 | 0 | 50317 | 0 | 1185216 | 33153 | 836864 | 338688 | 45103 | 0 | 691820 | 230000 | 300752 | 0 | 0 | 0 | 0 | 3984036 | 0 | 9919272 | 0 | 26940 | 82098 | 0 | 0 | 682516 | 193394 | 464044 | 4000 | 0 | 37619.76 | 781920 | 3822 | 239136 | 7134000 | 141039 | 1966000 | 5137010 | 0 | 0 | 14539636.36 | 787200 | 93504174.12 | 231041286.58