## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-02-2025 | [28 empty] | Date: | 22-02-2025 | [28 empty] | Date: | 22-02-2025 | [28 empty] | Date: | 22-02-2025 | [28 empty] | Date: | 22-02-2025 | [18 empty] | Date: | 22-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 40 | 107 | 42 | 575 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 29 | 0 | 50 | 0 | 0 | 18 | 0 | 63 | 0 | 0 | 0 | 300 | 320 | 0 | 31 | 0 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 5809 | 924 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 414 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 622 | 0 | 3777.75 | 9586.75 | 89.8
01:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 17 | 42 | 507 | 0 | 0 | 0 | 0 | 51 | 223 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 29 | 0 | 50 | 0 | 0 | 16 | 0 | 58 | 0 | 0 | 0 | 275 | 320 | 0 | 35 | 0 | 39 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 5400 | 922 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 395 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 560 | 0 | 3666.08 | 9066.08 | 89.79
02:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 42 | 450 | 0 | 0 | 0 | 0 | 51 | 223 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 29 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 285 | 320 | 0 | 34 | 0 | 39 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 5122 | 737 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 393 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 65 | 220 | 0 | 0 | 550 | 0 | 3452.52 | 8574.52 | 89.79
03:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 333 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 378 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 195 | 0 | 0 | 290 | 29 | 193 | 29 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 0 | 34 | 0 | 39 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 4963 | 737 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 410 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 65 | 220 | 0 | 0 | 500 | 0 | 3315.97 | 8278.97 | 89.78
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 376 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 195 | 0 | 0 | 310 | 29 | 203 | 29 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 305 | 320 | 0 | 34 | 0 | 39 | 2 | 120 | 23 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 4811 | 736 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 378 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 65 | 220 | 0 | 0 | 500 | 0 | 3272.77 | 8083.77 | 89.78
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 378 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 195 | 0 | 0 | 300 | 29 | 198 | 29 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 310 | 320 | 0 | 34 | 0 | 39 | 2 | 120 | 23 | 0 | 64 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 4864 | 737 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 347 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 65 | 220 | 0 | 0 | 500 | 0 | 3257.26 | 8121.26 | 89.77
06:00 | 0 | 5 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 30 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 40 | 2 | 42 | 377 | 0 | 0 | 0 | 0 | 3 | 225 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 195 | 0 | 0 | 300 | 29 | 183 | 29 | 0 | 50 | 3 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 305 | 320 | 0 | 34 | 0 | 39 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 5 | 22 | 147 | 0 | 0 | 0 | 5024 | 736 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624.03 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 382 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 65 | 220 | 0 | 0 | 500 | 0 | 3320.53 | 8344.53 | 89.77
07:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 376 | 0 | 0 | 13 | 15 | 0 | 13 | 16 | 45 | 0 | 17 | 35 | 14 | 0 | 340 | 0 | 0 | 0 | 17 | 33 | 270 | 0 | 0 | 1 | 0 | 11 | 10 | 0 | 0 | 31 | 66 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 24 | 0 | 40 | 49 | 26 | 456 | 35 | 0 | 7 | 0 | 51 | 225 | 0 | 0 | 0 | 938 | 0 | 51 | 20 | 187 | 0 | 0 | 275 | 29 | 183 | 29 | 39 | 50 | 49 | 0 | 0 | 0 | 58 | 9 | 5 | 0 | 280 | 320 | 0 | 34 | 0 | 39 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 143 | 0 | 1.93 | 6 | 5618.93 | 925 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.17 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 3 | 0 | 2.17 | 0 | 0 | 0 | 0 | 136 | 0 | 318 | 0 | 0.19 | 2.5 | 0 | 0 | 35 | 1 | 0 | 0 | 0 | 0.2 | 7 | 0.03 | 16 | 307 | 5 | 65 | 180 | 0 | 0 | 490 | 17 | 3536.26 | 9155.19 | 89.76
08:00 | 0 | 50 | 0 | 0 | 0 | 231 | 0 | 0 | 389 | 0 | 0 | 17 | 18 | 0 | 40 | 72 | 45 | 0 | 21 | 34 | 14 | 0 | 340 | 0 | 0 | 0 | 17 | 16 | 270 | 0 | 0 | 7 | 0 | 13 | 22 | 0 | 0 | 35 | 66 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 24 | 0 | 40 | 51 | 2 | 505 | 36 | 0 | 18 | 0 | 51 | 225 | 0 | 0 | 0 | 1100 | 0 | 51 | 20 | 187 | 0 | 0 | 275 | 29 | 183 | 29 | 51 | 50 | 51 | 0 | 0 | 0 | 60 | 16 | 22 | 0 | 280 | 320 | 0 | 34 | 0 | 40 | 2 | 163 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 55 | 140 | 1 | 10.41 | 6 | 6059.41 | 876 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 20 | 0 | 13.9 | 0 | 0 | 0 | 0 | 131 | 0 | 319 | 0 | 1.22 | 5.5 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 1.3 | 43 | 0.15 | 16 | 307 | 4 | 65 | 180 | 0 | 0 | 490 | 17 | 3692.07 | 9751.48 | 89.76
09:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 372 | 0 | 0 | 17 | 18 | 0 | 74 | 98 | 15 | 0 | 55 | 35 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 0 | 270 | 0 | 0 | 15 | 0 | 0 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 40 | 34 | 2 | 505 | 0 | 0 | 0 | 0 | 34 | 227 | 0 | 0 | 0 | 1100 | 0 | 51 | 20 | 187 | 0 | 0 | 275 | 29 | 182 | 32 | 30 | 50 | 17 | 0 | 9 | 0 | 62 | 0 | 41 | 0 | 285 | 320 | 0 | 34 | 0 | 39 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 55 | 104 | 1 | 20 | 6 | 5745 | 870 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 45 | 0 | 28.28 | 0 | 0 | 0 | 0 | 134 | 0 | 319 | 0 | 2.57 | 5.5 | 0 | 0 | 95 | 14 | 17 | 0 | 0 | 2.3 | 87 | 0.31 | 16 | 307 | 4 | 65 | 180 | 0 | 0 | 490 | 17 | 3855.96 | 9600.96 | 89.75
10:00 | 0 | 50 | 0 | 0 | 0 | 180 | 0 | 0 | 351 | 0 | 0 | 17 | 18 | 0 | 77 | 108 | 15 | 0 | 55 | 35 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 16.5 | 270 | 0 | 0 | 23 | 0 | 10 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 40 | 34 | 2 | 455 | 0 | 0 | 0 | 0 | 34 | 223 | 0 | 0 | 0 | 1015 | 0 | 51 | 20 | 187 | 0 | 0 | 275 | 29 | 183 | 32 | 16 | 50 | 17 | 1 | 17 | 0 | 72 | 0 | 55 | 0 | 280 | 320 | 0 | 31 | 0 | 39 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 110 | 2 | 31.55 | 6 | 5576.05 | 917 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 65 | 0 | 40.74 | 0 | 0 | 0 | 0 | 167 | 0 | 320 | 0 | 3.56 | 5.5 | 0 | 0 | 74 | 21 | 33 | 0 | 0 | 4.2 | 100 | 0.45 | 16 | 240 | 4 | 65 | 220 | 0 | 0 | 450 | 17 | 3872.45 | 9448.5 | 89.75
11:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 380 | 0 | 0 | 17 | 18 | 0 | 86 | 112 | 15 | 0 | 55 | 35 | 10 | 0 | 300 | 0 | 0 | 0 | 17 | 8.5 | 270 | 0 | 0 | 27 | 8 | 22 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 40 | 34 | 2 | 452 | 0 | 0 | 0 | 0 | 34 | 221 | 0 | 0 | 0 | 1100 | 0 | 43 | 20 | 187 | 0 | 0 | 295 | 29 | 197 | 32 | 16 | 50 | 17 | 9 | 18 | 0 | 44 | 0 | 63 | 0 | 310 | 320 | 0 | 31 | 0 | 39 | 2 | 120 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 96 | 1 | 36.63 | 6 | 5809.13 | 916 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.45 | 0 | 0 | 734 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 8 | 79 | 0 | 25.16 | 0 | 0 | 0 | 0 | 181 | 0 | 414 | 0 | 2.82 | 2.5 | 0 | 0 | 74 | 28 | 34 | 0 | 0 | 5.5 | 101 | 0.55 | 16 | 264 | 4 | 65 | 220 | 0 | 0 | 450 | 17 | 4093.98 | 9903.11 | 89.74
12:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 45 | 0 | 96 | 127 | 15 | 0 | 55 | 35 | 17 | 0 | 360 | 0 | 0 | 0 | 17 | 16.5 | 331 | 0 | 0 | 28 | 17 | 22 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0 | 40 | 34 | 2 | 576 | 0 | 0 | 0 | 0 | 35 | 219 | 0 | 0 | 0 | 1224 | 0 | 43 | 20 | 185 | 0 | 0 | 285 | 28 | 192 | 32 | 16 | 50 | 17 | 9 | 0 | 0 | 56 | 0 | 68 | 0 | 310 | 320 | 0 | 31 | 0 | 39 | 2 | 120 | 24 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 9 | 58 | 94 | 1 | 39.94 | 6 | 6255.44 | 915 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.41 | 0 | 0 | 748 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 17 | 81 | 26 | 45.97 | 0 | 0 | 0 | 0 | 160 | 0 | 400 | 0 | 3.01 | 5.5 | 0 | 0 | 35 | 30 | 35 | 0 | 0 | 6 | 100 | 0.6 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 520 | 17 | 4259.49 | 10514.93 | 89.74
13:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 96 | 127 | 95 | 0 | 55 | 162 | 21 | 0 | 360 | 0 | 0 | 0 | 17 | 16.5 | 330 | 0 | 0 | 27 | 17 | 22 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 6 | 0 | 0 | 0 | 89 | 12 | 0 | 40 | 50 | 5 | 576 | 0 | 0 | 0 | 0 | 87 | 219 | 0 | 0 | 0 | 1224 | 19 | 43 | 20 | 184 | 0 | 0 | 300 | 29 | 183 | 32 | 16 | 50 | 17 | 0 | 14 | 0 | 60 | 0 | 66 | 0 | 300 | 320 | 0 | 31 | 0 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 65 | 1 | 27.49 | 6 | 6653.99 | 917 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.02 | 0 | 0 | 759 | 0 | 0 | 0 | 35 | 0 | 49 | 35 | 6 | 29 | 74 | 30 | 32 | 0 | 0 | 0 | 0 | 195 | 0 | 320 | 0 | 3.01 | 5.5 | 0 | 0 | 35 | 29 | 35 | 0 | 0 | 6 | 95 | 0.38 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 590 | 17 | 4348.91 | 11002.9 | 89.73
14:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 350 | 0 | 0 | 17 | 54 | 0 | 117 | 64 | 95 | 0 | 17 | 140 | 16 | 0 | 360 | 0 | 0 | 0 | 17 | 16.5 | 270 | 0 | 0 | 22 | 17 | 14 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 4 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 74 | 2 | 576 | 0 | 0 | 0 | 0 | 93 | 219 | 0 | 0 | 0 | 1137 | 17 | 43 | 20 | 182 | 0 | 0 | 275 | 29 | 183 | 32 | 16 | 50 | 17 | 0 | 17 | 0 | 56 | 0 | 58 | 0 | 295 | 320 | 0 | 29 | 0 | 38 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 70 | 1 | 19.21 | 6 | 6242.71 | 916 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.63 | 0 | 0 | 700 | 0 | 0 | 0 | 70 | 0 | 48 | 0 | 0 | 52 | 64 | 32 | 19.66 | 0 | 0 | 0 | 0 | 210 | 0 | 384 | 0 | 2.61 | 5.5 | 0 | 0 | 35 | 24 | 35 | 0 | 0 | 5.1 | 88 | 0.51 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 560 | 17 | 4312.01 | 10554.72 | 89.73
15:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 352 | 0 | 0 | 17 | 17 | 0 | 132 | 48 | 45 | 0 | 32 | 72 | 16 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 85 | 2 | 575 | 0 | 0 | 0 | 0 | 105 | 216 | 0 | 0 | 0 | 1100 | 13 | 43 | 20 | 182 | 0 | 0 | 300 | 29 | 200 | 32 | 16 | 50 | 17 | 0 | 17 | 0 | 56 | 0 | 45 | 0 | 310 | 320 | 0 | 29 | 0 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 70 | 1 | 20.36 | 6 | 6169.36 | 916 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.46 | 0 | 0 | 667 | 0 | 0 | 0 | 35 | 0 | 48 | 0 | 0 | 52 | 4 | 32 | 6.89 | 0 | 0 | 0 | 0 | 206 | 0 | 414 | 0 | 0.73 | 5.5 | 0 | 0 | 35 | 19 | 35 | 0 | 0 | 3.6 | 78 | 0.38 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 560 | 17 | 4125.56 | 10294.92 | 89.72
16:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 370 | 0 | 0 | 17 | 0 | 0 | 132 | 48 | 45 | 0 | 17 | 35 | 16 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 335 | 0 | 0 | 6 | 17 | 22 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 9 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 68 | 2 | 575 | 0 | 0 | 0 | 0 | 105 | 215 | 0 | 0 | 0 | 1110 | 8 | 43 | 20 | 182 | 0 | 0 | 270 | 29 | 184 | 30 | 16 | 50 | 17 | 0 | 17 | 0 | 40 | 0 | 20 | 0 | 300 | 320 | 0 | 31 | 0 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 70 | 0 | 8.29 | 6 | 6019.29 | 916 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.28 | 0 | 0 | 663 | 0 | 0 | 0 | 35 | 0 | 48 | 0 | 0 | 52 | 4 | 32 | 0.16 | 0 | 0 | 0 | 0 | 188 | 0 | 386 | 0 | 0.02 | 0 | 0 | 0 | 35 | 11 | 35 | 0 | 0 | 2.2 | 56 | 0.21 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 560 | 17 | 3983.87 | 10003.16 | 89.72
17:00 | 0 | 50 | 0 | 0 | 0 | 230 | 0 | 0 | 370 | 0 | 0 | 17 | 0 | 0 | 132 | 48 | 45 | 0 | 17 | 35 | 16 | 0 | 360 | 0 | 0 | 0 | 17 | 16.5 | 332 | 0 | 0 | 0 | 17 | 21 | 20 | 0 | 0 | 17 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 75 | 0 | 0 | 40 | 68 | 2 | 575 | 0 | 0 | 0 | 0 | 105 | 218 | 0 | 0 | 0 | 1110 | 2 | 51 | 20 | 145 | 0 | 0 | 285 | 29 | 195 | 35 | 16 | 51 | 17 | 0 | 17 | 0 | 34 | 0 | 7 | 0 | 305 | 320 | 0 | 31 | 0 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 71 | 0 | 0.93 | 6 | 6033.43 | 916 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.72 | 0 | 0 | 661 | 0 | 0 | 0 | 35 | 0 | 48 | 0 | 0 | 8 | 0 | 32 | 0.04 | 0 | 0 | 0 | 0 | 188 | 0 | 327 | 0 | 0.02 | 0 | 0 | 0 | 35 | 3 | 34 | 0 | 0 | 0.9 | 17 | 0.06 | 16 | 307 | 4 | 65 | 220 | 0 | 0 | 560 | 17 | 3807.74 | 9841.17 | 89.71
18:00 | 0 | 50 | 0 | 0 | 0 | 200 | 0 | 0 | 340 | 0 | 0 | 17 | 0 | 0 | 132 | 16 | 95 | 0 | 14 | 35 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 0 | 22 | 0 | 0 | 20 | 50 | 0 | 0 | 13 | 30 | 8 | 17 | 87 | 12 | 0 | 40 | 81 | 2 | 575 | 17 | 0 | 2 | 0 | 105 | 217 | 0 | 0 | 0 | 1212 | 0 | 51 | 38 | 143 | 0 | 0 | 270 | 29 | 182 | 34 | 27 | 50 | 30 | 9 | 17 | 0 | 54 | 4 | 0 | 28 | 290 | 280 | 0 | 35 | 0 | 38 | 2 | 130 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 71 | 0 | 0 | 4 | 6079 | 916 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 750 | 0 | 0 | 0 | 35 | 4 | 89 | 0 | 6 | 8 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 314 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 48 | 284 | 5 | 65 | 190 | 0 | 0 | 570 | 17 | 3904 | 9983 | 89.71
19:00 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 6 | 17 | 39 | 0 | 50 | 12 | 0 | 40 | 99 | 4 | 505 | 0 | 0 | 0 | 0 | 68 | 218 | 0 | 0 | 0 | 1100 | 0 | 51 | 20 | 107 | 0 | 0 | 325 | 29 | 216 | 34 | 50 | 50 | 51 | 8 | 17 | 0 | 70 | 0 | 0 | 0 | 270 | 320 | 0 | 35 | 0 | 38 | 2 | 130 | 24 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 71 | 0 | 0 | 6 | 5415 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 662 | 0 | 33 | 0 | 35 | 0 | 89 | 0 | 21 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 371 | 0 | 0 | 2.5 | 0 | 47 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 65 | 220 | 0 | 0 | 520 | 0 | 3785.5 | 9200.5 | 89.7
19:30 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 4 | 17 | 39 | 0 | 50 | 0 | 0 | 40 | 68 | 3 | 505 | 0 | 0 | 0 | 0 | 68 | 219 | 0 | 0 | 0 | 1100 | 0 | 51 | 20 | 150 | 0 | 0 | 335 | 29 | 216 | 34 | 51 | 50 | 51 | 9 | 0 | 0 | 70 | 0 | 0 | 0 | 335 | 320 | 0 | 35 | 0 | 38 | 2 | 130 | 24 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 9 | 0 | 71 | 0 | 0 | 6 | 5572 | 873 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659 | 0 | 0 | 0 | 35 | 0 | 89 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 382 | 0 | 0 | 2.5 | 0 | 60 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 65 | 220 | 0 | 0 | 520 | 0 | 3697.5 | 9269.5
20:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 2 | 17 | 39 | 0 | 50 | 0 | 0 | 40 | 68 | 4 | 505 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 20 | 190 | 0 | 0 | 320 | 29 | 209 | 34 | 51 | 50 | 51 | 9 | 0 | 0 | 60 | 0 | 0 | 0 | 320 | 320 | 0 | 35 | 0 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 58 | 71 | 0 | 0 | 6 | 5742 | 873 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659 | 0 | 0 | 0 | 35 | 0 | 89 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 0 | 0 | 2.5 | 0 | 60 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 530 | 0 | 3912.5 | 9654.5 | 89.7
21:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 16.5 | 335 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 1 | 17 | 39 | 0 | 97 | 0 | 0 | 40 | 76 | 23 | 575 | 0 | 0 | 0 | 0 | 72 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 20 | 195 | 0 | 0 | 320 | 29 | 195 | 34 | 51 | 50 | 51 | 9 | 10 | 0 | 66 | 0 | 0 | 0 | 325 | 320 | 0 | 35 | 0 | 38 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 58 | 71 | 0 | 0 | 6 | 6148.5 | 920 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762.74 | 0 | 0 | 0 | 41 | 0 | 89 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 2.5 | 0 | 60 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 65 | 220 | 0 | 0 | 590 | 0 | 4150.24 | 10298.74 | 89.69
22:00 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 16.5 | 335 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 17 | 39 | 0 | 99 | 0 | 0 | 40 | 97 | 26 | 575 | 0 | 0 | 0 | 0 | 102 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 20 | 195 | 0 | 0 | 300 | 29 | 182 | 35 | 51 | 50 | 51 | 9 | 17 | 0 | 66 | 0 | 0 | 0 | 320 | 320 | 0 | 35 | 0 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 58 | 71 | 0 | 0 | 6 | 6183.5 | 920 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.6 | 0 | 0 | 0 | 70 | 0 | 42 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 394 | 0 | 0 | 2.5 | 0 | 62 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 65 | 220 | 0 | 0 | 622 | 0 | 4134.1 | 10317.6 | 89.69
23:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 16.5 | 300 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 26 | 575 | 0 | 0 | 0 | 0 | 105 | 224 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 305 | 29 | 188 | 35 | 51 | 50 | 51 | 9 | 17 | 0 | 64 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 0 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 58 | 66 | 0 | 0 | 6 | 6094.5 | 920 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.7 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 394 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 65 | 220 | 0 | 0 | 622 | 0 | 3978.2 | 10072.7 | 89.69
Total KWH | 0 | 569280 | 0 | 0 | 0 | 5329969 | 0 | 0 | 9280800 | 0 | 0 | 223560 | 280800 | 0 | 1219104 | 872160 | 532680 | 0 | 441670 | 813600 | 268200 | 0 | 8314500 | 0 | 0 | 0 | 214978 | 423800 | 7357494 | 0 | 0 | 168831 | 175200 | 304800 | 342720 | 0 | 0 | 465436 | 657382 | 0 | 0 | 78240 | 88066 | 154398 | 56032 | 1188480 | 141120 | 1000 | 966360 | 1386680 | 656160 | 12189090.91 | 85309 | 0 | 41280 | 0 | 1558981 | 5268752 | 0 | 0 | 0 | 25947271 | 55215 | 1100736 | 449963 | 4382545 | 0 | 0 | 7124000 | 696000 | 4666000 | 758376 | 603840 | 1187570 | 647520 | 73080 | 298170 | 0 | 1356480 | 47102 | 452891 | 9504 | 7256000 | 7680600 | 0 | 788688 | 0 | 903840 | 52944 | 3656373 | 558936 | 0 | 1919040 | 713568 | 0 | 80000 | 0 | 0 | 174000 | 1044000 | 2326080 | 9750 | 230750 | 107040 | 139474784.91 | 21154909 | 7396992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373680 | 0 | 0 | 16793818 | 0 | 46173 | 0 | 802944 | 1847 | 533488 | 303264 | 20605 | 317107 | 443330 | 220155 | 262496 | 0 | 0 | 0 | 0 | 4526291 | 0 | 8959127 | 0 | 22560 | 75618 | 0 | 331200 | 813074 | 190173 | 808262 | 0 | 0 | 37975.32 | 761040 | 3663 | 235392 | 7200000 | 139929 | 1550000 | 5147900 | 0 | 0 | 13218909.09 | 223200 | 92915121.41 | 232389906.32

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-02-2025 | during | 23-02-2025 | during | 23-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 250 | 50 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 127 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 22 | 22 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 0 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 0 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16.5 | 16.5 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 96 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 0 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 25 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 45 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 17 | 7 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1901.5 | 1416.5 | 5084.87 | 4856.87 | 2850.79 | 2822.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 220 | 219 | 225 | 219 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 35 | 72 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 39 | 56 | 84 | 56 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 17 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 97 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 23 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 3.84 | 0 | 3.84 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 45 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 76 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 1 | 0 | 20 | 0 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2188 | 2464 | 3437.7 | 3482.86 | 3437.7 | 3482.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 192 | 195 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 320 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 34 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 20 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 66 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 10 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 51 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1001 | 1081 | 1999.53 | 1931.53 | 1819.2 | 1751.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-02-2025 | during | 23-02-2025 | during | 23-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 94 | 71 | 210 | 210 | 71 | 71 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.94 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 207.94 | 144 | 651.5 | 601.5 | 512.5 | 462.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 31 | 35 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 25 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 325 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 957 | 1043 | 1067.5 | 1067.5 | 1028 | 1028
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 920 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 360 | 308 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72.41 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Shutdown due to Inspection.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 0 | 0 | 0 | 0 | U/M #01 & #2 coal shortage.
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1347.41 | 1228 | 1972 | 1972 | 1432.02 | 1352.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 0 | 48 | 110 | 48 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 8 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 65 | 65 | 67 | 67 | 67 | 67 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 590 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1149.6 | 1190 | 1425.12 | 1486.12 | 1422 | 1483
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 199 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 400 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 26 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 17 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 89 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 41 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.01 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 748 | 762.74 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 45.97 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 81 | 0 | 80 | 0 | 80 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1556.48 | 1524.24 | 2336.84 | 2196.24 | 1984.06 | 1843.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 60 | 65 | 65 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 100 | 0 | 50 | 0 | 101 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 206 | 208 | 412.6 | 327 | 429.62 | 293.02
System Total |  |  |  |  | 27884.66 | 27150.742 | 10514.93 | 10298.74 | 18387 | 17841 | 14915.89 | 14518.85
Forecast Scenario (23-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10080 |  | 0 |  | 10080
|  |  |  | 1:00 | 9590 |  | 0 |  | 9590
|  |  |  | 2:00 | 9000 |  | 0 |  | 9000
|  |  |  | 3:00 | 8650 |  | 0 |  | 8650
|  |  |  | 4:00 | 8430 |  | 0 |  | 8430
|  |  |  | 5:00 | 8420 |  | 0 |  | 8420
|  |  |  | 6:00 | 8740 |  | 0 |  | 8740
|  |  |  | 7:00 | 9580 |  | 0 |  | 9580
|  |  |  | 8:00 | 10560 |  | 0 |  | 10560
|  |  |  | 9:00 | 10860 |  | 0 |  | 10860
|  |  |  | 10:00 | 10920 |  | 0 |  | 10920
|  |  |  | 11:00 | 10950 |  | 0 |  | 10950
|  |  |  | 12:00 | 11490 |  | 0 |  | 11490
|  |  |  | 13:00 | 11760 |  | 0 |  | 11760
|  |  |  | 14:00 | 11360 |  | 0 |  | 11360
|  |  |  | 15:00 | 11050 |  | 0 |  | 11050
|  |  |  | 16:00 | 10930 |  | 0 |  | 10930
|  |  |  | 17:00 | 10760 |  | 0 |  | 10760
|  |  |  | 18:00 | 11420 |  | 0 |  | 11420
|  |  |  | 18:30 | 11600 |  | 0 |  | 11600
|  |  |  | 19:00 | 12210 |  | 0 |  | 12210
|  |  |  | 19:30 | 11830 |  | 0 |  | 11830
|  |  |  | 20:00 | 11620 |  | 0 |  | 11620
|  |  |  | 21:00 | 11390 |  | 0 |  | 11390
|  |  |  | 22:00 | 10980 |  | 0 |  | 10980
|  |  |  | 23:00 | 10530 |  | 0 |  | 10530
Probable Maximum Temperature: |  |  | 28.80°C
Probable Maximum Demand at Day Peak: |  |  | 11490.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12210.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12210.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 251.28 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:57 hrs on 23-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10514.93 | MW | 12:00 Hr. | Energy Generated |  |  | 232.3899 |  | MKWHr.
| Day Peak Demand |  |  | 10603.93 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.429 |  | MKWHr.
| Evening Peak Generation |  |  | 10298.74 | MW | 21:00 Hr. | Energy Demand |  |  | 232.8189 |  | MKWHr.
| Evening Peak Demand |  |  | 10298.74 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.8 |  | °C
| Minimum Generation of the Day |  |  | 8083.77 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 827.11 |  | MMCFD
| Maximum Generation of the Day |  |  | 11002.9 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 6.0035 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.6223 | 0 | 5.343 | 0 | 0 | 0.16883 | 0 | 0 | 37.1341 | Gas | 111.4925 | Gas | 407433443.27
| Chattogram Zone |  |  | 5.9249 | 38.1364 | 5.8232 | 0 | 0.96636 | 0.056215 | 0 | 0.07824 | 50.9853 | Coal | 58.8865 | Coal | 399470228.2545
| Cumilla Zone |  |  | 20.2134 | 0 | 1.831 | 0 | 0 | 0.45289 | 1.3565 | 0 | 23.8538 | HFO | 18.6478 | HFO | 337249312.57
| Mymensingh Zone |  |  | 2.3261 | 0 | 1.325 | 0 | 0 | 0.2405 | 0 | 0 | 3.8916 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.61 | Hydro | 0.96636 | Hydro | 96636
| Khulna Zone |  |  | 7.397 | 0 | 0 | 0 | 0 | 0.37368 | 21.1549 | 0 | 28.9256 | Solar | 3.0134 | Solar | 48275168.2652
| Barishal Zone |  |  | 6.8378 | 20.4189 | 0.45859 | 0 | 0 | 0.003663 | 0 | 0 | 27.719 | Import | 39.3052 | Import | 201484945.68
| Rajshahi Zone |  |  | 13.561 | 0 | 2.2456 | 0 | 0 | 0.72839 | 16.7938 | 0 | 33.3288 | Wind | 0.07824 | Wind | 1145433.6
| Rangpur Zone |  |  | 0 | 0.3312 | 1.6213 | 0 | 0 | 0.98919 | 0 | 0 | 2.9417
| Total |  |  | 111.4925 | 58.8865 | 18.6478 | 0 | 0.96636 | 3.0134 | 39.3052 | 0.07824 | 232.3899
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 407433443.27 |  | Hydro | 96636
|  |  |  | Coal | 399470228.2545 |  | Solar | 48275168.2652
|  |  |  | HFO | 337249312.57 |  | Import | 201484945.68
|  |  |  | HSD | 0 |  | Wind | 1145433.6
[5 empty] | Total: | 139,51,55,167 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1549 | Peak Hr Flow | 920.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8035618 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.7938 | Peak Hr Flow | 762.74 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 188 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3565 | Peak Hr Flow | 66.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 848 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.3052 | Peak Hr Flow | 1748.74 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3274
|  |  |  | Chattogram |  | 0 |  | 1270
|  |  |  | Cumilla |  | 0 |  | 817
|  |  |  | Mymensingh |  | 0 |  | 861
|  |  |  | Sylhet |  | 0 |  | 409
|  |  |  | Khulna |  | 0 |  | 1168
|  |  |  | Barishal |  | 0 |  | 329
|  |  |  | Rajshahi |  | 0 |  | 1057
|  |  |  | Rangpur |  | 0 |  | 689
|  |  |  | Total |  | 0 |  | 9874
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1122 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1788.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:08 |  | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D Due to 132 Kv Transformer - 1 Shutdown due | [7 empty] | 8.0MW load
|  |  | to BPDB, Sunamganj Feeder Bay Extension work | [7 empty] | interrup.
| 08:11 | 14:51 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to 132Kv Transformer -1 Shutdown due to | [7 empty] | 8.0MW load
|  |  | BPDB, Sunamganj Feeder Bay Extension workk | [7 empty] | interrup.
| 08:12 | 11:35 | Kushtia 132/33kV S/S T-3 LT Scheduled S/D Due to T-3A 33 kV Bus Extension | [7 empty] | 25.0MW load
interrup.
| 08:13 | 11:34 | Kushtia 132/33kV S/S T-3 HT Scheduled S/D Due to T-3A 33 kV Bus Extension | [7 empty] | 25.0MW load
interrup.
| 08:21 | 13:51 | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to Due to DS clamp Maintenance of
Kusumhati feeder.
| 08:21 | 19:39 | Rampura 230/132kV S/S 230kV Busbar-1 Project Work S/D Due to G2G Project work
| 08:22 | 13:50 | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to Due to DS clamp Maintenance of
Kusumhati feeder.
| 08:25 |  | Goalpara-KPCL-2 Line S/D.
| 08:26 | 11:08 | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D
| 08:28 | 12:54 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D Due to T3 jumper connection | [7 empty] | 55.0MW load
interrup.
| 08:37 | 13:24 | Ghatail 132/33kV S/S T-2 LT Scheduled S/D | [7 empty] | 5.0MW load
interrup.
| 08:38 | 13:23 | Ghatail 132/33kV S/S T-2 HT Scheduled S/D | [7 empty] | 5.0MW load
interrup.
| 08:38 | 12:53 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Forced S/D Due to NLDC instruction.
(working for bhaluka End)
| 08:41 | 13:19 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Maintenance by PBS. | [7 empty] | 8.0MW load
interrup.
| 08:42 | 13:18 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Maintenance by PBS. | [7 empty] | 8.0MW load
interrup.
| 08:46 | 17:30 | Bibiyana-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to Annual
maintenance
| 08:51 | 17:46 | Khulshi 132/33kV S/S 425T(BSRM) HT Scheduled S/D Due to Annual maintenance
| 08:53 | 12:57 | Bhaluka 132/33kV S/S Bus A Scheduled S/D Due to T3 jumper connection | [7 empty] | 55.0MW load
interrup.
| 09:07 | 14:52 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Project Work S/D from Bog-Sherpur 132/33kV end.
and from Sirajganj 132/33kV end Due to Cradle Guard Removal Work
| 09:08 | 14:52 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Project Work S/D from Bog-Sherpur 132/33kV end.
and from Sirajganj 132/33kV end Due to Cradle Guard Removal Work
|  | 09:16 | Bogura 132/33kV S/S Transformer-2 LT is restored.
|  | 09:16 | Bogura 132/33kV S/S Transformer-2 HT is restored.
| 09:18 | 13:30 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to Oil Likeage repair
| 09:19 |  | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end.
| 09:19 | 13:28 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to Oil likeage repair
|  | 09:20 | Cox'sbazar-Dohazari 132 kV Ckt-2 is restored.
|  | 09:20 | Coxsbazar 132/33kV S/S Main Bus is restored.
| 09:24 | 15:26 | Madanganj 132/33kV S/S GT-2 LT Scheduled S/D
| 09:25 | 15:21 | Madanganj 132/33kV S/S GT-2 HT Scheduled S/D
| 09:27 | 13:27 | Rampura 230/132kV S/S NLDC Trafo HT Scheduled S/D Due to Annual Maintenance on NLDC side
|  | 09:32 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt is restored.
| 09:45 | 12:09 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to For hotspot
maintenance.
|  | 09:51 | Khulshi 132/33kV S/S 405T (T1) HT is restored.
| 09:58 |  | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Forced S/D
| 09:58 |  | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Disc cleaning work
| 10:06 | 14:53 | Mithapukur-Palashbari 132kV Ckt-2 Scheduled S/D from Palashbari 132/33kV end Due to
Maintenance purpose
| 10:07 | 14:52 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end Due to
Maintenance purpose
| 10:07 | 10:07 | Khulna(S) 230/132kV S/S TR-1 LT Scheduled S/D Due to Maintenance Work NWPGCL 800MW
Project
| 10:07 | 17:07 | Khulna(S) 230/132kV S/S TR-2 LT Scheduled S/D Due to Maintenance Work at NWPGCL Project
| 10:08 | 17:05 | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D Due to Maintenance Work at NWPGCL Project
|  | 10:11 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
|  | 10:11 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
|  | 10:25 | Bagerhat-Mongla 132 kV Ckt-1 is restored.
| 10:27 | 16:39 | Madunaghat 400/230kV S/S Madunaghat-Old Madunaghat 230kV Ckt.-2 Project Work S/D Due to
Project Work
| 10:27 | 13:27 | Rampura 230/132kV S/S NLDC Trafo LT Scheduled S/D Due to Annual Maintenance on NLDC side
| 10:27 | 14:01 | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to Oil Leakage Maintenance
by DPDC.
|  | 10:27 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
| 10:29 | 15:33 | Savar 132/33kV S/S Main Bus Scheduled S/D Due to For hotspot maintenance work.
|  | 10:33 | Mongla 132/33kV S/S Main Bus is restored.
| 10:43 | 16:36 | Khulna(S) 230/132kV S/S 230 KV Main Bus 1 Scheduled S/D Due to Maintenance Work at
NWPGCL Project
| 11:05 | 12:52 | Gopalganj 400/132kV S/S ATR-05 LT Project Work S/D
| 11:05 | 12:51 | Gopalganj 400/132kV S/S ATR-05 HT Project Work S/D
| 11:14 | 14:19 | Baroirhat 132/33kV S/S TR-2, 416T HT Scheduled S/D Due to 33 kv Bus-02 Annual maintenance
work
| 11:14 | 14:20 | Baroirhat 132/33kV S/S TR-2, 416T LT Scheduled S/D Due to 33 kv Bus-02 Annual maintenance
work
| 11:33 | 12:49 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to WZPDCL-2 33Kv Bus Side D/S | [7 empty] | 2.5MW load
|  |  | Maintenance | [7 empty] | interrup.
| 11:34 | 12:48 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to WZPDCL-2 33Kv Bus Side D/S | [7 empty] | 2.5MW load
|  |  | Maintenance | [7 empty] | interrup.
|  | 13:23 | Khulshi 132/33kV S/S 415T (T2) HT is restored.
| 14:39 | 17:27 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Oil leakage repair
| 14:39 | 17:27 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Oil leakage repair of ATR-1
| 14:45 | 15:57 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Tripped showing RYB 3 Phase O/C relays | [7 empty] | 27.0MW load
|  |  | Due to BUS Fault | [7 empty] | interrup.
| 14:46 | 18:29 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Tripped showing 50 Trip , 51 Trip relays. | [7 empty] | 35.0MW load
interrup.
| 14:48 | 15:24 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Tripped showing Instant E/F relays Due to | [7 empty] | 35.0MW load
|  |  | BUS Fault | [7 empty] | interrup.
| 15:03 | 15:12 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance
protection 21/1:z1,BN relays Due to Unknown
|  | 15:21 | Kaliakoir 400/230/132kV S/S Bibiyana1 is restored.
| 16:10 | 16:19 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to
Instructed by NLDC for bus coupler operation at Cox's GSS.
| 16:36 | 18:29 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Forced S/D Due to Cleaning of bird
droppings.
| 16:37 | 18:28 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Forced S/D Due to Cleaning og bird
droppings.
|  | 17:05 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT is restored.
|  | 17:09 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT is restored.
| 17:29 |  | Barapukuria Unit-1 was sync.
|  | 17:51 | Madaripur 132/33kV S/S T3-426T HT is restored.
| 17:57 | 20:52 | Madaripur 132/33kV S/S T3-426T LT Tripped showing Siemens relays Due to Earth Fault | [7 empty] | 12.0MW load
interrup.
| 17:57 | 20:51 | Madaripur 132/33kV S/S T3-426T HT Tripped showing Siemens relays Due to Over current | [7 empty] | 12.0MW load
interrup.
| 18:00 |  | A full interruption occured at the Savar Substation as both the Manikganj 162 Power
Station to Savar Ckt 1 and Ckt 2 tripped. Restored at 19:18 hours.
| 18:02 | 19:26 | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing ABB relays
Due to Rainy weather
| 18:05 | 19:19 | Aminbazar-Mirpur 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing ABB relays
Due to Rainy weather
| 18:14 | 21:27 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end
showing Distance relay 2.8 km relays Due to Bad weather
| 18:14 | 19:11 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB initiation relays Due to Bad
weather
| 18:30 | 19:30 | Sonargaon 132/33kV S/S Tr-1 HT Tripped showing Backup Protection Relay. relays Due to Due | [7 empty] | 18.0MW load
|  |  | to PBS 33kv Astha feed feeder earth fault. | [7 empty] | interrup.
| 18:30 | 19:30 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing DIR E/F & O/C Relay. relays Due to Due to | [7 empty] | 18.0MW load
|  |  | PBS 33kv Astha feed feeder earth fault. | [7 empty] | interrup.
| 18:32 | 19:20 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Back up protection relays. | [7 empty] | 4.0MW load
interrup.
| 18:32 | 19:25 | Madanganj 132/33kV S/S GT-2 LT Tripped showing Phase instantaneous fault relays. | [7 empty] | 4.0MW load
interrup.
| 18:34 | 23:20 | Fatullah-Shyampur(New) 132 kV Ckt-1 Tripped from Shyampur 230/132kV end showing
Siemens(SIPROTEC 7SA52) relays Due to Trip
| 18:44 | 19:49 | Bogura 132/33kV S/S Transformer-2 LT Project Work S/D Due to t-1&T-2 33kv BUS work | [7 empty] | 25.0MW load
interrup.
| 18:44 | 19:49 | Bogura 132/33kV S/S Transformer-2 HT Project Work S/D Due to T-2 & T-1 33kv bus work loop | [7 empty] | 25.0MW load
|  |  | connection | [7 empty] | interrup.
| 18:55 | 07:27 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Forced S/D from Sirajganj 132/33kV end Due to As
per the Instruction of ALDC bogura ,Sherpur Ckt -2 CB Open .Due to Shajadpur -Ullapara
Line Over Load,
| 18:55 | 07:25 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Forced S/D from Sirajganj 132/33kV end Due to As
per the Instruction of ALDC bogura, Sherpur Ckt -1 CB Open .Due to Shajadpur -Ullapara
Line Over Load,
| 19:00 | 20:35 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing Directional O/C & E/C Relay. relays Due to | [7 empty] | 15.0MW load
|  |  | Due to PBS Langolbond feeder 3 phase earth fault and at the same time auxiliary T2 fuse | [7 empty] | interrup.
barrel burst.
| 21:00 |  | Evening peak Generation is 10297 MW
| 00:31 |  | Haripur 230/132kV S/S Auto TR-1 HT Forced S/D Due to To prevent further damage to the
Transformer & the System from fire which has been lit inside the cable trench in front of
230/132 KV Auto TR-1.
| 00:31 |  | Haripur 230/132kV S/S Auto TR-1 LT Forced S/D Due to To prevent further damage to the
Transformer & the System from fire which has been lit inside the cable trench in front of
230/132 KV Auto TR-1.
| 05:00 |  | Minimum Generation is 8391 MW
| 07:16 |  | Purbasadipur 132/33kV S/S T-4 Transformer HT Scheduled S/D
| 07:16 |  | Purbasadipur 132/33kV S/S T-4 Transformer LT Scheduled S/D Due to Red hot Maintenance
| 07:37 |  | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Shutdown taken by
Manikganj Grid ss via NLDC.
| 07:50 |  | Bhaluka 132/33kV S/S Bus Section- 03 Project Work S/D Due to Development work | [7 empty] | 15.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 5329969 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9280800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8314500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7357494 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 223560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 872160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 441670 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 214978 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 304800 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 342720 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 268200 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16.5 | 423800 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 532680 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 1219104 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 569280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 25 | 813600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 168831 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 280800 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 7 | 175200 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 1416.5 | 37134146
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 55215 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 41280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 966360 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5268752 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 72 | 1558981 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 39 | 154398 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 88066 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 97 | 1188480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 656160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 1000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 657382 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 56032 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 76 | 1386680 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 141120 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 465436 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 85309 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25947271 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 78240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12189090.91 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2464 | 50985252.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 195 | 4666000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 320 | 7124000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 758376 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 696000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4382545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1100736 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 449963 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 9504 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1187570 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 647520 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1356480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 47102 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 10 | 298170 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 73080 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 603840 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 452891 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1081 | 23853777
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 2326080 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1044000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 174000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 230750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 107040 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 144 | 3891620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 903840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3656373 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 788688 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 52944 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 713568 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1919040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 20 | 80000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 558936 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7256000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7680600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1043 | 23609989
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 920 | 21154909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 308 | 7396992 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 373680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U/M #01 & #2 coal shortage.
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1228 | 28925581
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 235392 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 139929 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 65 | 1550000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 13218909.09 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5147900 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 223200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7200000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3663 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1190 | 27718993.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 46173 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 1847 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 20605 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 199 | 4526291 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8959127 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 220155 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 75618 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 16 | 317107 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 533488 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 41 | 802944 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 303264 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 762.74 | 16793818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 262496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 443330 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1524.24 | 33328823
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 331200 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 808262 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37975.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 813074 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190173 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 761040 | -
Rangpur Area Total |  |  |  |  | 950 | 208 | 2941724.32
Eastern Grid Total |  |  |  |  | 16856.242 | 6148.5 | 139474784.91
Western Grid Total |  |  |  |  | 10294.5 | 4150.24 | 92915121.41
National Grid Total |  |  |  |  | 27150.742 | 10298.74 | 232389906.32
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-02-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6630.65 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3243.2 | MW
i) Dhaka area |  |  | 3274.05 |  | MW | i) Khulna area |  |  |  | 1168 | MW
ii) Chattogram area |  |  | 1269.6 |  | MW | ii) Barishal area |  |  |  | 329 | MW
iii) Cumilla area |  |  | 817 |  | MW | iii) Rajshahi area |  |  |  | 1057.2 | MW
iv) Mymensingh area |  |  | 861 |  | MW | iv) Rangpur area |  |  |  | 689 | MW
v) Sylhet area |  |  | 409 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9873.85 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 18:30 | 133 | Postogola | 45 | 13:00
2 | AKSML | 104 | 16:00 | 68 | Jamalpur | 108 | 19:00 | 134 | Purbachal | 18 | 13:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jashore | 107 | 19:00 | 135 | Purbasadipur | 125 | 13:00
4 | Agargaon | 83 | 13:00 | 70 | Jhenaidah | 96 | 08:00 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 82 | 18:30 | 71 | Joydebpur | 138 | 16:00 | 137 | Rahim | 35 | 16:00
6 | Amnura | 60 | 09:00 | 72 | Joypurhat | 60 | 08:00 | 138 | Rajbari | 46 | 15:00
7 | Ashuganj | 74 | 14:00 | 73 | Juldah | 15 | 15:00 | 139 | Rajendrapur | 116 | 12:00
8 | BSRM | 191 | 04:00 | 74 | KSRM | 37 | 23:00 | 140 | Rajshahi | 86 | 13:00
9 | Bagerhat | 74 | 18:30 | 75 | Kabirpur | 190 | 08:00 | 141 | Rajshahi-230 | 66 | 20:00
10 | Bajitpur | 42 | 18:00 | 76 | Kachua | 56 | 18:30 | 142 | Ramganj | 82 | 21:00
11 | Bakulia | 85 | 13:00 | 77 | Kallyanpur | 78 | 12:00 | 143 | Rampur | 39 | 12:00
12 | Banani | 21.6 | 13:00 | 78 | Kalurghat | 36 | 18:00 | 144 | Rangamati | 16 | 18:30
13 | Bangabhaban | 4 | 11:00 | 79 | Kamrangirchar | 57 | 13:00 | 145 | Rangpur | 118 | 18:30
14 | Barapukuria | 63 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 3.6 | 10:00
15 | Barguna | 14 | 13:00 | 81 | Kazla | 91 | 12:00 | 147 | SSM | 0 | 00:00
16 | Barishal | 95 | 12:00 | 82 | Keranigonj | 76 | 21:00 | 148 | Saidpur | 108 | 09:00
17 | Barishal-230 | 66 | 21:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Satkhira | 94 | 18:30
18 | Baroaulia | 63 | 11:00 | 84 | Khulna | 85 | 13:00 | 150 | Satmasjid | 86 | 13:00
19 | Baroirhat | 40 | 18:30 | 85 | Khulshi | 142 | 23:00 | 151 | Savar | 184 | 15:00
20 | Bashundhara | 144 | 18:00 | 86 | Kishoreganj | 99 | 18:00 | 152 | SevenRings | 21.3 | 16:00
21 | BashundharaCement | 7 | 03:00 | 87 | Kodda | 155 | 22:00 | 153 | ShahCement | 32 | 01:00
22 | Beanibazar | 48 | 18:30 | 88 | Kulaura | 38 | 18:00 | 154 | Shahjadpur | 71 | 12:00
23 | Benapole | 56 | 08:00 | 89 | Kurigram | 58 | 09:00 | 155 | Shahjibazar | 91 | 18:30
24 | Bhaluka | 122 | 14:00 | 90 | Kushtia | 109 | 19:00 | 156 | Shahmirpur | 45 | 09:00
25 | Bhandaria | 37 | 19:00 | 91 | Lalbag | 60 | 13:00 | 157 | Shariatpur | 55 | 21:00
26 | Bhangura | 34 | 08:00 | 92 | Lalmonirhat | 47 | 18:30 | 158 | Sherpur | 134 | 08:00
27 | Bheramara(GK) | 53 | 12:00 | 93 | MI_Cement | 17 | 13:00 | 159 | Shikalbaha | 25 | 18:00
28 | Bhulta | 192 | 23:00 | 94 | Madanganj | 26 | 00:00 | 160 | Shitalakhya | 71.5 | 13:00
29 | Bog-Sherpur | 68 | 08:00 | 95 | Madaripur | 68 | 14:00 | 161 | Sholosohor | 41 | 15:00
30 | Bogura | 114 | 20:00 | 96 | Madartek | 68.45 | 13:00 | 162 | Shyampur | 182 | 11:00
31 | Borhanuddin | 58 | 20:00 | 97 | Madunaghat | 41 | 18:30 | 163 | Siddhirganj | 109 | 10:00
32 | Brahmanbaria | 118 | 18:30 | 98 | Magura | 40 | 08:00 | 164 | Sirajganj | 88 | 12:00
33 | Cantonment | 100 | 13:00 | 99 | Mahasthangarh | 56 | 08:00 | 165 | Sonargaon | 83 | 12:00
34 | Chandpur | 46 | 18:30 | 100 | Manikganj | 104 | 12:00 | 166 | Sreemongol | 52 | 18:30
35 | Chandraghona | 29 | 18:30 | 101 | Maniknagar | 59 | 12:00 | 167 | Sreepur | 101 | 12:00
36 | Chapai | 59 | 08:00 | 102 | Matarbari | 40 | 19:00 | 168 | Srinagar | 32.43 | 14:00
37 | Charsaidpur | 39 | 04:00 | 103 | Matuail | 62 | 11:00 | 169 | Sunamganj | 46 | 18:00
38 | Chauddagram | 53 | 18:30 | 104 | Millgate | 71 | 12:00 | 170 | Sylhet | 26 | 19:30
39 | Chhatak | 25 | 18:30 | 105 | Mirpur | 111 | 14:00 | 171 | Sylhet-132 | 101 | 18:00
40 | Chowmuhani | 176 | 18:30 | 106 | Mirsorai | 13 | 11:00 | 172 | TK | 19 | 00:00
41 | Chuadanga | 71 | 18:30 | 107 | Mirzapur | 41 | 09:00 | 173 | Tangail | 162 | 07:00
42 | Coxsbazar | 133 | 18:00 | 108 | Mithapukur | 50 | 08:00 | 174 | Thakurgaon | 80 | 19:00
43 | Cumilla(N) | 144 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 103 | 11:00
44 | Cumilla(S) | 147 | 18:30 | 110 | Mogbazar | 117.8 | 14:00 | 176 | Ullahpara | 29 | 07:00
45 | Daudkandi | 103 | 18:00 | 111 | Mongla | 34 | 18:30 | 177 | Ullon | 9 | 12:00
46 | Dhaka | 38 | 13:00 | 112 | Motijheel | 30 | 13:00 | 178 | Uttara | 71 | 13:00
47 | Dhamrai | 122 | 16:00 | 113 | Muktagacha | 31 | 08:00 | 179 | UttaraNew | 43 | 15:00
48 | Dhanmondi | 105 | 13:00 | 114 | Munshiganj | 75 | 18:00 | 180 | Zigatola | 60 | 13:00
49 | Dohazari | 90 | 18:00 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 98 | 13:00 | 116 | Mymensingh | 174 | 18:00
51 | Fatullah | 72 | 18:00 | 117 | Naogaon | 111 | 08:00
52 | Fenchuganj | 27 | 14:00 | 118 | Narail | 39 | 20:00
53 | Feni | 96 | 18:30 | 119 | Narinda | 70 | 13:00
54 | GPH | 99 | 09:00 | 120 | Narshingdi | 134 | 18:00
55 | Ghatail | 62 | 07:00 | 121 | Natore | 110 | 08:00
56 | Ghorashal | 15 | 10:00 | 122 | Nawabganj | 26.2 | 23:00
57 | Ghorashal-230 | 80 | 13:00 | 123 | Netrakona | 147 | 18:00
58 | Goalpara | 22 | 08:00 | 124 | New | 74.3 | 11:00
59 | Gollamari | 52 | 18:30 | 125 | Niamatpur | 94 | 09:00
60 | Gopalganj | 77 | 19:30 | 126 | Noapara | 36 | 13:00
61 | Gulshan | 80 | 12:00 | 127 | PHP | 7 | 11:00
62 | Halishahar | 70 | 15:00 | 128 | Pabna | 73 | 13:00
63 | HaripurSBU | 177 | 13:00 | 129 | Palashbari | 106 | 18:30
64 | Hasnabad | 64 | 11:00 | 130 | Panchagarh | 45 | 19:00
65 | Hathazari | 61 | 19:00 | 131 | Patuakhali | 54 | 21:00
66 | Ishurdi | 58 | 13:00 | 132 | Payra | 22 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9586.75 | 0 |  | 9586.75
1:00 | 9066.08 | 0 |  | 9066.08
2:00 | 8574.52 | 0 |  | 8574.52
3:00 | 8278.97 | 0 |  | 8278.97
4:00 | 8083.77 | 0 |  | 8083.77
5:00 | 8121.26 | 0 |  | 8121.26
6:00 | 8344.53 | 0 |  | 8344.53
7:00 | 9155.19 | 0 |  | 9155.19
8:00 | 9751.48 | 34 |  | 9787.48
9:00 | 9600.96 | 77 |  | 9680.96
10:00 | 9448.5 | 100 |  | 9552.5
11:00 | 9903.11 | 96 |  | 10003.11
12:00 | 10514.93 | 85 |  | 10603.93
13:00 | 11002.9 | 37 |  | 11041.9
14:00 | 10554.72 | 0 |  | 10554.72
15:00 | 10294.92 | 0 |  | 10294.92
16:00 | 10003.16 | 0 |  | 10003.16
17:00 | 9841.17 | 0 |  | 9841.17
18:00 | 9983 | 0 |  | 9983
19:00 | 9200.5 | 0 |  | 9200.5
19:30 | 9269.5 | 0 |  | 9269.5
20:00 | 9654.5 | 0 |  | 9654.5
21:00 | 10298.74 | 0 |  | 10298.74
22:00 | 10317.6 | 0 |  | 10317.6
23:00 | 10072.7 | 0 |  | 10072.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5809 | 3777.75 | 9586.75 | DAILY GENERATION CURVE
00:30 | 5604.5 | 3721.915 | 9326.415
01:00 | 5400 | 3666.08 | 9066.08 | 22-02-2025
01:30 | 5261 | 3559.3 | 8820.3
02:00 | 5122 | 3452.52 | 8574.52
02:30 | 5042.5 | 3384.245 | 8426.745
03:00 | 4963 | 3315.97 | 8278.97
03:30 | 4887 | 3294.37 | 8181.37
04:00 | 4811 | 3272.77 | 8083.77
04:30 | 4837.5 | 3265.015 | 8102.515
05:00 | 4864 | 3257.26 | 8121.26
05:30 | 4944 | 3288.895 | 8232.895
06:00 | 5024 | 3320.53 | 8344.53
06:30 | 5321.465 | 3428.395 | 8749.86
07:00 | 5618.93 | 3536.26 | 9155.19
07:30 | 5839.17 | 3614.165 | 9453.335
08:00 | 6059.41 | 3692.07 | 9751.48
08:30 | 5902.205 | 3774.015 | 9676.22
09:00 | 5745 | 3855.96 | 9600.96
09:30 | 5660.525 | 3864.205 | 9524.73
10:00 | 5576.05 | 3872.45 | 9448.5
10:30 | 5692.59 | 3983.215 | 9675.805
11:00 | 5809.13 | 4093.98 | 9903.11
11:30 | 6032.285 | 4176.735 | 10209.02
12:00 | 6255.44 | 4259.49 | 10514.93
12:30 | 6454.715 | 4304.2 | 10758.915
13:00 | 6653.99 | 4348.91 | 11002.9
13:30 | 6448.35 | 4330.46 | 10778.81
14:00 | 6242.71 | 4312.01 | 10554.72
14:30 | 6206.035 | 4218.785 | 10424.82
15:00 | 6169.36 | 4125.56 | 10294.92
15:30 | 6094.325 | 4054.715 | 10149.04
16:00 | 6019.29 | 3983.87 | 10003.16
16:30 | 6026.36 | 3895.805 | 9922.165
17:00 | 6033.43 | 3807.74 | 9841.17
17:30 | 6056.215 | 3855.87 | 9912.085
18:00 | 6079 | 3904 | 9983
18:30 | 5747 | 3844.75 | 9591.75
19:00 | 5415 | 3785.5 | 9200.5
19:30 | 5572 | 3697.5 | 9269.5
20:00 | 5742 | 3912.5 | 9654.5
20:30 | 5945.25 | 4031.37 | 9976.62 |  | Executive Engineer
21:00 | 6148.5 | 4150.24 | 10298.74 |  | Network Operation Division
21:30 | 6166 | 4142.17 | 10308.17
22:00 | 6183.5 | 4134.1 | 10317.6
22:30 | 6139 | 4056.15 | 10195.15
23:00 | 6094.5 | 3978.2 | 10072.7

## En-Curve
QF-LDC-12
Date | 22-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3179 | 1593.5 | 924 | 0 | 63 | 758.25 | 40 | 2728 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3175.5 | 1581.5 | 923 | 0 | 60.5 | 742.415 | 40 | 2601 | 0 | 0 | 202.5 | 0 | 0 | 0 | 0 | 22-02-2025
01:00 | 3172 | 1569.5 | 922 | 0 | 58 | 726.58 | 40 | 2474 | 0 | 0 | 104 | 0 | 0 | 0 | 0
01:30 | 3170 | 1573.5 | 829.5 | 0 | 56 | 721.3 | 40 | 2340.5 | 0 | 0 | 89.5 | 0 | 0 | 0 | 0 | Energy Generated | 232.3899 |  | MKWHr
02:00 | 3168 | 1577.5 | 737 | 0 | 54 | 716.02 | 40 | 2207 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | Energy not Served | 0.429 |  | MKWHr
02:30 | 3184.5 | 1585 | 737 | 0 | 53 | 668.245 | 40 | 2121 | 0 | 0 | 37.5 | 0 | 0 | 0.5 | 0 | Total Energy Requirement | 232.8189 |  | MKWHr
03:00 | 3201 | 1592.5 | 737 | 0 | 52 | 620.47 | 40 | 2035 | 0 | 0 | 0 | 0 | 0 | 1 | 0
03:30 | 3166.5 | 1530.5 | 736.5 | 0 | 52 | 618.37 | 40 | 2034 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0
04:00 | 3132 | 1468.5 | 736 | 0 | 52 | 616.27 | 40 | 2033 | 0 | 0 | 0 | 0 | 0 | 6 | 0
04:30 | 3116.5 | 1503 | 736.5 | 0 | 52 | 615.515 | 40 | 2034 | 0 | 0 | 0 | 0 | 0 | 5 | 0
05:00 | 3101 | 1537.5 | 737 | 0 | 52 | 614.76 | 40 | 2035 | 0 | 0 | 0 | 0 | 0 | 4 | 0
05:30 | 3115 | 1545.5 | 736.5 | 0 | 53 | 619.395 | 40 | 2034.5 | 0 | 10.5 | 76.5 | 0 | 0 | 2 | 0
06:00 | 3129 | 1553.5 | 736 | 0 | 54 | 624.03 | 40 | 2034 | 0 | 21 | 153 | 0 | 0 | 0 | 0
06:30 | 3075.5 | 1493.5 | 830.5 | 0 | 56 | 623.6 | 40 | 2112.5 | 10.76 | 27 | 480.5 | 0 | 0 | 0 | 0
07:00 | 3022 | 1433.5 | 925 | 0 | 58 | 623.17 | 40 | 2191 | 21.52 | 33 | 808 | 0 | 0 | 0 | 0
07:30 | 3032 | 1442.5 | 900.5 | 0 | 59 | 656.085 | 40 | 2296.5 | 74.25 | 77.5 | 875 | 0 | 0 | 0 | 17
08:00 | 3042 | 1451.5 | 876 | 0 | 60 | 689 | 40 | 2402 | 126.98 | 122 | 942 | 0 | 0 | 0 | 34
08:30 | 3022.5 | 1415.5 | 873 | 0 | 61 | 711 | 40 | 2402 | 191.72 | 135 | 824.5 | 0 | 0 | 0 | 55.5
09:00 | 3003 | 1379.5 | 870 | 0 | 62 | 733 | 40 | 2402 | 256.46 | 148 | 707 | 0 | 0 | 0 | 77
09:30 | 2961 | 1392.75 | 893.5 | 0 | 67 | 734 | 40 | 2281 | 301.48 | 153 | 701 | 0 | 0 | 0 | 88.5
10:00 | 2919 | 1406 | 917 | 0 | 72 | 735 | 40 | 2160 | 346.5 | 158 | 695 | 0 | 0 | 0 | 100
10:30 | 3022.5 | 1423 | 916.5 | 0 | 58 | 734.5 | 40 | 2213 | 396.305 | 164 | 708 | 0 | 0 | 0 | 98
11:00 | 3126 | 1440 | 916 | 0 | 44 | 734 | 40 | 2266 | 446.11 | 170 | 721 | 0 | 0 | 0 | 96
11:30 | 3164.5 | 1469 | 915.5 | 0 | 50 | 741 | 40 | 2446.5 | 461.02 | 195 | 725.5 | 0 | 0 | 1 | 90.5
12:00 | 3203 | 1498 | 915 | 0 | 56 | 748 | 40 | 2627 | 475.93 | 220 | 730 | 0 | 0 | 2 | 85
12:30 | 3171 | 1525 | 916 | 0 | 58 | 753.5 | 40 | 2662 | 467.915 | 249.5 | 912 | 0 | 0 | 4 | 61
13:00 | 3139 | 1552 | 917 | 0 | 60 | 759 | 40 | 2697 | 459.9 | 279 | 1094 | 0 | 0 | 6 | 37
13:30 | 3111.5 | 1519.5 | 916.5 | 0 | 58 | 729.5 | 40 | 2638.5 | 427.31 | 245 | 1088 | 0 | 0 | 5 | 18.5
14:00 | 3084 | 1487 | 916 | 0 | 56 | 700 | 40 | 2580 | 394.72 | 211 | 1082 | 0 | 0 | 4 | 0
14:30 | 3140.5 | 1489.75 | 916 | 0 | 56 | 683.5 | 40 | 2561 | 318.07 | 203 | 1013.5 | 0 | 0 | 3.5 | 0
15:00 | 3197 | 1492.5 | 916 | 0 | 56 | 667 | 40 | 2542 | 241.42 | 195 | 945 | 0 | 0 | 3 | 0
15:30 | 3144 | 1496.75 | 916 | 0 | 48 | 665 | 40 | 2547 | 189.29 | 195 | 902 | 0 | 0 | 6 | 0
16:00 | 3091 | 1501 | 916 | 0 | 40 | 663 | 40 | 2552 | 137.16 | 195 | 859 | 0 | 0 | 9 | 0
16:30 | 3073 | 1506.75 | 916 | 0 | 37 | 662 | 40 | 2552 | 90.915 | 195 | 836.5 | 0 | 0 | 13 | 0
17:00 | 3055 | 1512.5 | 916 | 0 | 34 | 661 | 40 | 2552 | 44.67 | 195 | 814 | 0 | 0 | 17 | 0
17:30 | 2942 | 1434.25 | 916 | 0 | 44 | 705.5 | 40 | 2620 | 22.835 | 237.5 | 935 | 0 | 0 | 15 | 0
18:00 | 2829 | 1356 | 916 | 0 | 54 | 750 | 40 | 2688 | 1 | 280 | 1056 | 0 | 0 | 13 | 0
18:30 | 2863.5 | 1322.75 | 894.5 | 0 | 62 | 706 | 40 | 2530 | 0.5 | 248 | 915 | 0 | 0 | 9.5 | 0
19:00 | 2898 | 1289.5 | 873 | 0 | 70 | 662 | 40 | 2372 | 0 | 216 | 774 | 0 | 0 | 6 | 0
19:30 | 3086 | 1379.5 | 873 | 0 | 70 | 659 | 40 | 2385 | 0 | 162 | 611 | 0 | 0 | 4 | 0
20:00 | 3204 | 1483.5 | 873 | 0 | 60 | 659 | 40 | 2502 | 0 | 162 | 669 | 0 | 0 | 2 | 0
20:30 | 3227 | 1537.75 | 896.5 | 0 | 63 | 710.87 | 40 | 2629 | 0 | 157 | 714 | 0 | 0 | 1.5 | 0
21:00 | 3250 | 1592 | 920 | 0 | 66 | 762.74 | 40 | 2756 | 0 | 152 | 759 | 0 | 0 | 1 | 0
21:30 | 3222.5 | 1594 | 920 | 0 | 66 | 760.17 | 40 | 2773 | 0 | 125 | 807 | 0 | 0 | 0.5 | 0
22:00 | 3195 | 1596 | 920 | 0 | 66 | 757.6 | 40 | 2790 | 0 | 98 | 855 | 0 | 0 | 0 | 0
22:30 | 3179 | 1589 | 920 | 0 | 65 | 756.65 | 40 | 2790 | 0 | 70 | 785.5 | 0 | 0 | 0 | 0
23:00 | 3163 | 1582 | 920 | 0 | 64 | 755.7 | 40 | 2790 | 0 | 42 | 716 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 06:00 | 386 | 15:00 | Payra | 422 | 05:00 | 409 | 13:00
Ashuganj | 415 | 6:00 | 389 | 12:00 | Rahanpur | 415 | 04:00 | 400 | 08:00
Bhulta | 412 | 06:00 | 387 | 12:00 | Rampal | 412 | 06:00 | 392 | 12:00
Bibiana | 405 | 18:00 | 393 | 16:00
BIPTC | 406 | 03:00 | 392 | 13:00
Bogura | 414 | 04:00 | 396 | 08:00
Gopalganj | 413 | 06:00 | 395 | 12:00
Kaliakoir | 392 | 18:00 | 360 | 12:00
Madunaghat | 412 | 07:00 | 398 | 13:00
Meghnaghat | 406 | 06:00 | 383 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 18:30 | 221 | 12:00 | Keranigonj | 239 | 18:30 | 221 | 12:00
AKSML | 236 | 06:00 | 226 | 12:00 | Khulna(S) | 240 | 05:00 | 226 | 12:00
Aminbazar | 239 | 18:00 | 222 | 11:00 | Madunaghat | 233 | 08:00 | 226 | 15:00
Ashuganj | 243 | 06:00 | 230 | 13:00 | Madunaghat-400 | 237 | 07:00 | 227 | 13:00
Ashuganj-400 | 243 | 06:00 | 230 | 13:00 | Maniknagar | 238 | 18:30 | 224 | 12:00
Baghabari | 241 | 03:00 | 230 | 12:00 | Meghnaghat | 245 | 18:30 | 230 | 12:00
Barapukuria | 225 | 02:00 | 208 | 08:00 | Meghnaghat-400 | 240 | 18:30 | 226 | 12:00
Barapukuria-230 | 225 | 02:00 | 208 | 08:00 | Mirsorai | 239 | 08:00 | 224 | 17:00
Barishal | 244 | 05:00 | 234 | 13:00 | Rajshahi | 239 | 04:00 | 225 | 19:00
Bheramara | 240 | 06:00 | 227 | 12:00 | Rampal | 237 | 05:00 | 23.6 | 02:00
Bhulta | 239 | 06:00 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 07:00 | 223 | 00:00 | Rampura | 240 | 18:30 | 223 | 12:00
BIPTC | 242 | 04:00 | 228 | 12:00 | Shikalbaha | 238 | 08:00 | 227 | 16:00
Bogura | 240 | 03:00 | 229 | 08:00 | Shyampur | 239 | 18:30 | 223 | 12:00
Bogura-400 | 239 | 04:00 | 228 | 08:00 | Siddhirganj | 240 | 18:30 | 226 | 12:00
Borhanuddin | 245 | 01:00 | 239 | 21:00 | Sirajgonj | 244 | 02:00 | 238 | 12:00
BSRM | 239 | 08:00 | 225 | 12:00 | Sreepur | 241 | 06:00 | 231 | 15:00
Cumilla(N) | 236 | 07:00 | 223 | 15:00 | Tongi | 238 | 18:00 | 222 | 11:00
Faridpur | 247 | 18:00 | 234 | 12:00
Fenchuganj | 237 | 00:00 | 230 | 11:00
Ghorashal | 240 | 18:00 | 235 | 01:00
Ghorashal-230 | 241 | 18:30 | 224 | 12:00
Gopalganj | 243 | 06:00 | 234 | 12:00
GPH | 238 | 08:00 | 224 | 15:00
Haripur | 238 | 06:00 | 224 | 12:00
Hasnabad | 237 | 06:00 | 222 | 12:00
Hathazari | 240 | 06:00 | 226 | 15:00
Ishurdi | 242 | 05:00 | 230 | 12:00
Jhenaidah | 239 | 04:00 | 224 | 12:00
Kaliakoir | 242 | 18:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 18:00 | 126 | 13:00 | Magura | 138 | 02:00 | 128 | 13:00
Agargaon | 138 | 18:30 | 127 | 12:00 | Mahasthangarh | 136 | 02:00 | 129 | 08:00
Agrabad | 136 | 07:00 | 127 | 15:00 | Manikganj | 141 | 18:00 | 129 | 15:00
AKS | 135 | 07:00 | 127 | 12:00 | Maniknagar | 135 | 06:00 | 125 | 12:00
Aminbazar | 145 | 18:00 | 133 | 21:00 | Matarbari | 132 | 08:00 | 113 | 19:00
Amnura | 142 | 18:00 | 129 | 12:00 | Matuail | 138 | 18:30 | 128 | 14:00
Ashuganj | 142 | 19:30 | 136 | 12:00 | Millgate | 144 | 18:30 | 127 | 12:00
Bagerhat | 139 | 04:00 | 126 | 19:00 | Mirpur | 143 | 06:00 | 132 | 12:00
Bajitpur | 137 | 05:00 | 129 | 13:00 | Mirzapur | 137 | 18:00 | 127 | 15:00
Bakulia | 133 | 07:00 | 129 | 12:00 | Mithapukur | 135 | 21:00 | 122 | 08:00
Banani | 137 | 18:30 | 126 | 12:00 | MI_Cement | 139 | 19:00 | 129 | 12:00
Bangabhaban | 136 | 18:00 | 125 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 134 | 02:00 | 123 | 08:00 | Mogbazar | 138 | 06:00 | 126 | 12:00
Barguna | 136 | 08:00 | 130 | 21:00 | Mongla | 138 | 04:00 | 127 | 19:00
Barishal | 136 | 03:00 | 130 | 12:00 | Motijheel | 136 | 18:00 | 125 | 12:00
Barishal-230 | 137 | 05:00 | 131 | 12:00 | Muktagacha | 133 | 06:00 | 123 | 19:00
Baroaulia | 135 | 06:00 | 128 | 15:00 | Munshiganj | 139 | 18:30 | 127 | 12:00
Baroirhat | 134 | 07:00 | 121 | 15:00 | Muradnagar | 137 | 07:00 | 126 | 15:00
Bashundhara | 141 | 18:30 | 125 | 12:00 | Mymensingh | 134 | 05:00 | 118 | 14:00
BashundharaCement | 139 | 19:00 | 127 | 11:00 | Naogaon | 134 | 01:00 | 125 | 08:00
Beanibazar | 135 | 03:00 | 128 | 15:00 | Narail | 139 | 03:00 | 127 | 12:00
Benapole | 137 | 04:00 | 123 | 12:00 | Narinda | 135 | 7:00 | 125 | 12:00
Bhaluka | 128 | 00:00 | 120 | 14:00 | Narshingdi | 138 | 19:00 | 124 | 12:00
Bhandaria | 134 | 07:00 | 126 | 19:30 | Natore | 138 | 02:00 | 131 | 12:00
Bhangura | 137 | 01:00 | 130 | 12:00 | Nawabganj | 141 | 18:30 | 129 | 12:00
Bheramara | 139 | 02:00 | 133 | 12:00 | Netrakona | 126 | 00:00 | 115 | 17:00
Bheramara(GK) | 139 | 03:00 | 134 | 12:00 | New | 141 | 18:00 | 127 | 12:00
Bhulta | 134 | 18:30 | 124 | 12:00 | Niamatpur | 140 | 06:00 | 131 | 20:00
Bog-Sherpur | 136 | 04:00 | 129 | 08:00 | Noapara | 139 | 05:00 | 127 | 12:00
Bogura | 137 | 04:00 | 130 | 08:00 | Pabna | 138 | 02:00 | 132 | 12:00
Bogura-230 | 137 | 02:00 | 130 | 08:00 | Palashbari | 133 | 06:00 | 122 | 08:00
Brahmanbaria | 137 | 19:30 | 130 | 12:00 | Panchagarh | 138 | 22:00 | 125 | 13:00
Cantonment | 138 | 18:30 | 127 | 12:00 | Patuakhali | 135 | 06:00 | 130 | 13:00
Chandpur | 137 | 06:00 | 119 | 17:00 | Payra | 136 | 05:00 | 132 | 21:00
Chandraghona | 138 | 07:00 | 130 | 15:00 | PHP | 134 | 07:00 | 119 | 15:00
Chapai | 137 | 02:00 | 131 | 08:00 | Postogola | 140 | 19:00 | 131 | 12:00
Charsaidpur | 140 | 18:30 | 128 | 12:00 | Purbachal | 139 | 18:30 | 125 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 06:00 | 121 | 15:00 | Purbasadipur | 130 | 16:00 | 120 | 13:00
Chhatak | 134 | 06:00 | 125 | 18:00 | Rahanpur | 139 | 00:00 | 135 | 11:00
Chowmuhani | 126 | 00:00 | 114 | 18:30 | Rahanpur-400 | 141 | 04:00 | 135 | 08:00
Chuadanga | 138 | 02:00 | 127 | 14:00 | Rahim | 137 | 18:30 | 128 | 12:00
Coxsbazar | 126 | 10:00 | 114 | 18:30 | Rajbari | 136 | 05:00 | 129 | 13:00
Cumilla(N) | 139 | 07:00 | 127 | 15:00 | Rajendrapur | 144 | 18:00 | 131 | 12:00
Cumilla(S) | 137 | 07:00 | 125 | 13:00 | Rajshahi | 139 | 02:00 | 132 | 12:00
Daudkandi | 136 | 19:00 | 125 | 13:00 | Rajshahi-230 | 138 | 02:00 | 125 | 13:00
Dhaka | 137 | 18:30 | 126 | 12:00 | Ramganj | 134 | 07:00 | 115 | 15:00
Dhamrai | 142 | 18:30 | 127 | 13:00 | Rampur | 138 | 08:00 | 127 | 15:00
Dhanmondi | 138 | 18:30 | 129 | 12:00 | Rampura | 138 | 18:30 | 126 | 12:00
Dohazari | 136 | 07:00 | 124 | 18:00 | Rangamati | 137 | 07:00 | 129 | 15:00
Faridpur | 137 | 18:00 | 130 | 13:00 | Rangpur | 132 | 21:00 | 120 | 07:00
Fatullah | 141 | 18:30 | 129 | 12:00 | Ruppur | 141 | 03:00 | 135 | 12:00
Fenchuganj | 139 | 07:00 | 134 | 13:00 | Saidpur | 132 | 04:00 | 120 | 08:00
Feni | 133 | 06:00 | 121 | 15:00 | Satkhira | 138 | 06:00 | 128 | 12:00
Ghatail | 132 | 18:00 | 124 | 08:00 | Satmasjid | 139 | 18:30 | 127 | 12:00
Ghorashal | 145 | 18:00 | 137 | 13:00 | Savar | 142 | 07:00 | 131 | 15:00
Goalpara | 139 | 05:00 | 129 | 12:00 | SevenRings | 145 | 18:30 | 137 | 12:00
Gollamari | 140 | 06:00 | 129 | 12:00 | ShahCement | 140 | 19:00 | 128 | 12:00
Gopalganj | 139 | 05:00 | 132 | 12:00 | Shahjadpur | 142 | 04:00 | 134 | 12:00
Gopalganj-400 | 140 | 02:00 | 134 | 12:00 | Shahjibazar | 138 | 03:00 | 132 | 18:30
Gulshan | 137 | 18:30 | 125 | 12:00 | Shahmirpur | 137 | 07:00 | 129 | 15:00
Halishahar | 138 | 07:00 | 127 | 15:00 | Shariatpur | 139 | 04:00 | 131 | 13:00
Haripur | 138 | 18:30 | 129 | 12:00 | Sherpur | 127 | 07:00 | 116 | 19:00
HaripurSBU | 138 | 18:30 | 128 | 13:00 | Shikalbaha | 127 | 07:00 | 118 | 14:00
Hasnabad | 142 | 18:00 | 130 | 11:00 | Shikalbaha-230 | 139 | 08:00 | 130 | 16:00
Hathazari | 140 | 04:00 | 131 | 15:00 | Shitalakhya | 139 | 19:00 | 129 | 12:00
Ishurdi | 141 | 01:00 | 135 | 12:00 | Sholosohor | 137 | 07:00 | 129 | 15:00
Jaldhaka | 130 | 05:00 | 118 | 08:00 | Shyampur | 140 | 18:30 | 130 | 11:00
Jamalpur | 132 | 06:00 | 120 | 19:00 | Shyampur-230 | 140 | 18:30 | 129 | 12:00
Jashore | 137 | 02:00 | 37 | 02:00 | Siddhirganj | 138 | 18:30 | 128 | 12:00
Jhenaidah | 138 | 04:00 | 130 | 12:00 | Sirajganj | 136 | 02:00 | 126 | 12:00
Jhenaidah-230 | 140 | 05:00 | 130 | 12:00 | Sonargaon | 138 | 19:00 | 126 | 12:00
Joydebpur | 144 | 18:00 | 130 | 15:00 | Sreemongol | 138 | 05:00 | 132 | 12:00
Joypurhat | 134 | 04:00 | 123 | 08:00 | Sreepur | 131 | 06:00 | 124 | 13:00
Juldah | 135 | 05:00 | 129 | 15:00 | Srinagar | 141 | 18:30 | 129 | 12:00
Kabirpur | 144 | 18:00 | 124 | 12:00 | SSM | 140 | 07:00 | 131 | 15:00
Kachua | 136 | 07:00 | 120 | 15:00 | Sunamganj | 133 | 04:00 | 125 | 18:30
Kaliakoir | 142 | 18:00 | 126 | 12:00 | Sylhet | 135 | 02:00 | 129 | 15:00
Kallyanpur | 134 | 06:00 | 124 | 12:00 | Sylhet-132 | 136 | 05:00 | 129 | 15:00
Kalurghat | 134 | 02:00 | 129 | 17:00 | Tangail | 134 | 18:00 | 124 | 15:00
Kamrangirchar | 140 | 18:30 | 122 | 12:00 | Thakurgaon | 136 | 22:00 | 123 | 13:00
Kaptai | 140 | 7:00 | 133 | 15:00 | TK | 138 | 07:00 | 130 | 12:00
Kazla | 136 | 18:30 | 126 | 12:00 | Tongi | 141 | 18:00 | 130 | 11:00
Keranigonj | 141 | 18:30 | 129 | 12:00 | Ullahpara | 138 | 03:00 | 129 | 12:00
Khagrachori | 137 | 07:00 | 128 | 15:00 | Ullon | 135 | 02:00 | 125 | 12:00
Khulna | 138 | 04:00 | 126 | 13:00 | Uttara | 142 | 18:30 | 131 | 21:00
Khulna(S) | 140 | 06:00 | 129 | 12:00 | UttaraNew | 142 | 18:30 | 126 | 12:00
Khulshi | 137 | 07:00 | 126 | 15:00 | Zigatola | 141 | 18:30 | 129 | 12:00
Kishoreganj | 133 | 04:00 | 126 | 14:00
Kodda | 147 | 18:00 | 130 | 15:00
KSRM | 138 | 08:00 | 128 | 15:00
Kulaura | 137 | 07:00 | 133 | 14:00
Kurigram | 133 | 02:00 | 17 | 18:30
Kushtia | 140 | 04:00 | 16 | 17:00
Lalbag | 140 | 18:30 | 129 | 12:00
Lalmonirhat | 132 | 22:00 | 121 | 07:00
Madanganj | 139 | 19:00 | 127 | 11:00
Madaripur | 140 | 06:00 | 133 | 12:00
Madartek | 137 | 18:30 | 125 | 12:00
Madunaghat | 134 | 08:00 | 129 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division