## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-02-2025 | during | 24-02-2025 | during | 24-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 10 | 50 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 301 | 405 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 330 | 450 | 450 | 380 | 380 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19 | 17 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 18 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 0 | line SD
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 210 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 62 | 112 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 70 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1632 | 2068 | 4840.77 | 4864.77 | 2617.29 | 2549.1
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 22 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 227 | 215 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 24 | 78 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 89 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 8 | 12 | 4 | 20 | 4 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 180 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 106 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 35 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 27 | 13 | 22 | 13 | 22 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 577 | 578 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2331 | 2906 | 3473.86 | 3488.86 | 3473.86 | 3329.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 219 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 290 | 270 | 356.56 | 356.56 | 320 | 320 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 36 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 10 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 163 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 112 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 8 | 37 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 173 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 78 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 11 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 7 | 9 | 9 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 96 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1064 | 1319 | 1966.53 | 1931.53 | 1786.2 | 1751.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-02-2025 | during | 24-02-2025 | during | 24-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 29 | 18 | 210 | 210 | 20 | 20 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1 | 0 | 1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 9 | 200 | 200 | 200 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 57 | 115 | 115 | 115 | 57 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 23.57 | 0 | 22 | 0 | 22 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 125.57 | 90 | 624.5 | 601.5 | 434.5 | 162.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 30 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 0 | 2.5 | 2.5 | 0 | 0 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 998 | 985 | 1097.5 | 1097.5 | 1057 | 1057
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 871 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 230 | 193 | 410 | 410 | 190 | 190 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 7 | 0 | 20 | 0 | 20 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | GT Shutdown due to Turning Gear Inspection.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1108 | 1065 | 2531.1 | 2511.1 | 1254.02 | 1234.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 80 | 32 | 110 | 32 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 65 | 132 | 136 | 136 | 136 | 136 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 610 | 622 | 622 | 622 | 622 | 622 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 126 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.09 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1293.09 | 1494 | 1478.12 | 1555.12 | 1475 | 1552
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 36 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 154 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 370 | 370 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 101 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 2.14 | 0 | 3.25 | 0 | 3.25 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 758.19 | 753 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 24.89 | 0 | 30 | 0 | 30 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 37 | 0 | 50 | 0 | 50 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1504.92 | 1676.5 | 2208.49 | 2125.24 | 1894.51 | 1811.26
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 61 | 62 | 62 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 7 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.5 | 0 | 2.2 | 0 | 2.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 2 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 6 | 0 | 90 | 0 | 81 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 172.5 | 238 | 434.2 | 324 | 394.22 | 293.02
System Total |  |  |  |  | 27884.66 | 27150.742 | 10229.08 | 11841.5 | 18655.07 | 18499.62 | 14386.6 | 13739.96
Forecast Scenario (24-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9810 |  | 0 |  | 9810
|  |  |  | 1:00 | 9350 |  | 0 |  | 9350
|  |  |  | 2:00 | 9060 |  | 0 |  | 9060
|  |  |  | 3:00 | 8730 |  | 0 |  | 8730
|  |  |  | 4:00 | 8500 |  | 0 |  | 8500
|  |  |  | 5:00 | 8390 |  | 0 |  | 8390
|  |  |  | 6:00 | 8680 |  | 0 |  | 8680
|  |  |  | 7:00 | 9760 |  | 0 |  | 9760
|  |  |  | 8:00 | 10360 |  | 0 |  | 10360
|  |  |  | 9:00 | 10260 |  | 0 |  | 10260
|  |  |  | 10:00 | 10060 |  | 0 |  | 10060
|  |  |  | 11:00 | 10100 |  | 0 |  | 10100
|  |  |  | 12:00 | 10260 |  | 0 |  | 10260
|  |  |  | 13:00 | 10660 |  | 0 |  | 10660
|  |  |  | 14:00 | 9960 |  | 0 |  | 9960
|  |  |  | 15:00 | 10280 |  | 0 |  | 10280
|  |  |  | 16:00 | 10290 |  | 0 |  | 10290
|  |  |  | 17:00 | 10330 |  | 0 |  | 10330
|  |  |  | 18:00 | 10940 |  | 0 |  | 10940
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 11910 |  | 0 |  | 11910
|  |  |  | 19:30 | 11810 |  | 0 |  | 11810
|  |  |  | 20:00 | 11630 |  | 0 |  | 11630
|  |  |  | 21:00 | 11400 |  | 0 |  | 11400
|  |  |  | 22:00 | 10900 |  | 0 |  | 10900
|  |  |  | 23:00 | 10500 |  | 0 |  | 10500
Probable Maximum Temperature: |  |  | 29.90°C
Probable Maximum Demand at Day Peak: |  |  | 10260.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11910.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11910.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 242.12 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:36 hrs on 24-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-02-2025 | [28 empty] | Date: | 23-02-2025 | [28 empty] | Date: | 23-02-2025 | [28 empty] | Date: | 23-02-2025 | [28 empty] | Date: | 23-02-2025 | [18 empty] | Date: | 23-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 17.7 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 40 | 110 | 29 | 575 | 0 | 0 | 0 | 0 | 105 | 224 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 35 | 51 | 50 | 51 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 0 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 58 | 66 | 0 | 0 | 0 | 5967.7 | 921 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.89 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 319 | 0 | 0 | 2.5 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 65 | 220 | 0 | 0 | 622 | 0 | 3847.39 | 9815.09 | 89.68
01:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 17.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 68 | 29 | 575 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 35 | 0 | 50 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 285 | 320 | 0 | 36 | 0 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 18 | 69 | 0 | 0 | 0 | 5652.9 | 921 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 694.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 321 | 0 | 0 | 2.5 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 622 | 0 | 3702.38 | 9355.28 | 89.67
02:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 14.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 68 | 33 | 576 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 35 | 0 | 50 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 0 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 0 | 69 | 0 | 0 | 0 | 5518.8 | 921 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 664.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 321 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 65 | 220 | 0 | 0 | 560 | 0 | 3549.21 | 9068.01 | 89.67
03:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 14.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 576 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 183 | 35 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 0 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 5262.7 | 920 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 673.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 322 | 0 | 0 | 2.5 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 65 | 220 | 0 | 0 | 500 | 0 | 3469.53 | 8732.23 | 89.66
04:00 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 0 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 14.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 505 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 195 | 0 | 0 | 280 | 29 | 185 | 35 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 0 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 5075.7 | 920 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 322 | 0 | 0 | 2.5 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 65 | 220 | 0 | 0 | 490 | 0 | 3429.12 | 8504.82 | 89.66
05:00 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 0 | 0 | 0 | 0 | 33 | 250 | 0 | 0 | 0 | 0 | 14.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 505 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 195 | 0 | 0 | 275 | 29 | 182 | 35 | 0 | 50 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 290 | 320 | 0 | 36 | 0 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 5007.7 | 920 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 320 | 0 | 0 | 2.5 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 65 | 180 | 0 | 0 | 490 | 0 | 3385.26 | 8392.96 | 89.65
06:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 0 | 0 | 0 | 0 | 33 | 250 | 0 | 0 | 0 | 0 | 14.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 505 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 195 | 0 | 0 | 310 | 29 | 182 | 35 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 0 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 6 | 12 | 72 | 0 | 0 | 1 | 5160.7 | 921 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 392 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 65 | 180 | 0 | 0 | 500 | 0 | 3523.38 | 8684.08 | 89.65
07:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 38 | 16 | 15 | 0 | 17 | 35 | 16 | 0 | 420 | 0 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 1 | 0 | 14.7 | 22 | 0 | 0 | 7 | 50 | 0 | 0 | 21 | 0 | 0 | 0 | 50 | 12 | 0 | 40 | 2 | 33 | 502 | 0 | 0 | 0 | 0 | 14 | 227 | 0 | 0 | 0 | 1143 | 1 | 51 | 1 | 185 | 0 | 0 | 365 | 28 | 182 | 35 | 0 | 50 | 5 | 0 | 12 | 0 | 52 | 0 | 5 | 0 | 300 | 300 | 0 | 36 | 0 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 56 | 70 | 0 | 2.31 | 3 | 5782.01 | 920 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 751.45 | 0 | 0 | 0 | 9 | 0 | 0 | 15 | 0 | 52.2 | 4 | 0 | 4.25 | 0 | 0 | 0 | 0 | 140 | 0 | 392 | 0 | 0.36 | 2.5 | 0 | 62 | 87 | 1 | 0 | 0 | 0 | 0.3 | 18 | 0.01 | 0 | 307 | 6 | 65 | 220 | 0 | 0 | 580 | 17 | 3933.07 | 9715.08 | 89.64
08:00 | 0 | 51 | 0 | 0 | 0 | 230 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 145 | 0 | 17 | 35 | 16 | 0 | 420 | 0 | 0 | 0 | 17 | 33 | 300 | 0 | 0 | 7 | 0 | 20 | 22 | 0 | 0 | 35 | 100 | 0 | 0 | 7 | 0 | 0 | 0 | 62 | 12 | 0 | 40 | 50 | 6 | 575 | 0 | 0 | 0 | 0 | 68 | 227 | 0 | 0 | 0 | 1217 | 5 | 51 | 45 | 185 | 0 | 0 | 275 | 29 | 182 | 35 | 0 | 50 | 38 | 0 | 17 | 0 | 50 | 0 | 20 | 0 | 285 | 320 | 0 | 36 | 0 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 20 | 0 | 0 | 9 | 56 | 62 | 1 | 11.97 | 2 | 6225.97 | 872 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 765.7 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 0 | 52.2 | 22 | 0 | 10.53 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0.79 | 5.5 | 0 | 62 | 92 | 5 | 0 | 0 | 0 | 0.5 | 12 | 0.03 | 32 | 307 | 5 | 65 | 220 | 0 | 0 | 622 | 54 | 4087.25 | 10313.22 | 89.64
09:00 | 0 | 51 | 0 | 0 | 0 | 230 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 62 | 32 | 95 | 0 | 17 | 35 | 16 | 0 | 420 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 15 | 0 | 19 | 22 | 0 | 0 | 35 | 45 | 0 | 0 | 1 | 0 | 24 | 0 | 24 | 12 | 0 | 40 | 51 | 8 | 577 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 1224 | 12 | 51 | 50 | 185 | 0 | 0 | 290 | 29 | 183 | 35 | 0 | 50 | 68 | 0 | 17 | 11 | 56 | 0 | 31 | 8 | 290 | 320 | 0 | 33 | 0 | 40 | 2 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 9 | 57 | 29 | 1 | 23.57 | 6 | 6150.57 | 871 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 758.19 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 0 | 52.2 | 37 | 0 | 24.89 | 0 | 0 | 0 | 0 | 173 | 0 | 370 | 0 | 2.14 | 2.5 | 0 | 62 | 95 | 2 | 7 | 0 | 0 | 0.5 | 6 | 0.09 | 32 | 307 | 5 | 65 | 220 | 0 | 0 | 610 | 54 | 4078.51 | 10229.08 | 89.63
10:00 | 0 | 51 | 0 | 0 | 0 | 230 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 97 | 32 | 95 | 0 | 17 | 50 | 22 | 0 | 420 | 0 | 0 | 0 | 17 | 16.5 | 300 | 0 | 0 | 15 | 16 | 18 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 29 | 0 | 24 | 12 | 2 | 40 | 17 | 2 | 575 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 1224 | 16 | 43 | 10 | 185 | 0 | 0 | 290 | 29 | 182 | 35 | 0 | 40 | 51 | 2 | 17 | 17 | 60 | 0 | 30 | 16 | 300 | 320 | 0 | 35 | 0 | 40 | 2 | 163 | 16 | 0 | 84 | 30 | 0 | 20 | 0 | 0 | 9 | 58 | 30 | 0 | 15.22 | 6 | 6121.72 | 916 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 762.09 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 52.2 | 35 | 0 | 36.81 | 0 | 0 | 0 | 0 | 174 | 0 | 280 | 0 | 2.48 | 2.5 | 0 | 56 | 35 | 0 | 32 | 0 | 0 | 4.2 | 4 | 0.12 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 600 | 17 | 3939.4 | 10061.12 | 89.63
11:00 | 0 | 51 | 0 | 0 | 0 | 230 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 85 | 32 | 45 | 0 | 35 | 54 | 22 | 0 | 370 | 0 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 26 | 17 | 18 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 12 | 2 | 46 | 17 | 2 | 576 | 0 | 0 | 0 | 0 | 51 | 227 | 0 | 0 | 0 | 1224 | 18 | 43 | 10 | 184 | 0 | 0 | 290 | 29 | 185 | 33 | 37 | 40 | 51 | 9 | 17 | 17 | 66 | 0 | 38 | 14 | 300 | 320 | 0 | 30 | 0 | 40 | 2 | 120 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 9 | 0 | 29 | 0 | 2.13 | 6 | 5993.13 | 917 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 754.75 | 0 | 0 | 0 | 35 | 0 | 10 | 0 | 0 | 52.2 | 13 | 0 | 10.29 | 0 | 0 | 0 | 0 | 173 | 0 | 280 | 0 | 1.26 | 0 | 0 | 56 | 0 | 24 | 0 | 0 | 0 | 5.4 | 26 | 0.14 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 600 | 17 | 3897.04 | 9890.17 | 89.62
12:00 | 0 | 51 | 0 | 0 | 0 | 230 | 0 | 0 | 340 | 0 | 0 | 17 | 0 | 0 | 96 | 16 | 45 | 0 | 35 | 54 | 22 | 0 | 370 | 0 | 0 | 0 | 35 | 0 | 250 | 0 | 0 | 29 | 17 | 17.5 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 3 | 0 | 32 | 0 | 24 | 12 | 4 | 46 | 17 | 2 | 576 | 0 | 0 | 0 | 0 | 66 | 220 | 0 | 0 | 0 | 1224 | 18 | 43 | 10 | 184 | 0 | 0 | 300 | 29 | 192 | 34 | 60 | 40 | 51 | 10 | 17 | 17 | 62 | 1 | 27 | 16 | 295 | 320 | 0 | 30 | 0 | 40 | 2 | 120 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 8 | 0 | 20 | 1 | 17.68 | 6 | 6041.18 | 917 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 757.06 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 15 | 52.2 | 95 | 20 | 5.27 | 0 | 0 | 0 | 0 | 170 | 0 | 350 | 0 | 0 | 0 | 0 | 62 | 0 | 19 | 32 | 0 | 0 | 6.2 | 51 | 0.34 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 610 | 17 | 4187.07 | 10228.25 | 89.62
13:00 | 0 | 51 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 54 | 0 | 0 | 88 | 16 | 45 | 0 | 35 | 54 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 27 | 17 | 18 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 5 | 0 | 32 | 0 | 50 | 12 | 2 | 46 | 17 | 2 | 576 | 0 | 0 | 0 | 0 | 95 | 220 | 0 | 0 | 0 | 1224 | 17 | 43 | 10 | 184 | 0 | 0 | 315 | 29 | 193 | 34 | 106 | 50 | 51 | 0 | 17 | 17 | 72 | 16 | 26 | 24 | 310 | 320 | 0 | 32 | 10 | 40 | 2 | 163 | 20 | 0 | 86 | 30 | 0 | 18 | 0 | 1 | 9 | 0 | 17 | 1 | 10.21 | 3 | 6383.21 | 918 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 760.81 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 16 | 52.2 | 100 | 30 | 22.34 | 0 | 0 | 0 | 0 | 178 | 0 | 350 | 0 | 1.67 | 2.5 | 0 | 62 | 35 | 36 | 33 | 0 | 0 | 5.9 | 46 | 0.5 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 622 | 17 | 4285.92 | 10669.13 | 89.61
14:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 392 | 0 | 0 | 17 | 0 | 0 | 53 | 16 | 15 | 0 | 35 | 17 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 16 | 250 | 0 | 0 | 26 | 0 | 18 | 0 | 0 | 0 | 35 | 15 | 0 | 0 | 27 | 0 | 32 | 0 | 12 | 12 | 2 | 46 | 17 | 8 | 500 | 0 | 0 | 0 | 0 | 51 | 219 | 0 | 0 | 0 | 1148 | 16 | 43 | 10 | 184 | 0 | 0 | 320 | 29 | 210 | 34 | 75 | 50 | 51 | 0 | 17 | 17 | 76 | 16 | 29 | 24 | 290 | 320 | 0 | 0 | 30 | 38 | 2 | 120 | 0 | 0 | 86 | 30 | 0 | 18 | 0 | 17 | 8 | 0 | 17 | 2 | 12.13 | 6 | 5795.13 | 918 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 761 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 16 | 52.2 | 90 | 30 | 50.89 | 0 | 0 | 0 | 0 | 171 | 0 | 340 | 0 | 4.17 | 2.5 | 0 | 62 | 35 | 32 | 35 | 0 | 0 | 5 | 101 | 0.46 | 16 | 250 | 5 | 65 | 180 | 0 | 0 | 560 | 17 | 4170.22 | 9965.35 | 89.61
15:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 395 | 0 | 0 | 17 | 0 | 0 | 17 | 16 | 15 | 0 | 35 | 17 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 16 | 330 | 0 | 0 | 20 | 0 | 17 | 5 | 0 | 0 | 35 | 15 | 0 | 0 | 12 | 0 | 32 | 0 | 12 | 12 | 1 | 46 | 17 | 2 | 530 | 0 | 0 | 0 | 0 | 51 | 218 | 0 | 0 | 0 | 1147 | 12 | 43 | 10 | 184 | 0 | 0 | 340 | 29 | 210 | 32 | 68 | 50 | 51 | 0 | 17 | 17 | 76 | 16 | 18 | 24 | 325 | 320 | 0 | 29 | 30 | 38 | 0 | 163 | 0 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 8 | 0 | 18 | 2 | 38.05 | 6 | 5987.05 | 918 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 762 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 21 | 52.2 | 72 | 30 | 40.33 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 3.43 | 2.5 | 0 | 63 | 35 | 26 | 35 | 0 | 0 | 3.6 | 96 | 0.35 | 16 | 295 | 5 | 65 | 220 | 0 | 0 | 560 | 17 | 4266.41 | 10253.46 | 89.6
16:00 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 408 | 0 | 0 | 17 | 0 | 0 | 39 | 16 | 15 | 0 | 17 | 17 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 20 | 335 | 0 | 0 | 11 | 0 | 16 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 17 | 0 | 32 | 0 | 12 | 12 | 1 | 46 | 17 | 6 | 578 | 0 | 0 | 0 | 0 | 51 | 216 | 0 | 0 | 0 | 1224 | 7 | 51 | 10 | 184 | 0 | 0 | 290 | 29 | 195 | 32 | 68 | 51 | 51 | 0 | 0 | 17 | 66 | 16 | 25 | 24 | 315 | 320 | 0 | 30 | 30 | 40 | 0 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 8 | 0 | 18 | 1 | 19.26 | 6 | 6060.26 | 918 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 761 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 21 | 52.2 | 44 | 30 | 24.29 | 0 | 0 | 0 | 0 | 159 | 0 | 414 | 0 | 2.16 | 2.5 | 0 | 61 | 35 | 14 | 35 | 0 | 0 | 2.1 | 77 | 0.21 | 16 | 307 | 5 | 65 | 220 | 0 | 0 | 600 | 17 | 4204.46 | 10264.72 | 89.6
17:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 409 | 0 | 0 | 17 | 0 | 0 | 58 | 32 | 15 | 0 | 17 | 54 | 22 | 0 | 380 | 0 | 0 | 0 | 5 | 20 | 335 | 0 | 0 | 4 | 0 | 16 | 22 | 0 | 0 | 35 | 30 | 0 | 0 | 12 | 0 | 32 | 17 | 50 | 12 | 0 | 46 | 38 | 10 | 576 | 12 | 0 | 0 | 0 | 54 | 216 | 0 | 0 | 0 | 1224 | 2 | 51 | 20 | 165 | 0 | 0 | 260 | 26 | 180 | 33 | 68 | 50 | 53 | 0 | 10 | 17 | 58 | 16 | 8 | 24 | 325 | 320 | 0 | 30 | 30 | 38 | 0 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 35 | 9 | 18 | 0 | 6.43 | 6 | 6205.43 | 917 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 756 | 0 | 0 | 0 | 39 | 0 | 50 | 10 | 21 | 8 | 17 | 30 | 7.92 | 0 | 0 | 0 | 0 | 158 | 0 | 414 | 0 | 0.69 | 2.5 | 0 | 61 | 35 | 5 | 35 | 0 | 0 | 0.7 | 28 | 0.08 | 16 | 307 | 4 | 130 | 220 | 0 | 0 | 600 | 17 | 4100.89 | 10306.32 | 89.59
18:00 | 0 | 45 | 0 | 0 | 0 | 230 | 0 | 0 | 406 | 0 | 0 | 24 | 0 | 0 | 78 | 64 | 120 | 0 | 18 | 108 | 22 | 0 | 350 | 0 | 0 | 0 | 5 | 20 | 300 | 0 | 0 | 0 | 7 | 17 | 22 | 0 | 0 | 35 | 80 | 0 | 0 | 17 | 51 | 32 | 17 | 89 | 50 | 0 | 46 | 70 | 17 | 576 | 17 | 0 | 13 | 0 | 89 | 216 | 0 | 0 | 0 | 1224 | 0 | 51 | 63 | 163 | 0 | 0 | 290 | 10 | 222 | 36 | 72 | 50 | 97 | 0 | 17 | 17 | 72 | 16 | 0 | 24 | 290 | 320 | 0 | 30 | 30 | 40 | 0 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 55 | 9 | 18 | 0 | 0 | 6 | 6743 | 917 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 755 | 0 | 0 | 0 | 70 | 5 | 70 | 50 | 35 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 350 | 0 | 0 | 2.5 | 0 | 61 | 55 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 5 | 100 | 190 | 0 | 0 | 600 | 90 | 4202.5 | 10945.5 | 89.59
19:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 35 | 0 | 0 | 112 | 48 | 210 | 0 | 35 | 162 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 17 | 17 | 22 | 0 | 0 | 35 | 180 | 0 | 0 | 27 | 51 | 78 | 35 | 89 | 50 | 0 | 46 | 106 | 12 | 578 | 53 | 0 | 22 | 0 | 105 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 163 | 0 | 0 | 270 | 10 | 219 | 36 | 96 | 50 | 173 | 7 | 17 | 0 | 78 | 0 | 0 | 37 | 295 | 320 | 0 | 30 | 30 | 40 | 0 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 18 | 0 | 0 | 6 | 7368 | 872 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 50 | 0 | 101 | 5 | 94 | 70 | 36 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 370 | 0 | 0 | 5.5 | 0 | 61 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 126 | 4473.5 | 11841.5 | 89.58
19:30 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 35 | 0 | 0 | 89 | 48 | 210 | 0 | 35 | 162 | 22 | 0 | 360 | 0 | 0 | 0 | 17 | 18 | 335 | 0 | 0 | 0 | 17 | 17 | 22 | 0 | 0 | 35 | 267 | 0 | 0 | 26 | 34 | 48 | 0 | 89 | 24 | 0 | 46 | 110 | 14 | 575 | 0 | 0 | 0 | 0 | 105 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 147 | 0 | 0 | 270 | 10 | 225 | 36 | 115 | 50 | 200 | 18 | 17 | 0 | 74 | 0 | 0 | 38 | 300 | 320 | 0 | 30 | 30 | 40 | 0 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 18 | 0 | 0 | 6 | 7361 | 874 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 50 | 0 | 113 | 5 | 94 | 70 | 36 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 370 | 0 | 0 | 5.5 | 0 | 61 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 108 | 4393.5 | 11754.5
20:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 35 | 0 | 0 | 95 | 48 | 160 | 0 | 35 | 162 | 22 | 0 | 360 | 0 | 0 | 0 | 17 | 18 | 335 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 0 | 35 | 216 | 0 | 0 | 24 | 34 | 39 | 0 | 89 | 24 | 0 | 46 | 110 | 17 | 576 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 147 | 0 | 0 | 270 | 10 | 226 | 36 | 115 | 50 | 200 | 13 | 17 | 0 | 78 | 0 | 0 | 38 | 295 | 320 | 0 | 33 | 30 | 40 | 0 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 18 | 0 | 0 | 6 | 7240 | 873 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 50 | 0 | 113 | 7 | 95 | 70 | 36 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 370 | 0 | 0 | 5.5 | 0 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 90 | 4359.5 | 11599.5 | 89.58
21:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 90 | 32 | 110 | 0 | 0 | 162 | 22 | 0 | 380 | 0 | 0 | 0 | 17 | 18 | 335 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 52 | 0 | 0 | 14 | 33 | 39 | 0 | 89 | 24 | 0 | 46 | 110 | 21 | 576 | 0 | 0 | 0 | 0 | 105 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 145 | 0 | 0 | 285 | 10 | 194 | 36 | 115 | 50 | 200 | 9 | 17 | 0 | 68 | 0 | 0 | 38 | 320 | 320 | 0 | 33 | 30 | 40 | 0 | 163 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 18 | 0 | 0 | 6 | 6968 | 921 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 50 | 0 | 113 | 11 | 96 | 35 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 5.5 | 0 | 61 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 54 | 4339.5 | 11307.5 | 89.57
22:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 85 | 32 | 60 | 0 | 0 | 162 | 22 | 0 | 350 | 0 | 0 | 0 | 17 | 18 | 335 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 35 | 52 | 0 | 0 | 15 | 16 | 39 | 0 | 100 | 24 | 0 | 40 | 110 | 25 | 577 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 165 | 0 | 0 | 270 | 10 | 182 | 36 | 115 | 50 | 120 | 9 | 17 | 0 | 72 | 0 | 0 | 38 | 295 | 320 | 0 | 33 | 30 | 40 | 0 | 163 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 18 | 0 | 0 | 6 | 6716 | 920 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 50 | 0 | 70 | 18 | 98 | 35 | 34 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 414 | 0 | 0 | 5.5 | 0 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 7 | 132 | 220 | 0 | 0 | 622 | 54 | 4294.5 | 11010.5 | 89.57
23:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 162 | 22 | 0 | 350 | 0 | 0 | 0 | 17 | 8 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 35 | 52 | 0 | 0 | 14 | 0 | 0 | 0 | 89 | 0 | 0 | 40 | 110 | 27 | 577 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 24 | 167 | 0 | 0 | 270 | 10 | 182 | 36 | 68 | 50 | 120 | 0 | 17 | 0 | 72 | 0 | 0 | 0 | 280 | 320 | 0 | 33 | 30 | 40 | 2 | 163 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 13 | 0 | 0 | 6 | 6358 | 921 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 70 | 19 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 414 | 0 | 0 | 2.5 | 0 | 64 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 220 | 0 | 0 | 622 | 17 | 4003.5 | 10361.5 | 89.56
Total KWH | 0 | 824640 | 0 | 0 | 0 | 5329969 | 0 | 0 | 9334800 | 0 | 0 | 259560 | 0 | 0 | 1310976 | 479520 | 1231211 | 0 | 369244 | 1388160 | 467640 | 0 | 9041000 | 0 | 0 | 0 | 241787 | 522200 | 7385930 | 0 | 0 | 165184 | 100800 | 384600 | 480960 | 0 | 0 | 612218 | 1031236 | 0 | 0 | 300960 | 172754 | 439920 | 50663 | 1034880 | 293760 | 15000 | 1023060 | 1379990 | 430560 | 13389090.91 | 46836 | 0 | 41280 | 0 | 1737127 | 5131814 | 0 | 0 | 0 | 28063634 | 124470 | 1116962 | 849745 | 4265455 | 0 | 0 | 7172000 | 558720 | 4732000 | 843480 | 1162560 | 1164530 | 1651200 | 77280 | 376610 | 175560 | 1503360 | 113870 | 245891 | 343984 | 7301500 | 7691500 | 0 | 768384 | 323000 | 929040 | 34224 | 3714709.1 | 418248 | 0 | 2049600 | 718752 | 0 | 459000 | 0 | 23040 | 519600 | 345600 | 854400 | 7100 | 172840 | 103440 | 147424618.01 | 22026909 | 5518080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504000 | 0 | 0 | 17716364 | 0 | 197232 | 0 | 1101600 | 64568 | 922352 | 453216 | 242005 | 519432 | 605940 | 311968 | 232496 | 0 | 0 | 0 | 0 | 4082518 | 0 | 9161527 | 0 | 18420 | 69750 | 0 | 1435200 | 695825 | 173572 | 690604 | 0 | 0 | 34287.84 | 434160 | 2481 | 460704 | 7091000 | 148741 | 2032000 | 5254690 | 0 | 14546 | 14327272.73 | 678000 | 97221460.57 | 244646078.58

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10229.08 | MW | 09:00 Hr. | Energy Generated |  |  | 244.6461 |  | MKWHr.
| Day Peak Demand |  |  | 10260.08 | MW | 09:00 Hr. | Energy Unserverd |  |  | 0.393 |  | MKWHr.
| Evening Peak Generation |  |  | 11841.5 | MW | 19:00 Hr. | Energy Demand |  |  | 245.0391 |  | MKWHr.
| Evening Peak Demand |  |  | 11910.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 29.7 |  | °C
| Minimum Generation of the Day |  |  | 8392.96 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 830.21 |  | MMCFD
| Maximum Generation of the Day |  |  | 11841.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.3579 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.9471 | 0 | 6.2059 | 0 | 0 | 0.16518 | 0 | 0 | 39.3182 | Gas | 110.2689 | Gas | 402973836.672
| Chattogram Zone |  |  | 5.5624 | 41.4527 | 6.8407 | 0 | 1.0231 | 0.13947 | 0 | 0.30096 | 55.3193 | Coal | 64.3207 | Coal | 442537162.1337
| Cumilla Zone |  |  | 20.2298 | 0 | 4.3742 | 0 | 0 | 0.24589 | 1.5034 | 0 | 26.3532 | HFO | 24.7499 | HFO | 449058682.96
| Mymensingh Zone |  |  | 0.8544 | 0 | 0.99168 | 0 | 0 | 0.17994 | 0 | 0 | 2.026 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.408 | Hydro | 1.0231 | Hydro | 102306
| Khulna Zone |  |  | 5.5181 | 0 | 0 | 0 | 0 | 0.504 | 22.0269 | 0 | 28.049 | Solar | 2.7358 | Solar | 43917177.9324
| Barishal Zone |  |  | 7.4354 | 21.4328 | 1.1387 | 0 | 0 | 0.002481 | 0 | 0 | 30.0094 | Import | 41.2466 | Import | 212435655.82
| Rajshahi Zone |  |  | 13.3138 | 0 | 3.8124 | 0 | 0 | 0.85686 | 17.7164 | 0 | 35.6994 | Wind | 0.30096 | Wind | 4406054.4
| Rangpur Zone |  |  | 0 | 1.4352 | 1.3864 | 0 | 0 | 0.64202 | 0 | 0 | 3.4636
| Total |  |  | 110.2689 | 64.3207 | 24.7499 | 0 | 1.0231 | 2.7358 | 41.2466 | 0.30096 | 244.6461
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 402973836.672 |  | Hydro | 102306
|  |  |  | Coal | 442537162.1337 |  | Solar | 43917177.9324
|  |  |  | HFO | 449058682.96 |  | Import | 212435655.82
|  |  |  | HSD | 0 |  | Wind | 4406054.4
[5 empty] | Total: | 155,54,30,875 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0269 | Peak Hr Flow | 872.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9917981.905 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.7164 | Peak Hr Flow | 753.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 348 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5034 | Peak Hr Flow | 78.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 832 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.2466 | Peak Hr Flow | 1703.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 20 |  | 4368
|  |  |  | Chattogram |  | 0 |  | 1218
|  |  |  | Cumilla |  | 0 |  | 991
|  |  |  | Mymensingh |  | 46 |  | 940
|  |  |  | Sylhet |  | 0 |  | 374
|  |  |  | Khulna |  | 0 |  | 1324
|  |  |  | Barishal |  | 0 |  | 325
|  |  |  | Rajshahi |  | 0 |  | 1155
|  |  |  | Rangpur |  | 0 |  | 719
|  |  |  | Total |  | 66 |  | 11414
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1122 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1788.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 |  | Goalpara-Kpcl,2 CKT is S/D.
| 08:28 | 18:55 | Rampura 230/132kV S/S 230kV Busbar-2 Project Work S/D
| 08:34 | 18:28 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Maintenance
Work
| 08:36 | 12:40 | Bogura(New)-Naogaon 132 kV Ckt-2 Tripped from Naogaon 132/33kV end showing no relays Due
to Trip and from Bogura 230/132kV end showing (Distance PROTN.Relay) Fault Type A to G,
A/R in PROGRESS, LO(Recloser). (67/67N- Relay) Phase-A, LOP relays.
| 08:46 | 18:04 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance
| 08:50 | 14:40 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Annual
maintenance
| 08:58 |  | Bibiyana-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to AM
| 09:00 |  | Day Peak Gen. 10229 MW
| 09:09 | 12:46 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Line Maintenance.
| 10:15 |  | Ashuganj-Kishoreganj 132kV Ckt-2 Project Work S/D from Kishoreganj 132/33kV end.
| 10:17 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Project Work S/D from Bajitpur 132/33kV end.
| 10:19 | 18:33 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to Tr - 1` R Phase Oil Centrifusing
| 10:20 | 14:42 | Maniknagar 132/33kV S/S Kazla Ckt -1 Scheduled S/D Due to Red phase LA change
| 10:35 | 12:26 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to shutdown taken by PBS for new
feeder commissioning
| 10:35 | 12:26 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to shutdown taken by PBS for new
feeder commissioning
| 10:35 | 12:26 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to shutdown taken by PBS for new
feeder commissioning
| 10:53 | 11:03 | Ishwardi-Natore 132kV Ckt-1 Tripped from Ishurdi 132/33kV end showing ABB relays. and
from Natore 132/33kV end showing Distance Relay relays Due to Ishurdi 132/33 kv side
fault
| 11:02 | 11:10 | Mymensingh RPCL-Tangail 132kV Ckt-1 Tripped from Muktagacha 132/33kV end showing | [7 empty] | 3.0MW load
|  |  | Overcurrent Relay, Distance Relay relays. | [7 empty] | interrup.
Muktagacha 132/33kV
end
| 11:02 | 11:11 | Muktagacha 132/33kV S/S RPCL-2 Tripped showing Overcurrent Relay, Distance Relay relays. | [7 empty] | 3.0MW load
interrup.
|  | 11:12 | Purbasadipur 132/33kV S/S T-4 Transformer HT is restored.
|  | 11:13 | Purbasadipur 132/33kV S/S T-4 Transformer LT is restored.
| 11:15 | 19:50 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Line checking
| 11:16 | 19:50 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Line checking
| 11:48 | 17:37 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end.
| 11:48 | 17:38 | Mithapukur-Palashbari 132kV Ckt-2 Scheduled S/D from Palashbari 132/33kV end.
| 12:07 |  | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to low voltage.
|  | 12:16 | Aminbazar 400/230/132kV S/S Gopalganj-2 is restored.
|  | 12:17 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 is restored.
| 13:05 |  | Hasnabad 132/33kV S/S 33kv Main Bus Scheduled S/D Due to Zinzira-2 ckt. Faulty Bus riser
change.
|  | 13:15 | Naogaon 132/33kV S/S T-2 HT is restored.
|  | 13:18 | Bhaluka 132/33kV S/S Bus Section- 03 is restored.
| 14:17 | 14:59 | Sirajganj 132/33kV S/S T3-(435) HT Scheduled S/D Due to For Energy Meter Change
| 14:17 | 14:59 | Sirajganj 132/33kV S/S T3-(435) LT Scheduled S/D Due to For Energy Meter Change
| 15:02 | 15:40 | Sirajganj 132/33kV S/S T4-(445) HT Scheduled S/D Due to For Energy Meter Change.
| 15:02 | 15:40 | Sirajganj 132/33kV S/S T4-(445) LT Scheduled S/D Due to For Energy Meter Change.
| 16:07 |  | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to 132 KV CSE installation & XLPE cable
Termination.
| 16:09 |  | Naogaon 132/33kV S/S T-3 LT Scheduled S/D Due to 132 KV CSE installation & XLPE cable
Termination.
| 17:32 |  | Goalpara-KPCL-2 Line S/D Withdraw.
|  | 18:00 | Bogura 132/33kV S/S Transformer-1 HT is restored.
|  | 18:33 | Sunamganj 132/33kV S/S Tr-1 HT is restored.
|  | 18:33 | Sunamganj 132/33kV S/S Tr-1 HT is restored.
|  | 18:33 | Sunamganj 132/33kV S/S Tr-1 HT is restored.
|  | 18:34 | Baghabari-Ullahpara 132 kV Ckt-1 is restored.
|  | 18:34 | Sunamganj 132/33kV S/S Tr-1 LT is restored.
| 05:00 |  | Minimum Generation: 8336 MW.
| 07:26 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due to CT change
| 07:26 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due to CT CHANGE
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 5329969 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 405 | 9334800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 9041000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7385930 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 479520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 369244 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 241787 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 384600 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 480960 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 467640 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 18 | 522200 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 210 | 1231211 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 1310976 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 824640 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1388160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 165184 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 100800 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2068 | 39318181
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 124470 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 41280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1023060 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5131814 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1737127 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 439920 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 172754 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 89 | 1034880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 430560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 15000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 180 | 1031236 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 35 | 50663 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1379990 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 293760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 612218 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 46836 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28063634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 27 | 300960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 578 | 13389090.91 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2906 | 55319252.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 219 | 4732000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 270 | 7172000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 843480 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 558720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 163 | 4265455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1116962 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 112 | 849745 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 37 | 343984 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1164530 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 173 | 1651200 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1503360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 113870 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 376610 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 175560 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 7 | 77280 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1162560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 245891 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1319 | 26353207
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 854400 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 345600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 519600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 172840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 103440 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 23040 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 90 | 2026020
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 323000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 929040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3714709.1 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 30 | 768384 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 34224 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718752 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2049600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 459000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 418248 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7301500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7691500 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 985 | 24407957.1
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 22026909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 193 | 5518080 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 504000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Shutdown due to Inspection.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1065 | 28048989
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 80 | 460704 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 148741 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 2032000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14327272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5254690 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 126 | 678000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7091000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2481 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1494 | 29994888.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 197232 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 64568 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 36 | 242005 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 154 | 4082518 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 370 | 9161527 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 311968 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 69750 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 519432 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 922352 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 101 | 1101600 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 453216 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 18420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 753 | 17716364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 232496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 605940 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1676.5 | 35699388
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 61 | 1435200 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 690604 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34287.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 695825 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173572 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 434160 | -
Rangpur Area Total |  |  |  |  | 950 | 238 | 3463648.84
Eastern Grid Total |  |  |  |  | 16856.242 | 7368 | 147424618.01
Western Grid Total |  |  |  |  | 10294.5 | 4473.5 | 97206914.57
National Grid Total |  |  |  |  | 27150.742 | 11841.5 | 244631532.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7825.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3523 | MW
i) Dhaka area |  |  | 4348.17 |  | MW | i) Khulna area |  |  |  | 1324 | MW
ii) Chattogram area |  |  | 1218.3 |  | MW | ii) Barishal area |  |  |  | 325 | MW
iii) Cumilla area |  |  | 991 |  | MW | iii) Rajshahi area |  |  |  | 1155 | MW
iv) Mymensingh area |  |  | 894 |  | MW | iv) Rangpur area |  |  |  | 719 | MW
v) Sylhet area |  |  | 374 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11348.47 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 61 | 08:00 | 133 | Postogola | 42 | 13:00
2 | AKSML | 102.9 | 12:00 | 68 | Jamalpur | 103 | 08:00 | 134 | Purbachal | 15 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jashore | 111 | 19:00 | 135 | Purbasadipur | 105 | 07:00
4 | Agargaon | 85 | 13:00 | 70 | Jhenaidah | 100 | 18:30 | 136 | Rahanpur | 0 | 00:00
5 | Agrabad | 80 | 18:30 | 71 | Joydebpur | 151 | 12:00 | 137 | Rahim | 37 | 17:00
6 | Amnura | 42 | 13:00 | 72 | Joypurhat | 60 | 08:00 | 138 | Rajbari | 56 | 19:00
7 | Ashuganj | 70 | 18:30 | 73 | Juldah | 14 | 00:00 | 139 | Rajendrapur | 110 | 19:00
8 | BSRM | 192 | 18:00 | 74 | KSRM | 36 | 10:00 | 140 | Rajshahi | 84 | 19:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 196 | 09:00 | 141 | Rajshahi-230 | 57 | 13:00
10 | Bajitpur | 37 | 19:30 | 76 | Kachua | 56 | 18:30 | 142 | Ramganj | 76 | 20:00
11 | Bakulia | 83 | 18:30 | 77 | Kallyanpur | 78 | 19:00 | 143 | Rampur | 32 | 18:30
12 | Banani | 23 | 13:00 | 78 | Kalurghat | 34 | 14:00 | 144 | Rangamati | 13 | 19:00
13 | Bangabhaban | 11 | 13:00 | 79 | Kamrangirchar | 64.8 | 13:00 | 145 | Rangpur | 110 | 18:30
14 | Barapukuria | 59 | 08:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 4 | 15:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 87 | 15:00 | 147 | SSM | 2 | 01:00
16 | Barishal | 82 | 13:00 | 82 | Keranigonj | 79 | 13:00 | 148 | Saidpur | 106 | 08:00
17 | Barishal-230 | 68 | 19:00 | 83 | Khagrachori | 24 | 19:00 | 149 | Satkhira | 96 | 19:00
18 | Baroaulia | 48 | 19:00 | 84 | Khulna | 83 | 13:00 | 150 | Satmasjid | 86 | 13:00
19 | Baroirhat | 40 | 18:30 | 85 | Khulshi | 163 | 18:30 | 151 | Savar | 194 | 12:00
20 | Bashundhara | 152 | 13:00 | 86 | Kishoreganj | 104 | 18:30 | 152 | SevenRings | 18.65 | 15:00
21 | BashundharaCement | 8 | 12:00 | 87 | Kodda | 238 | 18:30 | 153 | ShahCement | 38 | 10:00
22 | Beanibazar | 44 | 19:30 | 88 | Kulaura | 27 | 19:30 | 154 | Shahjadpur | 70 | 18:30
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 57 | 18:30 | 155 | Shahjibazar | 94 | 22:00
24 | Bhaluka | 122 | 18:00 | 90 | Kushtia | 116 | 18:30 | 156 | Shahmirpur | 48 | 16:00
25 | Bhandaria | 37 | 22:00 | 91 | Lalbag | 61 | 19:00 | 157 | Shariatpur | 55 | 21:00
26 | Bhangura | 28 | 18:30 | 92 | Lalmonirhat | 45 | 18:00 | 158 | Sherpur | 108 | 08:00
27 | Bheramara(GK) | 39 | 18:30 | 93 | MI_Cement | 16.6 | 17:00 | 159 | Shikalbaha | 23 | 18:00
28 | Bhulta | 234 | 10:00 | 94 | Madanganj | 29 | 21:00 | 160 | Shitalakhya | 69.4 | 12:00
29 | Bog-Sherpur | 72 | 08:00 | 95 | Madaripur | 71 | 19:00 | 161 | Sholosohor | 38 | 19:00
30 | Bogura | 117 | 18:30 | 96 | Madartek | 67.52 | 13:00 | 162 | Shyampur | 164 | 10:00
31 | Borhanuddin | 56 | 21:00 | 97 | Madunaghat | 39 | 18:30 | 163 | Siddhirganj | 116 | 12:00
32 | Brahmanbaria | 107 | 21:00 | 98 | Magura | 48 | 18:30 | 164 | Sirajganj | 96 | 19:00
33 | Cantonment | 104 | 13:00 | 99 | Mahasthangarh | 58 | 08:00 | 165 | Sonargaon | 86 | 20:00
34 | Chandpur | 48 | 18:00 | 100 | Manikganj | 99 | 18:30 | 166 | Sreemongol | 47 | 18:00
35 | Chandraghona | 27 | 18:30 | 101 | Maniknagar | 68 | 13:00 | 167 | Sreepur | 98 | 18:30
36 | Chapai | 62 | 13:00 | 102 | Matarbari | 41 | 19:00 | 168 | Srinagar | 31.65 | 14:00
37 | Charsaidpur | 37 | 17:00 | 103 | Matuail | 58 | 10:00 | 169 | Sunamganj | 38 | 19:30
38 | Chauddagram | 50 | 13:00 | 104 | Millgate | 68 | 12:00 | 170 | Sylhet | 24 | 19:30
39 | Chhatak | 20 | 09:00 | 105 | Mirpur | 108 | 12:00 | 171 | Sylhet-132 | 94 | 13:00
40 | Chowmuhani | 166 | 18:30 | 106 | Mirsorai | 9 | 17:00 | 172 | TK | 18 | 18:00
41 | Chuadanga | 73 | 18:30 | 107 | Mirzapur | 39 | 22:00 | 173 | Tangail | 157 | 08:00
42 | Coxsbazar | 121 | 18:30 | 108 | Mithapukur | 48 | 18:30 | 174 | Thakurgaon | 79 | 19:00
43 | Cumilla(N) | 109 | 11:00 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 107 | 12:00
44 | Cumilla(S) | 151 | 18:30 | 110 | Mogbazar | 127.4 | 12:00 | 176 | Ullahpara | 27 | 09:00
45 | Daudkandi | 100 | 18:30 | 111 | Mongla | 34 | 19:30 | 177 | Ullon | 16 | 18:30
46 | Dhaka | 42 | 13:00 | 112 | Motijheel | 31 | 13:00 | 178 | Uttara | 71 | 13:00
47 | Dhamrai | 106 | 10:00 | 113 | Muktagacha | 31 | 07:00 | 179 | UttaraNew | 32 | 13:00
48 | Dhanmondi | 115 | 13:00 | 114 | Munshiganj | 68 | 21:00 | 180 | Zigatola | 59 | 13:00
49 | Dohazari | 88 | 19:00 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 108 | 18:30 | 116 | Mymensingh | 162 | 18:30
51 | Fatullah | 79 | 12:00 | 117 | Naogaon | 95 | 18:30
52 | Fenchuganj | 29 | 18:00 | 118 | Narail | 44 | 19:00
53 | Feni | 91 | 18:00 | 119 | Narinda | 72 | 13:00
54 | GPH | 98 | 20:00 | 120 | Narshingdi | 136 | 19:30
55 | Ghatail | 48 | 09:00 | 121 | Natore | 110 | 19:00
56 | Ghorashal | 12 | 12:00 | 122 | Nawabganj | 38 | 21:00
57 | Ghorashal-230 | 62 | 23:00 | 123 | Netrakona | 133 | 09:00
58 | Goalpara | 18 | 08:00 | 124 | New | 77 | 12:00
59 | Gollamari | 56 | 19:00 | 125 | Niamatpur | 78 | 18:30
60 | Gopalganj | 82 | 19:00 | 126 | Noapara | 38 | 19:00
61 | Gulshan | 88 | 12:00 | 127 | PHP | 8 | 17:00
62 | Halishahar | 66 | 16:00 | 128 | Pabna | 75 | 19:00
63 | HaripurSBU | 182 | 11:00 | 129 | Palashbari | 108 | 07:00
64 | Hasnabad | 71 | 20:00 | 130 | Panchagarh | 43 | 18:30
65 | Hathazari | 63 | 18:30 | 131 | Patuakhali | 51.5 | 21:00
66 | Ishurdi | 63 | 19:00 | 132 | Payra | 22 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9815.09 | 0 |  | 9815.09
1:00 | 9355.28 | 0 |  | 9355.28
2:00 | 9068.01 | 0 |  | 9068.01
3:00 | 8732.23 | 0 |  | 8732.23
4:00 | 8504.82 | 0 |  | 8504.82
5:00 | 8392.96 | 0 |  | 8392.96
6:00 | 8684.08 | 0 |  | 8684.08
7:00 | 9715.08 | 51 |  | 9768.08
8:00 | 10313.22 | 45 |  | 10360.22
9:00 | 10229.08 | 30 |  | 10260.08
10:00 | 10061.12 | 0 |  | 10061.12
11:00 | 9890.17 | 31 |  | 9922.17
12:00 | 10228.25 | 30 |  | 10259.6
13:00 | 10669.13 | 0 |  | 10669.13
14:00 | 9965.35 | 0 |  | 9965.35
15:00 | 10253.46 | 28 |  | 10282.46
16:00 | 10264.72 | 26 |  | 10291.72
17:00 | 10306.32 | 26 |  | 10333.32
18:00 | 10945.5 | 0 |  | 10945.5
19:00 | 11841.5 | 66 |  | 11910.5
19:30 | 11754.5 | 53 |  | 11809.5
20:00 | 11599.5 | 30 |  | 11630.5
21:00 | 11307.5 | 0 |  | 11307.5
22:00 | 11010.5 | 15 |  | 11026.5
23:00 | 10361.5 | 15 |  | 10377.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 23-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3045 | 1562.2 | 921 | 0 | 62 | 755.89 | 40 | 2791 | 0 | 42 | 596 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3044 | 1567.3 | 921 | 0 | 59 | 725.385 | 40 | 2791 | 0 | 21 | 416 | 0 | 0 | 0.5 | 0 | 23-02-2025
01:00 | 3043 | 1572.4 | 921 | 0 | 56 | 694.88 | 40 | 2791 | 0 | 0 | 236 | 0 | 0 | 1 | 0
01:30 | 3041.5 | 1575.35 | 921 | 0 | 56 | 679.795 | 40 | 2669.5 | 0 | 0 | 227 | 0 | 0 | 1.5 | 0 | Energy Generated | 244.6461 |  | MKWHr
02:00 | 3040 | 1578.3 | 921 | 0 | 56 | 664.71 | 40 | 2548 | 0 | 0 | 218 | 0 | 0 | 2 | 0 | Energy not Served | 0.393 |  | MKWHr
02:30 | 3027 | 1580.75 | 920.5 | 0 | 54 | 668.87 | 40 | 2468.5 | 0 | 0 | 134.5 | 0 | 0 | 6 | 0 | Total Energy Requirement | 245.0391 |  | MKWHr
03:00 | 3014 | 1583.2 | 920 | 0 | 52 | 673.03 | 40 | 2389 | 0 | 0 | 51 | 0 | 0 | 10 | 0
03:30 | 2970 | 1579.2 | 920 | 0 | 52 | 670.825 | 40 | 2348.5 | 0 | 0 | 25.5 | 0 | 0 | 12.5 | 0
04:00 | 2926 | 1575.2 | 920 | 0 | 52 | 668.62 | 40 | 2308 | 0 | 0 | 0 | 0 | 0 | 15 | 0
04:30 | 2897 | 1546.7 | 920 | 0 | 51 | 667.69 | 40 | 2308.5 | 0 | 0 | 0 | 0 | 0 | 18 | 0
05:00 | 2868 | 1518.2 | 920 | 0 | 50 | 666.76 | 40 | 2309 | 0 | 0 | 0 | 0 | 0 | 21 | 0
05:30 | 2956 | 1527.2 | 920.5 | 0 | 51 | 667.32 | 40 | 2341.5 | 0 | 0 | 9.5 | 0 | 0 | 25.5 | 0
06:00 | 3044 | 1536.2 | 921 | 0 | 52 | 667.88 | 40 | 2374 | 0 | 0 | 19 | 0 | 0 | 30 | 0
06:30 | 3084.5 | 1591.2 | 920.5 | 0 | 52 | 709.665 | 40 | 2484 | 19.115 | 16.5 | 256.6 | 0 | 0 | 25.5 | 25.5
07:00 | 3125 | 1646.2 | 920 | 0 | 52 | 751.45 | 40 | 2594 | 38.23 | 33 | 494.2 | 0 | 0 | 21 | 51
07:30 | 3033 | 1631.85 | 896 | 0 | 51 | 758.575 | 40 | 2688.5 | 68.025 | 58 | 775.2 | 0 | 0 | 14 | 48
08:00 | 2941 | 1617.5 | 872 | 0 | 50 | 765.7 | 40 | 2783 | 97.82 | 83 | 1056.2 | 0 | 0 | 7 | 45
08:30 | 2917 | 1600 | 871.5 | 0 | 53 | 761.945 | 40 | 2781.5 | 130.005 | 99 | 1013.2 | 0 | 0 | 4 | 37.5
09:00 | 2893 | 1582.5 | 871 | 0 | 56 | 758.19 | 40 | 2780 | 162.19 | 115 | 970.2 | 0 | 0 | 1 | 30
09:30 | 2840.5 | 1592.25 | 893.5 | 0 | 58 | 760.14 | 40 | 2771 | 187.01 | 129.5 | 872.7 | 0 | 0 | 0.5 | 15
10:00 | 2788 | 1602 | 916 | 0 | 60 | 762.09 | 40 | 2762 | 211.83 | 144 | 775.2 | 0 | 0 | 0 | 0
10:30 | 2787.5 | 1543 | 916.5 | 0 | 63 | 758.42 | 43 | 2762.5 | 230.525 | 150 | 721.2 | 0 | 0 | 0 | 15.5
11:00 | 2787 | 1484 | 917 | 0 | 66 | 754.75 | 46 | 2763 | 249.22 | 156 | 667.2 | 0 | 0 | 0 | 31
11:30 | 2814.5 | 1481.25 | 917 | 0 | 64 | 755.905 | 46 | 2771 | 304.855 | 186.5 | 716.7 | 0 | 0 | 1.5 | 30.5
12:00 | 2842 | 1478.5 | 917 | 0 | 62 | 757.06 | 46 | 2779 | 360.49 | 217 | 766.2 | 0 | 0 | 3 | 30
12:30 | 2888 | 1551 | 917.5 | 0 | 67 | 758.935 | 46 | 2785 | 371.055 | 226.5 | 833.7 | 0 | 0 | 4 | 15
13:00 | 2934 | 1623.5 | 918 | 0 | 72 | 760.81 | 46 | 2791 | 381.62 | 236 | 901.2 | 0 | 0 | 5 | 0
13:30 | 2938 | 1498 | 918 | 0 | 74 | 760.905 | 46 | 2655.5 | 415.135 | 210.5 | 785.2 | 0 | 0 | 16 | 0
14:00 | 2942 | 1372.5 | 918 | 0 | 76 | 761 | 46 | 2520 | 448.65 | 185 | 669.2 | 0 | 0 | 27 | 0
14:30 | 3025.5 | 1459 | 918 | 0 | 76 | 761.5 | 46 | 2557.5 | 419.705 | 187.5 | 639.2 | 0 | 0 | 19.5 | 14
15:00 | 3109 | 1545.5 | 918 | 0 | 76 | 762 | 46 | 2595 | 390.76 | 190 | 609.2 | 0 | 0 | 12 | 28
15:30 | 3081 | 1556.5 | 918 | 0 | 71 | 761.5 | 46 | 2682.5 | 326.89 | 190 | 611.2 | 0 | 0 | 14.5 | 27
16:00 | 3053 | 1567.5 | 918 | 0 | 66 | 761 | 46 | 2770 | 263.02 | 190 | 613.2 | 0 | 0 | 17 | 26
16:30 | 3060.5 | 1568 | 917.5 | 0 | 62 | 758.5 | 46 | 2769 | 177.42 | 206.5 | 705.6 | 0 | 0 | 14.5 | 26
17:00 | 3068 | 1568.5 | 917 | 0 | 58 | 756 | 46 | 2768 | 91.82 | 223 | 798 | 0 | 0 | 12 | 26
17:30 | 3036.5 | 1498.5 | 917 | 0 | 65 | 755.5 | 46 | 2768 | 46.41 | 293 | 1185.5 | 0 | 0 | 14.5 | 13
18:00 | 3005 | 1428.5 | 917 | 0 | 72 | 755 | 46 | 2768 | 1 | 363 | 1573 | 0 | 0 | 17 | 0
18:30 | 3035 | 1435 | 894.5 | 0 | 75 | 754 | 46 | 2780 | 0.5 | 439.5 | 1912 | 0 | 0 | 22 | 33
19:00 | 3065 | 1441.5 | 872 | 0 | 78 | 753 | 46 | 2792 | 0 | 516 | 2251 | 0 | 0 | 27 | 66
19:30 | 3059 | 1468.5 | 874 | 0 | 74 | 753 | 46 | 2789 | 0 | 470 | 2195 | 0 | 0 | 26 | 53
20:00 | 3064 | 1468.5 | 873 | 0 | 78 | 752 | 46 | 2789 | 0 | 464 | 2041 | 0 | 0 | 24 | 30
20:30 | 3077.5 | 1513.5 | 897 | 0 | 73 | 754 | 46 | 2789.5 | 0 | 449 | 1835 | 0 | 0 | 19 | 15
21:00 | 3091 | 1558.5 | 921 | 0 | 68 | 756 | 46 | 2790 | 0 | 434 | 1629 | 0 | 0 | 14 | 0
21:30 | 3071 | 1543 | 920.5 | 0 | 70 | 757 | 43 | 2790 | 0 | 429.5 | 1520.5 | 0 | 0 | 14.5 | 7.5
22:00 | 3051 | 1527.5 | 920 | 0 | 72 | 758 | 40 | 2790 | 0 | 425 | 1412 | 0 | 0 | 15 | 15
22:30 | 3044.5 | 1517.5 | 920.5 | 0 | 72 | 758 | 40 | 2792 | 0 | 297 | 1230 | 0 | 0 | 14.5 | 15
23:00 | 3038 | 1507.5 | 921 | 0 | 72 | 758 | 40 | 2794 | 0 | 169 | 1048 | 0 | 0 | 14 | 15
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5967.7 | 3847.39 | 9815.09 | DAILY GENERATION CURVE
00:30 | 5810.3 | 3774.885 | 9585.185
01:00 | 5652.9 | 3702.38 | 9355.28 | 23-02-2025
01:30 | 5585.85 | 3625.795 | 9211.645
02:00 | 5518.8 | 3549.21 | 9068.01
02:30 | 5390.75 | 3509.37 | 8900.12
03:00 | 5262.7 | 3469.53 | 8732.23
03:30 | 5169.2 | 3449.325 | 8618.525
04:00 | 5075.7 | 3429.12 | 8504.82
04:30 | 5041.7 | 3407.19 | 8448.89
05:00 | 5007.7 | 3385.26 | 8392.96
05:30 | 5084.2 | 3454.32 | 8538.52
06:00 | 5160.7 | 3523.38 | 8684.08
06:30 | 5471.355 | 3728.225 | 9199.58
07:00 | 5782.01 | 3933.07 | 9715.08
07:30 | 6003.99 | 4010.16 | 10014.15
08:00 | 6225.97 | 4087.25 | 10313.22
08:30 | 6188.27 | 4082.88 | 10271.15
09:00 | 6150.57 | 4078.51 | 10229.08
09:30 | 6136.145 | 4008.955 | 10145.1
10:00 | 6121.72 | 3939.4 | 10061.12
10:30 | 6057.425 | 3918.22 | 9975.645
11:00 | 5993.13 | 3897.04 | 9890.17
11:30 | 6017.155 | 4042.055 | 10059.21
12:00 | 6041.18 | 4187.07 | 10228.25
12:30 | 6212.195 | 4236.495 | 10448.69
13:00 | 6383.21 | 4285.92 | 10669.13
13:30 | 6089.17 | 4228.07 | 10317.24
14:00 | 5795.13 | 4170.22 | 9965.35
14:30 | 5891.09 | 4218.315 | 10109.405
15:00 | 5987.05 | 4266.41 | 10253.46
15:30 | 6023.655 | 4235.435 | 10259.09
16:00 | 6060.26 | 4204.46 | 10264.72
16:30 | 6132.845 | 4152.675 | 10285.52
17:00 | 6205.43 | 4100.89 | 10306.32
17:30 | 6474.215 | 4151.695 | 10625.91
18:00 | 6743 | 4202.5 | 10945.5
18:30 | 7055.5 | 4338 | 11393.5
19:00 | 7368 | 4473.5 | 11841.5
19:30 | 7361 | 4393.5 | 11754.5
20:00 | 7240 | 4359.5 | 11599.5
20:30 | 7104 | 4349.5 | 11453.5 |  | Executive Engineer
21:00 | 6968 | 4339.5 | 11307.5 |  | Network Operation Division
21:30 | 6842 | 4317 | 11159
22:00 | 6716 | 4294.5 | 11010.5
22:30 | 6537 | 4149 | 10686
23:00 | 6358 | 4003.5 | 10361.5

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 04:00 | 375 | 12:00 | Payra | 420 | 03:00 | 407 | 12:00
Ashuganj | 408 | 4:00 | 378 | 12:00 | Rahanpur | 415 | 10:00 | 404 | 13:00
Bhulta | 404 | 04:00 | 380 | 12:00 | Rampal | 406 | 05:00 | 383 | 12:00
Bibiana | 400 | 07:00 | 386 | 17:00
BIPTC | 401 | 06:00 | 394 | 13:00
Bogura | 417 | 10:00 | 400 | 13:00
Gopalganj | 408 | 04:00 | 390 | 12:00
Kaliakoir | 379 | 04:00 | 357 | 12:00
Madunaghat | 402 | 05:00 | 393 | 12:00
Meghnaghat | 396 | 05:00 | 374 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 06:00 | 217 | 12:00 | Keranigonj | 231 | 04:00 | 215 | 12:00
AKSML | 234 | 19:00 | 221 | 12:00 | Khulna(S) | 236 | 03:00 | 223 | 12:00
Aminbazar | 232 | 06:00 | 218 | 11:00 | Madunaghat | 234 | 10:00 | 223 | 12:00
Ashuganj | 239 | 05:00 | 229 | 11:00 | Madunaghat-400 | 232 | 19:00 | 224 | 12:00
Ashuganj-400 | 239 | 05:00 | 229 | 11:00 | Maniknagar | 232 | 04:00 | 221 | 15:00
Baghabari | 238 | 01:00 | 231 | 11:00 | Meghnaghat | 240 | 04:00 | 225 | 12:00
Barapukuria | 232 | 10:00 | 214 | 07:00 | Meghnaghat-400 | 235 | 05:00 | 220 | 12:00
Barapukuria-230 | 232 | 10:00 | 214 | 07:00 | Mirsorai | 233 | 19:00 | 221 | 15:00
Barishal | 241 | 04:00 | 233 | 12:00 | Rajshahi | 238 | 05:00 | 228 | 16:00
Bheramara | 237 | 04:00 | 227 | 12:00 | Rampal | 233 | 03:00 | 218 | 12:00
Bhulta | 235 | 04:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 19:00 | 224 | 01:00 | Rampura | 235 | 04:00 | 219 | 12:00
BIPTC | 240 | 04:00 | 227 | 15:00 | Shikalbaha | 233 | 19:00 | 222 | 12:00
Bogura | 241 | 10:00 | 232 | 08:00 | Shyampur | 232 | 03:00 | 217 | 12:00
Bogura-400 | 240 | 10:00 | 230 | 08:00 | Siddhirganj | 234 | 02:00 | 222 | 12:00
Borhanuddin | 245 | 05:00 | 237 | 12:00 | Sirajgonj | 243 | 00:00 | 238 | 12:00
BSRM | 232 | 19:00 | 220 | 12:00 | Sreepur | 239 | 05:00 | 229 | 15:00
Cumilla(N) | 230 | 05:00 | 220 | 12:00 | Tongi | 234 | 04:00 | 217 | 12:00
Faridpur | 242 | 04:00 | 229 | 12:00
Fenchuganj | 235 | 23:00 | 229 | 01:00
Ghorashal | 240 | 00:00 | 230 | 15:00
Ghorashal-230 | 235 | 05:00 | 222 | 12:00
Gopalganj | 240 | 04:00 | 230 | 11:00
GPH | 233 | 19:00 | 221 | 12:00
Haripur | 234 | 03:00 | 220 | 12:00
Hasnabad | 232 | 04:00 | 217 | 12:00
Hathazari | 234 | 19:00 | 224 | 12:00
Ishurdi | 240 | 03:00 | 229 | 12:00
Jhenaidah | 236 | 02:00 | 221 | 13:00
Kaliakoir | 233 | 04:00 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 02:00 | 123 | 12:00 | Magura | 138 | 03:00 | 127 | 12:00
Agargaon | 135 | 05:00 | 124 | 12:00 | Mahasthangarh | 137 | 10:00 | 128 | 08:00
Agrabad | 133 | 19:00 | 125 | 12:00 | Manikganj | 137 | 13:00 | 126 | 17:00
AKS | 130 | 00:00 | 125 | 14:00 | Maniknagar | 133 | 04:00 | 123 | 12:00
Aminbazar | 136 | 03:00 | 126 | 12:00 | Matarbari | 119 | 10:00 | 115 | 12:00
Amnura | 141 | 22:00 | 131 | 12:00 | Matuail | 134 | 04:00 | 125 | 12:00
Ashuganj | 140 | 08:00 | 135 | 16:00 | Millgate | 137 | 05:00 | 124 | 12:00
Bagerhat | 134 | 03:00 | 124 | 13:00 | Mirpur | 134 | 07:00 | 125 | 12:00
Bajitpur | 134 | 04:00 | 130 | 18:00 | Mirzapur | 135 | 13:00 | 125 | 16:00
Bakulia | 134 | 19:00 | 121 | 13:00 | Mithapukur | 142 | 10:00 | 125 | 08:00
Banani | 134 | 04:00 | 124 | 12:00 | MI_Cement | 135 | 00:00 | 125 | 12:00
Bangabhaban | 133 | 03:00 | 123 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 139 | 10:00 | 127 | 07:00 | Mogbazar | 136 | 03:00 | 125 | 11:00
Barguna | 137 | 19:00 | 130 | 12:00 | Mongla | 136 | 05:00 | 123 | 12:00
Barishal | 136 | 20:00 | 129 | 12:00 | Motijheel | 133 | 03:00 | 123 | 12:00
Barishal-230 | 136 | 20:00 | 129 | 12:00 | Muktagacha | 135 | 10:00 | 116 | 18:30
Baroaulia | 134 | 19:00 | 127 | 12:00 | Munshiganj | 134 | 07:00 | 125 | 12:00
Baroirhat | 129 | 19:00 | 122 | 10:00 | Muradnagar | 132 | 02:00 | 125 | 12:00
Bashundhara | 134 | 00:00 | 123 | 12:00 | Mymensingh | 135 | 10:00 | 115 | 18:30
BashundharaCement | 133 | 02:00 | 124 | 12:00 | Naogaon | 135 | 09:00 | 129 | 08:00
Beanibazar | 134 | 04:00 | 126 | 12:00 | Narail | 136 | 03:00 | 126 | 13:00
Benapole | 133 | 03:00 | 122 | 13:00 | Narinda | 133 | 04:00 | 123 | 12:00
Bhaluka | 128 | 12:00 | 122 | 08:00 | Narshingdi | 132 | 04:00 | 121 | 12:00
Bhandaria | 133 | 05:00 | 125 | 13:00 | Natore | 136 | 00:00 | 132 | 16:00
Bhangura | 136 | 00:00 | 132 | 13:00 | Nawabganj | 136 | 22:00 | 125 | 12:00
Bheramara | 138 | 00:00 | 133 | 13:00 | Netrakona | 129 | 12:00 | 118 | 08:00
Bheramara(GK) | 138 | 02:00 | 133 | 12:00 | New | 137 | 03:00 | 125 | 12:00
Bhulta | 129 | 12:00 | 120 | 15:00 | Niamatpur | 139 | 04:00 | 135 | 12:00
Bog-Sherpur | 136 | 10:00 | 129 | 08:00 | Noapara | 139 | 05:00 | 124 | 12:00
Bogura | 137 | 22:00 | 132 | 07:00 | Pabna | 139 | 04:00 | 133 | 12:00
Bogura-230 | 138 | 10:00 | 132 | 08:00 | Palashbari | 136 | 10:00 | 120 | 08:00
Brahmanbaria | 136 | 05:00 | 127 | 12:00 | Panchagarh | 143 | 10:00 | 122 | 12:00
Cantonment | 134 | 03:00 | 124 | 12:00 | Patuakhali | 138 | 19:00 | 130 | 12:00
Chandpur | 137 | 19:00 | 122 | 01:00 | Payra | 138 | 08:00 | 133 | 12:00
Chandraghona | 135 | 19:00 | 129 | 11:00 | PHP | 129 | 19:00 | 120 | 13:00
Chapai | 137 | 01:00 | 134 | 08:00 | Postogola | 139 | 03:00 | 127 | 12:00
Charsaidpur | 134 | 03:00 | 125 | 12:00 | Purbachal | 135 | 03:00 | 123 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 130 | 19:00 | 122 | 11:00 | Purbasadipur | 139 | 10:00 | 119 | 12:00
Chhatak | 135 | 14:00 | 125 | 12:00 | Rahanpur | 141 | 03:00 | 136 | 18:00
Chowmuhani | 128 | 18:30 | 120 | 09:00 | Rahanpur-400 | 141 | 10:00 | 136 | 12:00
Chuadanga | 136 | 01:00 | 125 | 12:00 | Rahim | 134 | 05:00 | 124 | 12:00
Coxsbazar | 120 | 02:00 | 115 | 12:00 | Rajbari | 134 | 02:00 | 127 | 12:00
Cumilla(N) | 135 | 22:00 | 127 | 11:00 | Rajendrapur | 134 | 05:00 | 123 | 17:00
Cumilla(S) | 133 | 19:00 | 125 | 12:00 | Rajshahi | 137 | 00:00 | 133 | 13:00
Daudkandi | 131 | 02:00 | 124 | 12:00 | Rajshahi-230 | 139 | 04:00 | 127 | 13:00
Dhaka | 134 | 03:00 | 124 | 12:00 | Ramganj | 133 | 19:30 | 120 | 01:00
Dhamrai | 135 | 03:00 | 125 | 12:00 | Rampur | 133 | 19:00 | 124 | 12:00
Dhanmondi | 135 | 03:00 | 124.5 | 12:00 | Rampura | 134 | 02:00 | 123 | 12:00
Dohazari | 129 | 18:30 | 122 | 12:00 | Rangamati | 133 | 19:00 | 127 | 12:00
Faridpur | 135 | 03:00 | 129 | 12:00 | Rangpur | 140 | 10:00 | 123 | 07:00
Fatullah | 136 | 04:00 | 126 | 12:00 | Ruppur | 139 | 04:00 | 134 | 17:00
Fenchuganj | 136 | 04:00 | 132 | 11:00 | Saidpur | 140 | 10:00 | 125 | 08:00
Feni | 129 | 22:00 | 122 | 11:00 | Satkhira | 137 | 04:00 | 124 | 12:00
Ghatail | 130 | 10:00 | 120 | 18:30 | Satmasjid | 135 | 05:00 | 124 | 12:00
Ghorashal | 140 | 04:00 | 134 | 15:00 | Savar | 134 | 05:00 | 122 | 13:00
Goalpara | 138 | 03:00 | 127 | 12:00 | SevenRings | 140 | 04:00 | 133 | 12:00
Gollamari | 137 | 04:00 | 127 | 12:00 | ShahCement | 134 | 03:00 | 125 | 12:00
Gopalganj | 137 | 04:00 | 129 | 12:00 | Shahjadpur | 140 | 00:00 | 135 | 10:00
Gopalganj-400 | 139 | 02:00 | 132 | 12:00 | Shahjibazar | 137 | 06:00 | 131 | 12:00
Gulshan | 134 | 03:00 | 123 | 12:00 | Shahmirpur | 134 | 19:00 | 126 | 12:00
Halishahar | 135 | 19:00 | 125 | 12:00 | Shariatpur | 138 | 05:00 | 130 | 12:00
Haripur | 134 | 06:00 | 124 | 12:00 | Sherpur | 134 | 10:00 | 112 | 18:30
HaripurSBU | 134 | 06:00 | 124 | 12:00 | Shikalbaha | 123 | 19:00 | 116 | 12:00
Hasnabad | 136 | 01:00 | 127 | 12:00 | Shikalbaha-230 | 134 | 08:00 | 127 | 11:00
Hathazari | 137 | 19:00 | 130 | 12:00 | Shitalakhya | 135 | 00:00 | 125 | 12:00
Ishurdi | 141 | 05:00 | 134 | 13:00 | Sholosohor | 134 | 19:00 | 127 | 12:00
Jaldhaka | 136 | 10:00 | 120 | 12:00 | Shyampur | 136 | 00:00 | 126 | 12:00
Jamalpur | 135 | 10:00 | 116 | 18:30 | Shyampur-230 | 135 | 04:00 | 126 | 12:00
Jashore | 136 | 03:00 | 123 | 13:00 | Siddhirganj | 134 | 04:00 | 125 | 12:00
Jhenaidah | 138 | 04:00 | 128 | 12:00 | Sirajganj | 136 | 03:00 | 128 | 08:00
Jhenaidah-230 | 138 | 02:00 | 128 | 13:00 | Sonargaon | 133 | 02:00 | 122 | 12:00
Joydebpur | 135 | 06:00 | 127 | 16:00 | Sreemongol | 136 | 04:00 | 131 | 16:00
Joypurhat | 134 | 10:00 | 126 | 08:00 | Sreepur | 129 | 03:00 | 123 | 16:00
Juldah | 133 | 18:00 | 126 | 12:00 | Srinagar | 137 | 23:00 | 125 | 12:00
Kabirpur | 139 | 13:00 | 121 | 12:00 | SSM | 138 | 18:30 | 130 | 12:00
Kachua | 136 | 19:00 | 125 | 01:00 | Sunamganj | 134 | 14:00 | 124 | 12:00
Kaliakoir | 139 | 13:00 | 126 | 12:00 | Sylhet | 134 | 04:00 | 128 | 12:00
Kallyanpur | 134 | 22:00 | 123 | 11:00 | Sylhet-132 | 135 | 14:00 | 127 | 12:00
Kalurghat | 135 | 19:00 | 128 | 12:00 | Tangail | 132 | 13:00 | 121 | 16:00
Kamrangirchar | 137 | 22:00 | 119 | 12:00 | Thakurgaon | 142 | 10:00 | 119 | 12:00
Kaptai | 136 | 19:00 | 131 | 12:00 | TK | 134 | 19:00 | 127 | 12:00
Kazla | 133 | 05:00 | 123 | 12:00 | Tongi | 137 | 03:00 | 126 | 12:00
Keranigonj | 136 | 23:00 | 125 | 12:00 | Ullahpara | 137 | 01:00 | 130 | 08:00
Khagrachori | 133 | 19:00 | 127 | 12:00 | Ullon | 134 | 03:00 | 124 | 12:00
Khulna | 135 | 04:00 | 125 | 12:00 | Uttara | 135 | 04:00 | 125 | 15:00
Khulna(S) | 137 | 03:00 | 127 | 13:00 | UttaraNew | 137 | 04:00 | 124 | 12:00
Khulshi | 132 | 19:00 | 124 | 12:00 | Zigatola | 137 | 20:00 | 125 | 12:00
Kishoreganj | 132 | 02:00 | 126 | 08:00
Kodda | 134 | 07:00 | 124 | 15:00
KSRM | 133 | 08:00 | 128 | 15:00
Kulaura | 137 | 07:00 | 131 | 12:00
Kurigram | 137 | 10:00 | 118 | 07:00
Kushtia | 138 | 02:00 | 131 | 13:00
Lalbag | 136 | 05:00 | 125 | 12:00
Lalmonirhat | 136 | 05::00 | 122 | 08:00
Madanganj | 133 | 02:00 | 124 | 12:00
Madaripur | 136 | 00:00 | 132 | 12:00
Madartek | 134 | 03:00 | 123 | 12:00
Madunaghat | 134 | 19:00 | 128 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division