## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-02-2025 | during | 25-02-2025 | during | 25-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 250 | 50 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 409 | 407 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 350 | 450 | 450 | 380 | 380 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 82 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 17 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 17 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 16 | 19 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 21 | 21 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 18 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 0 | 0 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 114 | 124 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 35 | 35 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 72 | 162 | 162 | 35 | 35 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1712 | 2121 | 5072.51 | 4840.51 | 2334.27 | 2302.27
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 220 | 219 | 219 | 219 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 4 | 78 | 64 | 72 | 64 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 51 | 85 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 13 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 26 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 4.04 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 52 | 300 | 300 | 50 | 50 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 17 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 85 | 102 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 88 | 100 | 100 | 50 | 50 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 54 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 18 | 19 | 0 | 28 | 0 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 577 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2590 | 2870 | 3559.9 | 3587.86 | 3144.9 | 3172.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 185 | 197 | 221 | 221 | 185 | 185 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 305 | 270 | 356.56 | 356.56 | 285 | 285 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 5 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 58 | 137 | 150 | 150 | 70 | 70 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 25 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 72 | 158 | 200 | 200 | 100 | 100 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 78 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 15 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 5 | 9 | 9 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 68 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1209 | 1379 | 1999.53 | 1931.53 | 1505.2 | 1437.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-02-2025 | during | 25-02-2025 | during | 25-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 11 | 210 | 210 | 21 | 21 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.1 | 0 | 1.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 200 | 200 | 9 | 9 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 58 | 115 | 115 | 58 | 58 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.64 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 135.64 | 90 | 650.6 | 601.5 | 213.6 | 164.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 39 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 33 | 35 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 64 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1014 | 999 | 1097.5 | 1097.5 | 1059 | 1059
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 25 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 158.5 | 158.5 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 142 | 109 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 80.19 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1146.19 | 1014 | 2855.6 | 2773.6 | 1304.02 | 1222.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 120 | 212 | 330 | 330 | 330 | 330 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 30 | 96 | 48 | 110 | 48 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 132 | 130 | 136 | 136 | 136 | 136 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 52 | 54 | 150 | 150 | 17 | 17 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1488.54 | 1648 | 1824.12 | 1885.12 | 1691.12 | 1752.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 37 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 131 | 133 | 220 | 220 | 130 | 130 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 370 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 32 | 32 | 32 | 32 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 8 | 8 | 8 | 8 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 49 | 90 | 90 | 90 | 90 | 90 | One Engine ( No :03) under 12K RH maintanance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 105 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 5.88 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 757.36 | 755 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 68.17 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1630.91 | 1693.5 | 2245.64 | 2085.04 | 1893.86 | 1733.26
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 63 | 60 | 63 | 63 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 93 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 190 | 0 | 101 | 0 | 101 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 420.8 | 259 | 461.6 | 325 | 429.62 | 293.02
System Total |  |  |  |  | 29204.66 | 28470.742 | 11347.08 | 12073.5 | 19767 | 19127.66 | 13575.59 | 13136.25
Forecast Scenario (25-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10012 |  | 0 |  | 10010
|  |  |  | 1:00 | 9362 |  | 0 |  | 9360
|  |  |  | 2:00 | 8955 |  | 0 |  | 8950
|  |  |  | 3:00 | 8687 |  | 0 |  | 8680
|  |  |  | 4:00 | 8585 |  | 0 |  | 8420
|  |  |  | 5:00 | 8457 |  | 0 |  | 8350
|  |  |  | 6:00 | 8737 |  | 0 |  | 8650
|  |  |  | 7:00 | 9782 |  | 0 |  | 9650
|  |  |  | 8:00 | 10841 |  | 0 |  | 10350
|  |  |  | 9:00 | 11111 |  | 0 |  | 10750
|  |  |  | 10:00 | 11111 |  | 0 |  | 10850
|  |  |  | 11:00 | 11264 |  | 0 |  | 10950
|  |  |  | 12:00 | 11725 |  | 0 |  | 11480
|  |  |  | 13:00 | 12069 |  | 0 |  | 11620
|  |  |  | 14:00 | 11721 |  | 0 |  | 11480
|  |  |  | 15:00 | 11379 |  | 0 |  | 11250
|  |  |  | 16:00 | 11098 |  | 0 |  | 11000
|  |  |  | 17:00 | 10875 |  | 0 |  | 10870
|  |  |  | 18:00 | 11760 |  | 0 |  | 11400
|  |  |  | 18:30 | 12000 |  | 0 |  | 12000
|  |  |  | 19:00 | 12312 |  | 0 |  | 12100
|  |  |  | 19:30 | 12193 |  | 0 |  | 12000
|  |  |  | 20:00 | 11861 |  | 0 |  | 11800
|  |  |  | 21:00 | 11691 |  | 0 |  | 11500
|  |  |  | 22:00 | 11426 |  | 0 |  | 11200
|  |  |  | 23:00 | 10840 |  | 0 |  | 10600
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 11480.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12312.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 255.661 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:06 hrs on 25-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-02-2025 | [28 empty] | Date: | 24-02-2025 | [28 empty] | Date: | 24-02-2025 | [28 empty] | Date: | 24-02-2025 | [28 empty] | Date: | 24-02-2025 | [18 empty] | Date: | 24-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 350 | 0 | 0 | 0 | 17 | 8 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 16 | 0 | 0 | 6 | 0 | 0 | 0 | 88 | 0 | 0 | 40 | 110 | 31 | 575 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 167 | 0 | 0 | 270 | 10 | 182 | 36 | 69 | 50 | 68 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 290 | 320 | 0 | 33 | 30 | 40 | 2 | 163 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 17 | 0 | 0 | 6 | 6026 | 921 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 70 | 4 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 2.5 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 132 | 220 | 0 | 35.38 | 622 | 0 | 3964.88 | 9990.88 | 89.56
01:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 74 | 29 | 575 | 0 | 0 | 0 | 0 | 51 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 167 | 0 | 0 | 270 | 10 | 182 | 36 | 0 | 50 | 0 | 0 | 17 | 0 | 64 | 0 | 0 | 0 | 270 | 320 | 0 | 33 | 30 | 40 | 2 | 163 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 18 | 0 | 0 | 6 | 5582 | 920 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 4 | 8.3 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 128 | 220 | 0 | 50 | 622 | 0 | 3812.8 | 9394.8 | 89.55
02:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 576 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 167 | 0 | 0 | 320 | 10 | 190 | 33 | 0 | 50 | 0 | 0 | 16 | 0 | 58 | 0 | 0 | 0 | 280 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 5181 | 921 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 8.3 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 414 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 41 | 560 | 0 | 3640.8 | 8821.8 | 89.55
03:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 525 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 959 | 0 | 51 | 0 | 167 | 0 | 0 | 305 | 10 | 183 | 33 | 0 | 51 | 0 | 0 | 16 | 0 | 62 | 0 | 0 | 0 | 290 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 5086 | 921 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613 | 0 | 0 | 0 | 0 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 414 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 41 | 500 | 0 | 3523.8 | 8609.8 | 89.54
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 506 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 905 | 0 | 51 | 0 | 167 | 0 | 0 | 305 | 10 | 185 | 33 | 0 | 51 | 0 | 0 | 16 | 0 | 60 | 0 | 0 | 0 | 285 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 5014 | 921 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 414 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 132 | 220 | 0 | 72 | 450 | 0 | 3391.8 | 8405.8 | 89.54
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 505 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 167 | 0 | 0 | 310 | 10 | 190 | 33 | 0 | 51 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 5011 | 922 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 350 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 132 | 220 | 0 | 72.54 | 450 | 0 | 3326.34 | 8337.34 | 89.53
06:00 | 0 | 34 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 30 | 505 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 167 | 0 | 0 | 305 | 10 | 184 | 33 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 310 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 17 | 9 | 21 | 0 | 0 | 0 | 5091 | 922 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 0 | 0 | 0 | 1 | 0 | 8.3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 350 | 0 | 0 | 2.5 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 132 | 220 | 0 | 72.82 | 470 | 17 | 3533.62 | 8624.62 | 89.53
07:00 | 0 | 52 | 0 | 0 | 0 | 231 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 33 | 32 | 95 | 0 | 0 | 35 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 2 | 0 | 14 | 22 | 0 | 0 | 22 | 80 | 0 | 0 | 13 | 0 | 0 | 0 | 76 | 24 | 0 | 40 | 33 | 28 | 544 | 0 | 0 | 0 | 0 | 63 | 225 | 0 | 0 | 0 | 967 | 2 | 51 | 27 | 167 | 0 | 0 | 320 | 10 | 198 | 33 | 32 | 50 | 73 | 0 | 17 | 0 | 60 | 0 | 5 | 0 | 280 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 22 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 20 | 0 | 2.77 | 2 | 5877.77 | 922 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 0 | 0 | 661 | 0 | 0 | 0 | 45 | 0 | 8.3 | 35 | 0 | 0 | 4 | 0 | 2.77 | 0 | 0 | 0 | 0 | 141 | 0 | 300 | 0 | 0.24 | 5.5 | 0 | 64 | 54 | 1 | 0 | 0 | 0 | 0.1 | 6 | 0.03 | 32 | 307 | 6 | 132 | 220 | 0 | 73 | 510 | 17 | 3701.8 | 9579.57 | 89.52
08:00 | 0 | 52 | 0 | 0 | 0 | 222 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 53 | 32 | 95 | 0 | 0 | 35 | 22 | 0 | 350 | 0 | 0 | 0 | 17 | 22 | 335 | 0 | 0 | 8 | 0 | 16 | 22 | 0 | 0 | 35 | 83 | 0 | 0 | 17 | 0 | 0 | 17 | 76 | 24 | 0 | 40 | 99 | 4 | 575 | 17 | 0 | 2 | 0 | 105 | 225 | 0 | 0 | 0 | 1110 | 7 | 51 | 75 | 167 | 0 | 0 | 270 | 10 | 183 | 33 | 54 | 50 | 115 | 0 | 17 | 0 | 52 | 1 | 22 | 0 | 285 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 0 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 10 | 1 | 15.23 | 0 | 6275.23 | 875 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.02 | 0 | 0 | 749.89 | 0 | 0 | 0 | 50 | 0 | 8.3 | 50 | 0 | 0 | 27 | 0 | 17.55 | 0 | 0 | 0 | 0 | 143 | 0 | 350 | 0 | 1.41 | 5.5 | 0 | 64 | 81 | 9 | 0 | 0 | 0 | 1.4 | 36 | 0.14 | 32 | 307 | 5 | 100 | 180 | 0 | 73 | 590 | 54 | 3985.21 | 10260.44 | 89.52
09:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 78 | 32 | 45 | 0 | 17 | 35 | 22 | 0 | 350 | 0 | 0 | 0 | 17 | 22 | 335 | 0 | 0 | 17 | 0 | 16 | 22 | 0 | 0 | 35 | 83 | 3 | 0 | 7 | 0 | 0 | 17 | 76 | 12 | 0 | 40 | 107 | 2 | 575 | 17 | 0 | 6 | 3 | 105 | 224 | 0 | 0 | 0 | 1100 | 13 | 51 | 90 | 177 | 0 | 0 | 270 | 11 | 184 | 33 | 106 | 50 | 155 | 0 | 11 | 0 | 58 | 8 | 40 | 0 | 285 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 15 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 57 | 9 | 5 | 1 | 29.48 | 0 | 6442.48 | 876 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.35 | 0 | 0 | 757.27 | 0 | 0 | 0 | 50 | 0 | 8.3 | 35 | 0 | 0 | 59 | 0 | 36.89 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 2.99 | 5.5 | 0 | 64 | 93 | 17 | 0 | 0 | 0 | 2.7 | 91 | 0.29 | 32 | 307 | 4 | 132 | 220 | 0 | 72 | 600 | 35 | 4188.29 | 10630.77 | 89.51
10:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 96 | 32 | 15 | 0 | 17 | 35 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 10 | 335 | 0 | 0 | 25 | 17 | 16 | 21 | 0 | 0 | 35 | 45 | 12 | 0 | 2 | 0 | 0 | 17 | 76 | 12 | 0 | 46 | 85 | 2 | 575 | 17 | 0 | 6 | 8 | 105 | 224 | 0 | 0 | 0 | 1105 | 17 | 43 | 50 | 175 | 0 | 0 | 265 | 18 | 184 | 30 | 68 | 50 | 68 | 2 | 11 | 0 | 56 | 8 | 51 | 0 | 295 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 56 | 9 | 5 | 2 | 40.57 | 0 | 6204.57 | 923 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.39 | 0 | 0 | 753.04 | 0 | 0 | 0 | 50 | 0 | 8.3 | 35 | 0 | 0 | 86 | 0 | 53.66 | 0 | 0 | 0 | 0 | 138 | 0 | 350 | 0 | 4.57 | 2.5 | 0 | 63 | 95 | 24 | 25 | 0 | 0 | 2.4 | 153 | 0.41 | 16 | 307 | 4 | 132 | 220 | 0 | 73 | 600 | 17 | 4343.27 | 10547.84 | 89.51
11:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 407 | 0 | 0 | 17 | 0 | 0 | 96 | 32 | 15 | 0 | 17 | 35 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 30 | 17 | 16 | 21 | 0 | 0 | 35 | 45 | 12 | 0 | 20 | 0 | 0 | 17 | 88 | 12 | 0 | 46 | 85 | 2 | 576 | 17 | 0 | 6 | 8 | 105 | 223 | 0 | 0 | 0 | 1150 | 19 | 43 | 50 | 185 | 0 | 0 | 270 | 25 | 188 | 30 | 68 | 50 | 68 | 9 | 11 | 0 | 62 | 8 | 62 | 0 | 295 | 320 | 0 | 33 | 30 | 40 | 2 | 120 | 20 | 0 | 65 | 30 | 0 | 18 | 0 | 0 | 56 | 9 | 5 | 2 | 47.04 | 0 | 6376.04 | 924 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.45 | 0 | 0 | 757.23 | 0 | 0 | 0 | 50 | 0 | 16 | 35 | 0 | 1 | 102 | 0 | 63.42 | 0 | 0 | 0 | 0 | 134 | 0 | 350 | 0 | 5.24 | 2.5 | 0 | 63 | 95 | 30 | 33 | 0 | 0 | 4.7 | 179 | 0.5 | 16 | 307 | 4 | 132 | 220 | 0 | 72.5 | 610 | 17 | 4442.54 | 10818.58 | 89.5
12:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 409 | 0 | 0 | 17 | 0 | 0 | 114 | 32 | 15 | 0 | 17 | 35 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 33 | 17 | 16 | 21 | 0 | 0 | 35 | 45 | 12 | 0 | 18 | 51 | 4 | 17 | 88 | 12 | 0 | 46 | 85 | 2 | 576 | 17 | 0 | 6 | 8 | 105 | 220 | 0 | 0 | 0 | 1224 | 19 | 43 | 58 | 185 | 0 | 0 | 305 | 28 | 185 | 30 | 68 | 50 | 72 | 9 | 11 | 0 | 66 | 8 | 66 | 25 | 290 | 320 | 0 | 33 | 30 | 40 | 2 | 163 | 24 | 0 | 64 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 5 | 2 | 50.64 | 10 | 6660.64 | 924 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.19 | 0 | 0 | 757.36 | 0 | 0 | 0 | 50 | 0 | 49 | 35 | 0 | 8 | 110 | 0 | 68.17 | 0 | 0 | 0 | 0 | 131 | 0 | 414 | 0 | 5.88 | 2.5 | 0 | 63 | 95 | 33 | 34 | 0 | 0 | 5.8 | 190 | 0.54 | 30 | 307 | 5 | 132 | 220 | 0 | 120 | 622 | 52 | 4686.44 | 11347.08 | 89.5
13:00 | 0 | 52 | 0 | 0 | 0 | 232 | 0 | 0 | 410 | 0 | 0 | 17 | 0 | 0 | 114 | 0 | 75 | 0 | 17 | 35 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 17 | 325 | 0 | 0 | 33 | 17 | 16 | 21 | 0 | 0 | 35 | 45 | 11 | 0 | 13 | 68 | 44 | 0 | 88 | 24 | 0 | 46 | 99 | 2 | 576 | 0 | 0 | 5 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 43 | 95 | 185 | 0 | 0 | 305 | 27 | 185 | 30 | 92 | 50 | 114 | 0 | 11 | 0 | 66 | 0 | 66 | 31 | 285 | 320 | 0 | 35 | 30 | 40 | 2 | 163 | 24 | 0 | 64 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 5 | 2 | 51.48 | 12 | 6789.48 | 924 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3 | 0 | 0 | 758.24 | 0 | 0 | 0 | 50 | 0 | 49 | 90 | 10 | 8 | 110 | 0 | 64.82 | 0 | 0 | 0 | 0 | 135 | 0 | 414 | 0 | 5.36 | 2.5 | 0 | 63 | 55 | 32 | 34 | 0 | 0 | 4.5 | 177 | 0.52 | 48 | 307 | 6 | 120 | 220 | 0 | 150 | 622 | 17 | 4700.24 | 11489.72 | 89.49
14:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 359 | 0 | 0 | 17 | 0 | 0 | 113 | 0 | 75 | 0 | 17 | 35 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 31 | 17 | 19 | 21 | 0 | 0 | 35 | 45 | 0 | 0 | 12 | 73 | 48 | 0 | 75 | 10 | 0 | 86 | 110 | 8 | 505 | 0 | 0 | 0 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 16 | 43 | 107 | 184 | 0 | 0 | 305 | 29 | 184 | 29 | 115 | 50 | 155 | 0 | 11 | 0 | 68 | 0 | 58 | 39 | 295 | 320 | 0 | 35 | 30 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 5 | 2 | 46.61 | 7 | 6849.61 | 924 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.44 | 0 | 0 | 710 | 0 | 0 | 0 | 50 | 0 | 49 | 113 | 15 | 8 | 105 | 25 | 58.12 | 0 | 0 | 0 | 0 | 132 | 0 | 370 | 0 | 5.13 | 2.5 | 0 | 63 | 36 | 30 | 40 | 0 | 0 | 5.2 | 163 | 0.45 | 48 | 270 | 6 | 100 | 220 | 0 | 170 | 560 | 17 | 4493.84 | 11343.45 | 89.49
15:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 0 | 113 | 0 | 15 | 0 | 17 | 35 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 23 | 35 | 16 | 21 | 0 | 0 | 35 | 45 | 0 | 0 | 14 | 84 | 49 | 0 | 75 | 0 | 0 | 40 | 110 | 8 | 504 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 13 | 43 | 100 | 175 | 0 | 0 | 310 | 29 | 218 | 29 | 115 | 50 | 155 | 0 | 11 | 0 | 66 | 0 | 43 | 40 | 295 | 320 | 0 | 35 | 29 | 39 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 9 | 1 | 35.63 | 12 | 6737.63 | 924 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.57 | 0 | 0 | 711 | 0 | 0 | 0 | 50 | 0 | 49 | 50 | 21 | 0 | 82 | 30 | 46.67 | 0 | 0 | 0 | 0 | 132 | 0 | 370 | 0 | 4 | 2.5 | 0 | 61 | 35 | 23 | 35 | 0 | 0 | 3.9 | 118 | 0.31 | 48 | 270 | 5 | 100 | 220 | 0 | 181 | 560 | 17 | 4328.95 | 11066.58 | 89.48
16:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 399 | 0 | 0 | 17 | 0 | 0 | 120 | 0 | 15 | 0 | 17 | 35 | 25 | 0 | 420 | 0 | 0 | 0 | 5 | 17 | 280 | 0 | 0 | 15 | 35 | 19 | 14 | 0 | 0 | 35 | 52 | 0 | 0 | 10 | 82 | 48 | 0 | 50 | 0 | 0 | 40 | 34 | 2 | 576 | 0 | 0 | 0 | 0 | 51 | 218 | 0 | 0 | 0 | 1224 | 8 | 43 | 50 | 185 | 0 | 0 | 330 | 29 | 178 | 33 | 115 | 50 | 100 | 0 | 11 | 0 | 66 | 0 | 27 | 48 | 310 | 320 | 0 | 35 | 29 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 10 | 1 | 21.2 | 12 | 6577.2 | 924 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.63 | 0 | 0 | 728 | 0 | 0 | 0 | 50 | 0 | 49 | 50 | 21 | 0 | 51 | 30 | 31.97 | 0 | 0 | 0 | 0 | 133 | 0 | 370 | 0 | 2.87 | 2.5 | 0 | 60 | 35 | 8 | 35 | 0 | 0 | 2.4 | 69 | 0.16 | 48 | 307 | 5 | 100 | 220 | 0 | 181 | 560 | 17 | 4242.53 | 10819.73 | 89.48
17:00 | 0 | 52 | 0 | 0 | 0 | 230 | 0 | 0 | 410 | 0 | 0 | 17 | 0 | 0 | 120 | 0 | 15 | 0 | 17 | 72 | 25 | 0 | 350 | 0 | 0 | 0 | 35 | 18 | 280 | 0 | 0 | 5 | 35 | 19 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 9 | 83 | 48 | 0 | 50 | 0 | 0 | 40 | 34 | 8 | 577 | 0 | 0 | 0 | 0 | 51 | 219 | 0 | 0 | 0 | 1224 | 3 | 51 | 50 | 185 | 0 | 0 | 335 | 29 | 154 | 33 | 115 | 50 | 100 | 0 | 11 | 0 | 68 | 0 | 9 | 48 | 300 | 320 | 0 | 35 | 30 | 39 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 11 | 0 | 7.42 | 12 | 6493.42 | 923 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.64 | 0 | 0 | 755 | 0 | 50 | 0 | 50 | 0 | 50 | 50 | 21 | 0 | 15 | 30 | 8.84 | 0 | 0 | 0 | 0 | 134 | 0 | 340 | 0 | 0.74 | 2.5 | 0 | 60 | 35 | 4 | 35 | 0 | 0 | 0.7 | 20 | 0.07 | 80 | 307 | 4 | 100 | 220 | 0 | 216 | 560 | 17 | 4218.49 | 10711.91 | 89.47
18:00 | 0 | 57 | 0 | 0 | 0 | 230 | 0 | 0 | 410 | 0 | 0 | 21 | 0 | 0 | 120 | 40 | 95 | 4 | 17 | 72 | 25 | 0 | 350 | 0 | 0 | 0 | 35 | 18 | 280 | 0 | 0 | 0 | 35 | 19 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 14 | 85 | 48 | 2 | 55 | 53 | 0 | 40 | 62 | 11 | 576 | 35 | 0 | 5 | 3 | 63 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 71 | 185 | 0 | 0 | 310 | 7 | 173 | 33 | 115 | 50 | 103 | 0 | 15 | 17 | 72 | 25 | 0 | 42 | 310 | 320 | 0 | 35 | 30 | 39 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 11 | 0 | 0.02 | 12 | 6804.02 | 924 | 114 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 754 | 0 | 50 | 0 | 56 | 5 | 75 | 75 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 340 | 0 | 0 | 5.5 | 0 | 60 | 55 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 5 | 100 | 220 | 0 | 214 | 560 | 17 | 4360.9 | 11164.92 | 89.47
19:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 407 | 0 | 0 | 35 | 0 | 0 | 124 | 82 | 195 | 15 | 35 | 72 | 25 | 0 | 350 | 0 | 0 | 0 | 55 | 18 | 333 | 0 | 0 | 0 | 35 | 19 | 21 | 0 | 0 | 35 | 52 | 26 | 0 | 19 | 85 | 78 | 17 | 100 | 88 | 0 | 40 | 102 | 13 | 577 | 54 | 0 | 18 | 17 | 105 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 137 | 185 | 0 | 0 | 270 | 5 | 197 | 33 | 115 | 50 | 158 | 5 | 15 | 17 | 78 | 16 | 0 | 47 | 295 | 320 | 0 | 35 | 30 | 39 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 11 | 0 | 0 | 12 | 7459 | 880 | 109 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 50 | 0 | 105 | 5 | 90 | 113 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 370 | 0 | 0 | 5.5 | 0 | 60 | 93 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 7 | 130 | 220 | 0 | 212 | 622 | 54 | 4614.5 | 12073.5 | 89.46
19:30 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 407 | 0 | 0 | 35 | 0 | 0 | 124 | 82 | 195 | 0 | 35 | 72 | 25 | 0 | 300 | 0 | 0 | 0 | 55 | 18 | 330 | 0 | 0 | 0 | 35 | 19 | 21 | 0 | 0 | 35 | 52 | 18 | 0 | 19 | 85 | 78 | 17 | 100 | 50 | 0 | 40 | 110 | 13 | 577 | 17 | 0 | 18 | 17 | 105 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 140 | 185 | 0 | 0 | 270 | 5 | 208 | 33 | 115 | 50 | 100 | 9 | 17 | 0 | 76 | 16 | 0 | 39 | 300 | 320 | 0 | 35 | 30 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 58 | 9 | 12 | 0 | 0 | 12 | 7301 | 880 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 50 | 0 | 113 | 7 | 90 | 113 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 370 | 0 | 0 | 5.5 | 0 | 61 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 7 | 132 | 220 | 0 | 213 | 622 | 54 | 4606.5 | 11907.5 | 89.46
20:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 407 | 0 | 0 | 35 | 0 | 0 | 124 | 64 | 195 | 0 | 35 | 72 | 25 | 0 | 300 | 0 | 0 | 0 | 55 | 18 | 310 | 0 | 0 | 0 | 35 | 19.5 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 25 | 85 | 78 | 17 | 100 | 50 | 0 | 40 | 110 | 12 | 575 | 10 | 0 | 19 | 17 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 138 | 185 | 0 | 0 | 270 | 5 | 209 | 36 | 115 | 50 | 100 | 9 | 17 | 0 | 70 | 0 | 0 | 39 | 295 | 320 | 0 | 35 | 30 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 11 | 0 | 0 | 12 | 7218.5 | 880 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 50 | 0 | 113 | 7 | 90 | 50 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 370 | 0 | 0 | 5.5 | 0 | 59 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 7 | 132 | 220 | 0 | 213 | 622 | 54 | 4544.5 | 11763 | 89.46
21:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 406 | 0 | 0 | 35 | 0 | 0 | 109 | 64 | 45 | 0 | 17 | 72 | 25 | 0 | 320 | 0 | 0 | 0 | 35 | 18 | 300 | 0 | 0 | 0 | 35 | 20 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 22 | 49 | 78 | 0 | 100 | 50 | 0 | 40 | 110 | 11 | 576 | 0 | 0 | 0 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 185 | 0 | 0 | 315 | 5 | 196 | 36 | 115 | 50 | 100 | 9 | 17 | 0 | 72 | 0 | 0 | 39 | 305 | 320 | 0 | 36 | 30 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 16 | 0 | 0 | 12 | 6935 | 927 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.15 | 0 | 0 | 0 | 113 | 0 | 90 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 370 | 0 | 0 | 5.5 | 0 | 60 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 7 | 132 | 220 | 0 | 214 | 622 | 54 | 4473.65 | 11408.65 | 89.45
22:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 100 | 64 | 45 | 0 | 0 | 35 | 25 | 0 | 400 | 0 | 0 | 0 | 17 | 18 | 300 | 0 | 0 | 0 | 17 | 16 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 1 | 0 | 78 | 0 | 100 | 0 | 0 | 40 | 110 | 19 | 576 | 0 | 0 | 0 | 0 | 105 | 224 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 189 | 0 | 0 | 270 | 5 | 189 | 36 | 115 | 50 | 100 | 9 | 17 | 0 | 68 | 0 | 0 | 0 | 310 | 320 | 0 | 36 | 30 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 15 | 0 | 0 | 12 | 6651 | 926 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.65 | 0 | 0 | 0 | 113 | 0 | 90 | 50 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 370 | 0 | 0 | 5.5 | 0 | 60 | 53 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 132 | 220 | 0 | 215 | 622 | 17 | 4391.15 | 11042.15 | 89.45
23:00 | 0 | 70 | 0 | 0 | 0 | 230 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 98 | 64 | 0 | 0 | 0 | 17 | 25 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 10 | 16 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 110 | 19 | 579 | 0 | 0 | 0 | 0 | 105 | 224 | 0 | 0 | 0 | 1228 | 0 | 51 | 40 | 195 | 0 | 0 | 280 | 5 | 184 | 36 | 115 | 50 | 100 | 3 | 17 | 0 | 66 | 0 | 0 | 0 | 300 | 320 | 0 | 36 | 30 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 12 | 0 | 0 | 12 | 6436 | 927 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.36 | 0 | 0 | 0 | 113 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 414 | 0 | 0 | 5.5 | 0 | 60 | 53 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 132 | 220 | 0 | 217 | 622 | 0 | 4193.86 | 10629.86 | 89.44
Total KWH | 0 | 1034880 | 0 | 0 | 0 | 5490969 | 0 | 0 | 9676800 | 0 | 0 | 259560 | 0 | 0 | 1863792 | 610560 | 1034749 | 23444 | 265054 | 796320 | 551520 | 0 | 8662500 | 0 | 0 | 0 | 265755 | 431000 | 7696640 | 0 | 0 | 219397 | 370800 | 405000 | 504720 | 0 | 0 | 603436 | 983564 | 95040 | 0 | 346560 | 741516 | 576656 | 164734 | 1459200 | 398400 | 1320 | 998600 | 1824101 | 376800 | 13243636.36 | 205745 | 0 | 90240 | 76867.2 | 1869273 | 5396836 | 0 | 0 | 0 | 27261815 | 127845 | 1111244 | 1456945 | 4282182 | 0 | 0 | 7272000 | 347040 | 4562000 | 794088 | 1800960 | 1196600 | 2043360 | 68880 | 351900 | 27360 | 1507200 | 104467 | 456445 | 400432 | 7188000 | 7682200 | 0 | 809856 | 713000 | 942960 | 56928 | 3584864 | 514272 | 0 | 1987200 | 710688 | 0 | 440000 | 0 | 0 | 1089600 | 172800 | 282240 | 14850 | 347000 | 161520 | 151486725.56 | 22151272 | 3256128 | 0 | 16800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534960 | 0 | 0 | 17323636 | 0 | 232609 | 0 | 1375776 | 23102 | 965824 | 992544 | 165333 | 53789 | 762210 | 208630 | 452256 | 0 | 0 | 0 | 0 | 3490900 | 0 | 9258545 | 0 | 38220 | 83736 | 0 | 1455272 | 1226407 | 215714 | 827107 | 0 | 0 | 33496.08 | 1206720 | 3364.5 | 922464 | 7222000 | 147375 | 2993000 | 5318760 | 0 | 1570909 | 13847272.73 | 477600 | 98853731.31 | 250340456.87

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11347.08 | MW | 12:00 Hr. | Energy Generated |  |  | 250.3405 |  | MKWHr.
| Day Peak Demand |  |  | 11454.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.035 |  | MKWHr.
| Evening Peak Generation |  |  | 12073.5 | MW | 19:00 Hr. | Energy Demand |  |  | 252.3755 |  | MKWHr.
| Evening Peak Demand |  |  | 12280.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 8337.34 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 825.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 12073.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.6564 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.4191 | 0 | 6.5249 | 0 | 0 | 0.2194 | 0 | 0 | 40.1635 | Gas | 108.5705 | Gas | 396219440.37
| Chattogram Zone |  |  | 5.7736 | 40.5055 | 9.0888 | 0 | 0.9986 | 0.12917 | 0 | 0.34656 | 56.8422 | Coal | 64.6009 | Coal | 433961743.8122
| Cumilla Zone |  |  | 19.9171 | 0 | 5.9024 | 0 | 0 | 0.45644 | 1.5072 | 0 | 27.7831 | HFO | 30.428 | HFO | 549757804.224
| Mymensingh Zone |  |  | 0.28224 | 0 | 1.4239 | 0 | 0 | 0.36185 | 0 | 0 | 2.068 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.63 | Hydro | 0.9986 | Hydro | 99860
| Khulna Zone |  |  | 3.2561 | 0 | 0.0168 | 0 | 0 | 0.53496 | 22.1513 | 0 | 25.9592 | Solar | 4.4138 | Solar | 71496265.3538
| Barishal Zone |  |  | 8.4591 | 22.6402 | 1.4001 | 0 | 0 | 0.0033645 | 0 | 0 | 32.5027 | Import | 40.9821 | Import | 209753001.72
| Rajshahi Zone |  |  | 12.8332 | 0 | 4.0176 | 0 | 0 | 1.2527 | 17.3236 | 0 | 35.4271 | Wind | 0.34656 | Wind | 5073638.4
| Rangpur Zone |  |  | 0 | 1.4553 | 2.0535 | 0 | 0 | 1.4559 | 0 | 0 | 4.9647
| Total |  |  | 108.5705 | 64.6009 | 30.428 | 0 | 0.9986 | 4.4138 | 40.9821 | 0.34656 | 250.3405
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 396219440.37 |  | Hydro | 99860
|  |  |  | Coal | 433961743.8122 |  | Solar | 71496265.3538
|  |  |  | HFO | 549757804.224 |  | Import | 209753001.72
|  |  |  | HSD | 0 |  | Wind | 5073638.4
[5 empty] | Total: | 166,63,61,753 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: |  |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1513 | Peak Hr Flow | 880.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: |  |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.3236 | Peak Hr Flow | 755.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: |  |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5072 | Peak Hr Flow | 78.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: |  |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.9821 | Peak Hr Flow | 1713.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 88 |  | 4552
|  |  |  | Chattogram |  | 0 |  | 1288
|  |  |  | Cumilla |  | 0 |  | 1025
|  |  |  | Mymensingh |  | 110 |  | 1028
|  |  |  | Sylhet |  | 0 |  | 384
|  |  |  | Khulna |  | 0 |  | 1318
|  |  |  | Barishal |  | 0 |  | 319
|  |  |  | Rajshahi |  | 0 |  | 1186
|  |  |  | Rangpur |  | 0 |  | 771
|  |  |  | Total |  | 198 |  | 11871
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1458.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 09:53 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Scheduled S/D Due to Bird Nest
Remove
| 08:19 | 17:22 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Disc | [7 empty] | 30.0MW load
|  |  | Change and Cleaning at Brick Field Area. | [7 empty] | interrup. Dohazari
132/33kV end
| 08:27 | 15:24 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Deep Disk Cleaning in bricks field area
| 08:33 | 17:20 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Tower painting work
| 08:45 | 12:51 | Sholosohor 132/33kV S/S Sholoshahar-Madunaghat Ckt-1 Scheduled S/D Due to Disc Changing
work by Khulshi Grid
| 08:46 | 12:51 | Khulshi-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to
Maintenance Work ( Insulator disk change)
| 08:58 |  | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to Dead line
cheecking. and from Sylhet 132/33kV end Due to Dead Line checking
| 09:21 | 17:16 | Kodda-Rajendrapur 132kV Ckt-2 Scheduled S/D from Rajendrapur 132/33kV end Due to Tower
Insulator Disc Change
| 09:23 | 16:46 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Tower checking
| 09:23 | 16:46 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to None
| 09:54 | 18:04 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from Ishurdi 230/132kV end.
| 10:26 | 14:50 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to OLTC oil Change.
| 10:26 | 14:50 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to OLTC oil Change.
| 10:35 | 18:04 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from BIPTC end Due to Shutdown is
taken from Ishwardi end
| 10:41 | 14:20 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Relay testing (SPMD)
| 12:00 |  | Day peak Generation is 11343 MW
| 13:15 | 14:43 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-1 Scheduled S/D Due to Disc Changing Work
by Khulshi Grid
| 13:15 | 19:50 | Tangail 132/33kV S/S Tr-4 LT Tripped showing Alstom MVAJM15JA0754A and Micom P122 relays
Due to Earth Fault
| 13:28 | 14:34 | Bogura 132/33kV S/S Transformer-1 HT Project Work S/D Due to Project work
| 14:26 | 17:09 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Realy testing (SPMD)
|  | 14:37 | Bogura 132/33kV S/S Transformer-1 LT is restored.
| 14:48 | 15:10 | Bogura 400/230kV S/S 400 KV BUS-01 Scheduled S/D Due to Bus LA Grounding Rearrangement.
| 15:21 | 16:22 | Bogura 400/230kV S/S 400 KV BUS-02 Scheduled S/D Due to Bus LA Grounding Rearrangement.
| 15:38 | 16:17 | Bogura 132/33kV S/S Transformer-1 HT Project Work S/D Due to Metering CT polarity change Work.
| 15:38 | 16:18 | Bogura 132/33kV S/S Transformer-1 LT Project Work S/D Due to Metering CT polarity change Work.
| 16:16 | 19:50 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to 33kv Shakhipur Feeder under ground cable fault.
|  | 16:46 | Bibiyana-Shahjibazar 230 kV Ckt-2 is restored.
| 17:16 |  | Bogura 132/33kV S/S Transformer-2 LT Project Work S/D Due to For T-1 Full load Test
| 19:00 |  | Evening Peak Gen. 12073 MW
| 07:16 |  | Bogura 132/33kV S/S Transformer-1 HT Project Work S/D Due to 33kv Bus Upgrading Work. | [7 empty] | 25.0MW load
interrup.
| 07:18 |  | Bogura 132/33kV S/S Transformer-2 HT Project Work S/D Due to 33kv Bus Upgrading Work. | [7 empty] | 25.0MW load
interrup.
| 07:19 |  | Bogura 132/33kV S/S Transformer-1 LT Project Work S/D Due to 33kv Bus Upgrading Work. | [7 empty] | 25.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 5490969 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 407 | 9676800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8662500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 23444 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7696640 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 82 | 610560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265054 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 265755 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 405000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 504720 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 551520 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 18 | 431000 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | line SD
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1034749 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 124 | 1863792 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1034880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 796320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 219397 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 35 | 370800 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2121 | 40163460
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 76867.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127845 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 90240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 998600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5396836 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1869273 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 576656 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 741516 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1459200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 376800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 95040 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 1320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 983564 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 164734 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 102 | 1824101 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 398400 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 603436 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 54 | 205745 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27261815 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 19 | 346560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 577 | 13243636.36 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2870 | 56842184.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 197 | 4562000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 270 | 7272000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 794088 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 347040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4282182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1111244 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 1456945 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 47 | 400432 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1196600 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 158 | 2043360 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1507200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 104467 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 351900 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 27360 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 5 | 68880 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1800960 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456445 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1379 | 27783103
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 282240 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 172800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1089600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 347000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 161520 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 90 | 2068010
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 713000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 942960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3584864 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 809856 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 56928 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 710688 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1987200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 440000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 514272 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7188000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Shutdown due to maintenance.
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7682200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 999 | 24629968
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 22151272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 25 | 16800 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 109 | 3256128 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 534960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Shutdown due to Turning Gear Inspection.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1014 | 25959160
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 212 | 1570909 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 96 | 922464 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 147375 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2993000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 13847272.73 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5318760 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 477600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7222000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3364.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1648 | 32502745.23
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 232609 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 23102 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 37 | 165333 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 133 | 3490900 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 370 | 9258545 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 208630 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 83736 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 53789 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 965824 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 105 | 1375776 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 992544 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38220 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755 | 17323636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 452256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 762210 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1693.5 | 35427110
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 1455272 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 827107 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33496.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 93 | 1226407 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 215714 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1206720 | -
Rangpur Area Total |  |  |  |  | 950 | 259 | 4964716.08
Eastern Grid Total |  |  |  |  | 16856.242 | 7459 | 151486725.56
Western Grid Total |  |  |  |  | 11614.5 | 4614.5 | 98853731.31
National Grid Total |  |  |  |  | 28470.742 | 12073.5 | 250340456.87
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8079.79 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3594.2 | MW
i) Dhaka area |  |  | 4464.29 |  | MW | i) Khulna area |  |  |  | 1317.8 | MW
ii) Chattogram area |  |  | 1288.5 |  | MW | ii) Barishal area |  |  |  | 319 | MW
iii) Cumilla area |  |  | 1025 |  | MW | iii) Rajshahi area |  |  |  | 1186.4 | MW
iv) Mymensingh area |  |  | 918 |  | MW | iv) Rangpur area |  |  |  | 771 | MW
v) Sylhet area |  |  | 384 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11673.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 19:00 | 133 | Postogola | 44 | 12:00
2 | AKSML | 121 | 16:00 | 68 | Jamalpur | 86 | 18:30 | 134 | Purbachal | 14 | 18:30
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 109 | 13:00 | 135 | Purbasadipur | 117 | 08:00
4 | Agargaon | 84 | 13:00 | 70 | Jhenaidah | 103 | 18:30 | 136 | Rahanpur | 12 | 18:30
5 | Agrabad | 80 | 18:00 | 71 | Joydebpur | 165 | 18:30 | 137 | Rahim | 49 | 16:00
6 | Amnura | 55 | 13:00 | 72 | Joypurhat | 65 | 08:00 | 138 | Rajbari | 54 | 19:30
7 | Ashuganj | 74 | 14:00 | 73 | Juldah | 12 | 12:00 | 139 | Rajendrapur | 114 | 19:00
8 | BSRM | 203 | 16:00 | 74 | KSRM | 30 | 18:00 | 140 | Rajshahi | 95 | 20:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 190 | 14:00 | 141 | Rajshahi-230 | 46 | 00:00
10 | Bajitpur | 36 | 20:00 | 76 | Kachua | 59 | 18:30 | 142 | Ramganj | 86 | 18:30
11 | Bakulia | 82 | 18:30 | 77 | Kallyanpur | 81 | 14:00 | 143 | Rampur | 32 | 18:00
12 | Banani | 22.4 | 13:00 | 78 | Kalurghat | 36 | 15:00 | 144 | Rangamati | 13 | 18:30
13 | Bangabhaban | 10 | 10:00 | 79 | Kamrangirchar | 62 | 18:30 | 145 | Rangpur | 114 | 19:00
14 | Barapukuria | 53 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Ruppur | 5.4 | 15:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 89 | 19:30 | 147 | SSM | 0 | 00:00
16 | Barishal | 88 | 13:00 | 82 | Keranigonj | 76 | 13:00 | 148 | Saidpur | 112 | 09:00
17 | Barishal-230 | 60 | 19:30 | 83 | Khagrachori | 24 | 18:30 | 149 | Satkhira | 94 | 19:00
18 | Baroaulia | 60 | 12:00 | 84 | Khulna | 79 | 20:00 | 150 | Satmasjid | 84 | 13:00
19 | Baroirhat | 41 | 18:30 | 85 | Khulshi | 160 | 19:30 | 151 | Savar | 204 | 12:00
20 | Bashundhara | 148 | 13:00 | 86 | Kishoreganj | 106 | 19:00 | 152 | SevenRings | 18.09 | 15:00
21 | BashundharaCement | 8 | 10:00 | 87 | Kodda | 250 | 18:30 | 153 | ShahCement | 37 | 23:00
22 | Beanibazar | 46 | 18:30 | 88 | Kulaura | 31 | 18:30 | 154 | Shahjadpur | 73 | 07:00
23 | Benapole | 50 | 18:30 | 89 | Kurigram | 60 | 08:00 | 155 | Shahjibazar | 98 | 18:30
24 | Bhaluka | 130 | 09:00 | 90 | Kushtia | 114 | 19:00 | 156 | Shahmirpur | 43 | 18:30
25 | Bhandaria | 46 | 21:00 | 91 | Lalbag | 60 | 12:00 | 157 | Shariatpur | 54 | 18:30
26 | Bhangura | 31 | 18:00 | 92 | Lalmonirhat | 45 | 19:00 | 158 | Sherpur | 104 | 10:00
27 | Bheramara(GK) | 39 | 18:30 | 93 | MI_Cement | 16.8 | 17:00 | 159 | Shikalbaha | 25 | 18:00
28 | Bhulta | 228 | 09:00 | 94 | Madanganj | 29 | 12:00 | 160 | Shitalakhya | 66 | 16:00
29 | Bog-Sherpur | 70 | 09:00 | 95 | Madaripur | 70 | 19:00 | 161 | Sholosohor | 41 | 18:30
30 | Bogura | 124 | 19:00 | 96 | Madartek | 68.1 | 13:00 | 162 | Shyampur | 142 | 02:00
31 | Borhanuddin | 55 | 19:30 | 97 | Madunaghat | 42 | 21:00 | 163 | Siddhirganj | 102 | 12:00
32 | Brahmanbaria | 118 | 18:00 | 98 | Magura | 49 | 18:30 | 164 | Sirajganj | 96 | 08:00
33 | Cantonment | 102 | 13:00 | 99 | Mahasthangarh | 54 | 18:30 | 165 | Sonargaon | 89 | 11:00
34 | Chandpur | 46 | 18:00 | 100 | Manikganj | 105 | 18:30 | 166 | Sreemongol | 48 | 18:00
35 | Chandraghona | 27 | 18:30 | 101 | Maniknagar | 58 | 10:00 | 167 | Sreepur | 92 | 09:00
36 | Chapai | 72 | 12:00 | 102 | Matarbari | 46 | 18:30 | 168 | Srinagar | 30.6 | 20:00
37 | Charsaidpur | 43 | 12:00 | 103 | Matuail | 60 | 16:00 | 169 | Sunamganj | 42 | 19:00
38 | Chauddagram | 58 | 14:00 | 104 | Millgate | 70 | 12:00 | 170 | Sylhet | 24 | 20:00
39 | Chhatak | 23 | 18:30 | 105 | Mirpur | 109 | 18:30 | 171 | Sylhet-132 | 89 | 18:00
40 | Chowmuhani | 160 | 19:30 | 106 | Mirsorai | 9 | 20:00 | 172 | TK | 17.5 | 18:30
41 | Chuadanga | 74 | 19:00 | 107 | Mirzapur | 41 | 12:00 | 173 | Tangail | 150 | 18:30
42 | Coxsbazar | 128 | 18:00 | 108 | Mithapukur | 48 | 18:30 | 174 | Thakurgaon | 79 | 09:00
43 | Cumilla(N) | 124 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Tongi | 105 | 11:00
44 | Cumilla(S) | 154 | 18:30 | 110 | Mogbazar | 118.1 | 15:00 | 176 | Ullahpara | 30 | 14:00
45 | Daudkandi | 104 | 18:30 | 111 | Mongla | 32 | 19:00 | 177 | Ullon | 37 | 18:30
46 | Dhaka | 40 | 12:00 | 112 | Motijheel | 29 | 13:00 | 178 | Uttara | 68 | 18:30
47 | Dhamrai | 112 | 18:00 | 113 | Muktagacha | 25 | 11:00 | 179 | UttaraNew | 31 | 18:00
48 | Dhanmondi | 111 | 14:00 | 114 | Munshiganj | 75 | 14:00 | 180 | Zigatola | 58 | 14:00
49 | Dohazari | 83 | 19:30 | 115 | Muradnagar | 0 | 00:00
50 | Faridpur | 112 | 18:30 | 116 | Mymensingh | 172 | 18:30
51 | Fatullah | 76 | 15:00 | 117 | Naogaon | 107 | 08:00
52 | Fenchuganj | 30 | 19:00 | 118 | Narail | 44 | 18:30
53 | Feni | 91 | 18:00 | 119 | Narinda | 69.5 | 13:00
54 | GPH | 92 | 04:00 | 120 | Narshingdi | 150 | 19:30
55 | Ghatail | 50 | 07:00 | 121 | Natore | 114 | 19:00
56 | Ghorashal | 12 | 11:00 | 122 | Nawabganj | 37.2 | 14:00
57 | Ghorashal-230 | 75 | 18:30 | 123 | Netrakona | 120 | 18:30
58 | Goalpara | 20 | 13:00 | 124 | New | 76 | 12:00
59 | Gollamari | 56 | 19:00 | 125 | Niamatpur | 89 | 13:00
60 | Gopalganj | 81.8 | 19:00 | 126 | Noapara | 37 | 18:30
61 | Gulshan | 90 | 13:00 | 127 | PHP | 9 | 07:00
62 | Halishahar | 74 | 14:00 | 128 | Pabna | 82 | 18:30
63 | HaripurSBU | 177 | 11:00 | 129 | Palashbari | 102 | 08:00
64 | Hasnabad | 67 | 00:00 | 130 | Panchagarh | 43 | 18:30
65 | Hathazari | 60 | 18:00 | 131 | Patuakhali | 51.5 | 21:00
66 | Ishurdi | 59 | 19:00 | 132 | Payra | 24 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9990.88 | 0 |  | 9990.88
1:00 | 9394.8 | 0 |  | 9394.8
2:00 | 8821.8 | 0 |  | 8821.8
3:00 | 8609.8 | 0 |  | 8609.8
4:00 | 8405.8 | 0 |  | 8405.8
5:00 | 8337.34 | 0 |  | 8337.34
6:00 | 8624.62 | 0 |  | 8624.62
7:00 | 9579.57 | 55 |  | 9636.57
8:00 | 10260.44 | 79 |  | 10343
9:00 | 10630.77 | 99 |  | 10733.77
10:00 | 10547.84 | 92 |  | 10643.84
11:00 | 10818.58 | 81 |  | 10903.58
12:00 | 11347.08 | 102 |  | 11454.08
13:00 | 11489.72 | 109 |  | 11603.72
14:00 | 11343.45 | 110 |  | 11458.45
15:00 | 11066.58 | 140 |  | 11212.58
16:00 | 10819.73 | 160 |  | 10986.73
17:00 | 10711.91 | 164 |  | 10882.91
18:00 | 11164.92 | 187 |  | 11359.92
19:00 | 12073.5 | 198 |  | 12280.5
19:30 | 11907.5 | 203 |  | 12119.5
20:00 | 11763 | 175 |  | 11946
21:00 | 11408.65 | 136 |  | 11550.65
22:00 | 11042.15 | 114 |  | 11161.15
23:00 | 10629.86 | 34 |  | 10665.86
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6026 | 3964.88 | 9990.88 | DAILY GENERATION CURVE
00:30 | 5804 | 3888.84 | 9692.84
01:00 | 5582 | 3812.8 | 9394.8 | 24-02-2025
01:30 | 5381.5 | 3726.8 | 9108.3
02:00 | 5181 | 3640.8 | 8821.8
02:30 | 5133.5 | 3582.3 | 8715.8
03:00 | 5086 | 3523.8 | 8609.8
03:30 | 5050 | 3457.8 | 8507.8
04:00 | 5014 | 3391.8 | 8405.8
04:30 | 5012.5 | 3359.07 | 8371.57
05:00 | 5011 | 3326.34 | 8337.34
05:30 | 5051 | 3429.98 | 8480.98
06:00 | 5091 | 3533.62 | 8624.62
06:30 | 5484.385 | 3617.71 | 9102.095
07:00 | 5877.77 | 3701.8 | 9579.57
07:30 | 6076.5 | 3843.505 | 9920.005
08:00 | 6275.23 | 3985.21 | 10260.44
08:30 | 6358.855 | 4086.75 | 10445.605
09:00 | 6442.48 | 4188.29 | 10630.77
09:30 | 6323.525 | 4265.78 | 10589.305
10:00 | 6204.57 | 4343.27 | 10547.84
10:30 | 6290.305 | 4392.905 | 10683.21
11:00 | 6376.04 | 4442.54 | 10818.58
11:30 | 6518.34 | 4564.49 | 11082.83
12:00 | 6660.64 | 4686.44 | 11347.08
12:30 | 6725.06 | 4693.34 | 11418.4
13:00 | 6789.48 | 4700.24 | 11489.72
13:30 | 6819.545 | 4597.04 | 11416.585
14:00 | 6849.61 | 4493.84 | 11343.45
14:30 | 6793.62 | 4411.395 | 11205.015
15:00 | 6737.63 | 4328.95 | 11066.58
15:30 | 6657.415 | 4285.74 | 10943.155
16:00 | 6577.2 | 4242.53 | 10819.73
16:30 | 6535.31 | 4230.51 | 10765.82
17:00 | 6493.42 | 4218.49 | 10711.91
17:30 | 6648.72 | 4289.695 | 10938.415
18:00 | 6804.02 | 4360.9 | 11164.92
18:30 | 7131.51 | 4487.7 | 11619.21
19:00 | 7459 | 4614.5 | 12073.5
19:30 | 7301 | 4606.5 | 11907.5
20:00 | 7218.5 | 4544.5 | 11763
20:30 | 7076.75 | 4509.075 | 11585.825 |  | Executive Engineer
21:00 | 6935 | 4473.65 | 11408.65 |  | Network Operation Division
21:30 | 6793 | 4432.4 | 11225.4
22:00 | 6651 | 4391.15 | 11042.15
22:30 | 6543.5 | 4292.505 | 10836.005
23:00 | 6436 | 4193.86 | 10629.86

## En-Curve
QF-LDC-12
Date | 24-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3038 | 1519.5 | 921 | 0 | 70 | 759 | 40 | 2827.38 | 0 | 102 | 708 | 0 | 0 | 6 | 0 | DAILY ENERGY CURVE
00:30 | 3033.5 | 1509 | 920.5 | 0 | 67 | 757 | 40 | 2835.19 | 0 | 57.15 | 462 | 0 | 0 | 11.5 | 0 | 24-02-2025
01:00 | 3029 | 1498.5 | 920 | 0 | 64 | 755 | 40 | 2843 | 0 | 12.3 | 216 | 0 | 0 | 17 | 0
01:30 | 3056.5 | 1487 | 920.5 | 0 | 61 | 707.5 | 40 | 2696 | 0 | 10.3 | 112 | 0 | 0 | 17.5 | 0 | Energy Generated | 250.3405 |  | MKWHr
02:00 | 3084 | 1475.5 | 921 | 0 | 58 | 660 | 40 | 2549 | 0 | 8.3 | 8 | 0 | 0 | 18 | 0 | Energy not Served | 2.035 |  | MKWHr
02:30 | 3072 | 1480.5 | 921 | 0 | 60 | 636.5 | 40 | 2473 | 0 | 8.3 | 4 | 0 | 0 | 20.5 | 0 | Total Energy Requirement | 252.3755 |  | MKWHr
03:00 | 3060 | 1485.5 | 921 | 0 | 62 | 613 | 40 | 2397 | 0 | 8.3 | 0 | 0 | 0 | 23 | 0
03:30 | 3060.5 | 1483 | 921 | 0 | 61 | 587 | 40 | 2322.5 | 0 | 8.3 | 0 | 0 | 0 | 24.5 | 0
04:00 | 3061 | 1480.5 | 921 | 0 | 60 | 561 | 40 | 2248 | 0 | 8.3 | 0 | 0 | 0 | 26 | 0
04:30 | 3032.5 | 1484 | 921.5 | 0 | 57 | 561 | 40 | 2245.27 | 0 | 8.3 | 0 | 0 | 0 | 22 | 0
05:00 | 3004 | 1487.5 | 922 | 0 | 54 | 561 | 40 | 2242.54 | 0 | 8.3 | 0 | 0 | 0 | 18 | 0
05:30 | 3000 | 1498 | 922 | 0 | 53 | 614 | 40 | 2280.18 | 0 | 25.3 | 31.5 | 0 | 0 | 17 | 0
06:00 | 2996 | 1508.5 | 922 | 0 | 52 | 667 | 40 | 2317.82 | 0 | 42.3 | 63 | 0 | 0 | 16 | 0
06:30 | 2985.5 | 1493 | 922 | 0 | 56 | 664 | 40 | 2391.41 | 14.885 | 67.3 | 453.5 | 0 | 0 | 14.5 | 27.5
07:00 | 2975 | 1477.5 | 922 | 0 | 60 | 661 | 40 | 2465 | 29.77 | 92.3 | 844 | 0 | 0 | 13 | 55
07:30 | 2945.5 | 1437.5 | 898.5 | 0 | 56 | 705.445 | 40 | 2592 | 97.76 | 92.3 | 1040 | 0 | 0 | 15 | 67
08:00 | 2916 | 1397.5 | 875 | 0 | 52 | 749.89 | 40 | 2719 | 165.75 | 92.3 | 1236 | 0 | 0 | 17 | 79
08:30 | 2933 | 1426 | 875.5 | 0 | 55 | 753.58 | 40 | 2718.5 | 258.725 | 92.3 | 1281 | 0 | 0 | 12 | 89
09:00 | 2950 | 1454.5 | 876 | 0 | 58 | 757.27 | 40 | 2718 | 351.7 | 92.3 | 1326 | 0 | 0 | 7 | 99
09:30 | 2941.5 | 1428.5 | 899.5 | 0 | 57 | 755.155 | 43 | 2720.5 | 435.85 | 100.8 | 1203 | 0 | 0 | 4.5 | 95.5
10:00 | 2933 | 1402.5 | 923 | 0 | 56 | 753.04 | 46 | 2723 | 520 | 109.3 | 1080 | 0 | 0 | 2 | 92
10:30 | 2936 | 1418 | 923.5 | 0 | 59 | 755.135 | 46 | 2750.75 | 568.175 | 113.15 | 1102.5 | 0 | 0 | 11 | 86.5
11:00 | 2939 | 1433.5 | 924 | 0 | 62 | 757.23 | 46 | 2778.5 | 616.35 | 117 | 1125 | 0 | 0 | 20 | 81
11:30 | 2982.5 | 1456 | 924 | 0 | 64 | 757.295 | 46 | 2845.25 | 640.285 | 173.5 | 1175 | 0 | 0 | 19 | 91.5
12:00 | 3026 | 1478.5 | 924 | 0 | 66 | 757.36 | 46 | 2912 | 664.22 | 230 | 1225 | 0 | 0 | 18 | 102
12:30 | 3019 | 1477 | 924 | 0 | 66 | 757.8 | 46 | 2927 | 646.6 | 250.5 | 1289 | 0 | 0 | 15.5 | 105.5
13:00 | 3012 | 1475.5 | 924 | 0 | 66 | 758.24 | 46 | 2942 | 628.98 | 271 | 1353 | 0 | 0 | 13 | 109
13:30 | 2921.5 | 1543 | 924 | 0 | 67 | 734.12 | 66 | 2867 | 609.965 | 294.5 | 1377 | 0 | 0 | 12.5 | 109.5
14:00 | 2831 | 1610.5 | 924 | 0 | 68 | 710 | 86 | 2792 | 590.95 | 318 | 1401 | 0 | 0 | 12 | 110
14:30 | 2845 | 1600 | 924 | 0 | 67 | 710.5 | 63 | 2796 | 521.015 | 339 | 1326.5 | 0 | 0 | 13 | 125
15:00 | 2859 | 1589.5 | 924 | 0 | 66 | 711 | 40 | 2800 | 451.08 | 360 | 1252 | 0 | 0 | 14 | 140
15:30 | 2871.5 | 1601 | 924 | 0 | 66 | 719.5 | 40 | 2854 | 361.655 | 362.5 | 1131 | 0 | 0 | 12 | 150
16:00 | 2884 | 1612.5 | 924 | 0 | 66 | 728 | 40 | 2908 | 272.23 | 365 | 1010 | 0 | 0 | 10 | 160
16:30 | 2867 | 1561.5 | 923.5 | 0 | 67 | 741.5 | 40 | 2926 | 179.32 | 391 | 1059.5 | 0 | 0 | 9.5 | 162
17:00 | 2850 | 1510.5 | 923 | 0 | 68 | 755 | 40 | 2944 | 86.41 | 417 | 1109 | 0 | 0 | 9 | 164
17:30 | 2845.5 | 1510 | 923.5 | 0 | 70 | 754.5 | 40 | 2942.5 | 43.415 | 464 | 1333.5 | 0 | 0 | 11.5 | 175.5
18:00 | 2841 | 1509.5 | 924 | 0 | 72 | 754 | 40 | 2941 | 0.42 | 511 | 1558 | 0 | 0 | 14 | 187
18:30 | 2885.5 | 1503 | 902 | 0 | 75 | 754.5 | 40 | 2971.5 | 0.21 | 572.5 | 1898.5 | 0 | 0 | 16.5 | 192.5
19:00 | 2930 | 1496.5 | 880 | 0 | 78 | 755 | 40 | 3002 | 0 | 634 | 2239 | 0 | 0 | 19 | 198
19:30 | 2941 | 1496.5 | 880 | 0 | 76 | 759 | 40 | 3004 | 0 | 601 | 2091 | 0 | 0 | 19 | 203
20:00 | 2925 | 1491 | 880 | 0 | 70 | 760 | 40 | 3000 | 0 | 585 | 1987 | 0 | 0 | 25 | 175
20:30 | 2936 | 1506.25 | 903.5 | 0 | 71 | 760.075 | 40 | 3001.5 | 0 | 505 | 1839 | 0 | 0 | 23.5 | 155.5
21:00 | 2947 | 1521.5 | 927 | 0 | 72 | 760.15 | 40 | 3003 | 0 | 425 | 1691 | 0 | 0 | 22 | 136
21:30 | 2918.5 | 1568.5 | 926.5 | 0 | 70 | 757.4 | 40 | 3003.5 | 0 | 372 | 1557.5 | 0 | 0 | 11.5 | 125
22:00 | 2890 | 1615.5 | 926 | 0 | 68 | 754.65 | 40 | 3004 | 0 | 319 | 1424 | 0 | 0 | 1 | 114
22:30 | 2904 | 1613.5 | 926.5 | 0 | 67 | 755.505 | 40 | 3008.5 | 0 | 276.5 | 1244 | 0 | 0 | 0.5 | 74
23:00 | 2918 | 1611.5 | 927 | 0 | 66 | 756.36 | 40 | 3013 | 0 | 234 | 1064 | 0 | 0 | 0 | 34
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 05:00 | 383 | 12:00 | Payra | 420 | 04:00 | 411 | 12:00
Ashuganj | 406 | 6:00 | 387 | 12:00 | Rahanpur | 416 | 04:00 | 402 | 08:00
Bhulta | 405 | 06:00 | 383 | 15:00 | Rampal | 413 | 05:00 | 388 | 12:00
Bibiana | 399 | 06:00 | 389 | 12:00
BIPTC | 401 | 04:00 | 392 | 17:00
Bogura | 413 | 03:00 | 398 | 08:00
Gopalganj | 411 | 05:00 | 391 | 13:00
Kaliakoir | 379 | 04:00 | 352 | 15:00
Madunaghat | 407 | 07:00 | 397 | 17:00
Meghnaghat | 399 | 04:00 | 381 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 04:00 | 219 | 12:00 | Keranigonj | 232 | 04:00 | 218 | 12:00
AKSML | 232 | 05:00 | 224 | 16:00 | Khulna(S) | 239 | 04:00 | 222 | 13:00
Aminbazar | 233 | 05:00 | 219 | 12:00 | Madunaghat | 233 | 07:00 | 226 | 16:00
Ashuganj | 240 | 06:00 | 229 | 15:00 | Madunaghat-400 | 234 | 08:00 | 227 | 02:00
Ashuganj-400 | 236 | 6:00 | 218 | 12:00 | Maniknagar | 232 | 05:00 | 221 | 12:00
Baghabari | 239 | 04:00 | 227 | 12:00 | Meghnaghat | 240 | 01:00 | 229 | 12:00
Barapukuria | 227 | 20:00 | 214 | 08:00 | Meghnaghat-400 | 235 | 05:00 | 223 | 15:00
Barapukuria-230 | 227 | 20:00 | 217 | 7:00 | Mirsorai | 234 | 08:00 | 223 | 16:00
Barishal | 243 | 06:00 | 235 | 11:00 | Rajshahi | 239 | 04:00 | 225 | 15:00
Bheramara | 236 | 04:00 | 224 | 12:00 | Rampal | 270 | 06:00 | 221 | 13:00
Bhulta | 235 | 04:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 05:00 | 224 | 09:00 | Rampura | 234 | 04:00 | 221 | 15:00
BIPTC | 240 | 05:00 | 224 | 12:00 | Shikalbaha | 234 | 08:00 | 225 | 16:00
Bogura | 240 | 05:00 | 230 | 08:00 | Shyampur | 233 | 04:00 | 220 | 12:00
Bogura-400 | 238 | 04:00 | 229 | 08:00 | Siddhirganj | 235 | 07:00 | 223 | 12:00
Borhanuddin | 245 | 04:00 | 240 | 12:00 | Sirajgonj | 245 | 04:00 | 236 | 12:00
BSRM | 233 | 08:00 | 220 | 16:00 | Sreepur | 237 | 00:00 | 227 | 12:00
Cumilla(N) | 233 | 08:00 | 223 | 12:00 | Tongi | 231 | 19:30 | 218 | 11:00
Faridpur | 242 | 04:00 | 231 | 12:00
Fenchuganj | 237 | 06:00 | 229 | 10:00
Ghorashal | 240 | 01:00 | 230 | 15:00
Ghorashal-230 | 234 | 04:00 | 222 | 15:00
Gopalganj | 241 | 05:00 | 229 | 13:00
GPH | 233 | 08:00 | 223 | 16:00
Haripur | 234 | 04:00 | 223 | 12:00
Hasnabad | 232 | 06:00 | 219 | 12:00
Hathazari | 235 | 08:00 | 226 | 16:00
Ishurdi | 239 | 04:00 | 227 | 12:00
Jhenaidah | 236 | 04:00 | 220 | 13:00
Kaliakoir | 234 | 04:00 | 217 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 124 | 12:00 | Madunaghat | 135 | 18:30 | 130 | 02:00
Agargaon | 135 | 04:00 | 126 | 12:00 | Magura | 138 | 04:00 | 126 | 12:00
Agrabad | 134 | 07:00 | 127 | 15:00 | Mahasthangarh | 136 | 03:00 | 128 | 08:00
AKS | 132 | 09:00 | 127 | 12:00 | Manikganj | 134 | 20:00 | 125 | 00:00
Aminbazar | 138 | 18:30 | 127 | 12:00 | Maniknagar | 133 | 06:00 | 124 | 15:00
Amnura | 140 | 00:00 | 131 | 08:00 | Matarbari | 127 | 21:00 | 109 | 12:00
Ashuganj | 141 | 07:00 | 135 | 12:00 | Matuail | 133 | 03:00 | 126 | 12:00
Bagerhat | 136 | 04:00 | 122 | 18:30 | Millgate | 136 | 03:00 | 125 | 15:00
Bajitpur | 136 | 03:00 | 130 | 10:00 | Mirpur | 136 | 02:00 | 126 | 12:00
Bakulia | 134 | 08:00 | 129 | 16:00 | Mirzapur | 131 | 00:00 | 121 | 10:00
Banani | 134 | 03:00 | 124 | 12:00 | Mithapukur | 137 | 22:00 | 124 | 08:00
Bangabhaban | 133 | 04:00 | 124 | 12:00 | MI_Cement | 135 | 05:00 | 126 | 15:00
Barapukuria | 137 | 20:00 | 127 | 08:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 137 | 08:00 | 132 | 11:00 | Mogbazar | 135 | 01:00 | 125 | 12:00
Barishal | 135 | 00:00 | 130 | 12:00 | Mongla | 136 | 05:00 | 124 | 18:30
Barishal-230 | 136 | 04:00 | 131 | 11:00 | Motijheel | 133 | 04:00 | 124 | 12:00
Baroaulia | 135 | 08:00 | 129 | 01:00 | Muktagacha | 130 | 00:00 | 116 | 10:00
Baroirhat | 131 | 05:00 | 125 | 14:00 | Munshiganj | 134 | 06:00 | 125 | 12:00
Bashundhara | 135 | 01:00 | 124 | 12:00 | Muradnagar | 134 | 08:00 | 127 | 12:00
BashundharaCement | 134 | 05:00 | 126 | 11:00 | Mymensingh | 128 | 00:00 | 115 | 10:00
Beanibazar | 135 | 04:00 | 128 | 11:00 | Naogaon | 134 | 04:00 | 125 | 08:00
Benapole | 137 | 04:00 | 121 | 13:00 | Narail | 138 | 04:00 | 126 | 12:00
Bhaluka | 128 | 02:00 | 120 | 11:00 | Narinda | 133 | 6:00 | 124 | 15:00
Bhandaria | 134 | 05:00 | 126 | 11:00 | Narshingdi | 132 | 01:00 | 121 | 15:00
Bhangura | 137 | 01:00 | 129 | 12:00 | Natore | 136 | 01:00 | 130 | 12:00
Bheramara | 137 | 01:00 | 131 | 12:00 | Nawabganj | 139 | 04:00 | 130 | 12:00
Bheramara(GK) | 139 | 04:00 | 131 | 14:00 | Netrakona | 126 | 00:00 | 115 | 18:30
Bhulta | 127 | 03:00 | 120 | 12:00 | New | 136 | 04:00 | 126 | 15:00
Bog-Sherpur | 136 | 03:00 | 129 | 08:00 | Niamatpur | 140 | 22:00 | 134 | 08:00
Bogura | 137 | 03:00 | 131 | 08:00 | Noapara | 138 | 03:00 | 125 | 18:30
Bogura-230 | 137 | 04:00 | 131 | 09:00 | Pabna | 138 | 03:00 | 131 | 12:00
Brahmanbaria | 135 | 01:00 | 127 | 12:00 | Palashbari | 132 | 02:00 | 120 | 08:00
Cantonment | 135 | 04:00 | 126 | 12:00 | Panchagarh | 141 | 20:00 | 127 | 13:00
Chandpur | 139 | 08:00 | 125 | 01:00 | Patuakhali | 137 | 08:00 | 131 | 11:00
Chandraghona | 136 | 08:00 | 131 | 01:00 | Payra | 138 | 08:00 | 134 | 11:00
Chapai | 138 | 04:00 | 132 | 08:00 | PHP | 131 | 08:00 | 124 | 12:00
Charsaidpur | 134 | 03:00 | 126 | 12:00 | Postogola | 137 | 04:00 | 129 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 132 | 07:00 | 125 | 16:00 | Purbachal | 135 | 04:00 | 125 | 12:00
Chhatak | 134 | 05:00 | 126 | 11:00 | Purbasadipur | 135 | 21:00 | 124 | 08:00
Chowmuhani | 127 | 07:00 | 123 | 01:00 | Rahanpur | 141 | 04:00 | 135 | 09:00
Chuadanga | 138 | 04:00 | 124 | 13:00 | Rahanpur-400 | 141 | 03:00 | 136 | 07:00
Coxsbazar | 121 | 03:00 | 112 | 12:00 | Rahim | 133 | 03:00 | 126 | 11:00
Cumilla(N) | 136 | 03:00 | 128 | 15:00 | Rajbari | 135 | 03:00 | 128 | 12:00
Cumilla(S) | 134 | 07:00 | 127 | 13:00 | Rajendrapur | 132 | 00:00 | 123 | 16:00
Daudkandi | 133 | 05:00 | 125 | 15:00 | Rajshahi | 138 | 05:00 | 131 | 12:00
Dhaka | 134 | 00:00 | 125 | 12:00 | Rajshahi-230 | 139 | 04:00 | 128 | 12:00
Dhamrai | 133 | 03:00 | 123 | 15:00 | Ramganj | 132 | 09:00 | 124 | 02:00
Dhanmondi | 135 | 05:00 | 126 | 12:00 | Rampur | 133 | 07:00 | 127 | 16:00
Dohazari | 132 | 09:00 | 126 | 01:00 | Rampura | 134 | 04:00 | 124 | 15:00
Faridpur | 135 | 04:00 | 130 | 11:00 | Rangamati | 134 | 07:00 | 130 | 02:00
Fatullah | 135 | 04:00 | 128 | 12:00 | Rangpur | 136 | 08:00 | 121 | 07:00
Fenchuganj | 137 | 03:00 | 133 | 09:00 | Ruppur | 139 | 04:00 | 132 | 14:00
Feni | 130 | 06:00 | 123 | 11:00 | Saidpur | 135 | 20:00 | 126 | 08:00
Ghatail | 127 | 00:00 | 115 | 09:00 | Satkhira | 137 | 05:00 | 124 | 18:30
Ghorashal | 140 | 04:00 | 133 | 15:00 | Satmasjid | 135 | 05:00 | 126 | 12:00
Goalpara | 137 | 04:00 | 128 | 12:00 | Savar | 135 | 05:00 | 125 | 12:00
Gollamari | 138 | 04:00 | 128 | 13:00 | SevenRings | 139 | 04:00 | 133 | 15:00
Gopalganj | 138 | 04:00 | 130 | 12:00 | ShahCement | 134 | 03:00 | 126 | 12:00
Gopalganj-400 | 140 | 05:00 | 133 | 12:00 | Shahjadpur | 140 | 00:00 | 133 | 12:00
Gulshan | 134 | 05:00 | 124 | 15:00 | Shahjibazar | 137 | 05:00 | 130 | 11:00
Halishahar | 135 | 08:00 | 129 | 03:00 | Shahmirpur | 136 | 19:00 | 130 | 01:00
Haripur | 133 | 05:00 | 126 | 12:00 | Shariatpur | 138 | 03:00 | 132 | 12:00
HaripurSBU | 139 | 19:00 | 126 | 12:00 | Sherpur | 128 | 00:00 | 112 | 10:00
Hasnabad | 136 | 01:00 | 129 | 15:00 | Shikalbaha | 124 | 08:00 | 118 | 01:00
Hathazari | 137 | 08:00 | 130 | 16:00 | Shikalbaha-230 | 135 | 07:00 | 130 | 03:00
Ishurdi | 139 | 03:00 | 133 | 12:00 | Shitalakhya | 135 | 05:00 | 126 | 13:00
Jaldhaka | 134 | 20:00 | 120 | 07:00 | Sholosohor | 134 | 07:00 | 130 | 01:00
Jamalpur | 131 | 00:00 | 118 | 07:00 | Shyampur | 134 | 04:00 | 128 | 11:00
Jashore | 136 | 04:00 | 123 | 18:30 | Shyampur-230 | 135 | 05:00 | 127 | 12:00
Jhenaidah | 138 | 04:00 | 127 | 13:00 | Siddhirganj | 133 | 05:00 | 126 | 15:00
Jhenaidah-230 | 139 | 05:00 | 127 | 13:00 | Sirajganj | 136 | 01:00 | 128 | 08:00
Joydebpur | 135 | 20:00 | 128 | 12:00 | Sonargaon | 133 | 05:00 | 124 | 15:00
Joypurhat | 133 | 02:00 | 120 | 08:00 | Sreemongol | 136 | 06:00 | 130 | 12:00
Juldah | 136 | 18:30 | 129 | 16:00 | Sreepur | 129 | 00:00 | 122 | 12:00
Kabirpur | 138 | 05:00 | 121 | 15:00 | Srinagar | 139 | 03:00 | 130 | 12:00
Kachua | 137 | 08:00 | 127 | 02:00 | SSM | 138 | 03:00 | 132 | 01:00
Kaliakoir | 137 | 20:00 | 125 | 15:00 | Sunamganj | 133 | 06:00 | 125 | 11:00
Kallyanpur | 136 | 04:00 | 125 | 03:00 | Sylhet | 135 | 04:00 | 127 | 18:00
Kalurghat | 135 | 08:00 | 130 | 01:00 | Sylhet-132 | 135 | 04:00 | 128 | 13:00
Kamrangirchar | 140 | 05:00 | 127 | 12:00 | Tangail | 128 | 00:00 | 117 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 141 | 20:00 | 128 | 00:00
Kazla | 133 | 05:00 | 124 | 12:00 | TK | 135 | 18:30 | 130 | 16:00
Keranigonj | 138 | 04:00 | 129 | 12:00 | Tongi | 138 | 04:00 | 128 | 11:00
Khagrachori | 134 | 08:00 | 128 | 16:00 | Ullahpara | 138 | 03:00 | 130 | 12:00
Khosba | N/A | N/A | N/A | N/A | Ullon | 135 | 03:00 | 124 | 12:00
Khulna | 137 | 04:00 | 126 | 13:00 | Uttara | 136 | 06:00 | 126 | 12:00
Khulna(S) | 139 | 04:00 | 128 | 13:00 | UttaraNew | 136 | 06:00 | 126 | 12:00
Khulshi | 133 | 08:00 | 127 | 16:00 | Zigatola | 140 | 04:00 | 131 | 12:00
Kishoreganj | 132 | 00:00 | 124 | 13:00
Kodda | 135 | 19:00 | 124 | 14:00
KSRM | 135 | 08:00 | 130 | 01:00
Kulaura | 136 | 02:00 | 132 | 12:00
Kurigram | 132 | 18:00 | 122 | 08:00
Kushtia | 138 | 06:00 | 129 | 15:00
Lalbag | 139 | 04:00 | 130 | 12:00
Lalmonirhat | 127 | 12:00 | 120 | 09:00
Madanganj | 135 | 08:00 | 126 | 11:00
Madaripur | 138 | 04:00 | 132 | 16:00
Madartek | 134 | 05:00 | 124 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division