## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-02-2025 | [28 empty] | Date: | 27-02-2025 | [28 empty] | Date: | 27-02-2025 | [28 empty] | Date: | 27-02-2025 | [28 empty] | Date: | 27-02-2025 | [18 empty] | Date: | 27-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 60 | 0 | 95 | 0 | 0 | 17 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 19.5 | 18 | 0 | 0 | 35 | 52 | 0 | 0 | 9 | 0 | 77 | 0 | 100 | 0 | 0 | 40 | 110 | 30 | 370 | 0 | 0 | 0 | 0 | 88 | 227 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 187 | 0 | 0 | 0 | 29 | 182 | 33 | 115 | 50 | 200 | 0 | 8 | 0 | 64 | 0 | 0 | 0 | 290 | 320 | 216 | 36 | 42 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 59 | 9 | 8 | 0 | 0 | 6 | 6576.5 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.99 | 0 | 0 | 0 | 113 | 27 | 91 | 50 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 7 | 100 | 180 | 0 | 322 | 600 | 17 | 3638.49 | 10214.99 | 89.2
01:00 | 0 | 17 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 52 | 0 | 0 | 0 | 17 | 17 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 18 | 0 | 0 | 35 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 88 | 0 | 0 | 40 | 110 | 25 | 274 | 0 | 0 | 0 | 0 | 88 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 187 | 0 | 0 | 0 | 29 | 183 | 33 | 96 | 50 | 155 | 0 | 8 | 0 | 58 | 0 | 0 | 0 | 280 | 320 | 216 | 36 | 42 | 39 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 10 | 0 | 0 | 6 | 6084 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.56 | 0 | 0 | 0 | 113 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 180 | 0 | 322 | 622 | 0 | 3548.06 | 9632.06 | 89.19
02:00 | 0 | 17 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 37 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 85 | 25 | 216 | 0 | 0 | 0 | 0 | 88 | 226 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 183 | 34 | 51 | 50 | 17 | 0 | 8 | 0 | 60 | 0 | 0 | 0 | 285 | 320 | 216 | 36 | 42 | 39 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 10 | 0 | 0 | 6 | 5641 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.04 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 2.5 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 180 | 0 | 322 | 622 | 0 | 3594.54 | 9235.54 | 89.19
03:00 | 0 | 0 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 12 | 25 | 220 | 0 | 0 | 0 | 0 | 17 | 226 | 0 | 0 | 0 | 1190 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 34 | 0 | 50 | 0 | 0 | 8 | 0 | 54 | 0 | 0 | 0 | 280 | 320 | 216 | 36 | 42 | 39 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 18 | 9 | 10 | 0 | 0 | 0 | 5217 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457.49 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 2.5 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 180 | 0 | 322 | 622 | 0 | 3590.99 | 8807.99 | 89.18
04:00 | 0 | 0 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1116 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 33 | 0 | 50 | 0 | 0 | 8 | 0 | 58 | 0 | 0 | 0 | 290 | 320 | 216 | 36 | 42 | 39 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 5010 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 2.5 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 7 | 100 | 180 | 0 | 323 | 550 | 0 | 3535.26 | 8545.26 | 89.18
05:00 | 0 | 0 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 157 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1054 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 202 | 33 | 0 | 50 | 0 | 0 | 8 | 0 | 60 | 0 | 0 | 0 | 300 | 320 | 216 | 36 | 42 | 39 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 4930 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 350 | 0 | 0 | 2.5 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 320 | 500 | 0 | 3501.65 | 8431.65 | 89.17
06:00 | 0 | 0 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 6 | 20 | 0 | 17 | 16 | 11 | 0 | 0 | 54 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 5 | 49 | 0 | 0 | 19 | 0 | 0 | 0 | 50 | 10 | 0 | 40 | 12 | 25 | 154 | 0 | 0 | 0 | 0 | 15 | 226 | 0 | 0 | 0 | 1052 | 0 | 51 | 3 | 187 | 0 | 0 | 0 | 29 | 183 | 33 | 15 | 50 | 17 | 0 | 8 | 0 | 58 | 0 | 0 | 0 | 295 | 320 | 216 | 36 | 42 | 39 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 22 | 12 | 0 | 0 | 2 | 5192 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.77 | 0 | 0 | 0 | 14 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 350 | 0 | 0 | 2.5 | 0 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 6 | 100 | 180 | 0 | 321 | 500 | 17 | 3778.27 | 8970.27 | 89.17
07:00 | 0 | 25 | 0 | 200 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 35 | 37 | 0 | 48 | 64 | 89 | 0 | 0 | 54 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 2 | 0 | 0 | 19 | 0 | 0 | 35 | 49 | 0 | 0 | 15 | 0 | 0 | 1 | 88 | 50 | 0 | 40 | 54 | 0 | 155 | 24 | 0 | 0 | 1 | 61 | 226 | 0 | 0 | 0 | 1147 | 2 | 51 | 63 | 187 | 0 | 0 | 0 | 29 | 182 | 33 | 62 | 50 | 57 | 0 | 8 | 7 | 56 | 0 | 6 | 0 | 285 | 302 | 216 | 36 | 42 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0.7 | 9 | 56 | 10 | 0 | 3.11 | 3 | 5979.81 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.67 | 0 | 0 | 745.72 | 0 | 0 | 0 | 35 | 0 | 0 | 60 | 0 | 0 | 4 | 0 | 2.83 | 0 | 0 | 0 | 0 | 191 | 0 | 350 | 0 | 0.24 | 2.5 | 0 | 58 | 32 | 1 | 34 | 0 | 0 | 0.2 | 11 | 0.01 | 16 | 307 | 6 | 135 | 220 | 0 | 322 | 520 | 17 | 4002.17 | 9981.98 | 89.16
08:00 | 0 | 52 | 0 | 200 | 0 | 130 | 0 | 0 | 354 | 0 | 0 | 35 | 54 | 0 | 65 | 64 | 95 | 8 | 17 | 54 | 22 | 0 | 450 | 0 | 0 | 0 | 17 | 11 | 280 | 0 | 0 | 9 | 9 | 17 | 19 | 0 | 0 | 35 | 52 | 5 | 0 | 14 | 0 | 0 | 17 | 88 | 24 | 2 | 40 | 91 | 4 | 217 | 17 | 0 | 1 | 12 | 104 | 226 | 0 | 0 | 0 | 1224 | 7 | 51 | 108 | 187 | 0 | 0 | 0 | 29 | 195 | 27 | 113 | 50 | 100 | 0 | 8 | 17 | 52 | 8 | 25 | 0 | 265 | 320 | 216 | 36 | 42 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 17 | 9 | 56 | 5 | 1 | 16.47 | 0 | 6407.47 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.05 | 0 | 0 | 752.41 | 0 | 0 | 0 | 35 | 0 | 0 | 70 | 0 | 0 | 24 | 0 | 15.97 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 1.38 | 5.5 | 0 | 61 | 95 | 7 | 35 | 0 | 0 | 1.1 | 52 | 0.16 | 16 | 307 | 5 | 100 | 220 | 0 | 321 | 580 | 17 | 4115.57 | 10523.04 | 89.16
09:00 | 0 | 52 | 0 | 240 | 0 | 40 | 0 | 0 | 353 | 0 | 0 | 35 | 54 | 0 | 88 | 48 | 60 | 15 | 17 | 54 | 22 | 0 | 450 | 0 | 0 | 0 | 17 | 11 | 280 | 0 | 0 | 16 | 35 | 18 | 15 | 0 | 0 | 35 | 34 | 12 | 0 | 9 | 0 | 0 | 17 | 88 | 24 | 3 | 40 | 107 | 0 | 270 | 17 | 0 | 0 | 17 | 105 | 227 | 0 | 0 | 0 | 1224 | 13 | 51 | 90 | 187 | 0 | 0 | 0 | 29 | 183 | 26 | 68 | 51 | 100 | 0 | 8 | 17 | 54 | 8 | 44 | 0 | 300 | 320 | 216 | 36 | 42 | 40 | 2 | 120 | 16 | 0 | 83 | 30 | 0 | 18 | 0 | 17 | 9 | 56 | 5 | 1 | 28.93 | 3 | 6420.93 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.36 | 0 | 0 | 752 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 50 | 0 | 33.5 | 0 | 0 | 0 | 0 | 204 | 0 | 414 | 0 | 2.78 | 5.5 | 0 | 61 | 75 | 10 | 35 | 0 | 0 | 3.1 | 100 | 0.31 | 16 | 307 | 5 | 100 | 220 | 0 | 361 | 560 | 17 | 4326.55 | 10747.48 | 89.15
10:00 | 0 | 52 | 0 | 278 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 54 | 0 | 88 | 48 | 30 | 0 | 35 | 54 | 25 | 0 | 450 | 0 | 0 | 0 | 17 | 11 | 280 | 0 | 0 | 22 | 35 | 15 | 15 | 0 | 0 | 35 | 51 | 0 | 0 | 10 | 0 | 0 | 0 | 50 | 0 | 4 | 40 | 85 | 0 | 525 | 0 | 0 | 0 | 0 | 68 | 221 | 0 | 0 | 0 | 1224 | 17 | 51 | 40 | 187 | 0 | 0 | 0 | 29 | 190 | 28 | 50 | 50 | 51 | 4 | 8 | 0 | 62 | 0 | 58 | 0 | 300 | 320 | 181 | 33 | 43 | 40 | 2 | 120 | 16 | 0 | 83 | 30 | 0 | 18 | 0 | 0 | 9 | 56 | 5 | 2 | 39.07 | 6 | 6337.07 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.43 | 0 | 0 | 753 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 8 | 69 | 0 | 49.28 | 0 | 0 | 0 | 0 | 204 | 0 | 414 | 0 | 4.15 | 5.5 | 0 | 61 | 45 | 25 | 35 | 0 | 0 | 4.2 | 99 | 0.42 | 16 | 307 | 4 | 100 | 220 | 0 | 371 | 560 | 17 | 4429.98 | 10767.05 | 89.15
11:00 | 0 | 52 | 0 | 265 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35 | 54 | 0 | 88 | 48 | 30 | 0 | 35 | 54 | 25 | 0 | 450 | 0 | 0 | 0 | 17 | 11 | 280 | 0 | 0 | 0 | 35 | 15 | 15 | 0 | 0 | 35 | 52 | 0 | 0 | 9 | 0 | 0 | 0 | 50 | 0 | 4 | 40 | 68 | 0 | 575 | 0 | 0 | 0 | 0 | 68 | 219 | 0 | 0 | 0 | 1224 | 19 | 51 | 40 | 187 | 0 | 0 | 0 | 29 | 210 | 28 | 50 | 50 | 51 | 9 | 8 | 0 | 70 | 0 | 66 | 0 | 310 | 320 | 140 | 35 | 40 | 40 | 2 | 163 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 2 | 45.72 | 6 | 6407.72 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.67 | 0 | 0 | 754 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 8 | 84 | 0 | 57.51 | 0 | 0 | 0 | 0 | 204 | 0 | 414 | 0 | 2.14 | 5.5 | 0 | 61 | 50 | 32 | 35 | 0 | 0 | 5 | 101 | 0.52 | 16 | 307 | 3 | 100 | 220 | 0 | 371 | 560 | 17 | 4478.34 | 10886.06 | 89.14
12:00 | 0 | 52 | 0 | 279 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 98 | 63 | 95 | 0 | 35 | 54 | 30 | 0 | 380 | 0 | 0 | 0 | 0 | 11 | 330 | 0 | 0 | 0 | 35 | 15 | 15 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 34 | 12 | 0 | 89 | 36 | 4 | 40 | 84 | 0 | 575 | 0 | 0 | 0 | 0 | 93 | 219 | 0 | 0 | 0 | 1195 | 20 | 51 | 63 | 184 | 0 | 160 | 0 | 29 | 183 | 28 | 74 | 51 | 81 | 9 | 8 | 0 | 74 | 0 | 69 | 24 | 300 | 320 | 140 | 35 | 40 | 40 | 2 | 163 | 16 | 0 | 84 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 2 | 49.14 | 6 | 6875.14 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.95 | 0 | 0 | 753 | 0 | 0 | 0 | 35 | 5 | 36 | 70 | 0 | 8 | 94 | 0 | 59.51 | 0 | 0 | 0 | 0 | 203 | 0 | 380 | 0 | 0 | 0 | 0 | 61 | 70 | 33 | 35 | 0 | 0 | 5.5 | 100 | 0.53 | 16 | 307 | 5 | 127 | 190 | 0 | 369 | 622 | 17 | 4608.49 | 11483.63 | 89.14
13:00 | 0 | 51 | 0 | 270 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 47 | 54 | 0 | 106 | 63 | 60 | 0 | 17 | 54 | 32 | 0 | 400 | 0 | 0 | 0 | 0 | 11 | 320 | 0 | 0 | 27 | 17 | 15 | 15 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 34 | 33 | 0 | 89 | 12 | 4 | 40 | 110 | 0 | 575 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 19 | 51 | 70 | 182 | 0 | 245 | 0 | 29 | 196 | 35 | 68 | 50 | 100 | 9 | 8 | 0 | 80 | 0 | 68 | 23 | 305 | 320 | 141 | 35 | 40 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 16 | 0 | 0 | 9 | 58 | 0 | 2 | 48.05 | 6 | 7044.05 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.63 | 0 | 0 | 755 | 0 | 0 | 0 | 35 | 5 | 49 | 50 | 0 | 8 | 87 | 0 | 60.06 | 0 | 0 | 0 | 0 | 201 | 0 | 414 | 0 | 5.26 | 5.5 | 0 | 60 | 35 | 32 | 35 | 0 | 0 | 5.6 | 100 | 0.52 | 16 | 307 | 5 | 127 | 220 | 0 | 370 | 622 | 17 | 4628.57 | 11672.62 | 89.13
14:00 | 0 | 51 | 0 | 10 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 0 | 106 | 63 | 30 | 0 | 17 | 54 | 32 | 0 | 420 | 0 | 0 | 0 | 0 | 11 | 314 | 0 | 0 | 24 | 0 | 0 | 15 | 0 | 0 | 35 | 52 | 0 | 0 | 6 | 34 | 40 | 0 | 89 | 36 | 3 | 40 | 110 | 0 | 575 | 0 | 0 | 0 | 0 | 105 | 216 | 0 | 0 | 0 | 1224 | 17 | 51 | 78 | 182 | 0 | 0 | 0 | 29 | 210 | 36 | 76 | 51 | 110 | 9 | 6 | 0 | 82 | 0 | 56 | 31 | 305 | 320 | 281 | 35 | 40 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 16 | 0 | 0 | 19 | 57 | 0 | 2 | 43.65 | 6 | 6709.65 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.88 | 0 | 0 | 755 | 0 | 0 | 0 | 35 | 5 | 49 | 90 | 0 | 0 | 66 | 0 | 50.55 | 0 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 4.6 | 5.5 | 0 | 61 | 35 | 29 | 35 | 0 | 0 | 4.6 | 89 | 0.44 | 16 | 307 | 5 | 127 | 220 | 0 | 371 | 622 | 17 | 4601.57 | 11311.22 | 89.13
15:00 | 0 | 51 | 0 | 110 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 54 | 0 | 106 | 62 | 88 | 0 | 17 | 54 | 32 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 316 | 0 | 0 | 18 | 0 | 15 | 20 | 0 | 0 | 35 | 52 | 0 | 0 | 9 | 34 | 40 | 17 | 89 | 62 | 3 | 40 | 110 | 0 | 550 | 17 | 0 | 0 | 0 | 105 | 216 | 0 | 0 | 0 | 1224 | 13 | 51 | 50 | 184 | 0 | 0 | 0 | 29 | 183 | 36 | 105 | 50 | 100 | 9 | 6 | 0 | 80 | 0 | 44 | 31 | 310 | 320 | 141 | 34 | 40 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 16 | 0 | 0 | 9 | 57 | 0 | 2 | 33.22 | 6 | 6740.22 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.56 | 0 | 0 | 754.83 | 0 | 0 | 0 | 35 | 4 | 49 | 50 | 0 | 0 | 50 | 0 | 40.08 | 0 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 3.41 | 5.5 | 0 | 61 | 70 | 22 | 35 | 0 | 0 | 3.5 | 103 | 0.33 | 16 | 307 | 5 | 127 | 220 | 0 | 370 | 622 | 17 | 4555.21 | 11295.43 | 89.12
16:00 | 0 | 51 | 0 | 175 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 54 | 0 | 97 | 30 | 110 | 0 | 17 | 54 | 32 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 314 | 0 | 0 | 10 | 0 | 15 | 20 | 0 | 0 | 17 | 15 | 0 | 0 | 8 | 34 | 40 | 17 | 50 | 24 | 1 | 40 | 51 | 0 | 547 | 17 | 0 | 19 | 0 | 51 | 217 | 0 | 0 | 0 | 1224 | 9 | 51 | 50 | 185 | 0 | 0 | 0 | 29 | 183 | 36 | 68 | 50 | 68 | 9 | 7 | 0 | 74 | 0 | 24 | 31 | 300 | 320 | 281 | 31 | 40 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 16 | 0 | 0 | 9 | 57 | 0 | 1 | 18.72 | 6 | 6541.72 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.13 | 0 | 0 | 751.68 | 0 | 0 | 0 | 50 | 4 | 49 | 35 | 0 | 0 | 30 | 30 | 22.75 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 1.97 | 5.5 | 0 | 62 | 35 | 11 | 35 | 0 | 0 | 1.1 | 68 | 0.2 | 32 | 307 | 5 | 127 | 220 | 0 | 372 | 610 | 17 | 4442.33 | 10984.05 | 89.12
17:00 | 0 | 51 | 8 | 111 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 106 | 30 | 110 | 4 | 17 | 90 | 32 | 0 | 380 | 0 | 0 | 0 | 10 | 11 | 324 | 0 | 0 | 3 | 0 | 15 | 20 | 0 | 0 | 17 | 15 | 2 | 0 | 14 | 34 | 40 | 17 | 50 | 24 | 0 | 40 | 51 | 0 | 550 | 17 | 0 | 19 | 1 | 51 | 218 | 0 | 0 | 0 | 1224 | 3 | 51 | 50 | 192 | 0 | 0 | 0 | 29 | 182 | 34 | 68 | 50 | 68 | 10 | 7 | 34 | 70 | 10 | 7 | 24 | 305 | 320 | 281 | 31 | 40 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 16 | 0 | 11 | 9 | 57 | 0 | 0 | 6.05 | 6 | 6461.05 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.96 | 0 | 0 | 756.21 | 0 | 0 | 0 | 58 | 5 | 65 | 35 | 0 | 0 | 10 | 30 | 6.52 | 0 | 0 | 0 | 0 | 188 | 0 | 350 | 0 | 0.54 | 5.5 | 0 | 61 | 35 | 4 | 35 | 0 | 0 | 0.7 | 13 | 0.6 | 32 | 307 | 5 | 127 | 180 | 0 | 371 | 600 | 17 | 4234.03 | 10695.08 | 89.11
18:00 | 0 | 69 | 8 | 110 | 0 | 100 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 106 | 75 | 145 | 22 | 17 | 115 | 32 | 0 | 400 | 0 | 0 | 0 | 35 | 11 | 300 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 17 | 16 | 24 | 0 | 1 | 49 | 60 | 17 | 56 | 60 | 0 | 40 | 51 | 7 | 550 | 53 | 0 | 19 | 20 | 75 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 73 | 195 | 0 | 0 | 0 | 29 | 193 | 36 | 71 | 50 | 88 | 28 | 8 | 34 | 76 | 20 | 0 | 24 | 320 | 320 | 281 | 31 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 16 | 0 | 36 | 9 | 57 | 0 | 0 | 0 | 6 | 7059 | 925 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 755.71 | 0 | 52 | 0 | 108 | 10 | 90 | 70 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 0 | 0 | 5.5 | 0 | 61 | 65 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 64 | 292 | 7 | 100 | 220 | 0 | 370 | 540 | 54 | 4509.21 | 11568.21 | 89.11
19:00 | 0 | 69 | 26 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 35 | 54 | 0 | 122 | 95 | 195 | 40 | 48 | 162 | 32 | 0 | 450 | 0 | 0 | 0 | 55 | 11 | 325 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 32 | 82 | 23 | 0 | 1 | 84 | 70 | 35 | 76 | 50 | 0 | 40 | 87 | 15 | 550 | 72 | 0 | 20 | 8 | 102 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 195 | 0 | 0 | 0 | 29 | 182 | 36 | 107 | 50 | 136 | 27 | 8 | 47 | 76 | 8 | 0 | 0 | 280 | 320 | 281 | 35 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 54.3 | 9 | 57 | 0 | 0 | 0 | 6 | 7693.3 | 879 | 0 | 0 | 41 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.38 | 0 | 53 | 0 | 113 | 9 | 90 | 113 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 414 | 0 | 0 | 5.5 | 0 | 61 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 7 | 127 | 220 | 0 | 369 | 530 | 72 | 4642.88 | 12336.18 | 89.1
19:30 | 0 | 69 | 26 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 35 | 54 | 0 | 114 | 110 | 145 | 15 | 55 | 162 | 32 | 0 | 450 | 0 | 0 | 0 | 55 | 11 | 325 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 35 | 85 | 12 | 0 | 0 | 84 | 72 | 35 | 76 | 12 | 0 | 40 | 87 | 18 | 550 | 17 | 0 | 12 | 8 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 195 | 0 | 0 | 0 | 29 | 183 | 36 | 115 | 50 | 136 | 27 | 8 | 20 | 74 | 8 | 0 | 0 | 285 | 320 | 281 | 35 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 17 | 9 | 57 | 0 | 0 | 0 | 6 | 7428 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.76 | 0 | 50 | 0 | 113 | 9 | 90 | 50 | 34 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 414 | 0 | 0 | 5.5 | 0 | 61 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 7 | 127 | 220 | 0 | 370 | 600 | 72 | 4592.26 | 12020.26
20:00 | 0 | 69 | 26 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 35 | 35 | 0 | 116 | 80 | 95 | 0 | 55 | 162 | 32 | 0 | 450 | 0 | 0 | 0 | 55 | 11 | 330 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 35 | 85 | 0 | 0 | 0 | 51 | 32 | 0 | 76 | 12 | 0 | 40 | 110 | 22 | 551 | 17 | 0 | 12 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 197 | 0 | 0 | 0 | 29 | 183 | 36 | 115 | 50 | 136 | 29 | 8 | 34 | 72 | 0 | 0 | 0 | 285 | 320 | 281 | 35 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 17 | 9 | 58 | 0 | 0 | 0 | 5 | 7229 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.82 | 0 | 50 | 0 | 113 | 9 | 90 | 50 | 36 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 414 | 0 | 0 | 5.5 | 0 | 59 | 86 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 7 | 127 | 220 | 0 | 371 | 600 | 72 | 4574.32 | 11803.32 | 89.1
21:00 | 0 | 69 | 26 | 0 | 0 | 230 | 0 | 0 | 403 | 0 | 0 | 17 | 35 | 0 | 114 | 80 | 95 | 0 | 0 | 54 | 32 | 0 | 450 | 0 | 0 | 0 | 35 | 11 | 329 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 35 | 88 | 0 | 0 | 0 | 34 | 32 | 0 | 86 | 12 | 0 | 40 | 110 | 18 | 551 | 0 | 0 | 12 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 195 | 0 | 0 | 0 | 29 | 190 | 36 | 115 | 50 | 136 | 29 | 8 | 0 | 72 | 0 | 0 | 0 | 315 | 320 | 281 | 35 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 17 | 9 | 58 | 0 | 0 | 0 | 0 | 6997 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.04 | 0 | 41 | 0 | 113 | 4 | 90 | 50 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 414 | 0 | 0 | 5.5 | 0 | 61 | 95 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 8 | 127 | 220 | 0 | 371 | 622 | 72 | 4606.54 | 11603.54 | 89.09
22:00 | 0 | 68 | 26 | 0 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 0 | 94 | 48 | 45 | 0 | 0 | 54 | 32 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 328 | 0 | 0 | 0 | 25 | 15 | 19 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 0 | 32 | 0 | 87 | 12 | 0 | 40 | 110 | 24 | 488 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 195 | 0 | 0 | 0 | 29 | 200 | 36 | 115 | 51 | 100 | 29 | 8 | 0 | 66 | 0 | 0 | 0 | 315 | 320 | 281 | 35 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 6680 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.63 | 0 | 41 | 0 | 113 | 4 | 90 | 50 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 414 | 0 | 0 | 2.5 | 0 | 62 | 95 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 8 | 127 | 220 | 0 | 369 | 622 | 17 | 4556.13 | 11236.13 | 89.09
23:00 | 0 | 68 | 26 | 40 | 0 | 230 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 0 | 86 | 32 | 0 | 0 | 0 | 54 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 280 | 0 | 0 | 0 | 35 | 15 | 19 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 0 | 31 | 0 | 76 | 0 | 0 | 40 | 110 | 29 | 486 | 0 | 0 | 0 | 0 | 105 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 197 | 0 | 0 | 0 | 29 | 182 | 36 | 115 | 51 | 100 | 29 | 8 | 0 | 70 | 0 | 0 | 0 | 305 | 320 | 281 | 35 | 43 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 6518 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762.83 | 0 | 0 | 0 | 113 | 0 | 91 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 414 | 0 | 0 | 2.5 | 0 | 62 | 72 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 8 | 100 | 220 | 0 | 369 | 622 | 17 | 4399.33 | 10917.33 | 89.08
Total KWH | 0 | 997440 | 161760 | 3620100 | 0 | 2434531 | 0 | 0 | 9579600 | 0 | 0 | 648000 | 1069920 | 0 | 1888560 | 998400 | 1494916 | 111469 | 336799 | 1346400 | 617400 | 0 | 10170000 | 0 | 0 | 0 | 265323 | 282500 | 7580594 | 0 | 0 | 121104 | 173880 | 279600 | 424800 | 0 | 0 | 615982 | 960982 | 81600 | 0 | 219840 | 446014 | 454944 | 171395 | 1608960 | 451200 | 28438 | 964800 | 1979664 | 300000 | 9658181.82 | 260945 | 0 | 113760 | 84684.6 | 2008945 | 5242792 | 0 | 0 | 0 | 28418179 | 138510 | 1160482 | 1505454 | 4566545 | 0 | 350200 | 14000 | 698880 | 4687000 | 803592 | 1780800 | 1197820 | 2187360 | 257040 | 197440 | 188100 | 1560000 | 84043 | 467945 | 197248 | 7269500 | 7671800 | 5659000 | 824256 | 995000 | 938400 | 53424 | 3571691 | 372336 | 0 | 2061120 | 718848 | 0 | 420000 | 0 | 210240 | 265200 | 1084800 | 85440 | 14350 | 330090 | 90480 | 153352836.42 | 22177454 | 0 | 0 | 40320 | 6784 | 0 | 0 | 0 | 0 | 0 | 0 | 533520 | 0 | 0 | 0 | 0 | 239052 | 0 | 1499616 | 75553 | 899888 | 1026144 | 73614 | 64584 | 586580 | 196161 | 402000 | 0 | 0 | 0 | 0 | 4831936 | 0 | 9909236 | 0 | 31500 | 95940 | 0 | 1425163 | 1054148 | 206800 | 953116 | 0 | 0 | 31548.9 | 845280 | 3558 | 511872 | 0 | 147258 | 2701000 | 5220310 | 0 | 8457336 | 14168727.27 | 517200 | 78933199.17 | 232286035.59

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-02-2025 | during | 28-02-2025 | during | 28-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 230 | 230 | 230 | 130 | 130 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 279 | 0 | 270 | 270 | 110 | 110 | Reliable test run by OEM
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 325 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 63 | 95 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 48 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 15 | 15 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 19 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 32 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 11 | 11 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 26 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 98 | 122 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 69 | 105 | 105 | 50 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 35 | 0 | 0 | 0 | 150 | 150 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 1982 | 2385 | 5092.91 | 5060.91 | 2916.24 | 2884.24
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 20 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 222 | 219 | 219 | 219 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 93 | 102 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 12 | 70 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 34 | 84 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 89 | 76 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 15 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 23 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.29 | 0 | 4.26 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 82 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 84 | 87 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 32 | 116 | 116 | 116 | 116 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 72 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1195 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 1 | 15 | 22 | 15 | 22 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 575 | 550 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2488 | 2793 | 3494.15 | 3502.86 | 3494.12 | 3502.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 160 | 0 | 250 | 250 | 0 | 0 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 28 | 36 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 184 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 63 | 123 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 24 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 81 | 136 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 76 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 8 | 10.42 | 10.42 | 8 | 8 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 47 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 27 | 9 | 9 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 74 | 107 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1088 | 1075 | 1869.56 | 1804.56 | 1479.2 | 1414.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-02-2025 | during | 28-02-2025 | during | 28-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 21 | 21 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 57 | 200 | 200 | 56 | 56 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.14 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 54.3 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 129.14 | 126.3 | 653.6 | 601.5 | 320.6 | 268.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 43 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 35 | 35 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 140 | 281 | 280 | 280 | 280 | 280 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1188 | 1314 | 1387.5 | 1387.5 | 1349 | 1349
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 925 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 41 | 40 | 40 | 40 | 40 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 11 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81.95 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1006.95 | 931 | 2963.1 | 2883.1 | 1160.02 | 1080.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 369 | 369 | 450 | 450 | 400 | 400 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 64 | 16 | 110 | 16 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 127 | 127 | 134 | 134 | 135 | 135 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 530 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 190 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 72 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1653.53 | 1696 | 1910.12 | 2003.12 | 1861.12 | 1954.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 53 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 5 | 9 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 0 | 214 | 214 | 0.01 | 0.01 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 203 | 184 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 380 | 414 | 413.79 | 413.79 | 400 | 400 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 36 | 90 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 0 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 753 | 755.38 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.51 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1643.51 | 1801.88 | 2582.84 | 2412.24 | 2064.07 | 1893.47
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 61 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 78 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 75 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 100 | 0 | 100 | 0 | 100 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 304.5 | 214 | 457.6 | 322 | 423.62 | 288.02
System Total |  |  |  |  | 29204.66 | 28470.742 | 11483.63 | 12336.18 | 20411.38 | 19977.79 | 15067.99 | 14634.43
Forecast Scenario (28-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10200 |  | 0 |  | 10200
|  |  |  | 1:00 | 9800 |  | 0 |  | 9800
|  |  |  | 2:00 | 9400 |  | 0 |  | 9400
|  |  |  | 3:00 | 9000 |  | 0 |  | 9000
|  |  |  | 4:00 | 8700 |  | 0 |  | 8700
|  |  |  | 5:00 | 8700 |  | 0 |  | 8700
|  |  |  | 6:00 | 8958 |  | 0 |  | 8958
|  |  |  | 7:00 | 9422 |  | 0 |  | 9422
|  |  |  | 8:00 | 9834 |  | 0 |  | 9834
|  |  |  | 9:00 | 9909 |  | 0 |  | 9909
|  |  |  | 10:00 | 9824 |  | 0 |  | 9824
|  |  |  | 11:00 | 10028 |  | 0 |  | 10028
|  |  |  | 12:00 | 10483 |  | 0 |  | 10483
|  |  |  | 13:00 | 10940 |  | 0 |  | 10940
|  |  |  | 14:00 | 9850 |  | 0 |  | 9850
|  |  |  | 15:00 | 9337 |  | 0 |  | 9337
|  |  |  | 16:00 | 9135 |  | 0 |  | 9135
|  |  |  | 17:00 | 9060 |  | 0 |  | 9060
|  |  |  | 18:00 | 9719 |  | 0 |  | 9719
|  |  |  | 18:30 | 10300 |  | 0 |  | 10300
|  |  |  | 19:00 | 10870 |  | 0 |  | 10870
|  |  |  | 19:30 | 10736 |  | 0 |  | 10736
|  |  |  | 20:00 | 10713 |  | 0 |  | 10713
|  |  |  | 21:00 | 10712 |  | 0 |  | 10712
|  |  |  | 22:00 | 10495 |  | 0 |  | 10495
|  |  |  | 23:00 | 10092 |  | 0 |  | 10092
Probable Maximum Temperature: |  |  | 30.60°C
Probable Maximum Demand at Day Peak: |  |  | 10483.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10870.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10870.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 235.181 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:20 hrs on 28-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11483.63 | MW | 12:00 Hr. | Energy Generated |  |  | 256.0449 |  | MKWHr.
| Day Peak Demand |  |  | 11567.63 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.641 |  | MKWHr.
| Evening Peak Generation |  |  | 12336.18 | MW | 19:00 Hr. | Energy Demand |  |  | 257.6859 |  | MKWHr.
| Evening Peak Demand |  |  | 12460.18 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30.5 |  | °C
| Minimum Generation of the Day |  |  | 8431.65 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 838.22 |  | MMCFD
| Maximum Generation of the Day |  |  | 12336.18 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.6199 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.9891 | 0 | 9.4929 | 0 | 0 | 0.1211 | 0 | 0 | 44.6031 | Gas | 107.7544 | Gas | 392667750.28
| Chattogram Zone |  |  | 5.5428 | 38.0764 | 9.2391 | 0 | 0.9648 | 0.16695 | 0 | 0.21984 | 54.2098 | Coal | 69.1966 | Coal | 418494329.2392
| Cumilla Zone |  |  | 13.676 | 0 | 6.2 | 0 | 0 | 0.46794 | 1.56 | 0 | 21.9039 | HFO | 33.7408 | HFO | 615066795.302
| Mymensingh Zone |  |  | 0.08544 | 0 | 1.6507 | 0 | 0 | 0.34444 | 0 | 0 | 2.0806 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.5554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5554 | Hydro | 0.9648 | Hydro | 96480
| Khulna Zone |  |  | 0 | 0 | 0.047104 | 0 | 0 | 0.53352 | 22.1775 | 0 | 22.7581 | Solar | 3.7412 | Solar | 60073005.374
| Barishal Zone |  |  | 8.0686 | 29.6951 | 1.0291 | 0 | 0 | 0.003558 | 0 | 0 | 38.7963 | Import | 40.4274 | Import | 205382246.23
| Rajshahi Zone |  |  | 14.8371 | 0 | 4.0746 | 0 | 0 | 1.0201 | 16.6899 | 0 | 36.6217 | Wind | 0.21984 | Wind | 3218457.6
| Rangpur Zone |  |  | 0 | 1.4252 | 2.0073 | 0 | 0 | 1.0836 | 0 | 0 | 4.5161
| Total |  |  | 107.7544 | 69.1966 | 33.7408 | 0 | 0.9648 | 3.7412 | 40.4274 | 0.21984 | 256.0449
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 392667750.28 |  | Hydro | 96480
|  |  |  | Coal | 418494329.2392 |  | Solar | 60073005.374
|  |  |  | HFO | 615066795.302 |  | Import | 205382246.23
|  |  |  | HSD | 0 |  | Wind | 3218457.6
[5 empty] | Total: | 169,49,99,064 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1775 | Peak Hr Flow | 879.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6579454 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.6899 | Peak Hr Flow | 755.38 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 300 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.56 | Peak Hr Flow | 76.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 580 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.4274 | Peak Hr Flow | 1710.38 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 30 |  | 4606
|  |  |  | Chattogram |  | 0 |  | 1248
|  |  |  | Cumilla |  | 0 |  | 1035
|  |  |  | Mymensingh |  | 89 |  | 974
|  |  |  | Sylhet |  | 0 |  | 421
|  |  |  | Khulna |  | 0 |  | 1337
|  |  |  | Barishal |  | 0 |  | 324
|  |  |  | Rajshahi |  | 0 |  | 1189
|  |  |  | Rangpur |  | 0 |  | 793
|  |  |  | Total |  | 119 |  | 11927
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 944.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1736.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 16:59 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Tr-03 &Tr-04 Section Isolator | [7 empty] | 12.0MW load
|  |  | Maintenance Work. | [7 empty] | interrup.
| 08:20 | 16:59 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Tr-03 &Tr-04 Section Isolator | [7 empty] | 12.0MW load
|  |  | Maintenance Work. | [7 empty] | interrup.
| 08:39 | 18:11 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Tower painting work, Mirpur grid works on that line
| 08:56 |  | Bogura 132/33kV S/S 132KV Bus-B Project Work S/D Due to Shutdown taken for T-2
transformer B-bus isolator change.
| 09:07 | 10:28 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to Auxiliary Transformer-2 corrective | [7 empty] | 30.0MW load
|  |  | maintenance work. Shutdown taken by PBS. | [7 empty] | interrup.
| 09:08 | 10:28 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to Auxiliary Transformer-2 corrective | [7 empty] | 30.0MW load
|  |  | maintenance work. Shutdown taken by PBS. | [7 empty] | interrup.
| 09:14 |  | Jashore 132/33kV S/S T-1 LT Forced S/D Due to Oil centrifuse
| 09:16 |  | Jashore 132/33kV S/S T-1 HT Forced S/D Due to Oil centrifuse
| 09:16 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 09:52 | 13:14 | Khagrachori 132/33kV S/S TR-1 LT Scheduled S/D Due to Protection Relay test.
| 09:54 | 13:13 | Khagrachori 132/33kV S/S TR-1 HT Scheduled S/D Due to Protection Relay test.
|  | 09:57 | Bogura 132/33kV S/S Transformer-4 LT is restored.
|  | 09:57 | Bogura 132/33kV S/S Transformer-4 HT is restored.
| 10:00 | 16:29 | Rahanpur 400/132kV S/S AT-02 LT Project Work S/D
| 10:01 | 16:29 | Rahanpur 400/132kV S/S AT-02 HT Project Work S/D
| 10:04 | 12:32 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Interlock work
| 10:12 | 14:23 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Scheduled S/D
| 10:48 | 12:14 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to PBS 33kv MIEZ feeder corrective | [7 empty] | 30.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 10:48 | 12:14 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to PBS 33kv MIEZ feeder corrective | [7 empty] | 30.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 11:09 |  | Kallyanpur 132/33kV S/S GT-1 (132kV) LT Scheduled S/D Due to Oil Centrifuging Work.
| 11:09 |  | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to Oil Centrifuging Work.
| 11:32 | 17:08 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Interlock work
| 11:34 | 17:08 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Interlock work
| 11:56 | 12:41 | Ullahpara 132/33kV S/S Power Transformer -1 LT Scheduled S/D Due to Replacing Energy
Meter of TR-1
| 11:57 | 12:39 | Ullahpara 132/33kV S/S Power Transformer -1 HT Scheduled S/D Due to Replacing Energy
Meter of TR-1
|  | 12:44 | Rampur 230/132/33 S/S Halishahar-1 is restored.
|  | 12:44 | Rampur 230/132/33 S/S Halishahar-2 is restored.
|  | 12:58 | Halishahar-Khulshi 132kV Ckt-1 is restored.
| 13:03 | 13:33 | Ullahpara 132/33kV S/S Power Transformer-2 LT Scheduled S/D Due to Replacing Energy Meter
of TR-2
| 13:04 | 13:31 | Ullahpara 132/33kV S/S Power Transformer-2 HT Scheduled S/D Due to Replacing Energy Meter
of TR-2
| 13:15 | 16:09 | Khagrachori 132/33kV S/S TR-2 LT Scheduled S/D Due to Protection relay test.
| 13:16 | 16:07 | Khagrachori 132/33kV S/S TR-2 HT Scheduled S/D Due to Protection relay test.
| 13:44 | 15:00 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to 33 kv Bus -2 (Feeder-6) Red hot | [7 empty] | 12.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 13:50 | 15:00 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to 33 kv Bus -2 (Feeder-6) Red hot | [7 empty] | 12.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 14:23 |  | Ashuganj 450 MW CCPP(South), FGMO is OFF with remarks:-
| 14:25 |  | Ashuganj 450 MW CCPP(South) GT Shutdown with remarks:- Generator EE @TE Vibration
|  | 14:58 | Sylhet 132/33kV S/S Sylhet-90MW P/S is restored.
| 15:08 | 16:23 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Forced S/D Due to removal a kite
|  | 16:37 | Hathazari 230/132/33kV S/S T-02 HT is restored.
|  | 16:37 | Hathazari 230/132/33kV S/S T-02 LT is restored.
|  | 17:40 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt is restored.
|  | 17:42 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 17:44 | Naogaon 132/33kV S/S T-3 LT is restored.
| 17:54 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 23:07 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 23:23 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 00:07 |  | Meghnaghat CCPP(Summit)-2 GT Ready with remarks:- None
| 00:08 |  | Meghnaghat CCPP(Summit)-2 ST Ready with remarks:- None
| 05:00 |  | Minimum Generation is 8654 MW
| 06:01 |  | BIPTC S/S 21T01 HT Scheduled S/D Due to Emergency replacement of failed oil cooling pump
of L-2 phase converter transformer of block-01
| 06:01 |  | BIPTC S/S 21T01 LT Scheduled S/D Due to Emergency replacement of failed oil cooling pump
of L-2 phase converter transformer of block-01
| 06:01 |  | BIPTC S/S 11T01 HT Scheduled S/D Due to Emergency replacement of failed oil cooling pump
of L-2 phase converter transformer of block-01
| 06:01 |  | BIPTC S/S 11T01 LT Scheduled S/D Due to Emergency replacement of failed oil cooling pump
of L-2 phase converter transformer of block-01
| 06:41 | 07:45 | Tongi 230/132/33kV S/S T-02 LT Scheduled S/D Due to Bus-1 conductor replacement work
| 06:41 | 07:45 | Tongi 230/132/33kV S/S T-02 HT Scheduled S/D Due to Bus-1 conductor replacement work
| 06:42 |  | Rampura 230/132kV S/S Auto Transformer - 04 HT Project Work S/D Due to G2G Project work
| 06:42 |  | Rampura 230/132kV S/S Auto Transformer - 04 LT Project Work S/D Due to G2G Project work
| 06:43 |  | Rampura 230/132kV S/S NLDC Trafo HT Project Work S/D Due to G2G Project work
| 06:44 |  | Rampura 230/132kV S/S NLDC Trafo LT Project Work S/D Due to G2G Project work
| 06:58 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D Due to 33 kV bus maintenance. | [7 empty] | 35.0MW load
interrup.
| 06:58 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D Due to 33kV bus maintenance | [7 empty] | 35.0MW load
interrup.
| 06:59 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Scheduled S/D Due to 33kV bus maintenance | [7 empty] | 35.0MW load
interrup.
| 06:59 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Scheduled S/D Due to 33kV bus maintenance | [7 empty] | 35.0MW load
interrup.
| 07:10 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Red hot repair | [7 empty] | 5.0MW load
interrup.
| 07:10 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Red hot repair | [7 empty] | 20.5MW load
interrup.
| 07:11 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Red hot repair | [7 empty] | 5.0MW load
interrup.
| 07:11 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Red hot repair | [7 empty] | 20.5MW load
interrup.
| 07:25 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Project Work S/D from Ishurdi 230/132kV end. and from
Ghorashal 230kV end Due to 400kV Stringing purpose work Ghorashal to purbachal.
| 07:25 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Project Work S/D from Ishurdi 230/132kV end. and from
Ghorashal 230kV end Due to 400kV Stringing purpose work Ghorashal to purbachal.
| 07:35 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to 33 Bus Maintenace | [7 empty] | 27.0MW load
interrup.
| 07:46 |  | Mohathanghar 33kv bus S/D. | [7 empty] | 50MW load interrup.
| 07:46 |  | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to 33 Bus Maintenace | [7 empty] | 27.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 230 | 2434531 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 3620100 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 9579600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10170000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 111469 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7580594 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 648000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 95 | 998400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 48 | 336799 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 265323 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 279600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 424800 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 617400 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 11 | 282500 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 26 | 161760 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1494916 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 122 | 1888560 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 69 | 997440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1346400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 121104 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1069920 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 173880 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2385 | 44603096
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 84684.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138510 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 113760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5242792 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 102 | 2008945 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 70 | 454944 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 84 | 446014 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1608960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 300000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 23 | 81600 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 28438 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 82 | 960982 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 35 | 171395 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 87 | 1979664 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 451200 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 32 | 615982 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 72 | 260945 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28418179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 219840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 550 | 9658181.82 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2793 | 54209816.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4687000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 350200 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 14000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 803592 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 698880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4566545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1160482 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 1505454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 197248 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1197820 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2187360 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1560000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 84043 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 197440 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 47 | 188100 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 257040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 107 | 1780800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 467945 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1075 | 21903949
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 85440 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 57 | 1084800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 265200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 330090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 90480 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.3 | 210240 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 126.3 | 2080600
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 43 | 995000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 938400 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3571691 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 824256 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 53424 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718848 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2061120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 372336 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7269500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 281 | 5659000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7671800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1314 | 30555375
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 22177454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 41 | 40320 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 11 | 6784 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 533520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 931 | 22758078
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 369 | 8457336 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 511872 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 147258 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 127 | 2701000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 14168727.27 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5220310 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 517200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7069000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3558 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1696 | 38796261.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 53 | 239052 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 9 | 75553 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 73614 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 184 | 4831936 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9909236 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 196161 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 95940 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 64584 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 899888 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1499616 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1026144 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755.38 | 16689913 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 402000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 586580 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1801.88 | 36621717
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 61 | 1425163 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 953116 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31548.9 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 75 | 1054148 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206800 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 845280 | -
Rangpur Area Total |  |  |  |  | 950 | 214 | 4516055.9
Eastern Grid Total |  |  |  |  | 16856.242 | 7693.3 | 153352836.42
Western Grid Total |  |  |  |  | 11614.5 | 4642.88 | 102692112.17
National Grid Total |  |  |  |  | 28470.742 | 12336.18 | 256044948.59
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8164.54 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3643.2 | MW
i) Dhaka area |  |  | 4575.54 |  | MW | i) Khulna area |  |  |  | 1337.2 | MW
ii) Chattogram area |  |  | 1248 |  | MW | ii) Barishal area |  |  |  | 324.2 | MW
iii) Cumilla area |  |  | 1035 |  | MW | iii) Rajshahi area |  |  |  | 1188.8 | MW
iv) Mymensingh area |  |  | 885 |  | MW | iv) Rangpur area |  |  |  | 793 | MW
v) Sylhet area |  |  | 421 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11807.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 18:30 | 133 | Payra | 22 | 19:00
2 | AKSML | 23 | 13:00 | 68 | Jamalpur | 91 | 08:00 | 134 | Postogola | 45 | 13:00
3 | Aftabnagar | 28 | 12:00 | 69 | Jashore | 96 | 13:00 | 135 | Purbachal | 10 | 13:00
4 | Agargaon | 88 | 13:00 | 70 | Jhenaidah | 101 | 18:30 | 136 | Purbasadipur | 115 | 12:00
5 | Agrabad | 78 | 18:30 | 71 | Joydebpur | 164 | 18:30 | 137 | Rahanpur | 11.5 | 09:00
6 | Amnura | 49 | 08:00 | 72 | Joypurhat | 70 | 08:00 | 138 | Rahim | 38 | 17:00
7 | Ashuganj | 104 | 19:00 | 73 | Juldah | 11 | 18:00 | 139 | Rajbari | 56 | 19:00
8 | BSRM | 195 | 22:00 | 74 | KSRM | 30 | 01:00 | 140 | Rajendrapur | 114 | 19:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 192 | 14:00 | 141 | Rajshahi | 88 | 19:00
10 | Bajitpur | 37 | 19:30 | 76 | Kachua | 61 | 18:30 | 142 | Rajshahi-230 | 60 | 13:00
11 | Bakulia | 79 | 18:30 | 77 | Kallyanpur | 80 | 18:00 | 143 | Ramganj | 100 | 18:30
12 | Banani | 24 | 11:00 | 78 | Kalurghat | 36 | 15:00 | 144 | Rampur | 36 | 12:00
13 | Bangabhaban | 11 | 12:00 | 79 | Kamrangirchar | 63.2 | 13:00 | 145 | Rangamati | 13 | 18:00
14 | Barapukuria | 57 | 08:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 111 | 13:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 88 | 18:30 | 147 | Ruppur | 5.6 | 11:00
16 | Barishal | 85 | 13:00 | 82 | Keranigonj | 60 | 18:00 | 148 | SSM | 15 | 06:00
17 | Barishal-230 | 56 | 21:00 | 83 | Khagrachori | 26 | 18:00 | 149 | Saidpur | 110 | 11:00
18 | Baroaulia | 60 | 13:00 | 84 | Khosba | 25 | 19:00 | 150 | Satkhira | 101 | 08:00
19 | Baroirhat | 60 | 18:00 | 85 | Khulna | 65 | 13:00 | 151 | Satmasjid | 86 | 13:00
20 | Bashundhara | 155 | 13:00 | 86 | Khulshi | 158 | 19:00 | 152 | Savar | 180 | 18:30
21 | BashundharaCement | 8 | 12:00 | 87 | Kishoreganj | 113 | 18:30 | 153 | SevenRings | 19.19 | 22:00
22 | Beanibazar | 46 | 18:30 | 88 | Kodda | 267 | 09:00 | 154 | ShahCement | 39 | 12:00
23 | Benapole | 62 | 13:00 | 89 | Kulaura | 30 | 18:30 | 155 | Shahjadpur | 73 | 09:00
24 | Bhaluka | 112 | 12:00 | 90 | Kurigram | 56 | 18:30 | 156 | Shahjibazar | 98 | 00:00
25 | Bhandaria | 50 | 19:30 | 91 | Kushtia | 112 | 13:00 | 157 | Shahmirpur | 39 | 18:00
26 | Bhangura | 35 | 08:00 | 92 | Lalbag | 76 | 13:00 | 158 | Shariatpur | 56 | 21:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | Lalmonirhat | 49 | 18:30 | 159 | Sherpur | 116 | 19:30
28 | Bhulta | 270 | 11:00 | 94 | MI_Cement | 17 | 15:00 | 160 | Shikalbaha | 21 | 11:00
29 | Bog-Sherpur | 72 | 08:00 | 95 | Madanganj | 43 | 13:00 | 161 | Shitalakhya | 68.7 | 13:00
30 | Bogura | 125 | 18:30 | 96 | Madaripur | 77 | 18:30 | 162 | Sholosohor | 37 | 19:00
31 | Borhanuddin | 57 | 21:00 | 97 | Madartek | 67.01 | 19:00 | 163 | Shyampur | 172 | 12:00
32 | Brahmanbaria | 92 | 18:00 | 98 | Madunaghat | 43 | 18:30 | 164 | Siddhirganj | 106 | 14:00
33 | Cantonment | 106 | 13:00 | 99 | Magura | 49 | 18:30 | 165 | Sirajganj | 96 | 07:00
34 | Chandpur | 48 | 18:00 | 100 | Mahasthangarh | 64 | 08:00 | 166 | Sonargaon | 83 | 01:00
35 | Chandraghona | 28 | 18:30 | 101 | Manikganj | 117 | 18:30 | 167 | Sreemongol | 54 | 19:00
36 | Chapai | 64 | 09:00 | 102 | Maniknagar | 60 | 12:00 | 168 | Sreepur | 82 | 17:00
37 | Charsaidpur | 42 | 12:00 | 103 | Matarbari | 40 | 18:30 | 169 | Srinagar | 34.8 | 15:00
38 | Chauddagram | 51 | 18:30 | 104 | Matuail | 62 | 10:00 | 170 | Sunamganj | 43 | 18:30
39 | Chhatak | 24 | 12:00 | 105 | Millgate | 74 | 12:00 | 171 | Sylhet | 24 | 20:00
40 | Chowmuhani | 156 | 18:30 | 106 | Mirpur | 111 | 18:30 | 172 | Sylhet-132 | 88 | 18:00
41 | Chuadanga | 77 | 18:30 | 107 | Mirsorai | 9 | 10:00 | 173 | TK | 22.5 | 18:30
42 | Coxsbazar | 122 | 18:00 | 108 | Mirzapur | 38 | 06:00 | 174 | Tangail | 160 | 10:00
43 | Cumilla(N) | 118 | 19:30 | 109 | Mithapukur | 50 | 18:30 | 175 | Thakurgaon | 78 | 19:00
44 | Cumilla(S) | 157 | 14:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 117 | 12:00
45 | Daudkandi | 104 | 18:30 | 111 | Mogbazar | 119.7 | 12:00 | 177 | Ullahpara | 30 | 07:00
46 | Dhaka | 46 | 12:00 | 112 | Mongla | 43 | 19:00 | 178 | Ullon | 34 | 18:30
47 | Dhamrai | 116 | 12:00 | 113 | Motijheel | 31 | 12:00 | 179 | Uttara | 70 | 13:00
48 | Dhanmondi | 108 | 13:00 | 114 | Muktagacha | 31 | 18:00 | 180 | UttaraNew | 35 | 18:30
49 | Dohazari | 76 | 19:30 | 115 | Munshiganj | 75 | 18:00 | 181 | Zigatola | 60 | 18:30
50 | Faridpur | 113 | 19:00 | 116 | Muradnagar | 0 | 00:00
51 | Fatullah | 77 | 15:00 | 117 | Mymensingh | 166 | 18:00
52 | Fenchuganj | 30 | 18:30 | 118 | Naogaon | 111 | 08:00
53 | Feni | 74 | 13:00 | 119 | Narail | 45 | 18:30
54 | GPH | 94 | 06:00 | 120 | Narinda | 63 | 13:00
55 | Ghatail | 60 | 18:30 | 121 | Narshingdi | 147 | 18:30
56 | Ghorashal | 11 | 00:00 | 122 | Natore | 118 | 12:00
57 | Ghorashal-230 | 72 | 22:00 | 123 | Nawabganj | 30.8 | 21:00
58 | Goalpara | 30 | 13:00 | 124 | Netrakona | 129 | 09:00
59 | Gollamari | 56 | 13:00 | 125 | New | 77 | 12:00
60 | Gopalganj | 82.2 | 19:00 | 126 | Niamatpur | 92 | 08:00
61 | Gulshan | 92 | 13:00 | 127 | Noapara | 51 | 19:00
62 | Halishahar | 61.5 | 19:00 | 128 | PHP | 9 | 02:00
63 | HaripurSBU | 168 | 12:00 | 129 | Pabna | 88 | 18:30
64 | Hasnabad | 85 | 12:00 | 130 | Palashbari | 105 | 08:00
65 | Hathazari | 61 | 18:30 | 131 | Panchagarh | 45 | 19:00
66 | Ishurdi | 56 | 19:00 | 132 | Patuakhali | 53.4 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 10214.99 | 0 |  | 10214.99
1:00 | 9632.06 | 0 |  | 9632.06
2:00 | 9235.54 | 0 |  | 9235.54
3:00 | 8807.99 | 0 |  | 8807.99
4:00 | 8545.26 | 0 |  | 8545.26
5:00 | 8431.65 | 0 |  | 8431.65
6:00 | 8970.27 | 0 |  | 8970.27
7:00 | 9981.98 | 69 |  | 10054.09
8:00 | 10523.04 | 124 |  | 10653.04
9:00 | 10747.48 | 120 |  | 10872.48
10:00 | 10767.05 | 81 |  | 10852.05
11:00 | 10886.06 | 83 |  | 10973.06
12:00 | 11483.63 | 80 |  | 11567.63
13:00 | 11672.62 | 86 |  | 11762.62
14:00 | 11311.22 | 98 |  | 11413.22
15:00 | 11295.43 | 103 |  | 11403.43
16:00 | 10984.05 | 98 |  | 11086.05
17:00 | 10695.08 | 95 |  | 10794.08
18:00 | 11568.21 | 118 |  | 11691.21
19:00 | 12336.18 | 119 |  | 12460.18
19:30 | 12020.26 | 106 |  | 12131.26
20:00 | 11803.32 | 135 |  | 11944.4
21:00 | 11603.54 | 102 |  | 11710.54
22:00 | 11236.13 | 80 |  | 11320.13
23:00 | 10917.33 | 50 |  | 10969.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6576.5 | 3638.49 | 10214.99 | DAILY GENERATION CURVE
00:30 | 6330.25 | 3593.275 | 9923.525
01:00 | 6084 | 3548.06 | 9632.06 | 27-02-2025
01:30 | 5862.5 | 3571.3 | 9433.8
02:00 | 5641 | 3594.54 | 9235.54
02:30 | 5429 | 3592.765 | 9021.765
03:00 | 5217 | 3590.99 | 8807.99
03:30 | 5113.5 | 3563.125 | 8676.625
04:00 | 5010 | 3535.26 | 8545.26
04:30 | 4970 | 3518.455 | 8488.455
05:00 | 4930 | 3501.65 | 8431.65
05:30 | 5061 | 3639.96 | 8700.96
06:00 | 5192 | 3778.27 | 8970.27
06:30 | 5585.905 | 3890.22 | 9476.125
07:00 | 5979.81 | 4002.17 | 9981.98
07:30 | 6193.64 | 4058.87 | 10252.51
08:00 | 6407.47 | 4115.57 | 10523.04
08:30 | 6414.2 | 4221.06 | 10635.26
09:00 | 6420.93 | 4326.55 | 10747.48
09:30 | 6379 | 4378.265 | 10757.265
10:00 | 6337.07 | 4429.98 | 10767.05
10:30 | 6372.395 | 4454.16 | 10826.555
11:00 | 6407.72 | 4478.34 | 10886.06
11:30 | 6641.43 | 4543.415 | 11184.845
12:00 | 6875.14 | 4608.49 | 11483.63
12:30 | 6959.595 | 4618.53 | 11578.125
13:00 | 7044.05 | 4628.57 | 11672.62
13:30 | 6876.85 | 4615.07 | 11491.92
14:00 | 6709.65 | 4601.57 | 11311.22
14:30 | 6724.935 | 4578.39 | 11303.325
15:00 | 6740.22 | 4555.21 | 11295.43
15:30 | 6640.97 | 4498.77 | 11139.74
16:00 | 6541.72 | 4442.33 | 10984.05
16:30 | 6501.385 | 4338.18 | 10839.565
17:00 | 6461.05 | 4234.03 | 10695.08
17:30 | 6760.025 | 4371.62 | 11131.645
18:00 | 7059 | 4509.21 | 11568.21
18:30 | 7376.15 | 4576.045 | 11952.195
19:00 | 7693.3 | 4642.88 | 12336.18
19:30 | 7428 | 4592.26 | 12020.26
20:00 | 7229 | 4574.32 | 11803.32
20:30 | 7113 | 4590.43 | 11703.43 |  | Executive Engineer
21:00 | 6997 | 4606.54 | 11603.54 |  | Network Operation Division
21:30 | 6838.5 | 4581.335 | 11419.835
22:00 | 6680 | 4556.13 | 11236.13
22:30 | 6599 | 4477.73 | 11076.73
23:00 | 6518 | 4399.33 | 10917.33

## En-Curve
QF-LDC-12
Date | 27-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2938 | 1569 | 926 | 0 | 64 | 133.99 | 40 | 2885 | 0 | 229 | 1421 | 0 | 0 | 9 | 0 | DAILY ENERGY CURVE
00:30 | 2938 | 1558.25 | 925.5 | 0 | 61 | 193.275 | 40 | 2848 | 0 | 127 | 1220.5 | 0 | 0 | 12 | 0 | 27-02-2025
01:00 | 2938 | 1547.5 | 925 | 0 | 58 | 252.56 | 40 | 2811 | 0 | 25 | 1020 | 0 | 0 | 15 | 0
01:30 | 2938.5 | 1550.5 | 925.5 | 0 | 59 | 331.8 | 40 | 2780 | 0 | 23 | 766.5 | 0 | 0 | 19 | 0 | Energy Generated | 256.0449 |  | MKWHr
02:00 | 2939 | 1553.5 | 926 | 0 | 60 | 411.04 | 40 | 2749 | 0 | 21 | 513 | 0 | 0 | 23 | 0 | Energy not Served | 1.641 |  | MKWHr
02:30 | 2938.5 | 1543 | 926 | 0 | 57 | 434.265 | 40 | 2734 | 0 | 12.5 | 310.5 | 0 | 0 | 26 | 0 | Total Energy Requirement | 257.6859 |  | MKWHr
03:00 | 2938 | 1532.5 | 926 | 0 | 54 | 457.49 | 40 | 2719 | 0 | 4 | 108 | 0 | 0 | 29 | 0
03:30 | 2937.5 | 1512.5 | 926 | 0 | 56 | 512.625 | 40 | 2598.5 | 0 | 2 | 71 | 0 | 0 | 20.5 | 0
04:00 | 2937 | 1492.5 | 926 | 0 | 58 | 567.76 | 40 | 2478 | 0 | 0 | 34 | 0 | 0 | 12 | 0
04:30 | 2916 | 1497 | 925.5 | 0 | 59 | 618.455 | 40 | 2383.5 | 0 | 0 | 34 | 0 | 0 | 15 | 0
05:00 | 2895 | 1501.5 | 925 | 0 | 60 | 669.15 | 40 | 2289 | 0 | 0 | 34 | 0 | 0 | 18 | 0
05:30 | 2885.5 | 1495.5 | 925.5 | 0 | 59 | 701.96 | 40 | 2341 | 0 | 8 | 226 | 0 | 0 | 18.5 | 0
06:00 | 2876 | 1489.5 | 926 | 0 | 58 | 734.77 | 40 | 2393 | 0 | 16 | 418 | 0 | 0 | 19 | 0
06:30 | 2883.5 | 1542 | 926 | 0 | 57 | 740.245 | 40 | 2451 | 19.03 | 52.5 | 747.85 | 0 | 0 | 17 | 34.5
07:00 | 2891 | 1594.5 | 926 | 0 | 56 | 745.72 | 40 | 2509 | 38.06 | 89 | 1077.7 | 0 | 0 | 15 | 69
07:30 | 2807 | 1574 | 903 | 0 | 54 | 749.065 | 40 | 2609.5 | 112.095 | 107 | 1282.35 | 0 | 0 | 14.5 | 96.5
08:00 | 2723 | 1553.5 | 880 | 0 | 52 | 752.41 | 40 | 2710 | 186.13 | 125 | 1487 | 0 | 0 | 14 | 124
08:30 | 2756 | 1566 | 879.5 | 0 | 53 | 752.205 | 40 | 2746.5 | 268.555 | 130 | 1432 | 0 | 0 | 11.5 | 122
09:00 | 2789 | 1578.5 | 879 | 0 | 54 | 752 | 40 | 2783 | 350.98 | 135 | 1377 | 0 | 0 | 9 | 120
09:30 | 2771.5 | 1576.5 | 901.5 | 0 | 58 | 752.5 | 40 | 2915.5 | 404.265 | 135 | 1193 | 0 | 0 | 9.5 | 100.5
10:00 | 2754 | 1574.5 | 924 | 0 | 62 | 753 | 40 | 3048 | 457.55 | 135 | 1009 | 0 | 0 | 10 | 81
10:30 | 2740 | 1602 | 924.5 | 0 | 66 | 753.5 | 40 | 3073 | 476.055 | 135 | 1007 | 0 | 0 | 9.5 | 82
11:00 | 2726 | 1629.5 | 925 | 0 | 70 | 754 | 40 | 3098 | 494.56 | 135 | 1005 | 0 | 0 | 9 | 83
11:30 | 2840 | 1573.75 | 925 | 0 | 72 | 753.5 | 40 | 3113.5 | 506.595 | 198 | 1158 | 0 | 0 | 4.5 | 81.5
12:00 | 2954 | 1518 | 925 | 0 | 74 | 753 | 40 | 3129 | 518.63 | 261 | 1311 | 0 | 0 | 0 | 80
12:30 | 3010.5 | 1549.25 | 924.5 | 0 | 77 | 754 | 40 | 3143.5 | 527.375 | 268 | 1284 | 0 | 0 | 0 | 83
13:00 | 3067 | 1580.5 | 924 | 0 | 80 | 755 | 40 | 3158 | 536.12 | 275 | 1257 | 0 | 0 | 0 | 86
13:30 | 2886.5 | 1582 | 925 | 0 | 81 | 755 | 40 | 3159 | 495.42 | 274 | 1291 | 0 | 0 | 3 | 92
14:00 | 2706 | 1583.5 | 926 | 0 | 82 | 755 | 40 | 3160 | 454.72 | 273 | 1325 | 0 | 0 | 6 | 98
14:30 | 2671 | 1611.5 | 926 | 0 | 81 | 754.915 | 40 | 3147 | 420.41 | 272 | 1372 | 0 | 0 | 7.5 | 100.5
15:00 | 2636 | 1639.5 | 926 | 0 | 80 | 754.83 | 40 | 3134 | 386.1 | 271 | 1419 | 0 | 0 | 9 | 103
15:30 | 2737 | 1634 | 926 | 0 | 77 | 753.255 | 40 | 3128 | 306.985 | 270 | 1259 | 0 | 0 | 8.5 | 100.5
16:00 | 2838 | 1628.5 | 926 | 0 | 74 | 751.68 | 40 | 3122 | 227.87 | 269 | 1099 | 0 | 0 | 8 | 98
16:30 | 2775 | 1558 | 925.5 | 0 | 72 | 753.945 | 40 | 3117.5 | 146.62 | 278 | 1162 | 0 | 0 | 11 | 96.5
17:00 | 2712 | 1487.5 | 925 | 0 | 70 | 756.21 | 40 | 3113 | 65.37 | 287 | 1225 | 0 | 0 | 14 | 95
17:30 | 2774.5 | 1553 | 925 | 0 | 73 | 755.96 | 40 | 3075 | 33.185 | 397 | 1497.5 | 0 | 0 | 7.5 | 106.5
18:00 | 2837 | 1618.5 | 925 | 0 | 76 | 755.71 | 40 | 3037 | 1 | 507 | 1770 | 0 | 0 | 1 | 118
18:30 | 2870.5 | 1629 | 902 | 0 | 76 | 755.545 | 40 | 3039 | 0.5 | 560 | 2078.65 | 0 | 0 | 1 | 118.5
19:00 | 2904 | 1639.5 | 879 | 0 | 76 | 755.38 | 40 | 3041 | 0 | 613 | 2387.3 | 0 | 0 | 1 | 119
19:30 | 2904 | 1647.5 | 879 | 0 | 74 | 753.76 | 40 | 3112 | 0 | 574 | 2036 | 0 | 0 | 0 | 106
20:00 | 2910 | 1653.5 | 879 | 0 | 72 | 754.82 | 40 | 3112 | 0 | 473 | 1909 | 0 | 0 | 0 | 135
20:30 | 2913.5 | 1666 | 902 | 0 | 72 | 755.93 | 40 | 3124 | 0 | 439.5 | 1790.5 | 0 | 0 | 0 | 118.5
21:00 | 2917 | 1678.5 | 925 | 0 | 72 | 757.04 | 40 | 3136 | 0 | 406 | 1672 | 0 | 0 | 0 | 102
21:30 | 2921.5 | 1680 | 925.5 | 0 | 69 | 757.335 | 40 | 3104 | 0 | 385 | 1537.5 | 0 | 0 | 0 | 91
22:00 | 2926 | 1681.5 | 926 | 0 | 66 | 757.63 | 40 | 3072 | 0 | 364 | 1403 | 0 | 0 | 0 | 80
22:30 | 2901.5 | 1654 | 926 | 0 | 68 | 760.23 | 40 | 3071 | 0 | 323.5 | 1332.5 | 0 | 0 | 0 | 65
23:00 | 2877 | 1626.5 | 926 | 0 | 70 | 762.83 | 40 | 3070 | 0 | 283 | 1262 | 0 | 0 | 0 | 50
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 405 | 06:00 | 285 | 15:00 | Payra | 418 | 07:00 | 410 | 14:00
Ashuganj | 407 | 6:00 | 379 | 14:00 | Rahanpur | 419 | 00:00 | 395 | 10:00
Bhulta | 405 | 06:00 | 379 | 14:00 | Rampal | 412 | 06:00 | 393 | 11:00
Bibiana | 400 | 19:00 | 388 | 11:00
BIPTC | 400 | 04:00 | 390 | 13:00
Bogura | 411 | 01:00 | 389 | 10:00
Gopalganj | 410 | 06:00 | 393 | 14:00
Kaliakoir | 382 | 18:30 | 363 | 11:00
Madunaghat | 408 | 06:00 | 99 | 16:00
Meghnaghat | 401 | 06:00 | 383 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 06:00 | 220 | 11:00 | Keranigonj | 233 | 06:00 | 219 | 11:00
AKSML | 237 | 06:00 | 224 | 11:00 | Khulna(S) | 239 | 06:00 | 225 | 11:00
Aminbazar | 235 | 05:00 | 221 | 16:00 | Madunaghat | 235 | 07:00 | 225 | 11:00
Ashuganj | 237 | 00:00 | 225 | 15:00 | Madunaghat-400 | 236 | 08:00 | 227 | 11:00
Ashuganj-400 | 237 | 00:00 | 225 | 15:00 | Maniknagar | 233 | 05:00 | 220 | 11:00
Baghabari | 236 | 00:00 | 226 | 07:00 | Meghnaghat | 242 | 05:00 | 229 | 14:00
Barapukuria | 226 | 00:00 | 211 | 10:00 | Meghnaghat-400 | 236 | 06:00 | 224 | 11:00
Barapukuria-230 | 226 | 00:00 | 211 | 10:00 | Mirsorai | 235 | 18:30 | 221 | 11:00
Barishal | 242 | 06:00 | 236 | 11:00 | Rajshahi | 237 | 18:30 | 222 | 11:00
Bheramara | 235 | 19:00 | 222 | 11:00 | Rampal | 238 | 06:00 | 225 | 11:00
Bhulta | 234 | 06:00 | 220 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 07:00 | 224 | 11:00 | Rampura | 235 | 06:00 | 220 | 11:00
BIPTC | 237 | 17:00 | 223 | 11:00 | Shikalbaha | 234 | 19:30 | 226 | 11:00
Bogura | 240 | 00:00 | 225 | 10:00 | Shyampur | 233 | 06:00 | 220 | 11:00
Bogura-400 | 236 | 22:00 | 223 | 11:00 | Siddhirganj | 236 | 05:00 | 223 | 11:00
Borhanuddin | 245 | 18:30 | 241 | 10:00 | Sirajgonj | 243 | 00:00 | 232 | 10:00
BSRM | 234 | 18:30 | 221 | 11:00 | Sreepur | 236 | 00:00 | 223 | 11:00
Cumilla(N) | 232 | 01:00 | 221 | 11:00 | Tongi | 234 | 04:00 | 216 | 10:00
Faridpur | 243 | 06:00 | 232 | 11:00
Fenchuganj | 235 | 01:00 | 229 | 13:00
Ghorashal | 240 | 01:00 | 225 | 00:00
Ghorashal-230 | 234 | 06:00 | 218 | 11:00
Gopalganj | 241 | 06:00 | 231 | 14:00
GPH | 233 | 07:00 | 223 | 11:00
Haripur | 233 | 01:00 | 222 | 11:00
Hasnabad | 232 | 03:00 | 221 | 14:00
Hathazari | 236 | 19:00 | 226 | 11:00
Ishurdi | 237 | 19:00 | 225 | 10:00
Jhenaidah | 234 | 02:00 | 220 | 11:00
Kaliakoir | 230 | 08:00 | 211 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 123 | 11:00 | Madunaghat | 134 | 00:00 | 129 | 11:00
Agargaon | 136 | 06:00 | 126 | 14:00 | Magura | 138 | 04:00 | 126 | 10:00
Agrabad | 135 | 07:00 | 125 | 11:00 | Mahasthangarh | 135 | 00:00 | 125 | 08:00
AKS | 134 | 07:00 | 126 | 10:00 | Manikganj | 135 | 19:00 | 127 | 11:00
Aminbazar | 138 | 05:00 | 129 | 15:00 | Maniknagar | 133 | 04:00 | 123 | 11:00
Amnura | 141 | 19:30 | 123 | 10:00 | Matarbari | 131 | 00:00 | 119 | 11:00
Ashuganj | 140 | 06:00 | 134 | 14:00 | Matuail | 134.5 | 06:00 | 126 | 11:00
Bagerhat | 138 | 06:00 | 126 | 11:00 | Millgate | 135 | 00:00 | 123 | 11:00
Bajitpur | 135 | 19:00 | 125 | 15:00 | Mirpur | 136 | 07:00 | 128 | 11:00
Bakulia | 135 | 18:30 | 127 | 11:00 | Mirzapur | 132 | 00:00 | 125 | 11:00
Banani | 133 | 02:00 | 124 | 13:00 | Mithapukur | 135 | 00:00 | 121 | 10:00
Bangabhaban | 133 | 04:00 | 123 | 11:00 | MI_Cement | 135 | 06:00 | 126 | 11:00
Barapukuria | 135 | 21:00 | 124 | 13:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 137 | 06:00 | 131 | 14:00 | Mogbazar | 135 | 01:00 | 125 | 11:00
Barishal | 136 | 04:00 | 130 | 14:00 | Mongla | 138 | 05:00 | 127 | 11:00
Barishal-230 | 136 | 06:00 | 131 | 12:00 | Motijheel | 133 | 04:00 | 123 | 11:00
Baroaulia | 135 | 18:30 | 128 | 11:00 | Muktagacha | 127 | 00:00 | 118 | 08:00
Baroirhat | 132 | 00:00 | 123 | 11:00 | Munshiganj | 134 | 06:00 | 126 | 11:00
Bashundhara | 135 | 07:00 | 122 | 11:00 | Muradnagar | 134 | 06:00 | 126 | 11:00
BashundharaCement | 137 | 05:00 | 126 | 12:00 | Mymensingh | 127 | 00:00 | 108 | 13:00
Beanibazar | 134 | 03:00 | 124 | 13:00 | Naogaon | 133 | 00:00 | 121 | 08:00
Benapole | 137 | 06:00 | 125 | 11:00 | Narail | 135 | 00:00 | 126 | 11:00
Bhaluka | 126 | 00:00 | 115 | 14:00 | Narinda | 133 | 6:00 | 124 | 15:00
Bhandaria | 134 | 18:30 | 127 | 19:30 | Narshingdi | 130 | 01:00 | 122 | 18:30
Bhangura | 136 | 00:00 | 129 | 07:00 | Natore | 135 | 00:00 | 127 | 11:00
Bheramara | 135 | 01:00 | 128 | 10:00 | Nawabganj | 140 | 06:00 | 130 | 11:00
Bheramara(GK) | 136 | 03:00 | 128 | 11:00 | Netrakona | 124 | 00:00 | 108 | 13:00
Bhulta | 127 | 05:00 | 120 | 11:00 | New | 136 | 06:00 | 123 | 11:00
Bog-Sherpur | 135 | 00:00 | 125 | 11:00 | Niamatpur | 140 | 05:00 | 128 | 10:00
Bogura | 137 | 00:00 | 127 | 08:00 | Noapara | 139 | 06:00 | 127 | 13:00
Bogura-230 | 137 | 00:00 | 127 | 10:00 | Pabna | 136 | 04:00 | 129 | 10:00
Brahmanbaria | 134 | 06:00 | 128 | 11:00 | Palashbari | 132 | 00:00 | 115 | 08:00
Cantonment | 136 | 06:00 | 126 | 14:00 | Panchagarh | 143 | 21:00 | 121 | 10:00
Chandpur | 139 | 00:00 | 126 | 03:00 | Patuakhali | 138 | 18:30 | 132 | 22:00
Chandraghona | 135 | 08:00 | 129 | 11:00 | Payra | 137 | 06:00 | 134 | 10:00
Chapai | 137 | 00:00 | 124 | 11:00 | PHP | 133 | 08:00 | 122 | 11:00
Charsaidpur | 133 | 02:00 | 126 | 14:00 | Postogola | 136 | 01:00 | 128 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 134 | 07:00 | 123 | 00:00 | Purbachal | 133 | 01:00 | 123 | 14:00
Chhatak | 133 | 06:00 | 120 | 13:00 | Purbasadipur | 134 | 20:00 | 118 | 10:00
Chowmuhani | 130 | 04:00 | 122 | 11:00 | Rahanpur | 139 | 00:00 | 128 | 11:00
Chuadanga | 138 | 06:00 | 127 | 11:00 | Rahanpur-400 | 139 | 00:00 | 127 | 16:00
Coxsbazar | 123 | 09:00 | 119 | 15:00 | Rahim | 133 | 06:00 | 125 | 11:00
Cumilla(N) | 136 | 01:00 | 127 | 11:00 | Rajbari | 135 | 06:00 | 128 | 14:00
Cumilla(S) | 135 | 18:30 | 127 | 11:00 | Rajendrapur | 134 | 00:00 | 122 | 16:00
Daudkandi | 133 | 05:00 | 124 | 11:00 | Rajshahi | 137 | 00:00 | 129 | 07:00
Dhaka | 134 | 07:00 | 124 | 11:00 | Rajshahi-230 | 137 | 18:30 | 121 | 10:00
Dhamrai | 134 | 00:00 | 124 | 14:00 | Ramganj | 134 | 00:00 | 123 | 16:00
Dhanmondi | 134 | 02:00 | 126 | 11:00 | Rampur | 134 | 07:00 | 127 | 11:00
Dohazari | 132 | 05:00 | 125 | 10:00 | Rampura | 134 | 06:00 | 124 | 11:00
Faridpur | 135 | 02:00 | 10 | 15:00 | Rangamati | 135 | 06:00 | 129 | 10:00
Fatullah | 136 | 06:00 | 127 | 11:00 | Rangpur | 133 | 22:00 | 119 | 08:00
Fenchuganj | 136 | 03:00 | 132 | 11:00 | Ruppur | 137 | 03:00 | 131 | 10:00
Feni | 132 | 07:00 | 123 | 16:00 | Saidpur | 134 | 21:00 | 118 | 07:00
Ghatail | 126 | 00:00 | 120 | 08:00 | Satkhira | 137 | 05:00 | 126 | 11:00
Ghorashal | 141 | 08:00 | 132 | 11:00 | Satmasjid | 135 | 06:00 | 126 | 11:00
Goalpara | 138 | 06:00 | 129 | 13:00 | Savar | 138 | 06:00 | 127 | 14:00
Gollamari | 136 | 00:00 | 130 | 10:00 | SevenRings | 140 | 00:00 | 132 | 11:00
Gopalganj | 139 | 06:00 | 131 | 14:00 | ShahCement | 133 | 02:00 | 126 | 11:00
Gopalganj-400 | 140 | 06:00 | 134 | 10:00 | Shahjadpur | 140 | 00:00 | 132 | 07:00
Gulshan | 134 | 06:00 | 123 | 11:00 | Shahjibazar | 136 | 05:00 | 129 | 16:00
Halishahar | 134 | 02:00 | 128 | 13:00 | Shahmirpur | 136 | 05:00 | 128 | 11:00
Haripur | 132 | 00:00 | 126 | 11:00 | Shariatpur | 138 | 03:00 | 132 | 11:00
HaripurSBU | 133 | 02:00 | 126 | 11:00 | Sherpur | 124 | 18:30 | 110 | 08:00
Hasnabad | 137 | 05:00 | 129 | 15:00 | Shikalbaha | 124 | 01:00 | 118 | 16:00
Hathazari | 136 | 06:00 | 130 | 11:00 | Shikalbaha-230 | 137 | 18:30 | 130 | 10:00
Ishurdi | 138 | 06:00 | 131 | 10:00 | Shitalakhya | 135 | 06:00 | 126 | 11:00
Jaldhaka | 133 | 21:00 | 116 | 07:00 | Sholosohor | 134 | 07:00 | 129 | 11:00
Jamalpur | 126 | 00:00 | 115 | 20:00 | Shyampur | 134 | 02:00 | 127 | 11:00
Jashore | 138 | 04:00 | 126 | 11:00 | Shyampur-230 | 136 | 06:00 | 127 | 11:00
Jhenaidah | 137 | 03:00 | 128 | 11:00 | Siddhirganj | 133 | 00:00 | 127 | 11:00
Jhenaidah-230 | 138 | 03:00 | 128 | 11:00 | Sirajganj | 135 | 00:00 | 125 | 11:00
Joydebpur | 137 | 03:00 | 126 | 11:00 | Sonargaon | 133 | 07:00 | 125 | 11:00
Joypurhat | 132 | 00:00 | 117 | 08:00 | Sreemongol | 135 | 04:00 | 129 | 14:00
Juldah | 136 | 18:00 | 130 | 11:00 | Sreepur | 128 | 00:00 | 119 | 13:00
Kabirpur | 138 | 19:00 | 120 | 11:00 | Srinagar | 135 | 23:00 | 130 | 16:00
Kachua | 136 | 00:00 | 127 | 11:00 | SSM | 140 | 08:00 | 132 | 16:00
Kaliakoir | 137 | 18:30 | 126 | 11:00 | Sunamganj | 133 | 06:00 | 120 | 12:00
Kallyanpur | 135 | 00:00 | 128 | 11:00 | Sylhet | 134 | 06:00 | 124 | 13:00
Kalurghat | 136 | 19:00 | 129 | 11:00 | Sylhet-132 | 134 | 03:00 | 123 | 14:00
Kamrangirchar | 139 | 07:00 | 127 | 14:00 | Tangail | 129 | 03:00 | 122 | 11:00
Kaptai | 137 | 1:00 | 131 | 11:00 | Thakurgaon | 141 | 21:00 | 120 | 10:00
Kazla | 132 | 02:00 | 124 | 11:00 | TK | 135 | 08:00 | 130 | 13:00
Keranigonj | 139 | 06:00 | 130 | 14:00 | Tongi | 138 | 04:00 | 126 | 10:00
Khagrachori | 134 | 06:00 | 127 | 11:00 | Ullahpara | 137 | 00:00 | 127 | 11:00
Khosba | 134 | 06:00 | 125 | 11:00 | Ullon | 133 | 02:00 | 124 | 11:00
Khulna | 138 | 06:00 | 128 | 11:00 | Uttara | 136 | 07:00 | 127 | 16:00
Khulna(S) | 139 | 06:00 | 130 | 10:00 | UttaraNew | 137 | 01:00 | 128 | 11:00
Khulshi | 134 | 07:00 | 126 | 10:00 | Zigatola | 139 | 07:00 | 131 | 11:00
Kishoreganj | 133 | 06:00 | 113 | 14:00
Kodda | 137 | 19:00 | 124 | 15:00
KSRM | 136 | 18:30 | 128 | 10:00
Kulaura | 136 | 07:00 | 131 | 11:00
Kurigram | 133 | 23:00 | 119 | 07:00
Kushtia | 137 | 03:00 | 128 | 11:00
Lalbag | 140 | 06:00 | 130 | 11:00
Lalmonirhat | 131 | 00:00 | 120 | 08:00
Madanganj | 134 | 01:00 | 126 | 15:00
Madaripur | 139 | 05:00 | 132 | 14:00
Madartek | 134 | 06:00 | 123 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division