## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-02-2025 | during | 01-03-2025 | during | 01-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 150 | 150 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 270 | 270 | 110 | 110 | Reliable test run by OEM
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 329 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 44 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 32 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 16 | 15 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 19 | 21 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 18 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 84 | 59 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 68 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 70 | 70 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 90 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 43 | 48 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 72 | 72 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5925.764 | 2045 | 1992 | 5098.01 | 5068.01 | 2892.74 | 2862.74
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 26 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 208 | 219 | 203 | 203 | 203 | 203 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 68 | 105 | 105 | 70 | 70 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 8 | 32 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 75 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 25 | 30 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 32 | 32 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.29 | 0 | 4.29 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 50 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 17 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 73 | 68 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 36 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 28 | 35 | 116 | 116 | 35 | 35 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1162 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 10 | 5 | 0 | 5 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 500 | 480 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2435 | 2402 | 3468.15 | 3464.86 | 3276.15 | 3272.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 194 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 35 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 50 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 24 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 73 | 100 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 80 | 66 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 13 | 20.83 | 20.83 | 8 | 8 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 9 | 48 | 9 | 48 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 37 | 68 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 839 | 891 | 1629.97 | 1603.97 | 1479.2 | 1453.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-02-2025 | during | 01-03-2025 | during | 01-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 15 | 210 | 210 | 21 | 21 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 59 | 200 | 200 | 125 | 125 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 75 | 75 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.66 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 117.66 | 89 | 653.6 | 601.5 | 349.6 | 297.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 43 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 36 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 30 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 286 | 242 | 280 | 280 | 280 | 280 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1290 | 1314 | 1387.5 | 1387.5 | 1349 | 1349
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 458 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 41 | 41 | 41 | 41 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71.68 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 529.68 | 880 | 2966.1 | 2884.1 | 1163.02 | 1081.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 466 | 520 | 530 | 530 | 530 | 530 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 16 | 110 | 16 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 127 | 130 | 130 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 580 | 710 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1657.5 | 1962 | 2608.12 | 2701.12 | 2613.12 | 2706.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 18 | 86 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 175 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 400 | 400 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 72 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.22 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 755 | 723.61 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.35 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 89 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1586.07 | 1559.11 | 2511.74 | 2341.24 | 2277.96 | 2107.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 64 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 78 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.5 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 97 | 0 | 100 | 0 | 100 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 320.5 | 192 | 443.6 | 308 | 583.62 | 448.02
System Total |  |  |  |  | 29204.66 | 28470.742 | 10820.41 | 11281.11 | 20766.79 | 20360.3 | 15984.41 | 15577.92
Forecast Scenario (01-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9687 |  | 0 |  | 9687
|  |  |  | 1:00 | 9166 |  | 0 |  | 9166
|  |  |  | 2:00 | 8675 |  | 0 |  | 8675
|  |  |  | 3:00 | 8379 |  | 0 |  | 8379
|  |  |  | 4:00 | 8184 |  | 0 |  | 8184
|  |  |  | 5:00 | 8221 |  | 0 |  | 8221
|  |  |  | 6:00 | 8445 |  | 0 |  | 8445
|  |  |  | 7:00 | 9255 |  | 0 |  | 9255
|  |  |  | 8:00 | 9887 |  | 0 |  | 9887
|  |  |  | 9:00 | 9781 |  | 0 |  | 9781
|  |  |  | 10:00 | 9652 |  | 0 |  | 9652
|  |  |  | 11:00 | 10300 |  | 0 |  | 10300
|  |  |  | 12:00 | 10600 |  | 0 |  | 10600
|  |  |  | 13:00 | 10900 |  | 0 |  | 10900
|  |  |  | 14:00 | 10700 |  | 0 |  | 10700
|  |  |  | 15:00 | 10642 |  | 0 |  | 10642
|  |  |  | 16:00 | 10800 |  | 0 |  | 10800
|  |  |  | 17:00 | 11100 |  | 0 |  | 11100
|  |  |  | 18:00 | 11300 |  | 0 |  | 11300
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 11500 |  | 0 |  | 11500
|  |  |  | 19:30 | 11550 |  | 0 |  | 11550
|  |  |  | 20:00 | 11600 |  | 0 |  | 11600
|  |  |  | 21:00 | 11475 |  | 0 |  | 11475
|  |  |  | 22:00 | 11000 |  | 0 |  | 11000
|  |  |  | 23:00 | 10400 |  | 0 |  | 10400
Probable Maximum Temperature: |  |  | 33.80°C
Probable Maximum Demand at Day Peak: |  |  | 10600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 241.649 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:38 hrs on 01-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-02-2025 | [28 empty] | Date: | 28-02-2025 | [28 empty] | Date: | 28-02-2025 | [28 empty] | Date: | 28-02-2025 | [28 empty] | Date: | 28-02-2025 | [18 empty] | Date: | 28-02-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 26 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 40 | 0 | 63 | 32 | 0 | 0 | 9.3 | 54 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 180 | 0 | 0 | 0 | 35 | 16.4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 40 | 110 | 30 | 490 | 0 | 0 | 0 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 186 | 36 | 77 | 50 | 51 | 9 | 8 | 0 | 68 | 0 | 0 | 0 | 300 | 320 | 243 | 35 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 6055.7 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.06 | 0 | 0 | 0 | 113 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 125 | 180 | 0 | 369 | 622 | 0 | 4246.56 | 10302.26 | 89.08
01:00 | 0 | 17 | 26 | 110 | 0 | 130 | 0 | 0 | 364 | 0 | 0 | 0 | 54 | 0 | 33 | 0 | 0 | 0 | 35 | 17 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 76 | 0 | 0 | 40 | 107 | 35 | 490 | 0 | 0 | 0 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 51 | 0 | 0 | 8 | 0 | 60 | 0 | 0 | 0 | 295 | 320 | 252 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 19 | 0 | 0 | 0 | 0 | 5884 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 350 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 125 | 180 | 0 | 371 | 622 | 0 | 3900.72 | 9784.72 | 89.07
02:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 352 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 488 | 0 | 0 | 0 | 0 | 51 | 222 | 0 | 0 | 0 | 1123 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 51 | 0 | 0 | 8 | 0 | 64 | 0 | 0 | 0 | 295 | 320 | 243 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 5449 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 350 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 127 | 180 | 0 | 371 | 622 | 0 | 3904.12 | 9353.12 | 89.07
03:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 351 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16.5 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 489 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 980 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 184 | 36 | 0 | 51 | 0 | 0 | 8 | 0 | 58 | 0 | 0 | 0 | 300 | 320 | 243 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5221.5 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 350 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 127 | 180 | 0 | 371 | 622 | 0 | 3807.87 | 9029.37 | 89.06
04:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 351 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 491 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 906 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 51 | 0 | 0 | 8 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 248 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5130 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 350 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 127 | 180 | 0 | 371 | 500 | 0 | 3628.95 | 8758.95 | 89.06
05:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 351 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 490 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 906 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 51 | 0 | 0 | 8 | 0 | 56 | 0 | 0 | 0 | 300 | 320 | 242 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5131 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 658.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 350 | 0 | 0 | 2.5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 5 | 127 | 180 | 0 | 370 | 450 | 0 | 3523.98 | 8654.98 | 89.05
06:00 | 0 | 2 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 17 | 10 | 0 | 0 | 0 | 12 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 36 | 489 | 0 | 0 | 0 | 0 | 1 | 222 | 0 | 0 | 0 | 1080 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 196 | 36 | 0 | 50 | 0 | 0 | 8 | 0 | 56 | 0 | 0 | 0 | 310 | 320 | 242 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 56 | 0 | 0 | 0 | 0 | 5482 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762.46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 350 | 0 | 0 | 2.5 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 127 | 220 | 0 | 371 | 490 | 0 | 3444.96 | 8926.96 | 89.05
07:00 | 0 | 51 | 18 | 110 | 0 | 130 | 0 | 0 | 383 | 0 | 0 | 0 | 35 | 0 | 41 | 32 | 0 | 0 | 0 | 75 | 22 | 0 | 400 | 0 | 0 | 0 | 17 | 12 | 335 | 0 | 0 | 1 | 0 | 16 | 19 | 0 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 45 | 0 | 0 | 40 | 26 | 8 | 490 | 0 | 0 | 0 | 0 | 34 | 223 | 0 | 0 | 0 | 1224 | 2 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 198 | 36 | 23 | 50 | 28 | 7 | 8 | 0 | 58 | 0 | 4 | 0 | 305 | 320 | 270 | 36 | 42 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 56 | 10 | 0 | 2.03 | 0 | 5891.03 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 0 | 0 | 760.76 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2.03 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 0.18 | 5.5 | 0 | 64 | 0 | 1 | 0 | 0 | 0 | 0.2 | 8 | 0.03 | 0 | 307 | 5 | 127 | 220 | 0 | 371 | 580 | 0 | 3554.39 | 9445.42 | 89.04
08:00 | 0 | 51 | 25 | 110 | 0 | 130 | 0 | 0 | 372 | 0 | 0 | 0 | 17 | 0 | 52 | 16 | 30 | 0 | 0 | 90 | 22 | 0 | 400 | 0 | 0 | 0 | 17 | 12 | 335 | 0 | 0 | 6 | 13 | 16 | 19 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 1 | 40 | 54 | 5 | 489 | 0 | 0 | 0 | 0 | 75 | 225 | 0 | 0 | 0 | 1224 | 7 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 36 | 34 | 50 | 34 | 9 | 8 | 0 | 60 | 0 | 16 | 0 | 300 | 320 | 275 | 36 | 42 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 65 | 12 | 0 | 10.02 | 0 | 6050.02 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.25 | 0 | 0 | 758 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 9.54 | 0 | 0 | 0 | 0 | 205 | 0 | 414 | 0 | 0.87 | 5.5 | 0 | 61 | 70 | 6 | 35 | 0 | 0 | 1.6 | 44 | 0.13 | 0 | 307 | 5 | 127 | 220 | 0 | 371 | 622 | 0 | 3792.89 | 9842.91 | 89.04
09:00 | 0 | 51 | 25 | 110 | 0 | 130 | 0 | 0 | 396 | 0 | 0 | 0 | 17 | 0 | 57 | 16 | 30 | 0 | 0 | 90 | 22 | 0 | 400 | 0 | 0 | 0 | 17 | 17 | 250 | 0 | 0 | 12 | 28 | 16 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 4 | 0 | 0 | 0 | 75 | 0 | 2 | 40 | 68 | 20 | 490 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 12 | 51 | 0 | 189 | 0 | 0 | 0 | 29 | 226 | 36 | 34 | 50 | 17 | 9 | 8 | 0 | 54 | 0 | 31 | 0 | 280 | 320 | 281 | 36 | 43 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 59 | 5 | 1 | 20.45 | 3 | 6130.45 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.22 | 0 | 0 | 756 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 20.74 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 1.83 | 5.5 | 0 | 61 | 90 | 12 | 35 | 0 | 0 | 3 | 75 | 0.26 | 0 | 307 | 4 | 127 | 220 | 0 | 370 | 580 | 0 | 3732.55 | 9863 | 89.03
10:00 | 0 | 51 | 25 | 110 | 0 | 129 | 0 | 0 | 406 | 0 | 0 | 13 | 17 | 0 | 70 | 16 | 15 | 0 | 0 | 35 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 335 | 0 | 0 | 18 | 36 | 16 | 19 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 2 | 3 | 40 | 34 | 22 | 500 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1224 | 15 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 183 | 36 | 34 | 50 | 17 | 9 | 8 | 0 | 62 | 0 | 45 | 0 | 290 | 320 | 280 | 36 | 43 | 40 | 2 | 163 | 16 | 0 | 83 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 1 | 28.25 | 6 | 6143.25 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.63 | 0 | 0 | 757 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 30.61 | 10 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 2.53 | 5.5 | 0 | 61 | 95 | 20 | 34 | 0 | 0 | 4.2 | 98 | 0.38 | 0 | 307 | 4 | 127 | 220 | 0 | 368 | 560 | 8 | 3847.85 | 9991.1 | 89.03
11:00 | 0 | 51 | 25 | 110 | 0 | 150 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 0 | 73 | 40 | 15 | 0 | 0 | 50 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 12 | 327 | 0 | 0 | 23 | 72 | 16 | 19 | 0 | 0 | 13 | 32 | 0 | 0 | 2 | 0 | 0 | 0 | 75 | 50 | 4 | 40 | 34 | 22 | 500 | 0 | 0 | 0 | 0 | 105 | 208 | 0 | 0 | 0 | 1100 | 18 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 211 | 33 | 40 | 50 | 17 | 9 | 8 | 0 | 72 | 0 | 54 | 0 | 300 | 320 | 292 | 32 | 42 | 40 | 2 | 163 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 59 | 5 | 2 | 32.96 | 6 | 6281.96 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 0 | 0 | 754 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 0 | 0 | 84 | 0 | 37.5 | 18 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 3.24 | 5.5 | 0 | 62 | 95 | 25 | 34 | 0 | 0 | 5.1 | 98 | 0.47 | 0 | 250 | 8 | 127 | 220 | 0 | 437 | 550 | 17 | 3934.79 | 10216.75 | 89.02
12:00 | 0 | 51 | 25 | 110 | 0 | 150 | 0 | 0 | 404 | 0 | 0 | 44 | 43 | 0 | 84 | 64 | 60 | 0 | 0 | 162 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 16 | 327 | 0 | 0 | 26 | 72 | 16 | 19 | 0 | 0 | 28 | 70 | 0 | 0 | 14 | 0 | 8 | 17 | 75 | 50 | 4 | 40 | 73 | 25 | 500 | 17 | 0 | 20 | 0 | 105 | 208 | 0 | 0 | 0 | 1162 | 19 | 51 | 26 | 187 | 0 | 0 | 0 | 29 | 194 | 36 | 37 | 51 | 73 | 9 | 8 | 0 | 80 | 1 | 57 | 0 | 300 | 320 | 286 | 32 | 40 | 40 | 2 | 120 | 16 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 59 | 5 | 2 | 36.66 | 6 | 6726.66 | 458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.68 | 0 | 0 | 755 | 0 | 0 | 0 | 35 | 0 | 0 | 72 | 0 | 8 | 89 | 0 | 36.35 | 18 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 3.22 | 5.5 | 0 | 61 | 95 | 27 | 34 | 0 | 0 | 6.5 | 97 | 0.5 | 0 | 307 | 7 | 100 | 180 | 0 | 466 | 580 | 17 | 4093.75 | 10820.41 | 89.02
13:00 | 0 | 51 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 0 | 95 | 64 | 95 | 0 | 0 | 162 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 16 | 300 | 0 | 0 | 25 | 90 | 16 | 20 | 0 | 0 | 35 | 70 | 0 | 0 | 13 | 0 | 0 | 0 | 72 | 50 | 3 | 40 | 92 | 34 | 500 | 0 | 0 | 25 | 0 | 105 | 208 | 0 | 0 | 0 | 1224 | 18 | 51 | 68 | 187 | 0 | 0 | 0 | 29 | 184 | 36 | 51 | 51 | 168 | 9 | 8 | 0 | 78 | 0 | 52 | 0 | 290 | 320 | 233 | 32 | 40 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 59 | 5 | 2 | 22.47 | 6 | 7012.47 | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.24 | 0 | 0 | 753 | 0 | 0 | 0 | 38 | 0 | 0 | 35 | 0 | 8 | 88 | 0 | 46.67 | 8 | 0 | 0 | 0 | 172 | 0 | 350 | 0 | 4.07 | 5.5 | 0 | 62 | 95 | 27 | 34 | 0 | 0 | 4 | 100 | 0.46 | 16 | 307 | 9 | 127 | 220 | 0 | 494 | 570 | 17 | 4386.94 | 11399.41 | 89.01
14:00 | 0 | 50 | 25 | 110 | 0 | 151 | 0 | 0 | 347 | 0 | 0 | 0 | 54 | 0 | 52 | 16 | 0 | 0 | 0 | 72 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 18 | 260 | 0 | 0 | 21 | 90 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 72 | 0 | 3 | 40 | 93 | 33 | 496 | 0 | 0 | 26 | 0 | 105 | 208 | 0 | 0 | 0 | 1224 | 16 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 203 | 35 | 51 | 51 | 51 | 9 | 8 | 0 | 72 | 0 | 45 | 0 | 285 | 320 | 231 | 32 | 40 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 17 | 0 | 0 | 9 | 59 | 5 | 2 | 29.4 | 6 | 6125.4 | 555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.87 | 0 | 0 | 755 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 40.62 | 3 | 0 | 0 | 0 | 185 | 0 | 350 | 0 | 3.42 | 5.5 | 0 | 62 | 35 | 10 | 34 | 0 | 0 | 2.7 | 102 | 0.45 | 0 | 307 | 9 | 127 | 220 | 0 | 496 | 550 | 0 | 4059.56 | 10184.96 | 89.01
15:00 | 0 | 50 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 34 | 16 | 0 | 0 | 0 | 72 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 18 | 260 | 0 | 0 | 16 | 80 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 72 | 0 | 2 | 40 | 93 | 27 | 480 | 0 | 0 | 26 | 0 | 88 | 208 | 0 | 0 | 0 | 1224 | 12 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 205 | 33 | 53 | 50 | 51 | 9 | 8 | 0 | 68 | 0 | 32 | 0 | 310 | 320 | 250 | 32 | 40 | 39 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 17 | 0 | 0 | 9 | 59 | 7 | 1 | 20.34 | 6 | 6110.34 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.49 | 0 | 0 | 757.25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 29.2 | 7 | 0 | 0 | 0 | 184 | 0 | 350 | 0 | 2.54 | 5.5 | 0 | 61 | 35 | 12 | 35 | 0 | 0 | 3.3 | 83 | 0.32 | 0 | 307 | 8 | 127 | 220 | 0 | 488 | 550 | 0 | 3887.6 | 9997.94 | 89
16:00 | 0 | 50 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 34 | 16 | 0 | 0 | 0 | 35 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 18 | 322 | 0 | 0 | 4 | 72 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 50 | 0 | 1 | 40 | 51 | 24 | 480 | 0 | 0 | 26 | 0 | 51 | 218 | 0 | 0 | 0 | 1224 | 7 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 33 | 50 | 50 | 34 | 9 | 8 | 0 | 64 | 0 | 17 | 0 | 300 | 320 | 241 | 35 | 40 | 39 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 17 | 0 | 0 | 9 | 59 | 9 | 1 | 11.8 | 6 | 6042.8 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.08 | 0 | 0 | 754.45 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 17.52 | 11 | 0 | 0 | 0 | 181 | 0 | 414 | 0 | 1.54 | 2.5 | 0 | 63 | 0 | 7 | 35 | 0 | 0 | 1.8 | 61 | 0.13 | 0 | 307 | 7 | 127 | 220 | 0 | 495 | 550 | 0 | 3798.02 | 9840.82 | 89
17:00 | 0 | 50 | 25 | 110 | 0 | 150 | 0 | 0 | 384 | 0 | 0 | 0 | 35 | 0 | 34 | 16 | 0 | 0 | 0 | 35 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 320 | 0 | 0 | 3 | 72 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 51 | 29 | 480 | 0 | 0 | 26 | 0 | 51 | 218 | 0 | 0 | 0 | 1160 | 2 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 201 | 35 | 50 | 50 | 34 | 19 | 8 | 0 | 62 | 0 | 5 | 0 | 295 | 320 | 250 | 35 | 43 | 40 | 2 | 163 | 22 | 0 | 86 | 30 | 0 | 17 | 0 | 0 | 9 | 59 | 11 | 0 | 7.21 | 6 | 5948.71 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.64 | 0 | 0 | 698.35 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 5.84 | 19 | 0 | 0 | 0 | 181 | 0 | 414 | 0 | 0.5 | 2.5 | 0 | 63 | 0 | 3 | 35 | 0 | 0 | 0.4 | 15 | 0.07 | 0 | 300 | 7 | 127 | 220 | 0 | 500 | 580 | 0 | 3679.3 | 9628.01 | 88.99
18:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 7 | 35 | 0 | 34 | 48 | 15 | 0 | 0 | 102 | 22 | 0 | 400 | 0 | 0 | 0 | 17 | 18 | 322 | 0 | 0 | 0 | 72 | 16.5 | 21 | 0 | 0 | 2 | 50 | 0 | 0 | 10 | 17 | 12 | 0 | 54 | 24 | 0 | 40 | 58 | 29 | 481 | 0 | 0 | 26 | 0 | 66 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 18 | 195 | 0 | 0 | 0 | 29 | 203 | 35 | 63 | 50 | 34 | 28 | 13 | 0 | 64 | 0 | 0 | 0 | 300 | 320 | 271 | 35 | 43 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 0 | 0 | 9 | 59 | 12 | 0 | 0 | 6 | 6396.5 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 661.88 | 0 | 0 | 0 | 40 | 0 | 30 | 20 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 178 | 0 | 414 | 0 | 0 | 5.5 | 0 | 65 | 50 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 9 | 127 | 220 | 0 | 512 | 670 | 5 | 3906.63 | 10303.13 | 88.99
19:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 35 | 48 | 0 | 59 | 32 | 45 | 0 | 17 | 90 | 22 | 0 | 400 | 0 | 0 | 0 | 35 | 18 | 329 | 0 | 0 | 0 | 72 | 15 | 21 | 0 | 0 | 35 | 50 | 0 | 0 | 10 | 34 | 32 | 0 | 50 | 36 | 0 | 40 | 68 | 30 | 480 | 0 | 0 | 26 | 0 | 68 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 195 | 0 | 0 | 0 | 29 | 182 | 35 | 68 | 50 | 100 | 28 | 13 | 0 | 66 | 0 | 0 | 24 | 280 | 320 | 242 | 36 | 43 | 40 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 30 | 0 | 9 | 59 | 15 | 0 | 0 | 6 | 6688 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723.61 | 0 | 0 | 0 | 70 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 175 | 0 | 414 | 0 | 0 | 5.5 | 0 | 64 | 50 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 11 | 127 | 220 | 0 | 520 | 710 | 35 | 4593.11 | 11281.11 | 88.99
19:30 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 0 | 40 | 32 | 0 | 0 | 35 | 90 | 22 | 0 | 400 | 0 | 0 | 0 | 35 | 18 | 333 | 0 | 0 | 0 | 94 | 15 | 21 | 0 | 0 | 35 | 51 | 0 | 0 | 6 | 34 | 0 | 0 | 50 | 12 | 0 | 40 | 68 | 30 | 480 | 0 | 0 | 9 | 0 | 68 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 195 | 0 | 0 | 0 | 29 | 182 | 35 | 68 | 50 | 100 | 28 | 13 | 0 | 66 | 0 | 0 | 0 | 275 | 320 | 242 | 36 | 42 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 9 | 59 | 16 | 0 | 0 | 6 | 6565 | 881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.87 | 0 | 0 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 171 | 0 | 360 | 0 | 0 | 5.5 | 0 | 63 | 35 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 11 | 127 | 220 | 0 | 516 | 810 | 35 | 4643.37 | 11208.37
20:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 0 | 42 | 32 | 0 | 0 | 55 | 90 | 22 | 4 | 400 | 0 | 0 | 0 | 35 | 18 | 330 | 0 | 0 | 0 | 108 | 16 | 21 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 68 | 33 | 480 | 0 | 0 | 0 | 0 | 68 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 195 | 0 | 0 | 0 | 29 | 189 | 35 | 68 | 50 | 68 | 29 | 15 | 0 | 70 | 0 | 0 | 0 | 290 | 320 | 244 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 9 | 59 | 17 | 0 | 0 | 6 | 6526 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.48 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 172 | 0 | 360 | 0 | 0 | 5.5 | 0 | 62 | 35 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 127 | 220 | 0 | 526 | 820 | 0 | 4577.98 | 11103.98 | 88.98
21:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 0 | 34 | 32 | 0 | 0 | 55 | 54 | 22 | 8 | 370 | 0 | 0 | 0 | 17 | 18 | 332 | 0 | 0 | 0 | 108 | 16 | 21 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 68 | 34 | 480 | 0 | 0 | 0 | 0 | 68 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 195 | 0 | 0 | 0 | 29 | 182 | 36 | 68 | 50 | 34 | 29 | 16 | 0 | 72 | 0 | 0 | 0 | 290 | 320 | 241 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 9 | 59 | 17 | 0 | 0 | 6 | 6363 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.69 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 171 | 0 | 360 | 0 | 0 | 5.5 | 0 | 62 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 127 | 220 | 0 | 537 | 872 | 0 | 4673.19 | 11036.19 | 88.98
22:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 402 | 0 | 0 | 17 | 35 | 0 | 19 | 32 | 0 | 0 | 55 | 54 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 108 | 15 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 68 | 42 | 480 | 0 | 0 | 0 | 0 | 68 | 207 | 0 | 0 | 0 | 1165 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 36 | 68 | 50 | 34 | 28 | 16 | 0 | 68 | 0 | 0 | 0 | 300 | 320 | 241 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 9 | 59 | 17 | 0 | 0 | 6 | 6149 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 169 | 0 | 360 | 0 | 0 | 5.5 | 0 | 61 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 127 | 220 | 0 | 532 | 930 | 0 | 4645.91 | 10794.91 | 88.98
23:00 | 0 | 35 | 8 | 110 | 0 | 150 | 0 | 0 | 381 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 54 | 16 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 68 | 42 | 480 | 0 | 0 | 0 | 0 | 68 | 161 | 0 | 0 | 0 | 1009 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 36 | 45 | 50 | 17 | 9 | 16 | 0 | 72 | 0 | 0 | 0 | 285 | 320 | 241 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 9 | 59 | 17 | 0 | 0 | 6 | 5613 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 169 | 0 | 360 | 0 | 0 | 5.5 | 95 | 63 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 12 | 90 | 180 | 0 | 538 | 982 | 0 | 4687.47 | 10300.47 | 88.97
Total KWH | 0 | 1011485 | 511680 | 2614500 | 0 | 3377688 | 0 | 0 | 9342000 | 0 | 0 | 349128 | 952200 | 0 | 974016 | 502080 | 327687 | 0 | 248201 | 1349280 | 582840 | 21120 | 9709500 | 0 | 0 | 0 | 132319 | 374400 | 7645203 | 0 | 0 | 162176 | 1178400 | 393000 | 475560 | 0 | 0 | 217036 | 557018 | 0 | 0 | 188640 | 51070 | 44160 | 30544 | 1168320 | 213120 | 23043 | 936660 | 1388357 | 732000 | 11549090.91 | 20073 | 0 | 218400 | 0 | 1659345 | 5134953 | 0 | 0 | 0 | 27834543 | 126090 | 1204296 | 332872 | 4600000 | 0 | 0 | 0 | 701280 | 4667000 | 860544 | 918720 | 1185510 | 1065120 | 288120 | 249310 | 0 | 1527360 | 7517 | 359636 | 20256 | 7260000 | 7676800 | 6358000 | 824904 | 993000 | 939960 | 55488 | 3671427 | 431928 | 0 | 2059200 | 720288 | 0 | 434000 | 260020 | 0 | 188400 | 1128000 | 164160 | 10650 | 210590 | 94560 | 145795841.91 | 16236363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508320 | 0 | 0 | 17609931 | 0 | 0 | 0 | 825120 | 0 | 220144 | 215712 | 0 | 27269 | 555370 | 0 | 287256 | 1007818 | 0 | 0 | 0 | 4541291 | 0 | 9263563 | 0 | 24420 | 95040 | 148000 | 1415127 | 796619 | 165459 | 811420 | 0 | 0 | 31737.6 | 758160 | 3971 | 80448 | 7091000 | 194664 | 2966000 | 5153450 | 0 | 10728119 | 15873454.55 | 128400 | 97763646.15 | 243559488.06

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-02-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10820.41 | MW | 12:00 Hr. | Energy Generated |  |  | 243.5595 |  | MKWHr.
| Day Peak Demand |  |  | 10893.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.511 |  | MKWHr.
| Evening Peak Generation |  |  | 11281.11 | MW | 19:00 Hr. | Energy Demand |  |  | 245.0705 |  | MKWHr.
| Evening Peak Demand |  |  | 11351.11 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 8654.98 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 857.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 11399.41 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.903 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.5147 | 0 | 7.5576 | 0 | 0 | 0.16218 | 0 | 0 | 42.2345 | Gas | 108.9206 | Gas | 398315106.15
| Chattogram Zone |  |  | 5.867 | 39.3836 | 5.5674 | 0 | 0.93666 | 0.14913 | 0 | 0.18864 | 52.0925 | Coal | 74.6393 | Coal | 440221023.5733
| Cumilla Zone |  |  | 13.4679 | 0 | 2.6326 | 0 | 0 | 0.35964 | 1.5274 | 0 | 17.9875 | HFO | 20.2737 | HFO | 348422712.68
| Mymensingh Zone |  |  | 0.16416 | 0 | 1.411 | 0 | 0 | 0.22124 | 0 | 0 | 1.7964 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.685 | Hydro | 0.93666 | Hydro | 93666
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.50832 | 16.2364 | 0 | 16.7447 | Solar | 3.2269 | Solar | 51950683.376
| Barishal Zone |  |  | 8.3141 | 33.6926 | 0.20885 | 0 | 0 | 0.003971 | 0 | 0 | 42.2195 | Import | 35.3737 | Import | 195965086.71
| Rajshahi Zone |  |  | 14.9077 | 0 | 1.2882 | 0 | 0 | 0.86705 | 17.6099 | 0 | 34.6729 | Wind | 0.18864 | Wind | 2761689.6
| Rangpur Zone |  |  | 0 | 1.5631 | 1.608 | 0 | 0 | 0.95536 | 0 | 0 | 4.1265
| Total |  |  | 108.9206 | 74.6393 | 20.2737 | 0 | 0.93666 | 3.2269 | 35.3737 | 0.18864 | 243.5595
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 398315106.15 |  | Hydro | 93666
|  |  |  | Coal | 440221023.5733 |  | Solar | 51950683.376
|  |  |  | HFO | 348422712.68 |  | Import | 195965086.71
|  |  |  | HSD | 0 |  | Wind | 2761689.6
[5 empty] | Total: | 143,77,29,968 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.2364 | Peak Hr Flow | 880.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 4033327.295 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.6099 | Peak Hr Flow | 723.61 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 272 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5274 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 526 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 35.3737 | Peak Hr Flow | 1669.61 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3962
|  |  |  | Chattogram |  | 0 |  | 1225
|  |  |  | Cumilla |  | 0 |  | 997
|  |  |  | Mymensingh |  | 67 |  | 991
|  |  |  | Sylhet |  | 0 |  | 392
|  |  |  | Khulna |  | 0 |  | 1272
|  |  |  | Barishal |  | 0 |  | 322
|  |  |  | Rajshahi |  | 0 |  | 1156
|  |  |  | Rangpur |  | 0 |  | 745
|  |  |  | Total |  | 67 |  | 11062
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 944.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1736.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 | 10:06 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to 230 Kv Bus conductor replacement work
| 08:17 | 10:06 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to 230kv Bus conductor replacement work
| 08:20 | 14:38 | Siddhirganj 132/33kV S/S T-2 LT Scheduled S/D Due to Ten delta Test
| 08:22 |  | Halishahar-Julda 132kV Ckt-1 Project Work S/D from Juldah 132/33kV end Due to Halishahar
project work and from Halishahar 132/33kV end Due to Due to terminal tower jumper loop
connection work of Khulsi ckt -3 by ESPNER project.
| 08:23 | 14:38 | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to Ten delta Test
| 08:27 |  | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Project Work S/D Due to Project work
|  | 08:52 | Rampura 230/132kV S/S Auto Transformer - 04 HT is restored.
|  | 08:54 | Rampura 230/132kV S/S Auto Transformer - 04 LT is restored.
| 08:57 | 10:49 | Barishal 132/33kV S/S 132 kv Summit power Scheduled S/D Due to Line PT oil lekage
| 09:11 | 18:03 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 132/33kV end Due to
Maintenance work Haripur SS ends
| 09:11 | 18:04 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Siddhirganj 132/33kV end Due to
Maintenance work Haripur SS ends and from Haripur 230/132kVend.
| 09:13 | 18:04 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end.
|  | 09:20 | Rampura 230/132kV S/S NLDC Trafo LT is restored.
|  | 09:20 | Rampura 230/132kV S/S NLDC Trafo HT is restored.
|  | 09:32 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
|  | 09:33 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT is restored.
|  | 09:35 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT is restored.
|  | 09:36 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT is restored.
| 09:48 | 23:43 | Haripur 230/132kV S/S 132kV Main Bus Sec-1 Scheduled S/D
| 09:57 |  | Sirajgonj 225MW CCPP Unit-1 GT Synchronized with remarks:- GT has been synchronized with
grid as per NLDC demand.
| 09:57 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
|  | 10:03 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT is restored.
| 10:23 |  | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to Project work.
| 10:23 |  | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to Project work.
|  | 10:25 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 10:27 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 10:31 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 10:31 | Barishal 230/132kV S/S T-4 LT is restored.
| 11:19 | 18:02 | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D Due to GIS Bay commission in Halishahar
Grid ss
| 11:40 | 12:14 | Bashundhara-Tongi 132 kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Main
protection Trip B-Phase relays.
|  | 11:45 | Mahasthangarh 132/33kV S/S 406T MTR1 HT is restored.
| 12:00 |  | Day Peak Generation: 10817 MW
|  | 12:20 | BIPTC S/S 21T01 LT is restored.
|  | 12:20 | BIPTC S/S 11T01 LT is restored.
|  | 12:20 | BIPTC S/S 11T01 HT is restored.
|  | 12:20 | BIPTC S/S 21T01 HT is restored.
| 15:04 | 18:05 | BIPTC S/S 22T01 LT Scheduled S/D Due to For replacement of burnt main MCB & magnetic
contactor of one cooler group for converter transformer
| 15:04 | 18:05 | BIPTC S/S 22T01 HT Scheduled S/D Due to For replacement of burnt main MCB & magnetic
contactor of one cooler group for converter transformer
| 15:38 | 17:39 | Tongi 230/132/33kV S/S T-01 LT Scheduled S/D Due to 230 kV Busbar-1 replacement work. | [7 empty] | 10.0MW load
interrup.
| 15:38 | 17:39 | Tongi 230/132/33kV S/S T-01 HT Scheduled S/D Due to 230 kV Busbar-1 replacement work.
| 16:01 |  | Sirajgonj 225MW CCPP Unit-1 ST Synchronized with remarks:- ST has been synchronized with
grid as per NLDC demand.
| 16:01 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 16:05 |  | Payra 1320 MW Synchronized with remarks:- unit-2
|  | 16:37 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
|  | 16:39 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
| 17:44 | 18:31 | Tongi 230/132/33kV S/S T-02 HT Scheduled S/D
| 17:44 | 18:31 | Tongi 230/132/33kV S/S T-02 LT Scheduled S/D Due to For PT connection.
|  | 19:17 | Jashore 132/33kV S/S T-1 HT is restored.
|  | 19:18 | Jashore 132/33kV S/S T-1 LT is restored.
| 22:08 |  | Barapukuria Unit-3 was sync.
| 06:21 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to Annual Maintenance.
| 06:23 |  | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to | [7 empty] | 30.0MW load
|  |  | Maintenance work for fenchugang 232/132/33 kV grid sub station | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 06:47 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Scheduled S/D Due to Emergency
working of Fenchugonj end
| 06:51 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Scheduled S/D Due to Emergency
working of Fenchugonj end
| 07:07 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to 33kV Kashipur (WZ) feeder red | [7 empty] | 18.0MW load
|  |  | hot maintenance | [7 empty] | interrup.
| 07:08 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to 33kV Kashipur (WZ) feeder red | [7 empty] | 18.0MW load
|  |  | hot maintenance | [7 empty] | interrup.
| 07:28 |  | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to REB -4, 33kV Busbar maintenance | [7 empty] | 20.0MW load
interrup.
| 07:29 |  | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to None | [7 empty] | 20.0MW load
interrup.
| 07:38 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
| 07:44 |  | Ashuganj-Ghorasal 132kV Ckt-2 Project Work S/D from Ashuganj 230/132/33kV end Due to
Re-routing of 3 nos Tower
| 07:45 |  | Faridpur 132/33kV S/S ATR-1 LT Scheduled S/D
| 07:46 |  | Faridpur 132/33kV S/S ATR-1 HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-02-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 150 | 3377688 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2614500 | Reliable test run by OEM
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9342000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9709500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 329 | 7645203 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 349128 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 502080 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 248201 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 132319 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 393000 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 475560 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 582840 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 18 | 374400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 511680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 327687 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 59 | 974016 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 68 | 1011485 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 21120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1349280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 162176 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 48 | 952200 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 72 | 1178400 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 1992 | 42234463
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126090 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 218400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 936660 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5134953 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1659345 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 32 | 44160 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 51070 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 1168320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 732000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23043 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 557018 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 30544 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 1388357 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 213120 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 217036 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 20073 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27834543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 188640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 480 | 11549090.91 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2402 | 52092462.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4667000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 860544 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 701280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4600000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1204296 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 332872 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 24 | 20256 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1185510 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1065120 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1527360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 7517 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 249310 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 288120 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 918720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 359636 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 891 | 17987541
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 15 | 164160 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 59 | 1128000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 188400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 210590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 94560 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 89 | 1796360
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 43 | 993000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 939960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3671427 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 824904 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 55488 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 720288 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2059200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 30 | 260020 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 434000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 431928 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7260000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 242 | 6358000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7676800 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1314 | 31685015
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 16236363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 508320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 880 | 16744683
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 520 | 10728119 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 80448 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 194664 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 127 | 2966000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 710 | 15873454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5153450 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 128400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7091000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3971 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1962 | 42219506.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 86 | 1007818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 175 | 4541291 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9263563 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 95040 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 27269 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 220144 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 825120 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 215712 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 723.61 | 17609931 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 287256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 555370 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1559.11 | 34672934
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 64 | 1415127 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 148000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 811420 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31737.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 796619 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 165459 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 758160 | -
Rangpur Area Total |  |  |  |  | 950 | 192 | 4126522.6
Eastern Grid Total |  |  |  |  | 16856.242 | 6688 | 145795841.91
Western Grid Total |  |  |  |  | 11614.5 | 4593.11 | 97763646.15
National Grid Total |  |  |  |  | 28470.742 | 11281.11 | 243559488.06
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-02-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7500.35 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3494.8 | MW
i) Dhaka area |  |  | 3962.35 |  | MW | i) Khulna area |  |  |  | 1272 | MW
ii) Chattogram area |  |  | 1225 |  | MW | ii) Barishal area |  |  |  | 322 | MW
iii) Cumilla area |  |  | 997 |  | MW | iii) Rajshahi area |  |  |  | 1155.8 | MW
iv) Mymensingh area |  |  | 924 |  | MW | iv) Rangpur area |  |  |  | 745 | MW
v) Sylhet area |  |  | 392 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10995.15 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 67 | 18:30 | 133 | Payra | 22 | 18:00
2 | AKSML | 16 | 03:00 | 68 | Jamalpur | 114 | 08:00 | 134 | Postogola | 38 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jashore | 95 | 13:00 | 135 | Purbachal | 8 | 13:00
4 | Agargaon | 81 | 13:00 | 70 | Jhenaidah | 104 | 18:30 | 136 | Purbasadipur | 119 | 10:00
5 | Agrabad | 68 | 19:00 | 71 | Joydebpur | 129 | 12:00 | 137 | Rahanpur | 11 | 08:00
6 | Amnura | 50 | 08:00 | 72 | Joypurhat | 72 | 09:00 | 138 | Rahim | 40 | 00:00
7 | Ashuganj | 75 | 12:00 | 73 | Juldah | 11 | 00:00 | 139 | Rajbari | 54 | 19:00
8 | BSRM | 204 | 22:00 | 74 | KSRM | 24 | 02:00 | 140 | Rajendrapur | 106 | 13:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 190 | 12:00 | 141 | Rajshahi | 83 | 13:00
10 | Bajitpur | 35 | 18:30 | 76 | Kachua | 58 | 20:00 | 142 | Rajshahi-230 | 62 | 13:00
11 | Bakulia | 68 | 18:30 | 77 | Kallyanpur | 84 | 13:00 | 143 | Ramganj | 102 | 19:00
12 | Banani | 18 | 12:00 | 78 | Kalurghat | 28 | 12:00 | 144 | Rampur | 30 | 00:00
13 | Bangabhaban | 3 | 00:00 | 79 | Kamrangirchar | 54.6 | 00:00 | 145 | Rangamati | 13 | 18:00
14 | Barapukuria | 58 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 111 | 13:00
15 | Barguna | 16 | 13:00 | 81 | Kazla | 83 | 13:00 | 147 | Ruppur | 5 | 12:00
16 | Barishal | 73 | 13:00 | 82 | Keranigonj | 59 | 13:00 | 148 | SSM | 11 | 06:00
17 | Barishal-230 | 78 | 13:00 | 83 | Khagrachori | 28 | 18:30 | 149 | Saidpur | 112 | 09:00
18 | Baroaulia | 49 | 07:00 | 84 | Khosba | 30 | 12:00 | 150 | Satkhira | 103 | 19:00
19 | Baroirhat | 57 | 18:30 | 85 | Khulna | 64 | 19:00 | 151 | Satmasjid | 84 | 13:00
20 | Bashundhara | 149 | 13:00 | 86 | Khulshi | 152 | 18:30 | 152 | Savar | 148 | 12:00
21 | BashundharaCement | 8 | 23:00 | 87 | Kishoreganj | 110 | 19:00 | 153 | SevenRings | 18.61 | 00:00
22 | Beanibazar | 44 | 18:30 | 88 | Kodda | 202 | 00:00 | 154 | ShahCement | 37 | 00:00
23 | Benapole | 62 | 08:00 | 89 | Kulaura | 29 | 18:00 | 155 | Shahjadpur | 57 | 07:00
24 | Bhaluka | 110 | 09:00 | 90 | Kurigram | 56 | 13:00 | 156 | Shahjibazar | 84 | 00:00
25 | Bhandaria | 40 | 00:00 | 91 | Kushtia | 108 | 13:00 | 157 | Shahmirpur | 33 | 18:30
26 | Bhangura | 36 | 08:00 | 92 | Lalbag | 67 | 00:00 | 158 | Shariatpur | 58 | 21:00
27 | Bheramara(GK) | 39 | 18:30 | 93 | Lalmonirhat | 46 | 08:00 | 159 | Sherpur | 120 | 21:00
28 | Bhulta | 261 | 01:00 | 94 | MI_Cement | 18.2 | 01:00 | 160 | Shikalbaha | 16 | 18:30
29 | Bog-Sherpur | 72 | 08:00 | 95 | Madanganj | 37 | 13:00 | 161 | Shitalakhya | 51.6 | 12:00
30 | Bogura | 118 | 19:30 | 96 | Madaripur | 76 | 13:00 | 162 | Sholosohor | 31 | 12:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madartek | 70.41 | 13:00 | 163 | Shyampur | 160 | 12:00
32 | Brahmanbaria | 94 | 19:00 | 98 | Madunaghat | 34 | 12:00 | 164 | Siddhirganj | 90 | 00:00
33 | Cantonment | 98 | 13:00 | 99 | Magura | 50 | 18:30 | 165 | Sirajganj | 80 | 18:30
34 | Chandpur | 48 | 13:00 | 100 | Mahasthangarh | 62 | 12:00 | 166 | Sonargaon | 77 | 00:00
35 | Chandraghona | 27 | 18:30 | 101 | Manikganj | 111 | 18:30 | 167 | Sreemongol | 57 | 18:30
36 | Chapai | 64 | 08:00 | 102 | Maniknagar | 52 | 13:00 | 168 | Sreepur | 68 | 08:00
37 | Charsaidpur | 40 | 08:00 | 103 | Matarbari | 40 | 18:30 | 169 | Srinagar | 35.6 | 12:00
38 | Chauddagram | 56 | 13:00 | 104 | Matuail | 52 | 00:00 | 170 | Sunamganj | 38 | 18:00
39 | Chhatak | 28 | 18:30 | 105 | Millgate | 59 | 09:00 | 171 | Sylhet | 24 | 20:00
40 | Chowmuhani | 145 | 13:00 | 106 | Mirpur | 108 | 12:00 | 172 | Sylhet-132 | 82 | 13:00
41 | Chuadanga | 80 | 13:00 | 107 | Mirsorai | 8 | 18:30 | 173 | TK | 22 | 18:30
42 | Coxsbazar | 111 | 19:30 | 108 | Mirzapur | 35 | 22:00 | 174 | Tangail | 144 | 13:00
43 | Cumilla(N) | 122 | 18:30 | 109 | Mithapukur | 50 | 08:00 | 175 | Thakurgaon | 83 | 09:00
44 | Cumilla(S) | 141 | 12:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 97 | 00:00
45 | Daudkandi | 109 | 19:00 | 111 | Mogbazar | 98.4 | 13:00 | 177 | Ullahpara | 30 | 07:00
46 | Dhaka | 28 | 11:00 | 112 | Mongla | 28 | 00:00 | 178 | Ullon | 37 | 13:00
47 | Dhamrai | 90 | 18:30 | 113 | Motijheel | 26 | 12:00 | 179 | Uttara | 68 | 18:30
48 | Dhanmondi | 98 | 13:00 | 114 | Muktagacha | 26 | 10:00 | 180 | UttaraNew | 34 | 12:00
49 | Dohazari | 81 | 18:00 | 115 | Munshiganj | 76 | 13:00 | 181 | Zigatola | 60 | 13:00
50 | Faridpur | 103 | 18:30 | 116 | Muradnagar | 11.01 | 18:00
51 | Fatullah | 60 | 00:00 | 117 | Mymensingh | 183 | 13:00
52 | Fenchuganj | 29 | 18:30 | 118 | Naogaon | 99 | 09:00
53 | Feni | 68 | 13:00 | 119 | Narail | 46 | 19:00
54 | GPH | 95 | 07:00 | 120 | Narinda | 47 | 12:00
55 | Ghatail | 60 | 09:00 | 121 | Narshingdi | 142 | 19:00
56 | Ghorashal | 12 | 18:30 | 122 | Natore | 114 | 19:00
57 | Ghorashal-230 | 67 | 22:00 | 123 | Nawabganj | 35.2 | 13:00
58 | Goalpara | 28 | 13:00 | 124 | Netrakona | 134 | 11:00
59 | Gollamari | 48 | 00:00 | 125 | New | 60 | 11:00
60 | Gopalganj | 79 | 18:30 | 126 | Niamatpur | 96 | 09:00
61 | Gulshan | 68 | 12:00 | 127 | Noapara | 42 | 19:00
62 | Halishahar | 44 | 19:00 | 128 | PHP | 8 | 13:00
63 | HaripurSBU | 149 | 01:00 | 129 | Pabna | 79 | 19:00
64 | Hasnabad | 71 | 00:00 | 130 | Palashbari | 102 | 07:00
65 | Hathazari | 57 | 18:30 | 131 | Panchagarh | 43 | 18:30
66 | Ishurdi | 52 | 18:30 | 132 | Patuakhali | 57 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-02-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 10302.26 | 30 |  | 10333.61
1:00 | 9784.72 | 70 |  | 9857.72
2:00 | 9353.12 | 70 |  | 9426.12
3:00 | 9029.37 | 70 |  | 9102.37
4:00 | 8758.95 | 70 |  | 8831.95
5:00 | 8654.98 | 70 |  | 8727.98
6:00 | 8926.96 | 0 |  | 8926.96
7:00 | 9445.42 | 100 |  | 9549.42
8:00 | 9842.91 | 86 |  | 9932.78
9:00 | 9863 | 150 |  | 10020
10:00 | 9991.1 | 117 |  | 10113.1
11:00 | 10216.75 | 83 |  | 10303.75
12:00 | 10820.41 | 70 |  | 10893.41
13:00 | 11399.41 | 70 |  | 11472.41
14:00 | 10184.96 | 71 |  | 10259.16
15:00 | 9997.94 | 53 |  | 10053.33
16:00 | 9840.82 | 60 |  | 9903.82
17:00 | 9628.01 | 49 |  | 9679.01
18:00 | 10303.13 | 52 |  | 10357.13
19:00 | 11281.11 | 67 |  | 11351.11
19:30 | 11208.37 | 60 |  | 11271.37
20:00 | 11103.98 | 54 |  | 11159.98
21:00 | 11036.19 | 29 |  | 11066.19
22:00 | 10794.91 | 20 |  | 10815.91
23:00 | 10300.47 | 0 |  | 10300.47
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-02-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6055.7 | 4246.56 | 10302.26 | DAILY GENERATION CURVE
00:30 | 5969.85 | 4073.64 | 10043.49
01:00 | 5884 | 3900.72 | 9784.72 | 28-02-2025
01:30 | 5666.5 | 3902.42 | 9568.92
02:00 | 5449 | 3904.12 | 9353.12
02:30 | 5335.25 | 3855.995 | 9191.245
03:00 | 5221.5 | 3807.87 | 9029.37
03:30 | 5175.75 | 3718.41 | 8894.16
04:00 | 5130 | 3628.95 | 8758.95
04:30 | 5130.5 | 3576.465 | 8706.965
05:00 | 5131 | 3523.98 | 8654.98
05:30 | 5306.5 | 3484.47 | 8790.97
06:00 | 5482 | 3444.96 | 8926.96
06:30 | 5686.515 | 3499.675 | 9186.19
07:00 | 5891.03 | 3554.39 | 9445.42
07:30 | 5970.525 | 3673.64 | 9644.165
08:00 | 6050.02 | 3792.89 | 9842.91
08:30 | 6090.235 | 3762.72 | 9852.955
09:00 | 6130.45 | 3732.55 | 9863
09:30 | 6136.85 | 3790.2 | 9927.05
10:00 | 6143.25 | 3847.85 | 9991.1
10:30 | 6212.605 | 3891.32 | 10103.925
11:00 | 6281.96 | 3934.79 | 10216.75
11:30 | 6504.31 | 4014.27 | 10518.58
12:00 | 6726.66 | 4093.75 | 10820.41
12:30 | 6869.565 | 4240.345 | 11109.91
13:00 | 7012.47 | 4386.94 | 11399.41
13:30 | 6568.935 | 4223.25 | 10792.185
14:00 | 6125.4 | 4059.56 | 10184.96
14:30 | 6117.87 | 3973.58 | 10091.45
15:00 | 6110.34 | 3887.6 | 9997.94
15:30 | 6076.57 | 3842.81 | 9919.38
16:00 | 6042.8 | 3798.02 | 9840.82
16:30 | 5995.755 | 3738.66 | 9734.415
17:00 | 5948.71 | 3679.3 | 9628.01
17:30 | 6172.605 | 3792.965 | 9965.57
18:00 | 6396.5 | 3906.63 | 10303.13
18:30 | 6542.25 | 4249.87 | 10792.12
19:00 | 6688 | 4593.11 | 11281.11
19:30 | 6565 | 4643.37 | 11208.37
20:00 | 6526 | 4577.98 | 11103.98
20:30 | 6444.5 | 4625.585 | 11070.085 |  | Executive Engineer
21:00 | 6363 | 4673.19 | 11036.19 |  | Network Operation Division
21:30 | 6256 | 4659.55 | 10915.55
22:00 | 6149 | 4645.91 | 10794.91
22:30 | 5881 | 4666.69 | 10547.69
23:00 | 5613 | 4687.47 | 10300.47

## En-Curve
QF-LDC-12
Date | 28-02-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2737 | 1626.9 | 926 | 0 | 68 | 760.06 | 40 | 3074 | 0 | 218 | 852.3 | 0 | 0 | 0 | 30 | DAILY ENERGY CURVE
00:30 | 2768 | 1626.7 | 926 | 0 | 64 | 759.14 | 40 | 3075 | 0 | 130.5 | 653.65 | 0 | 0 | 0.5 | 50 | 28-02-2025
01:00 | 2799 | 1626.5 | 926 | 0 | 60 | 758.22 | 40 | 3076 | 0 | 43 | 455 | 0 | 0 | 1 | 70
01:30 | 2791 | 1626.5 | 926 | 0 | 62 | 757.42 | 40 | 3024.5 | 0 | 38 | 298 | 0 | 0 | 5.5 | 70 | Energy Generated | 243.5595 |  | MKWHr
02:00 | 2783 | 1626.5 | 926 | 0 | 64 | 756.62 | 40 | 2973 | 0 | 33 | 141 | 0 | 0 | 10 | 70 | Energy not Served | 1.511 |  | MKWHr
02:30 | 2783 | 1626.75 | 926 | 0 | 61 | 708.495 | 40 | 2902 | 0 | 29 | 106 | 0 | 0 | 9 | 70 | Total Energy Requirement | 245.0705 |  | MKWHr
03:00 | 2783 | 1627 | 926 | 0 | 58 | 660.37 | 40 | 2831 | 0 | 25 | 71 | 0 | 0 | 8 | 70
03:30 | 2785 | 1629.25 | 926 | 0 | 57 | 660.41 | 40 | 2705.5 | 0 | 16.5 | 61.5 | 0 | 0 | 13 | 70
04:00 | 2787 | 1631.5 | 926 | 0 | 56 | 660.45 | 40 | 2580 | 0 | 8 | 52 | 0 | 0 | 18 | 70
04:30 | 2784 | 1633 | 926 | 0 | 56 | 659.465 | 40 | 2529 | 0 | 8 | 52 | 0 | 0 | 19.5 | 70
05:00 | 2781 | 1634.5 | 926 | 0 | 56 | 658.48 | 40 | 2478 | 0 | 8 | 52 | 0 | 0 | 21 | 70
05:30 | 2812 | 1658.5 | 738 | 0 | 56 | 710.47 | 40 | 2639 | 0 | 14 | 104 | 0 | 0 | 19 | 35
06:00 | 2843 | 1682.5 | 550 | 0 | 56 | 762.46 | 40 | 2800 | 0 | 20 | 156 | 0 | 0 | 17 | 0
06:30 | 2887.5 | 1636.5 | 503 | 0 | 57 | 761.61 | 40 | 2918 | 13.58 | 60.5 | 296 | 0 | 0 | 12.5 | 50
07:00 | 2932 | 1590.5 | 456 | 0 | 58 | 760.76 | 40 | 3036 | 27.16 | 101 | 436 | 0 | 0 | 8 | 100
07:30 | 2927.5 | 1565 | 456 | 0 | 59 | 759.38 | 40 | 3055 | 84.285 | 103 | 591 | 0 | 0 | 4 | 93
08:00 | 2923 | 1539.5 | 456 | 0 | 60 | 758 | 40 | 3074 | 141.41 | 105 | 746 | 0 | 0 | 0 | 86
08:30 | 2847 | 1540 | 456 | 0 | 57 | 757 | 40 | 3053 | 207.955 | 112.5 | 780.5 | 0 | 0 | 2 | 118
09:00 | 2771 | 1540.5 | 456 | 0 | 54 | 756 | 40 | 3032 | 274.5 | 120 | 815 | 0 | 0 | 4 | 150
09:30 | 2816 | 1565 | 456 | 0 | 58 | 756.5 | 40 | 3026 | 332.55 | 124 | 750.5 | 0 | 0 | 2.5 | 133.5
10:00 | 2861 | 1589.5 | 456 | 0 | 62 | 757 | 40 | 3020 | 390.6 | 128 | 686 | 0 | 0 | 1 | 117
10:30 | 2883 | 1604 | 456 | 0 | 67 | 755.5 | 40 | 2959.5 | 427.925 | 158 | 751.5 | 0 | 0 | 1.5 | 100
11:00 | 2905 | 1618.5 | 456 | 0 | 72 | 754 | 40 | 2899 | 465.25 | 188 | 817 | 0 | 0 | 2 | 83
11:30 | 2903 | 1545 | 457 | 0 | 76 | 754.5 | 40 | 2987.5 | 470.58 | 204 | 1073 | 0 | 0 | 8 | 76.5
12:00 | 2901 | 1471.5 | 458 | 0 | 80 | 755 | 40 | 3076 | 475.91 | 220 | 1329 | 0 | 0 | 14 | 70
12:30 | 2842 | 1553 | 597.5 | 0 | 79 | 754 | 40 | 3116.5 | 463.91 | 225 | 1425.5 | 0 | 0 | 13.5 | 70
13:00 | 2783 | 1634.5 | 737 | 0 | 78 | 753 | 40 | 3157 | 451.91 | 230 | 1522 | 0 | 0 | 13 | 70
13:30 | 2748 | 1575.5 | 646 | 0 | 75 | 754 | 40 | 3146 | 433.185 | 205.5 | 1159 | 0 | 0 | 10 | 70.5
14:00 | 2713 | 1516.5 | 555 | 0 | 72 | 755 | 40 | 3135 | 414.46 | 181 | 796 | 0 | 0 | 7 | 71
14:30 | 2750.5 | 1526 | 503.5 | 0 | 70 | 756.125 | 40 | 3122.5 | 364.325 | 176 | 771.5 | 0 | 0 | 11 | 62
15:00 | 2788 | 1535.5 | 452 | 0 | 68 | 757.25 | 40 | 3110 | 314.19 | 171 | 747 | 0 | 0 | 15 | 53
15:30 | 2842 | 1585 | 452 | 0 | 66 | 755.85 | 40 | 3114.5 | 250.03 | 167 | 633 | 0 | 0 | 14 | 56.5
16:00 | 2896 | 1634.5 | 452 | 0 | 64 | 754.45 | 40 | 3119 | 185.87 | 163 | 519 | 0 | 0 | 13 | 60
16:30 | 2908 | 1621.75 | 452 | 0 | 63 | 726.4 | 40 | 3101 | 124.265 | 163 | 524 | 0 | 0 | 11 | 54.5
17:00 | 2920 | 1609 | 452 | 0 | 62 | 698.35 | 40 | 3083 | 62.66 | 163 | 529 | 0 | 0 | 9 | 49
17:30 | 2959 | 1624 | 452 | 0 | 63 | 680.115 | 40 | 3171 | 31.455 | 217.5 | 718 | 0 | 0 | 9.5 | 50.5
18:00 | 2998 | 1639 | 452 | 0 | 64 | 661.88 | 40 | 3259 | 0.25 | 272 | 907 | 0 | 0 | 10 | 52
18:30 | 3007 | 1630.25 | 666 | 0 | 65 | 692.745 | 40 | 3282 | 0.125 | 304.5 | 1094.5 | 0 | 0 | 10 | 59.5
19:00 | 3016 | 1621.5 | 880 | 0 | 66 | 723.61 | 40 | 3305 | 0 | 337 | 1282 | 0 | 0 | 10 | 67
19:30 | 3012 | 1573.5 | 881 | 0 | 66 | 755.87 | 40 | 3400 | 0 | 303 | 1171 | 0 | 0 | 6 | 60
20:00 | 3036 | 1594.5 | 880 | 0 | 70 | 758.48 | 40 | 3419 | 0 | 283 | 1023 | 0 | 0 | 0 | 54
20:30 | 3043.5 | 1580.5 | 903.5 | 0 | 71 | 757.585 | 40 | 3450.5 | 0 | 283 | 940.5 | 0 | 0 | 0 | 41.5
21:00 | 3051 | 1566.5 | 927 | 0 | 72 | 756.69 | 40 | 3482 | 0 | 283 | 858 | 0 | 0 | 0 | 29
21:30 | 3046.5 | 1575 | 926.5 | 0 | 70 | 756.55 | 40 | 3478.5 | 0 | 258 | 764.5 | 0 | 0 | 0 | 24.5
22:00 | 3042 | 1583.5 | 926 | 0 | 68 | 756.41 | 40 | 3475 | 0 | 233 | 671 | 0 | 0 | 0 | 20
22:30 | 2992 | 1557 | 926.5 | 0 | 70 | 757.19 | 40 | 3474.5 | 0 | 165 | 564 | 0 | 0 | 1.5 | 10
23:00 | 2942 | 1530.5 | 927 | 0 | 72 | 757.97 | 40 | 3474 | 0 | 97 | 457 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-02-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 402 | 04:00 | 391 | 12:00 | Payra | 417 | 04:00 | 411 | 12:00
Ashuganj | 409 | 14:00 | 392 | 19:00 | Rahanpur | 409 | 00:00 | 396 | 07:00
Bhulta | 399 | 04:00 | 391 | 15:00 | Rampal | 412 | 04:00 | 396 | 20:00
Bibiana | 400 | 21:00 | 393 | 23:00
BIPTC | 409 | 14:00 | 392 | 19:00
Bogura | 406 | 00:00 | 388 | 08:00
Gopalganj | 410 | 05:00 | 398 | 13:00
Kaliakoir | 382 | 08:00 | 376 | 15:00
Madunaghat | 405 | 05:00 | 401 | 16:00
Meghnaghat | 397 | 03:00 | 389 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 04:00 | 225 | 14:00 | Keranigonj | 230 | 05:00 | 223 | 15:00
AKSML | 232 | 18:30 | 226 | 02:00 | Khulna(S) | 240 | 05:00 | 226 | 13:00
Aminbazar | 232 | 05:00 | 225 | 15:00 | Madunaghat | 232 | 08:00 | 228 | 21:00
Ashuganj | 234 | 04:00 | 231 | 07:00 | Madunaghat-400 | 233 | 13:00 | 228 | 02:00
Ashuganj-400 | 234 | 04:00 | 231 | 07:00 | Maniknagar | 230 | 04:00 | 226 | 15:00
Baghabari | 236 | 00:00 | 227 | 12:00 | Meghnaghat | 239 | 05:00 | 234 | 23:00
Barapukuria | 223 | 00:00 | 207 | 07:00 | Meghnaghat-400 | 233 | 04:00 | 228 | 15:00
Barapukuria-230 | 223 | 00:00 | 207 | 07:00 | Mirsorai | 229 | 08:00 | 224 | 15:00
Barishal | 242 | 03:00 | 236 | 14:00 | Rajshahi | 235 | 03:00 | 223 | 13:00
Bheramara | 236 | 14:00 | 223 | 13:00 | Rampal | 238 | 05:00 | 226 | 19:00
Bhulta | 232 | 04:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 18:30 | 226 | 22:00 | Rampura | 232 | 05:00 | 223 | 17:00
BIPTC | 238 | 03:00 | 223 | 13:00 | Shikalbaha | 233 | 19:00 | 227 | 03:00
Bogura | 236 | 00:00 | 224 | 08:00 | Shyampur | 231 | 03:00 | 225 | 11:00
Bogura-400 | 235 | 00:00 | 223 | 08:00 | Siddhirganj | 232 | 04:00 | 229 | 23:00
Borhanuddin | 245 | 03:00 | 241 | 12:00 | Sirajgonj | 242 | 00:00 | 235 | 08:00
BSRM | 229 | 12:00 | 223 | 15:00 | Sreepur | 235 | 00:00 | 228 | 08:00
Cumilla(N) | 229 | 05:00 | 225 | 15:00 | Tongi | 230 | 04:00 | 223 | 00:00
Faridpur | 241 | 03:00 | 235 | 12:00
Fenchuganj | 235 | 21:00 | 232 | 11:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 231 | 05:00 | 226 | 11:00
Gopalganj | 241 | 05:00 | 234 | 13:00
GPH | 230 | 09:00 | 225 | 15:00
Haripur | 232 | 04:00 | 227 | 15:00
Hasnabad | 231 | 04:00 | 224 | 15:00
Hathazari | 233 | 03:00 | 228 | 23:00
Ishurdi | 237 | 03:00 | 225 | 13:00
Jhenaidah | 236 | 02:00 | 220 | 13:00
Kaliakoir | 230 | 04:00 | 225 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 04:00 | 128 | 12:00 | Madunaghat | 134 | 11:00 | 130 | 20:00
Agargaon | 134 | 04:00 | 129 | 15:00 | Magura | 136 | 02:00 | 127 | 18:30
Agrabad | 132 | 08:00 | 129 | 02:00 | Mahasthangarh | 134 | 00:00 | 125 | 08:00
AKS | 130 | 00:00 | 127 | 19:30 | Manikganj | 134 | 07:00 | 130 | 04:00
Aminbazar | 135 | 04:00 | 130 | 15:00 | Maniknagar | 131 | 05:00 | 128 | 11:00
Amnura | 141 | 00:00 | 125 | 07:00 | Matarbari | 124 | 08:00 | 117 | 20:00
Ashuganj | 137 | 03:00 | 135 | 00:00 | Matuail | 134.3 | 10:00 | 129 | 00:00
Bagerhat | 136 | 04:00 | 127 | 19:00 | Millgate | 134 | 06:00 | 128 | 08:00
Bajitpur | 133 | 00:00 | 129 | 11:00 | Mirpur | 134 | 00:00 | 130 | 11:00
Bakulia | 134 | 18:30 | 130 | 03:00 | Mirzapur | 131 | 00:00 | 127 | 04:00
Banani | 132 | 03:00 | 127 | 12:00 | Mithapukur | 132 | 00:00 | 118 | 07:00
Bangabhaban | 131 | 03:00 | 128 | 12:00 | MI_Cement | 133 | 04:00 | 130 | 10:00
Barapukuria | 133 | 00:00 | 122 | 07:00 | Modern | N/A | 00:00 | N/A | 00:00
Barguna | 137 | 16:00 | 131 | 12:00 | Mogbazar | 134 | 03:00 | 130 | 00:00
Barishal | 135 | 05:00 | 130 | 12:00 | Mongla | 136 | 05:00 | 127 | 19:00
Barishal-230 | 136 | 03:00 | 130 | 21:00 | Motijheel | 131 | 03:00 | 128 | 12:00
Baroaulia | 133 | 00:00 | 130 | 07:00 | Muktagacha | 125 | 14:00 | 118 | 11:00
Baroirhat | 130 | 18:30 | 124 | 23:00 | Munshiganj | 132 | 04:00 | 129 | 00:00
Bashundhara | 134 | 05:00 | 128 | 09:00 | Muradnagar | 131 | 04:00 | 128 | 12:00
BashundharaCement | 132 | 18:30 | 128 | 15:00 | Mymensingh | 128 | 18:30 | 114 | 13:00
Beanibazar | 133 | 03:00 | 129 | 12:00 | Naogaon | 131 | 00:00 | 120 | 08:00
Benapole | 137 | 02:00 | 124 | 13:00 | Narail | 138 | 05:00 | 125 | 13:00
Bhaluka | 128 | 21:00 | 118 | 08:00 | Narinda | 131 | 05:00 | 128 | 11:00
Bhandaria | 131 | 05:00 | 126 | 20:00 | Narshingdi | 130 | 10:00 | 126 | 00:00
Bhangura | 135 | 00:00 | 128 | 08:00 | Natore | 135 | 00:00 | 127 | 07:00
Bheramara | 136 | 03:00 | 128 | 13:00 | Nawabganj | 138 | 02:00 | 134 | 12:00
Bheramara(GK) | 136 | 03:00 | 129 | 13:00 | Netrakona | 125 | 00:00 | 112 | 11:00
Bhulta | 127 | 18:30 | 124 | 11:00 | New | 134 | 02:00 | 130 | 11:00
Bog-Sherpur | 134 | 00:00 | 126 | 07:00 | Niamatpur | 134 | 00:00 | 128 | 09:00
Bogura | 137 | 02:00 | 127 | 08:00 | Noapara | 136 | 00:00 | 127 | 13:00
Bogura-230 | 135 | 00:00 | 127 | 08:00 | Pabna | 136 | 00:00 | 129 | 08:00
Brahmanbaria | 132 | 09:00 | 129 | 00:00 | Palashbari | 131 | 01:00 | 116 | 08:00
Cantonment | 133 | 03:00 | 129 | 15:00 | Panchagarh | 132 | 18:00 | 120 | 07:00
Chandpur | 135 | 18:00 | 125 | 23:00 | Patuakhali | 135 | 18:30 | 131 | 14:00
Chandraghona | 134 | 09:00 | 131 | 15:00 | Payra | 136 | 03:00 | 133 | 22:00
Chapai | 133 | 00:00 | 126 | 07:00 | PHP | 128 | 05:00 | 123 | 15:00
Charsaidpur | 133 | 05:00 | 129 | 11:00 | Postogola | 135 | 04:00 | 122 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 129 | 06:00 | 124 | 15:00 | Purbachal | 133 | 04:00 | 128 | 11:00
Chhatak | 131 | 04:00 | 127 | 12:00 | Purbasadipur | 128 | 13:00 | 118 | 07:00
Chowmuhani | 125 | 10:00 | 121 | 15:00 | Rahanpur | 136 | 00:00 | 129 | 08:00
Chuadanga | 137 | 05:00 | 122 | 13:00 | Rahanpur-400 | 135 | 00:00 | 130 | 07:00
Coxsbazar | 123 | 04:00 | 117 | 20:00 | Rahim | 132 | 04:00 | 130 | 00:00
Cumilla(N) | 133 | 05:00 | 129 | 15:00 | Rajbari | 135 | 05:00 | 129 | 13:00
Cumilla(S) | 132 | 05:00 | 127 | 12:00 | Rajendrapur | 132 | 10:00 | 128 | 16:00
Daudkandi | 130 | 08:00 | 126 | 13:00 | Rajshahi | 137 | 03:00 | 129 | 13:00
Dhaka | 132 | 03:00 | 128 | 12:00 | Rajshahi-230 | 136 | 01:00 | 121 | 08:00
Dhamrai | 133 | 02:00 | 128 | 11:00 | Ramganj | 130 | 18:30 | 120 | 23:00
Dhanmondi | 133 | 06:00 | 130 | 23:00 | Rampur | 132 | 08:00 | 129 | 01:00
Dohazari | 131 | 07:00 | 124 | 21:00 | Rampura | 132 | 03:00 | 128 | 12:00
Faridpur | 135 | 01:00 | 131 | 13:00 | Rangamati | 133 | 08:00 | 131 | 00:00
Fatullah | 134 | 04:00 | 131 | 11:00 | Rangpur | 128 | 00:00 | 115 | 07:00
Fenchuganj | 136 | 03:00 | 134 | 11:00 | Ruppur | 136 | 00:00 | 131 | 08:00
Feni | 128 | 00:00 | 123 | 23:00 | Saidpur | 130 | 15:00 | 117 | 07:00
Ghatail | 124 | 14:00 | 119 | 03:00 | Satkhira | 136 | 05:00 | 125 | 13:00
Ghorashal | 139 | 05:00 | 137 | 06:00 | Satmasjid | 134 | 05:00 | 129 | 13:00
Goalpara | 140 | 05:00 | 129 | 13:00 | Savar | 134 | 19:00 | 129 | 10:00
Gollamari | 138 | 02:00 | 130 | 13:00 | SevenRings | 138 | 05:00 | 135 | 15:00
Gopalganj | 138 | 04:00 | 131 | 19:00 | ShahCement | 136 | 02:00 | 129 | 11:00
Gopalganj-400 | 140 | 05:00 | 135 | 13:00 | Shahjadpur | 138 | 00:00 | 133 | 12:00
Gulshan | 131 | 01:00 | 127 | 12:00 | Shahjibazar | 135 | 03:00 | 132 | 00:00
Halishahar | 135 | 18:30 | 130 | 14:00 | Shahmirpur | 135 | 11:00 | 131 | 04:00
Haripur | 132 | 04:00 | 128 | 11:00 | Shariatpur | 138 | 04:00 | 132 | 13:00
HaripurSBU | 132 | 04:00 | 128 | 11:00 | Sherpur | 121 | 14:00 | 107 | 03:00
Hasnabad | 136 | 03:00 | 132 | 11:00 | Shikalbaha | 123 | 09:00 | 119 | 00:00
Hathazari | 135 | 03:00 | 132 | 23:00 | Shikalbaha-230 | 135 | 12:00 | 130 | 02:00
Ishurdi | 138 | 03:00 | 131 | 13:00 | Shitalakhya | 133 | 04:00 | 130 | 10:00
Jaldhaka | 127 | 15:00 | 115 | 07:00 | Sholosohor | 133 | 08:00 | 130 | 03:00
Jamalpur | 125 | 14:00 | 110 | 03:00 | Shyampur | 135 | 18:00 | 131 | 12:00
Jashore | 136 | 02:00 | 125 | 13:00 | Shyampur-230 | 134 | 04:00 | 129 | 15:00
Jhenaidah | 137 | 00:00 | 127 | 13:00 | Siddhirganj | 134 | 10:00 | 130 | 22:00
Jhenaidah-230 | 139 | 03:00 | 127 | 13:00 | Sirajganj | 134 | 00:00 | 127 | 07:00
Joydebpur | 135 | 10:00 | 130 | 21:00 | Sonargaon | 131 | 03:00 | 126 | 15:00
Joypurhat | 129 | 00:00 | 118 | 08:00 | Sreemongol | 133 | 03:00 | 132 | 00:00
Juldah | 136 | 11:00 | 130 | 04:00 | Sreepur | 128 | 04:00 | 124 | 08:00
Kabirpur | 137 | 01:00 | 126 | 15:00 | Srinagar | 137 | 05:00 | 133 | 19:30
Kachua | 133 | 18:30 | 124 | 23:00 | SSM | 138 | 00:00 | 132 | 14:00
Kaliakoir | 137 | 08:00 | 131 | 12:00 | Sunamganj | 132 | 00:00 | 127 | 18:00
Kallyanpur | 136 | 05:00 | 130 | 15:00 | Sylhet | 134 | 05:00 | 130 | 12:00
Kalurghat | 134 | 09:00 | 131 | 03:00 | Sylhet-132 | 133 | 04:00 | 130 | 11:00
Kamrangirchar | 138 | 09:00 | 130 | 12:00 | Tangail | 127 | 14:00 | 123 | 07:00
Kaptai | 134 | 4:00 | 124 | 12:00 | Thakurgaon | 132 | 18:00 | 117 | 07:00
Kazla | 132 | 06:00 | 128 | 00:00 | TK | 134 | 09:00 | 131 | 21:00
Keranigonj | 137 | 04:00 | 133 | 11:00 | Tongi | 135 | 04:00 | 131 | 11:00
Khagrachori | 132 | 08:00 | 130 | 02:00 | Ullahpara | 136 | 03:00 | 129 | 07:00
Khosba | 131 | 04:00 | 127 | 14:00 | Ullon | 133 | 04:00 | 128 | 11:00
Khulna | 136 | 01:00 | 128 | 12:00 | Uttara | 134 | 19:30 | 129 | 11:00
Khulna(S) | 139 | 03:00 | 130 | 13:00 | UttaraNew | 134 | 04:00 | 130 | 11:00
Khulshi | 132 | 08:00 | 128 | 22:00 | Zigatola | 138 | 04:00 | 135 | 12:00
Kishoreganj | 131 | 03:00 | 118 | 08:00
Kodda | 135 | 08:00 | 130 | 15:00
KSRM | 134 | 09:00 | 130 | 16:00
Kulaura | 136 | 05:00 | 133 | 12:00
Kurigram | 130 | 00:00 | 112 | 07:00
Kushtia | 136 | 03:00 | 126 | 13:00
Lalbag | 138 | 04:00 | 134 | 12:00
Lalmonirhat | 129 | 00:00 | 119 | 07:00
Madanganj | 132 | 18:30 | 128 | 15:00
Madaripur | 137 | 07:00 | 133 | 23:00
Madartek | 132 | 04:00 | 128 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division