## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-03-2025 | during | 02-03-2025 | during | 02-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 150 | 151 | 230 | 230 | 150 | 150 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 260 | 260 | 110 | 110 | Reliable test run by OEM
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 403 | 386 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 50 | 8 | 50 | Liquid fuel shortage
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 1 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 146 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 21 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 32 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 18 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 26 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 208 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 79 | 128 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 68 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 163 | 65 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6189 | 5925.764 | 1871 | 2522 | 5110.9 | 5122.9 | 2871.1 | 2883.1
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 23 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 29 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 203 | 203 | 203 | 203 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 37 | 105 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 40 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 85 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 60 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 25 | 4 | 23 | 4 | 23 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 13 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.61 | 0 | 3.61 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 106 | 300 | 300 | 52 | 52 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 29 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 26 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 135 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 980 | 1214 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 447 | 445 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1849 | 2783 | 3424.47 | 3445.86 | 3176.47 | 3197.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 34 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 175 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 2 | 118 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 3 | 189 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 76 | 82 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 50 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 14 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 47 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 102 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 718 | 1238 | 1733.97 | 1668.97 | 1516.03 | 1451.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-03-2025 | during | 02-03-2025 | during | 02-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 22 | 22 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 126 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 89 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.03 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 33 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 172.03 | 254 | 651.6 | 601.5 | 447.6 | 397.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 42 | 38 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 30 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 35 | 35 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 50 | 50 | 60 | 60 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 243 | 243 | 280 | 280 | 280 | 280 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1344 | 1311 | 1447.5 | 1447.5 | 1449 | 1449
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 925 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 41 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 47 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87.86 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 617.1 | 617.1 | 617.1 | 617.1 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1012.86 | 967 | 2967.1 | 2885.1 | 1781.12 | 1699.12
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 541 | 147 | 330 | 264 | 160 | 160 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 13 | 110 | 16 | 110 | 16 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 8 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 127 | 100 | 130 | 130 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1200 | 1244 | 1244 | 1244 | 1244 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 2346 | 2146 | 2408.12 | 2435.12 | 2243.12 | 2336.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 165 | 143 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 137 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 89 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 94 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 95 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.42 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 731.45 | 760 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.72 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1609.09 | 1857.5 | 2582.74 | 2412.24 | 2125.96 | 1955.46
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 60 | 62 | 62 | 60 | 60 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 115 | 163 | 160 | 160 | 160 | 160 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 78 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 75 | 75 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 100 | 0 | 100 | 0 | 179 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 422.1 | 376 | 618.6 | 484 | 661.62 | 448.02
System Total |  |  |  |  | 28986.61 | 28470.742 | 11344.08 | 13454.5 | 20945 | 20503.19 | 16272.02 | 15817.21
Forecast Scenario (02-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11700 |  | 0 |  | 11700
|  |  |  | 1:00 | 11000 |  | 0 |  | 11000
|  |  |  | 2:00 | 10600 |  | 0 |  | 10600
|  |  |  | 3:00 | 10800 |  | 0 |  | 10800
|  |  |  | 4:00 | 11000 |  | 0 |  | 11000
|  |  |  | 5:00 | 10500 |  | 0 |  | 10500
|  |  |  | 6:00 | 9500 |  | 0 |  | 9500
|  |  |  | 7:00 | 10200 |  | 0 |  | 10200
|  |  |  | 8:00 | 10500 |  | 0 |  | 10500
|  |  |  | 9:00 | 10600 |  | 0 |  | 10600
|  |  |  | 10:00 | 11200 |  | 0 |  | 11200
|  |  |  | 11:00 | 11700 |  | 0 |  | 11700
|  |  |  | 12:00 | 12000 |  | 0 |  | 12000
|  |  |  | 13:00 | 11800 |  | 0 |  | 11800
|  |  |  | 14:00 | 11850 |  | 0 |  | 11850
|  |  |  | 15:00 | 11600 |  | 0 |  | 11600
|  |  |  | 16:00 | 11500 |  | 0 |  | 11500
|  |  |  | 17:00 | 12000 |  | 0 |  | 12000
|  |  |  | 18:00 | 12600 |  | 0 |  | 12600
|  |  |  | 18:30 | 12575 |  | 0 |  | 12575
|  |  |  | 19:00 | 12525 |  | 0 |  | 12525
|  |  |  | 19:30 | 12700 |  | 0 |  | 12700
|  |  |  | 20:00 | 12800 |  | 0 |  | 12800
|  |  |  | 21:00 | 13000 |  | 0 |  | 13000
|  |  |  | 22:00 | 12500 |  | 0 |  | 12500
|  |  |  | 23:00 | 12000 |  | 0 |  | 12000
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 12000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 270.173 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:09 hrs on 02-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-03-2025 | [28 empty] | Date: | 01-03-2025 | [28 empty] | Date: | 01-03-2025 | [28 empty] | Date: | 01-03-2025 | [28 empty] | Date: | 01-03-2025 | [18 empty] | Date: | 01-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 110 | 0 | 150 | 0 | 0 | 381 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 19 | 335 | 0 | 0 | 0 | 22 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 34 | 42 | 480 | 0 | 0 | 0 | 0 | 68 | 161 | 0 | 0 | 0 | 940 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 194 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 66 | 0 | 0 | 0 | 305 | 320 | 251 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 9 | 59 | 18 | 0 | 0 | 0 | 5321 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 675.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 168 | 0 | 360 | 0 | 0 | 5.5 | 110 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 90 | 180 | 0 | 534 | 1040 | 0 | 4578.22 | 9899.22 | 88.97
01:00 | 0 | 0 | 8 | 110 | 0 | 150 | 0 | 0 | 380 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 19 | 332 | 0 | 0 | 0 | 22 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 42 | 406 | 0 | 0 | 0 | 0 | 68 | 161 | 0 | 0 | 0 | 861 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 204 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 64 | 0 | 0 | 0 | 310 | 320 | 271 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 47 | 58 | 18 | 0 | 0 | 0 | 5188 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 166 | 0 | 360 | 0 | 0 | 2.5 | 170 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 90 | 180 | 0 | 538 | 850 | 0 | 4282.21 | 9470.21 | 88.97
02:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 380 | 0 | 35 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 19 | 335 | 0 | 0 | 0 | 22 | 12 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 42 | 406 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 715 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 195 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 58 | 0 | 0 | 0 | 305 | 320 | 251 | 36 | 43 | 40 | 2 | 120 | 24 | 0 | 41 | 30 | 0 | 18 | 50 | 0 | 47 | 16 | 19 | 0 | 0 | 0 | 4866 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 165 | 0 | 360 | 0 | 0 | 2.5 | 160 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 10 | 90 | 180 | 0 | 540 | 800 | 0 | 4188.31 | 9054.31 | 88.96
03:00 | 0 | 0 | 0 | 110 | 0 | 152 | 0 | 0 | 380 | 0 | 35 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 20 | 335 | 0 | 0 | 0 | 69 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 34 | 406 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 703 | 0 | 51 | 0 | 157 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 56 | 0 | 0 | 0 | 310 | 320 | 243 | 36 | 43 | 40 | 2 | 120 | 22 | 0 | 41 | 30 | 0 | 18 | 50 | 0 | 18 | 8 | 20 | 0 | 0 | 0 | 4801 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 165 | 0 | 360 | 0 | 0 | 2.5 | 160 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 90 | 180 | 0 | 535 | 800 | 0 | 4078.33 | 8879.33 | 88.96
04:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 20 | 335 | 0 | 0 | 0 | 163 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 42 | 378 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 655 | 0 | 51 | 0 | 108 | 0 | 0 | 0 | 24 | 196 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 295 | 320 | 230 | 5 | 43 | 40 | 2 | 120 | 22 | 0 | 10 | 30 | 0 | 18 | 50 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 4616 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 165 | 0 | 360 | 0 | 0 | 2.5 | 160 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 90 | 180 | 0 | 537 | 700 | 0 | 3931.83 | 8547.83 | 88.96
05:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 20 | 270 | 0 | 0 | 0 | 163 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 42 | 376 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 655 | 0 | 51 | 0 | 108 | 0 | 0 | 0 | 5 | 196 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 56 | 0 | 0 | 0 | 315 | 320 | 222 | 5 | 43 | 40 | 2 | 120 | 22 | 0 | 10 | 30 | 0 | 18 | 50 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4520 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 165 | 0 | 320 | 0 | 0 | 2.5 | 138 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 90 | 180 | 0 | 537 | 700 | 0 | 3873.33 | 8393.33 | 88.95
06:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 20 | 335 | 0 | 0 | 0 | 163 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 42 | 377 | 0 | 0 | 0 | 0 | 10 | 161 | 0 | 0 | 0 | 650 | 0 | 51 | 0 | 184 | 0 | 0 | 0 | 9 | 184 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 60 | 0 | 0 | 0 | 315 | 320 | 213 | 5 | 43 | 40 | 2 | 163 | 22 | 0 | 10 | 30 | 0 | 18 | 50 | 0 | 32 | 32 | 22 | 0 | 0 | 0 | 4827 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 155 | 0 | 360 | 0 | 0 | 2.5 | 130 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 9 | 127 | 220 | 0 | 538 | 700 | 0 | 4012.54 | 8839.54 | 88.95
07:00 | 0 | 6 | 16 | 110 | 0 | 150 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 0 | 0 | 0 | 0 | 19 | 330 | 0 | 0 | 1 | 163 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 18 | 420 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 854 | 2 | 51 | 0 | 184 | 0 | 0 | 0 | 29 | 220 | 36 | 0 | 51 | 0 | 0 | 16 | 0 | 52 | 0 | 4 | 0 | 320 | 320 | 268 | 20 | 43 | 40 | 2 | 163 | 22 | 0 | 83 | 30 | 0 | 18 | 50 | 0 | 66 | 65 | 22 | 0 | 2.21 | 0 | 5427.71 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 0 | 570.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 2.05 | 176 | 0 | 0 | 0 | 141 | 0 | 414 | 0 | 0.18 | 5.5 | 135 | 61 | 0 | 1 | 0 | 0 | 0 | 0.2 | 8 | 0.02 | 0 | 271 | 9 | 127 | 220 | 0 | 538 | 780 | 0 | 4400.38 | 9828.09 | 88.95
08:00 | 0 | 30 | 16 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 22 | 48 | 0 | 0 | 0 | 0 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 19 | 335 | 0 | 0 | 8 | 163 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 40 | 5 | 8 | 480 | 0 | 0 | 0 | 0 | 37 | 161 | 0 | 0 | 0 | 952 | 7 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 36 | 6 | 50 | 6 | 9 | 16 | 0 | 52 | 0 | 19 | 0 | 295 | 320 | 242 | 32 | 43 | 40 | 2 | 120 | 22 | 0 | 83 | 30 | 0 | 18 | 50 | 0 | 66 | 85 | 19 | 0 | 10.52 | 0 | 5568.52 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.08 | 0 | 0 | 656.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 10.66 | 176 | 0 | 0 | 0 | 129 | 0 | 414 | 0 | 0.87 | 5.5 | 135 | 61 | 90 | 7 | 33 | 0 | 0 | 1.4 | 39 | 0.1 | 0 | 307 | 8 | 127 | 220 | 0 | 538 | 940 | 0 | 4840.48 | 10409 | 88.94
09:00 | 0 | 52 | 26 | 110 | 0 | 150 | 0 | 0 | 397 | 0 | 0 | 0 | 8 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 19 | 280 | 0 | 0 | 15 | 163 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 17 | 2 | 475 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 855 | 12 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 33 | 16 | 50 | 0 | 9 | 16 | 0 | 54 | 0 | 37 | 0 | 280 | 320 | 242 | 32 | 43 | 30 | 2 | 120 | 22 | 0 | 83 | 30 | 0 | 18 | 50 | 0 | 69 | 87 | 15 | 1 | 21.29 | 4 | 5373.29 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.39 | 0 | 0 | 753.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 53 | 0 | 22.66 | 176 | 0 | 0 | 0 | 132 | 0 | 350 | 0 | 0 | 5.5 | 153 | 61 | 95 | 15 | 34 | 0 | 0 | 3.1 | 83 | 0.31 | 0 | 307 | 7 | 129 | 180 | 0 | 579 | 900 | 0 | 4977.33 | 10350.62 | 88.94
10:00 | 0 | 17 | 26 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 19 | 280 | 0 | 0 | 23 | 163 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 17 | 2 | 470 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 855 | 16 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 206 | 36 | 16 | 50 | 0 | 9 | 16 | 0 | 46 | 0 | 45 | 0 | 295 | 320 | 272 | 32 | 43 | 30 | 2 | 120 | 22 | 0 | 83 | 30 | 0 | 18 | 50 | 0 | 69 | 65 | 5 | 1 | 31.08 | 6 | 5361.08 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.74 | 0 | 0 | 692.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 38 | 171 | 0 | 0 | 0 | 156 | 0 | 350 | 0 | 3.23 | 5.5 | 122 | 61 | 35 | 23 | 34 | 0 | 0 | 4.8 | 100 | 0.45 | 0 | 307 | 7 | 129 | 180 | 0 | 583 | 900 | 0 | 4978.87 | 10339.95 | 88.94
11:00 | 0 | 17 | 26 | 110 | 0 | 150 | 0 | 0 | 403 | 0 | 0 | 0 | 18 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 17 | 323 | 0 | 0 | 27 | 163 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 4 | 40 | 17 | 2 | 450 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 863 | 17 | 43 | 0 | 163 | 0 | 0 | 0 | 29 | 206 | 31 | 16 | 50 | 0 | 9 | 14 | 0 | 54 | 0 | 57 | 0 | 325 | 320 | 271 | 35 | 42 | 29 | 2 | 163 | 23 | 0 | 83 | 30 | 0 | 18 | 50 | 0 | 69 | 88 | 5 | 2 | 37.56 | 6 | 5544.56 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.22 | 0 | 0 | 667.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 92 | 0 | 48.22 | 166 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 3.94 | 5.5 | 88 | 61 | 35 | 24 | 34 | 0 | 0 | 0 | 100 | 0.53 | 0 | 307 | 7 | 127 | 220 | 0 | 585 | 940 | 0 | 5091.18 | 10635.74 | 88.93
12:00 | 0 | 51 | 26 | 110 | 0 | 150 | 0 | 0 | 403 | 0 | 0 | 1 | 0 | 0 | 79 | 16 | 0 | 0 | 0 | 35 | 25 | 0 | 400 | 0 | 0 | 0 | 30 | 16 | 320 | 0 | 0 | 27 | 163 | 19 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 4 | 0 | 0 | 0 | 60 | 24 | 4 | 70 | 26 | 2 | 447 | 0 | 0 | 0 | 0 | 37 | 161 | 0 | 0 | 0 | 980 | 19 | 43 | 2 | 175 | 0 | 0 | 0 | 29 | 183 | 32 | 36 | 50 | 3 | 9 | 16 | 0 | 76 | 0 | 64 | 0 | 305 | 320 | 243 | 35 | 42 | 29 | 2 | 163 | 24 | 0 | 83 | 30 | 0 | 18 | 50 | 0 | 55 | 65 | 5 | 2 | 39.03 | 6 | 5954.03 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.86 | 0 | 0 | 731.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 51.72 | 165 | 0 | 0 | 0 | 143 | 0 | 414 | 0 | 4.42 | 5.5 | 115 | 62 | 75 | 30 | 34 | 0 | 0 | 6.1 | 100 | 0 | 13 | 307 | 8 | 127 | 220 | 0 | 541 | 1130 | 0 | 5390.05 | 11344.08 | 88.93
13:00 | 0 | 51 | 25 | 110 | 0 | 151 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 135 | 31 | 0 | 420 | 0 | 0 | 0 | 55 | 16 | 314 | 0 | 0 | 28 | 163 | 19 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 4 | 0 | 0 | 0 | 62 | 75 | 4 | 40 | 76 | 3 | 447 | 0 | 0 | 0 | 0 | 98 | 161 | 0 | 0 | 0 | 1030 | 19 | 43 | 31 | 182 | 0 | 0 | 0 | 29 | 183 | 34 | 72 | 50 | 60 | 9 | 16 | 0 | 80 | 0 | 62 | 0 | 300 | 320 | 248 | 35 | 42 | 29 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 16 | 50 | 0 | 55 | 65 | 5 | 2 | 39.82 | 6 | 6533.82 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.15 | 0 | 0 | 758.45 | 0 | 0 | 0 | 2 | 0 | 0 | 25 | 0 | 0 | 96 | 0 | 36.01 | 163 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 2.22 | 5.5 | 155 | 61 | 75 | 30 | 34 | 0 | 0 | 5.7 | 100 | 0.53 | 16 | 307 | 10 | 127 | 220 | 0 | 452 | 1244 | 0 | 5494.56 | 12028.38 | 88.93
14:00 | 0 | 51 | 25 | 110 | 0 | 151 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 94 | 16 | 0 | 0 | 0 | 144 | 31 | 0 | 450 | 0 | 0 | 0 | 35 | 16.5 | 317 | 0 | 0 | 24 | 163 | 19 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 6 | 0 | 0 | 0 | 62 | 12 | 3 | 40 | 90 | 2 | 450 | 0 | 0 | 0 | 0 | 105 | 161 | 0 | 0 | 0 | 1032 | 16 | 43 | 60 | 184 | 0 | 0 | 0 | 29 | 194 | 34 | 91 | 50 | 100 | 9 | 16 | 0 | 80 | 0 | 55 | 0 | 300 | 320 | 269 | 35 | 39 | 29 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 16 | 50 | 0 | 45 | 55 | 5 | 2 | 30.16 | 6 | 6552.66 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6 | 0 | 0 | 758 | 0 | 0 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 74 | 0 | 42.09 | 156 | 0 | 0 | 0 | 139 | 0 | 414 | 0 | 3.69 | 5.5 | 161 | 61 | 75 | 26 | 34 | 0 | 0 | 5.1 | 100 | 0.47 | 16 | 307 | 10 | 120 | 220 | 0 | 324 | 1244 | 0 | 5363.45 | 11916.11 | 88.92
15:00 | 0 | 51 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 81 | 32 | 0 | 0 | 0 | 144 | 32 | 0 | 450 | 0 | 0 | 0 | 35 | 16.5 | 270 | 0 | 0 | 19 | 163 | 20 | 0 | 0 | 0 | 10 | 106 | 0 | 0 | 2 | 0 | 0 | 0 | 73 | 12 | 2 | 40 | 92 | 2 | 450 | 0 | 0 | 0 | 0 | 105 | 161 | 0 | 0 | 0 | 1111 | 13 | 43 | 62 | 182 | 0 | 0 | 0 | 29 | 182 | 33 | 90 | 50 | 115 | 15 | 14 | 0 | 82 | 0 | 38 | 0 | 310 | 320 | 242 | 35 | 38 | 28 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 16 | 50 | 0 | 67 | 93 | 5 | 1 | 23.71 | 6 | 6688.21 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.97 | 0 | 0 | 765 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 59 | 0 | 31.69 | 149 | 0 | 0 | 0 | 137 | 0 | 414 | 0 | 2.68 | 5.5 | 132 | 60 | 75 | 19 | 34 | 0 | 0 | 0 | 91 | 0.37 | 16 | 307 | 10 | 127 | 220 | 0 | 284 | 1244 | 8 | 5245.21 | 11933.42 | 88.92
16:00 | 0 | 51 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 54 | 0 | 0 | 96 | 32 | 0 | 0 | 0 | 90 | 32 | 3 | 450 | 0 | 0 | 0 | 35 | 16.5 | 270 | 0 | 0 | 9 | 163 | 20 | 15 | 0 | 0 | 35 | 106 | 0 | 0 | 6 | 0 | 0 | 0 | 72 | 12 | 1 | 40 | 92 | 2 | 447 | 0 | 0 | 0 | 0 | 105 | 161 | 0 | 0 | 0 | 1172 | 8 | 43 | 77 | 182 | 0 | 0 | 0 | 29 | 182 | 34 | 71 | 50 | 155 | 37 | 14 | 0 | 76 | 0 | 24 | 0 | 310 | 320 | 242 | 35 | 38 | 28 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 16 | 50 | 0 | 68 | 90 | 5 | 1 | 14.4 | 1 | 6735.9 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 755 | 0 | 0 | 0 | 38 | 0 | 0 | 35 | 0 | 0 | 36 | 0 | 18.8 | 145 | 0 | 0 | 0 | 135 | 0 | 414 | 0 | 1.64 | 5.5 | 155 | 62 | 55 | 11 | 33 | 0 | 0 | 2.2 | 47 | 0.41 | 32 | 307 | 9 | 127 | 220 | 0 | 169 | 1200 | 17 | 4993.55 | 11729.45 | 88.92
17:00 | 0 | 51 | 25 | 110 | 0 | 150 | 0 | 0 | 356 | 0 | 0 | 54 | 0 | 0 | 96 | 32 | 0 | 0 | 0 | 90 | 32 | 13 | 380 | 0 | 0 | 0 | 55 | 16.5 | 270 | 0 | 0 | 3 | 163 | 21 | 20 | 0 | 0 | 35 | 106 | 0 | 0 | 3 | 0 | 0 | 0 | 86 | 12 | 0 | 40 | 92 | 5 | 452 | 0 | 0 | 0 | 0 | 105 | 161 | 0 | 0 | 0 | 1214 | 2 | 43 | 87 | 125 | 0 | 0 | 0 | 29 | 182 | 34 | 70 | 50 | 155 | 53 | 16 | 0 | 68 | 0 | 8 | 0 | 295 | 320 | 247 | 35 | 38 | 28 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 16 | 50 | 0 | 68 | 104 | 5 | 0 | 4.49 | 6 | 6648.99 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 90 | 0 | 0 | 55 | 0 | 0 | 13 | 0 | 5.7 | 144 | 0 | 0 | 0 | 133 | 0 | 414 | 0 | 0.52 | 5.5 | 165 | 61 | 54 | 4 | 34 | 0 | 0 | 0.8 | 16 | 0.08 | 32 | 307 | 9 | 127 | 220 | 0 | 148 | 1100 | 17 | 4836.6 | 11485.59 | 88.91
18:00 | 4 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 54 | 30 | 0 | 96 | 78 | 18 | 5 | 35 | 162 | 32 | 14 | 380 | 0 | 0 | 0 | 55 | 18 | 325 | 0 | 0 | 0 | 0 | 21 | 20 | 0 | 0 | 35 | 106 | 0 | 0 | 1 | 24 | 32 | 6 | 0 | 45 | 0 | 40 | 105 | 18 | 443 | 17 | 0 | 4 | 1 | 105 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 105 | 127 | 0 | 0 | 0 | 29 | 181 | 34 | 68 | 50 | 158 | 48 | 14 | 0 | 74 | 16 | 0 | 26 | 300 | 320 | 243 | 35 | 38 | 28 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 88 | 125 | 5 | 0 | 0 | 6 | 7010 | 925 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 94 | 4 | 46 | 95 | 9 | 0 | 0 | 12 | 0 | 141 | 0 | 0 | 0 | 134 | 0 | 414 | 0 | 0 | 5.5 | 165 | 62 | 74 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 10 | 127 | 220 | 0 | 148 | 1100 | 54 | 5046.5 | 12056.5 | 88.91
19:00 | 8 | 68 | 25 | 110 | 0 | 151 | 0 | 0 | 386 | 0 | 0 | 54 | 54 | 0 | 128 | 146 | 208 | 15 | 55 | 162 | 32 | 16 | 450 | 0 | 0 | 0 | 55 | 18 | 280 | 0 | 0 | 0 | 65 | 21 | 15 | 0 | 0 | 35 | 106 | 13 | 0 | 0 | 85 | 40 | 29 | 88 | 100 | 0 | 40 | 110 | 25 | 445 | 135 | 0 | 29 | 23 | 105 | 161 | 0 | 0 | 0 | 1214 | 0 | 51 | 118 | 182 | 0 | 0 | 0 | 29 | 181 | 34 | 102 | 50 | 189 | 47 | 14 | 70 | 82 | 50 | 0 | 39 | 315 | 320 | 243 | 35 | 38 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 33 | 89 | 126 | 0 | 0 | 0 | 6 | 8108 | 879 | 0 | 0 | 41 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 50 | 0 | 94 | 5 | 89 | 95 | 35 | 0 | 0 | 30 | 0 | 143 | 0 | 0 | 0 | 137 | 0 | 414 | 0 | 0 | 5.5 | 163 | 60 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 100 | 220 | 0 | 147 | 1200 | 54 | 5346.5 | 13454.5 | 88.91
19:30 | 12 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 350 | 0 | 0 | 54 | 54 | 0 | 113 | 130 | 180 | 15 | 55 | 162 | 32 | 28 | 450 | 0 | 0 | 0 | 55 | 18 | 280 | 0 | 0 | 0 | 136 | 21 | 7 | 0 | 0 | 35 | 106 | 51 | 0 | 0 | 85 | 48 | 17 | 88 | 50 | 0 | 40 | 110 | 21 | 450 | 90 | 0 | 26 | 25 | 105 | 161 | 0 | 0 | 0 | 1214 | 0 | 51 | 120 | 194 | 0 | 0 | 0 | 29 | 183 | 35 | 115 | 50 | 155 | 47 | 16 | 70 | 80 | 25 | 0 | 39 | 285 | 320 | 243 | 35 | 38 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 54.5 | 89 | 105 | 0 | 0 | 0 | 6 | 7971.5 | 878 | 0 | 0 | 35 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 43 | 0 | 94 | 5 | 89 | 50 | 35 | 0 | 0 | 30 | 0 | 146 | 0 | 0 | 0 | 139 | 0 | 414 | 0 | 0 | 5.5 | 163 | 61 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 100 | 220 | 0 | 124 | 1230 | 54 | 5287.5 | 13259
20:00 | 15 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 350 | 0 | 0 | 54 | 54 | 0 | 113 | 130 | 180 | 15 | 55 | 162 | 32 | 26 | 340 | 0 | 0 | 0 | 55 | 18 | 240 | 0 | 0 | 0 | 144 | 21 | 21 | 0 | 0 | 35 | 106 | 50 | 0 | 0 | 85 | 48 | 17 | 88 | 50 | 0 | 40 | 110 | 30 | 448 | 90 | 0 | 26 | 25 | 105 | 161 | 0 | 0 | 0 | 1214 | 0 | 51 | 120 | 195 | 0 | 0 | 0 | 29 | 183 | 35 | 115 | 50 | 155 | 47 | 14 | 70 | 78 | 25 | 0 | 39 | 280 | 320 | 192 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 54.5 | 89 | 105 | 0 | 0 | 0 | 6 | 7795.5 | 878 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 50 | 0 | 94 | 6 | 89 | 50 | 37 | 0 | 0 | 30 | 0 | 147 | 0 | 0 | 0 | 140 | 0 | 370 | 0 | 0 | 5.5 | 165 | 61 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 8 | 100 | 180 | 0 | 144 | 1244 | 54 | 5267.5 | 13063 | 88.9
21:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 351 | 0 | 0 | 54 | 54 | 0 | 113 | 130 | 60 | 0 | 55 | 90 | 32 | 43 | 400 | 0 | 0 | 0 | 55 | 18 | 270 | 0 | 0 | 0 | 144 | 21 | 21 | 0 | 0 | 35 | 106 | 0 | 0 | 0 | 85 | 48 | 17 | 88 | 50 | 0 | 40 | 110 | 34 | 449 | 17 | 0 | 26 | 8 | 105 | 161 | 0 | 0 | 0 | 1214 | 0 | 51 | 120 | 175 | 0 | 0 | 0 | 29 | 204 | 35 | 115 | 50 | 51 | 47 | 16 | 21 | 80 | 8 | 0 | 39 | 300 | 320 | 220 | 35 | 42 | 30 | 2 | 163 | 24 | 0 | 83 | 30 | 0 | 18 | 50 | 54.5 | 89 | 105 | 0 | 0 | 0 | 6 | 7469.5 | 925 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 50 | 0 | 94 | 6 | 89 | 35 | 37 | 8 | 0 | 30 | 0 | 154 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 0 | 5.5 | 167 | 61 | 53 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 8 | 127 | 180 | 0 | 159 | 1244 | 17 | 5275.5 | 12745 | 88.9
22:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 407 | 0 | 0 | 54 | 54 | 0 | 87 | 115 | 60 | 0 | 55 | 90 | 32 | 50 | 400 | 0 | 0 | 0 | 55 | 18 | 328 | 0 | 0 | 0 | 144 | 21 | 21 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 85 | 48 | 17 | 88 | 50 | 0 | 40 | 110 | 29 | 450 | 0 | 0 | 26 | 0 | 105 | 161 | 0 | 0 | 0 | 1214 | 0 | 51 | 50 | 192 | 0 | 0 | 0 | 29 | 184 | 34 | 115 | 50 | 51 | 47 | 16 | 17 | 76 | 0 | 0 | 39 | 305 | 320 | 192 | 35 | 42 | 30 | 2 | 163 | 24 | 0 | 83 | 30 | 0 | 18 | 50 | 54.5 | 89 | 105 | 0 | 0 | 0 | 6 | 7353.5 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 50 | 0 | 94 | 6 | 89 | 35 | 32 | 8 | 0 | 30 | 0 | 159 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 5.5 | 165 | 62 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 10 | 127 | 220 | 0 | 160 | 1244 | 17 | 5296.5 | 12650 | 88.9
23:00 | 0 | 68 | 25 | 110 | 0 | 150 | 0 | 0 | 406 | 0 | 0 | 54 | 54 | 0 | 78 | 82 | 15 | 0 | 55 | 90 | 32 | 43 | 400 | 0 | 0 | 0 | 35 | 19 | 328 | 0 | 0 | 0 | 144 | 22 | 21 | 0 | 0 | 35 | 51 | 0 | 0 | 0 | 51 | 47 | 0 | 88 | 50 | 0 | 40 | 110 | 38 | 450 | 0 | 0 | 26 | 0 | 105 | 147 | 0 | 0 | 0 | 1218 | 0 | 51 | 50 | 192 | 0 | 0 | 0 | 29 | 182 | 32 | 68 | 50 | 51 | 48 | 16 | 0 | 74 | 0 | 0 | 0 | 270 | 320 | 192 | 35 | 42 | 30 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 50 | 0 | 89 | 105 | 0 | 0 | 0 | 6 | 6992 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 94 | 0 | 88 | 35 | 5 | 8 | 0 | 8 | 0 | 160 | 0 | 0 | 0 | 148 | 0 | 360 | 0 | 0 | 2.5 | 163 | 62 | 75 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 13 | 127 | 220 | 0 | 166 | 1244 | 17 | 5106.5 | 12098.5 | 88.89
Total KWH | 25776 | 873965 | 437366 | 2621700 | 0 | 3598156 | 0 | 0 | 9417600 | 0 | 50800 | 518472 | 482040 | 0 | 1478592 | 933600 | 719356 | 62403 | 328578 | 1437120 | 682920 | 234240 | 9386500 | 0 | 0 | 0 | 528100 | 418000 | 7473121 | 0 | 0 | 186052 | 3198000 | 421200 | 340200 | 0 | 0 | 333709 | 1029982 | 98928 | 0 | 44640 | 442306 | 269904 | 116150 | 1074240 | 509760 | 24840 | 984000 | 1354067 | 522720 | 10290909.09 | 205745 | 0 | 163680 | 80596.8 | 1598290 | 3797032 | 0 | 0 | 0 | 23558179 | 129735 | 1083928 | 913309 | 4031273 | 0 | 0 | 0 | 647040 | 4717000 | 834984 | 1114560 | 1196930 | 1442880 | 500640 | 371760 | 165300 | 1619520 | 87581 | 409818 | 144512 | 7368500 | 7676000 | 6050000 | 739728 | 977000 | 770160 | 55392 | 3537818 | 551352 | 0 | 1701120 | 717408 | 0 | 420000 | 1231570 | 234360 | 1420800 | 1706400 | 218880 | 11050 | 253530 | 90960 | 147496332.89 | 22214545 | 0 | 0 | 71040 | 128640 | 0 | 0 | 0 | 0 | 0 | 0 | 570960 | 0 | 0 | 15817455 | 0 | 222454 | 0 | 831744 | 21336 | 514336 | 586080 | 147087 | 46056 | 645150 | 134587 | 317248 | 3922545 | 0 | 0 | 0 | 3755136 | 0 | 9412436 | 0 | 23820 | 111312 | 3550000 | 1435200 | 1138404 | 191941 | 837619 | 0 | 0 | 36937.68 | 779040 | 3660 | 646752 | 6698000 | 230579 | 2791000 | 5162250 | 0 | 9272728 | 25060363.64 | 286800 | 117615241.32 | 265111574.21

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11344.08 | MW | 12:00 Hr. | Energy Generated |  |  | 265.1116 |  | MKWHr.
| Day Peak Demand |  |  | 11344.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13454.5 | MW | 19:00 Hr. | Energy Demand |  |  | 265.1116 |  | MKWHr.
| Evening Peak Demand |  |  | 13454.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.6 |  | °C
| Minimum Generation of the Day |  |  | 8393.33 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 867.94 |  | MMCFD
| Maximum Generation of the Day |  |  | 13454.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.328 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.4102 | 0 | 11.2576 | 0 | 0 | 0.18605 | 0 | 0 | 45.8539 | Gas | 109.0131 | Gas | 395726848.9
| Chattogram Zone |  |  | 4.3198 | 33.8491 | 7.2774 | 0 | 0.984 | 0.15457 | 0 | 0.04464 | 46.6294 | Coal | 79.8654 | Coal | 494647080.8549
| Cumilla Zone |  |  | 12.8829 | 0 | 4.3688 | 0 | 0 | 0.40982 | 1.6195 | 0 | 19.281 | HFO | 31.9692 | HFO | 529679843.876
| Mymensingh Zone |  |  | 0.21888 | 0 | 3.4525 | 0 | 0 | 0.26458 | 0 | 0 | 3.936 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.796 | Hydro | 0.984 | Hydro | 98400
| Khulna Zone |  |  | 0 | 0 | 0.19968 | 0 | 0 | 0.57096 | 22.2145 | 0 | 22.9852 | Solar | 3.5838 | Solar | 57580294.6848
| Barishal Zone |  |  | 8.1838 | 41.0311 | 0.93355 | 0 | 0 | 0.00366 | 0 | 0 | 50.1521 | Import | 39.6515 | Import | 199244534.95
| Rajshahi Zone |  |  | 17.2014 | 0 | 2.5037 | 0 | 0 | 0.98622 | 15.8175 | 0 | 36.5088 | Wind | 0.04464 | Wind | 653529.6
| Rangpur Zone |  |  | 0 | 4.9852 | 1.976 | 0 | 0 | 1.0079 | 0 | 0 | 7.9691
| Total |  |  | 109.0131 | 79.8654 | 31.9692 | 0 | 0.984 | 3.5838 | 39.6515 | 0.04464 | 265.1116
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 395726848.9 |  | Hydro | 98400
|  |  |  | Coal | 494647080.8549 |  | Solar | 57580294.6848
|  |  |  | HFO | 529679843.876 |  | Import | 199244534.95
|  |  |  | HSD | 0 |  | Wind | 653529.6
[5 empty] | Total: | 167,76,30,532 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2145 | Peak Hr Flow | 879.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 5866465000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.8175 | Peak Hr Flow | 760.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 308 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6195 | Peak Hr Flow | 82.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 624 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.6515 | Peak Hr Flow | 1721.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4870
|  |  |  | Chattogram |  | 0 |  | 1339
|  |  |  | Cumilla |  | 0 |  | 1181
|  |  |  | Mymensingh |  | 0 |  | 1086
|  |  |  | Sylhet |  | 0 |  | 464
|  |  |  | Khulna |  | 0 |  | 1549
|  |  |  | Barishal |  | 0 |  | 389
|  |  |  | Rajshahi |  | 0 |  | 1314
|  |  |  | Rangpur |  | 0 |  | 845
|  |  |  | Total |  | 0 |  | 13037
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 944.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1736.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 | 14:30 | Faridpur 132/33kV S/S Bus-B Scheduled S/D
| 08:11 | 10:35 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to WZPDCL Maintenance.
| 08:12 | 10:35 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to WZPDCL Maintenance. | [7 empty] | 15.0MW load
interrup.
|  | 08:58 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 is restored.
|  | 08:58 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 is restored.
|  | 08:59 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
|  | 09:07 | Fenchuganj -Sylhet 132kV Ckt-1 is restored.
| 09:13 |  | Bibiyana-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to AM
| 09:18 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:- Plant is running at part load due
to low gas pressure
| 09:27 | 12:35 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Dead line checking
|  | 09:27 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 09:28 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
| 09:30 | 15:07 | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D Due to gas Leakages | [7 empty] | 12.0MW load
interrup.
| 09:30 | 15:06 | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D Due to Gas Leakages | [7 empty] | 12.0MW load
interrup.
| 09:35 | 14:30 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning
| 09:35 | 14:30 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disk cleaning
| 09:35 | 14:30 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disk cleaning
|  | 10:02 | Noapara 132/33kV S/S T-1 HT is restored.
|  | 10:05 | Noapara 132/33kV S/S T-1 LT is restored.
| 10:13 | 15:33 | Khulna(S) 230/132kV S/S TR-2 LT Scheduled S/D Due to 800MW NWPGCL Maintenance Work
| 10:14 | 15:31 | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D Due to 800MW NWPGCL Maintenance Work
| 10:30 | 15:15 | Khulna(S) 230/132kV S/S 230 KV Main Bus 1 Scheduled S/D Due to 800MW NWPGCL Maintenance
Work
| 10:40 | 15:30 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to Shutdown
instructed by NLDC
|  | 11:01 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
|  | 11:02 | Kabirpur 132/33kV S/S XFR, T-3 LT is restored.
| 12:00 |  | Day Peak Generation: 11341 MW.
| 12:02 | 12:58 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to
NLDC SDE. and from Kishoreganj 132/33kV end Due to 132 kv Bajitpur bus loop disconnection
work by project
| 12:10 | 12:51 | Kishoreganj 132/33kV S/S BUS-B Project Work S/D Due to 132 kv Bajitpur bus loop
disconnection work by project
| 12:28 | 12:42 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Project Work S/D Due to New T1 Moving work by
project
| 12:28 | 12:42 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Project Work S/D Due to New T1 Moving work by | [7 empty] | 30.0MW load
|  |  | project | [7 empty] | interrup.
| 12:38 | 15:31 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline checking
|  | 13:45 | Faridpur 132/33kV S/S ATR-1 HT is restored.
|  | 13:46 | Faridpur 132/33kV S/S ATR-1 LT is restored.
| 13:55 | 14:46 | Faridpur 132/33kV S/S ATR-2 LT Scheduled S/D Due to Hot spot Maintenance.
| 13:55 | 14:45 | Faridpur 132/33kV S/S ATR-2 HT Scheduled S/D Due to Hot spot Maintenance.
| 15:09 | 17:40 | Fatullah-Shyampur(New) 132 kV Ckt-1 Tripped from Fatullah 132/33kV end showing 21 trip,
zone-1 trip relays Due to Trip
| 15:46 | 18:25 | Bagerhat-Mongla 132 kV Ckt-1 Project Work S/D from Mongla 132/33kV end Due to G 2 G | [7 empty] | 15.0MW load
|  |  | project work | [7 empty] | interrup. Mongla
132/33kV end
| 16:03 | 18:36 | Mongla 132/33kV S/S 100MW ERBL Solar PS Project Work S/D Due to G 2 G project work | [7 empty] | 15.0MW load
interrup.
| 16:04 | 18:25 | Bagerhat-Mongla 132 kV Ckt-2 Project Work S/D from Mongla 132/33kV end Due to G 2 G | [7 empty] | 15.0MW load
|  |  | project work | [7 empty] | interrup. Mongla
132/33kV end
| 16:05 | 18:27 | Mongla 132/33kV S/S T-2 HT Project Work S/D Due to G 2 G project work | [7 empty] | 15.0MW load
interrup.
| 16:05 | 18:37 | Mongla 132/33kV S/S T-2 LT Project Work S/D Due to G 2 G project work | [7 empty] | 15.0MW load
interrup.
| 17:47 |  | Bhaluka - Sripur BR PowerGen P.P. line - 1 & 2 tripped from the Power Plant end without
operating any relay.
| 18:08 |  | Bhaluka - Sripur BR PowerGen line -1 & 2 were switched on.
| 19:00 |  | Evening Peak Gen. 13454 MW
| 20:13 | 21:57 | Ishurdi-Pabna 132kV ckt Forced S/D from Pabna 132/33kV end.
| 20:27 | 21:57 | Ishurdi-Pabna 132kV ckt Forced S/D from Ishurdi 132/33kV end Due to RED HOT at pabna end
| 21:17 | 00:58 | Mahasthangar-Palashbari 132kV Ckt-2 Forced S/D from Mahasthangarh 132/33kV end Due to | [7 empty] | 89.0MW load
|  |  | 363 tower cracking | [7 empty] | interrup.
Mahasthangarh
132/33kV end
| 07:11 |  | Kushtia 132/33kV S/S T2 HT Forced S/D Due to Oil leakage of Tr-02 33 kv side
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 151 | 3598156 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2621700 | Reliable test run by OEM
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 386 | 9417600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9386500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 62403 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7473121 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 25776 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 518472 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 933600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 328578 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 528100 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 421200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 340200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 682920 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 18 | 418000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 437366 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 208 | 719356 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 128 | 1478592 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 68 | 873965 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 234240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1437120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 186052 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 482040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 50800 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 65 | 3198000 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2522 | 45853857
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 23 | 80596.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 129735 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 29 | 163680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 984000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3797032 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1598290 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 40 | 269904 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 442306 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1074240 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 522720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 13 | 98928 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 106 | 1029982 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 29 | 116150 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1354067 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 509760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 333709 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 135 | 205745 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1214 | 23558179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 44640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 445 | 10290909.09 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2783 | 46629412.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4717000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 834984 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 647040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 4031273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1083928 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 118 | 913309 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 144512 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1196930 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 189 | 1442880 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 82 | 1619520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 50 | 87581 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 371760 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 165300 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 500640 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 102 | 1114560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 409818 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1238 | 19281035
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 218880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 126 | 1706400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1420800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 253530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 90960 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 33 | 234360 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 254 | 3935980
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 977000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 770160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3537818 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 739728 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 55392 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 717408 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1701120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 50 | 1231570 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 551352 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7368500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 243 | 6050000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7676000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1311 | 31796048
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 22214545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 41 | 71040 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 47 | 128640 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 570960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | U#1maintenance Shutdown,U#2 Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 967 | 22985185
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 147 | 9272728 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 646752 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 230579 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 100 | 2791000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 25060363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5162250 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 286800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6698000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3660 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2146 | 50152132.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 222454 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 21336 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 147087 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 143 | 3922545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 137 | 3755136 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9412436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 134587 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 111312 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 46056 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 514336 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 831744 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 586080 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 760 | 15817455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 317248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 645150 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1857.5 | 36508782
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 1435200 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 3550000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 837619 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36937.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 75 | 1138404 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 191941 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 779040 | -
Rangpur Area Total |  |  |  |  | 950 | 376 | 7969141.68
Eastern Grid Total |  |  |  |  | 16761.242 | 8108 | 147496332.89
Western Grid Total |  |  |  |  | 11614.5 | 5346.5 | 117615241.32
National Grid Total |  |  |  |  | 28375.742 | 13454.5 | 265111574.21
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-03-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8939.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4097.1 | MW
i) Dhaka area |  |  | 4870.04 |  | MW | i) Khulna area |  |  |  | 1549 | MW
ii) Chattogram area |  |  | 1338.6 |  | MW | ii) Barishal area |  |  |  | 388.9 | MW
iii) Cumilla area |  |  | 1181 |  | MW | iii) Rajshahi area |  |  |  | 1314.2 | MW
iv) Mymensingh area |  |  | 1086 |  | MW | iv) Rangpur area |  |  |  | 845 | MW
v) Sylhet area |  |  | 464 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13036.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 70 | 12:00 | 133 | Payra | 24 | 19:00
2 | AKSML | 24.4 | 15:00 | 68 | Jamalpur | 126 | 08:00 | 134 | Postogola | 49 | 13:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 128 | 19:00 | 135 | Purbachal | 9 | 19:00
4 | Agargaon | 92 | 19:00 | 70 | Jhenaidah | 117 | 19:00 | 136 | Purbasadipur | 124 | 13:00
5 | Agrabad | 82 | 18:30 | 71 | Joydebpur | 156 | 18:30 | 137 | Rahanpur | 12 | 09:00
6 | Amnura | 53 | 19:00 | 72 | Joypurhat | 69 | 19:00 | 138 | Rahim | 39 | 14:00
7 | Ashuganj | 84.5 | 19:30 | 73 | Juldah | 13 | 11:00 | 139 | Rajbari | 64 | 19:00
8 | BSRM | 203 | 22:00 | 74 | KSRM | 31 | 01:00 | 140 | Rajendrapur | 110 | 19:00
9 | Bagerhat | 82 | 19:00 | 75 | Kabirpur | 250 | 18:00 | 141 | Rajshahi | 92 | 19:00
10 | Bajitpur | 49 | 13:00 | 76 | Kachua | 71 | 19:00 | 142 | Rajshahi-230 | 66 | 13:00
11 | Bakulia | 85 | 19:00 | 77 | Kallyanpur | 92 | 19:30 | 143 | Ramganj | 124 | 18:30
12 | Banani | 22.2 | 15:00 | 78 | Kalurghat | 38 | 15:00 | 144 | Rampur | 34 | 18:30
13 | Bangabhaban | 5 | 10:00 | 79 | Kamrangirchar | 60.4 | 23:00 | 145 | Rangamati | 15 | 18:30
14 | Barapukuria | 60 | 08:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 125 | 19:00
15 | Barguna | 18 | 20:00 | 81 | Kazla | 109 | 18:30 | 147 | Ruppur | 4 | 11:00
16 | Barishal | 98 | 20:00 | 82 | Keranigonj | 75 | 19:00 | 148 | SSM | 16 | 00:00
17 | Barishal-230 | 84 | 19:00 | 83 | Khagrachori | 24 | 18:30 | 149 | Saidpur | 106 | 09:00
18 | Baroaulia | 60 | 11:00 | 84 | Khosba | 29 | 20:00 | 150 | Satkhira | 121 | 19:00
19 | Baroirhat | 59 | 18:30 | 85 | Khulna | 80 | 19:00 | 151 | Satmasjid | 94 | 14:00
20 | Bashundhara | 163 | 19:00 | 86 | Khulshi | 150 | 11:00 | 152 | Savar | 200 | 15:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 128 | 19:30 | 153 | SevenRings | 18.6 | 17:00
22 | Beanibazar | 50 | 19:00 | 88 | Kodda | 289 | 16:00 | 154 | ShahCement | 34 | 07:00
23 | Benapole | 66 | 08:00 | 89 | Kulaura | 35 | 18:30 | 155 | Shahjadpur | 74 | 11:00
24 | Bhaluka | 118 | 09:00 | 90 | Kurigram | 60 | 08:00 | 156 | Shahjibazar | 108 | 18:30
25 | Bhandaria | 45 | 19:30 | 91 | Kushtia | 122 | 13:00 | 157 | Shahmirpur | 44 | 18:30
26 | Bhangura | 37 | 14:00 | 92 | Lalbag | 73 | 19:00 | 158 | Shariatpur | 69 | 20:00
27 | Bheramara(GK) | 47 | 19:00 | 93 | Lalmonirhat | 48 | 18:30 | 159 | Sherpur | 148 | 09:00
28 | Bhulta | 250 | 23:00 | 94 | MI_Cement | 17 | 03:00 | 160 | Shikalbaha | 25 | 23:00
29 | Bog-Sherpur | 70 | 08:00 | 95 | Madanganj | 39 | 20:00 | 161 | Shitalakhya | 72.6 | 12:00
30 | Bogura | 138 | 18:30 | 96 | Madaripur | 91 | 19:00 | 162 | Sholosohor | 37 | 16:00
31 | Borhanuddin | 70 | 21:00 | 97 | Madartek | 70.85 | 12:00 | 163 | Shyampur | 178 | 10:00
32 | Brahmanbaria | 107 | 22:00 | 98 | Madunaghat | 42 | 12:00 | 164 | Siddhirganj | 109 | 14:00
33 | Cantonment | 106 | 13:00 | 99 | Magura | 57 | 19:00 | 165 | Sirajganj | 100 | 19:00
34 | Chandpur | 58 | 19:00 | 100 | Mahasthangarh | 66 | 08:00 | 166 | Sonargaon | 98 | 18:30
35 | Chandraghona | 32 | 21:00 | 101 | Manikganj | 125 | 19:00 | 167 | Sreemongol | 51 | 19:30
36 | Chapai | 64 | 12:00 | 102 | Maniknagar | 62 | 13:00 | 168 | Sreepur | 90 | 18:30
37 | Charsaidpur | 41 | 15:00 | 103 | Matarbari | 44 | 18:30 | 169 | Srinagar | 38.3 | 20:00
38 | Chauddagram | 69 | 18:30 | 104 | Matuail | 60 | 12:00 | 170 | Sunamganj | 48 | 19:00
39 | Chhatak | 27 | 15:00 | 105 | Millgate | 74 | 15:00 | 171 | Sylhet | 30 | 18:00
40 | Chowmuhani | 176 | 20:00 | 106 | Mirpur | 119 | 18:30 | 172 | Sylhet-132 | 96 | 18:00
41 | Chuadanga | 90 | 19:00 | 107 | Mirsorai | 8 | 15:00 | 173 | TK | 26.6 | 18:30
42 | Coxsbazar | 132 | 18:30 | 108 | Mirzapur | 40 | 08:00 | 174 | Tangail | 172 | 18:30
43 | Cumilla(N) | 129 | 18:30 | 109 | Mithapukur | 54 | 08:00 | 175 | Thakurgaon | 89 | 19:00
44 | Cumilla(S) | 164 | 15:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 108 | 15:00
45 | Daudkandi | 141 | 19:00 | 111 | Mogbazar | 118.8 | 13:00 | 177 | Ullahpara | 30 | 13:00
46 | Dhaka | 42 | 13:00 | 112 | Mongla | 32 | 12:00 | 178 | Ullon | 37 | 19:00
47 | Dhamrai | 112 | 18:30 | 113 | Motijheel | 33 | 13:00 | 179 | Uttara | 73 | 18:30
48 | Dhanmondi | 118 | 13:00 | 114 | Muktagacha | 34 | 08:00 | 180 | UttaraNew | 41 | 22:00
49 | Dohazari | 83 | 19:00 | 115 | Munshiganj | 80 | 20:00 | 181 | Zigatola | 63 | 19:00
50 | Faridpur | 133 | 20:00 | 116 | Muradnagar | 12 | 18:30
51 | Fatullah | 81 | 16:00 | 117 | Mymensingh | 183 | 19:30
52 | Fenchuganj | 27 | 18:00 | 118 | Naogaon | 113 | 13:00
53 | Feni | 90 | 20:00 | 119 | Narail | 53 | 19:00
54 | GPH | 94 | 18:00 | 120 | Narinda | 62.5 | 18:00
55 | Ghatail | 78 | 18:30 | 121 | Narshingdi | 164 | 19:00
56 | Ghorashal | 13 | 11:00 | 122 | Natore | 130 | 19:00
57 | Ghorashal-230 | 82 | 19:00 | 123 | Nawabganj | 45.6 | 19:30
58 | Goalpara | 30 | 13:00 | 124 | Netrakona | 130 | 13:00
59 | Gollamari | 54 | 13:00 | 125 | New | 79.3 | 12:00
60 | Gopalganj | 98 | 19:00 | 126 | Niamatpur | 98 | 08:00
61 | Gulshan | 84 | 15:00 | 127 | Noapara | 44 | 13:00
62 | Halishahar | 61 | 15:00 | 128 | PHP | 9 | 15:00
63 | HaripurSBU | 156 | 16:00 | 129 | Pabna | 99 | 19:00
64 | Hasnabad | 100 | 15:00 | 130 | Palashbari | 102 | 08:00
65 | Hathazari | 67 | 19:00 | 131 | Panchagarh | 47 | 19:00
66 | Ishurdi | 62 | 19:00 | 132 | Patuakhali | 61.6 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9899.22 | 0 |  | 9899.22
1:00 | 9470.21 | 0 |  | 9470.21
2:00 | 9054.31 | 0 |  | 9054.31
3:00 | 8879.33 | 0 |  | 8879.33
4:00 | 8547.83 | 0 |  | 8547.83
5:00 | 8393.33 | 0 |  | 8393.33
6:00 | 8839.54 | 0 |  | 8839.54
7:00 | 9828.09 | 0 |  | 9828.09
8:00 | 10409 | 0 |  | 10409
9:00 | 10350.62 | 0 |  | 10350.62
10:00 | 10339.95 | 0 |  | 10339.95
11:00 | 10635.74 | 0 |  | 10635.74
12:00 | 11344.08 | 0 |  | 11344.08
13:00 | 12028.38 | 0 |  | 12028.38
14:00 | 11916.11 | 0 |  | 11916.11
15:00 | 11933.42 | 0 |  | 11933.42
16:00 | 11729.45 | 0 |  | 11729.45
17:00 | 11485.59 | 0 |  | 11485.59
18:00 | 12056.5 | 0 |  | 12056.5
19:00 | 13454.5 | 0 |  | 13454.5
19:30 | 13259 | 0 |  | 13259
20:00 | 13063 | 0 |  | 13063
21:00 | 12745 | 0 |  | 12745
22:00 | 12650 | 0 |  | 12650
23:00 | 12098.5 | 0 |  | 12098.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5321 | 4578.22 | 9899.22 | DAILY GENERATION CURVE
00:30 | 5254.5 | 4430.215 | 9684.715
01:00 | 5188 | 4282.21 | 9470.21 | 01-03-2025
01:30 | 5027 | 4235.26 | 9262.26
02:00 | 4866 | 4188.31 | 9054.31
02:30 | 4833.5 | 4133.32 | 8966.82
03:00 | 4801 | 4078.33 | 8879.33
03:30 | 4708.5 | 4005.08 | 8713.58
04:00 | 4616 | 3931.83 | 8547.83
04:30 | 4568 | 3902.58 | 8470.58
05:00 | 4520 | 3873.33 | 8393.33
05:30 | 4673.5 | 3942.935 | 8616.435
06:00 | 4827 | 4012.54 | 8839.54
06:30 | 5127.355 | 4206.46 | 9333.815
07:00 | 5427.71 | 4400.38 | 9828.09
07:30 | 5498.115 | 4620.43 | 10118.545
08:00 | 5568.52 | 4840.48 | 10409
08:30 | 5470.905 | 4908.905 | 10379.81
09:00 | 5373.29 | 4977.33 | 10350.62
09:30 | 5367.185 | 4978.1 | 10345.285
10:00 | 5361.08 | 4978.87 | 10339.95
10:30 | 5452.82 | 5035.025 | 10487.845
11:00 | 5544.56 | 5091.18 | 10635.74
11:30 | 5749.295 | 5240.615 | 10989.91
12:00 | 5954.03 | 5390.05 | 11344.08
12:30 | 6243.925 | 5442.305 | 11686.23
13:00 | 6533.82 | 5494.56 | 12028.38
13:30 | 6543.24 | 5429.005 | 11972.245
14:00 | 6552.66 | 5363.45 | 11916.11
14:30 | 6620.435 | 5304.33 | 11924.765
15:00 | 6688.21 | 5245.21 | 11933.42
15:30 | 6712.055 | 5119.38 | 11831.435
16:00 | 6735.9 | 4993.55 | 11729.45
16:30 | 6692.445 | 4915.075 | 11607.52
17:00 | 6648.99 | 4836.6 | 11485.59
17:30 | 6829.495 | 4941.55 | 11771.045
18:00 | 7010 | 5046.5 | 12056.5
18:30 | 7559 | 5196.5 | 12755.5
19:00 | 8108 | 5346.5 | 13454.5
19:30 | 7971.5 | 5287.5 | 13259
20:00 | 7795.5 | 5267.5 | 13063
20:30 | 7632.5 | 5271.5 | 12904 |  | Executive Engineer
21:00 | 7469.5 | 5275.5 | 12745 |  | Network Operation Division
21:30 | 7411.5 | 5286 | 12697.5
22:00 | 7353.5 | 5296.5 | 12650
22:30 | 7172.75 | 5201.5 | 12374.25
23:00 | 6992 | 5106.5 | 12098.5

## En-Curve
QF-LDC-12
Date | 01-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2970 | 1550.5 | 927 | 0 | 66 | 675.72 | 40 | 3416 | 0 | 30 | 217 | 0 | 0 | 7 | 0 | DAILY ENERGY CURVE
00:30 | 2983 | 1551.5 | 926.5 | 0 | 65 | 593.215 | 40 | 3276 | 0 | 30 | 214 | 0 | 0 | 5.5 | 0 | 01-03-2025
01:00 | 2996 | 1552.5 | 926 | 0 | 64 | 510.71 | 40 | 3136 | 0 | 30 | 211 | 0 | 0 | 4 | 0
01:30 | 2984.5 | 1542.5 | 926 | 0 | 61 | 511.76 | 40 | 3014.5 | 0 | 26 | 152 | 0 | 0 | 4 | 0 | Energy Generated | 265.1116 |  | MKWHr
02:00 | 2973 | 1532.5 | 926 | 0 | 58 | 512.81 | 40 | 2893 | 0 | 22 | 93 | 0 | 0 | 4 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2965 | 1512 | 926.5 | 0 | 57 | 464.82 | 40 | 2879 | 0 | 45.5 | 74.5 | 0 | 0 | 2.5 | 0 | Total Energy Requirement | 265.1116 |  | MKWHr
03:00 | 2957 | 1491.5 | 927 | 0 | 56 | 416.83 | 40 | 2865 | 0 | 69 | 56 | 0 | 0 | 1 | 0
03:30 | 2956 | 1412.5 | 927 | 0 | 55 | 417.58 | 40 | 2753 | 0 | 116 | 34 | 0 | 0 | 2.5 | 0
04:00 | 2955 | 1333.5 | 927 | 0 | 54 | 418.33 | 40 | 2641 | 0 | 163 | 12 | 0 | 0 | 4 | 0
04:30 | 2889.5 | 1333.5 | 927 | 0 | 55 | 419.08 | 40 | 2629 | 0 | 163 | 12 | 0 | 0 | 2.5 | 0
05:00 | 2824 | 1333.5 | 927 | 0 | 56 | 419.83 | 40 | 2617 | 0 | 163 | 12 | 0 | 0 | 1 | 0
05:30 | 2888.5 | 1439.5 | 927 | 0 | 58 | 419.435 | 40 | 2631.5 | 0 | 163 | 49 | 0 | 0 | 0.5 | 0
06:00 | 2953 | 1545.5 | 927 | 0 | 60 | 419.04 | 40 | 2646 | 0 | 163 | 86 | 0 | 0 | 0 | 0
06:30 | 3032 | 1592.25 | 927 | 0 | 56 | 494.955 | 40 | 2852.5 | 17.11 | 182 | 140 | 0 | 0 | 0 | 0
07:00 | 3111 | 1639 | 927 | 0 | 52 | 570.87 | 40 | 3059 | 34.22 | 201 | 194 | 0 | 0 | 0 | 0
07:30 | 3072 | 1583.75 | 912 | 0 | 52 | 613.87 | 40 | 3236 | 91.425 | 229 | 288.5 | 0 | 0 | 0 | 0
08:00 | 3033 | 1528.5 | 897 | 0 | 52 | 656.87 | 40 | 3413 | 148.63 | 257 | 383 | 0 | 0 | 0 | 0
08:30 | 2965.5 | 1461.5 | 888 | 0 | 53 | 705.12 | 40 | 3371.5 | 232.69 | 257 | 405.5 | 0 | 0 | 0 | 0
09:00 | 2898 | 1394.5 | 879 | 0 | 54 | 753.37 | 40 | 3330 | 316.75 | 257 | 428 | 0 | 0 | 0 | 0
09:30 | 2933 | 1372 | 901.5 | 0 | 50 | 722.76 | 40 | 3314 | 375.025 | 231.5 | 405.5 | 0 | 0 | 0 | 0
10:00 | 2968 | 1349.5 | 924 | 0 | 46 | 692.15 | 40 | 3298 | 433.3 | 206 | 383 | 0 | 0 | 0 | 0
10:30 | 3011 | 1420.5 | 925 | 0 | 50 | 679.96 | 40 | 3296 | 464.885 | 206 | 394 | 0 | 0 | 0.5 | 0
11:00 | 3054 | 1491.5 | 926 | 0 | 54 | 667.77 | 40 | 3294 | 496.47 | 206 | 405 | 0 | 0 | 1 | 0
11:30 | 3024.5 | 1531 | 925.5 | 0 | 65 | 699.61 | 55 | 3438 | 512.8 | 231 | 505 | 0 | 0 | 2.5 | 0
12:00 | 2995 | 1570.5 | 925 | 0 | 76 | 731.45 | 70 | 3582 | 529.13 | 256 | 605 | 0 | 0 | 4 | 0
12:30 | 2993 | 1587.5 | 925 | 0 | 78 | 744.95 | 55 | 3639 | 522.28 | 255.5 | 882 | 0 | 0 | 4 | 0
13:00 | 2991 | 1604.5 | 925 | 0 | 80 | 758.45 | 40 | 3696 | 515.43 | 255 | 1159 | 0 | 0 | 4 | 0
13:30 | 2998.5 | 1598.75 | 925 | 0 | 80 | 758.225 | 40 | 3637.5 | 486.77 | 255 | 1187.5 | 0 | 0 | 5 | 0
14:00 | 3006 | 1593 | 925 | 0 | 80 | 758 | 40 | 3579 | 458.11 | 255 | 1216 | 0 | 0 | 6 | 0
14:30 | 2959.5 | 1618.5 | 925 | 0 | 81 | 761.5 | 40 | 3583.5 | 408.765 | 263 | 1280 | 0 | 0 | 4 | 0
15:00 | 2913 | 1644 | 925 | 0 | 82 | 765 | 40 | 3588 | 359.42 | 271 | 1344 | 0 | 0 | 2 | 0
15:30 | 2910.5 | 1629.5 | 925 | 0 | 79 | 760 | 40 | 3550 | 285.935 | 271 | 1376.5 | 0 | 0 | 4 | 0
16:00 | 2908 | 1615 | 925 | 0 | 76 | 755 | 40 | 3512 | 212.45 | 271 | 1409 | 0 | 0 | 6 | 0
16:30 | 2886.5 | 1549.5 | 925 | 0 | 72 | 755.5 | 40 | 3479.5 | 135.02 | 271 | 1489 | 0 | 0 | 4.5 | 0
17:00 | 2865 | 1484 | 925 | 0 | 68 | 756 | 40 | 3447 | 57.59 | 271 | 1569 | 0 | 0 | 3 | 0
17:30 | 2912.5 | 1519.75 | 925 | 0 | 71 | 755 | 40 | 3448 | 28.795 | 300.5 | 1768.5 | 0 | 0 | 2 | 0
18:00 | 2960 | 1555.5 | 925 | 0 | 74 | 754 | 40 | 3449 | 0 | 330 | 1968 | 0 | 0 | 1 | 0
18:30 | 2918 | 1604 | 902 | 0 | 78 | 757 | 40 | 3492.5 | 0 | 547.5 | 2416 | 0 | 0 | 0.5 | 0
19:00 | 2876 | 1652.5 | 879 | 0 | 82 | 760 | 40 | 3536 | 0 | 765 | 2864 | 0 | 0 | 0 | 0
19:30 | 2847 | 1624.5 | 878 | 0 | 80 | 757 | 40 | 3549 | 0 | 805 | 2678.5 | 0 | 0 | 0 | 0
20:00 | 2718 | 1491.5 | 878 | 0 | 78 | 758 | 40 | 3583 | 0 | 838 | 2678.5 | 0 | 0 | 0 | 0
20:30 | 2799 | 1544.5 | 901.5 | 0 | 79 | 758.5 | 40 | 3592 | 0 | 816.5 | 2373 | 0 | 0 | 0 | 0
21:00 | 2880 | 1597.5 | 925 | 0 | 80 | 759 | 40 | 3601 | 0 | 795 | 2067.5 | 0 | 0 | 0 | 0
21:30 | 2916 | 1627 | 925 | 0 | 78 | 758.5 | 40 | 3601.5 | 0 | 763 | 1988.5 | 0 | 0 | 0 | 0
22:00 | 2952 | 1656.5 | 925 | 0 | 76 | 758 | 40 | 3602 | 0 | 731 | 1909.5 | 0 | 0 | 0 | 0
22:30 | 2917 | 1646 | 925 | 0 | 75 | 755.5 | 40 | 3606 | 0 | 624.5 | 1785.25 | 0 | 0 | 0 | 0
23:00 | 2882 | 1635.5 | 925 | 0 | 74 | 753 | 40 | 3610 | 0 | 518 | 1661 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 402 | 04:00 | 400 | 05:00 | Payra | 416 | 03:00 | 405 | 12:00
Ashuganj | 406 | 5:00 | 390 | 12:00 | Rahanpur | 415 | 04:00 | 399 | 08:00
Bhulta | 399 | 03:00 | 376 | 12:00 | Rampal | 411 | 04:00 | 384 | 12:00
Bibiana | 399 | 19:00 | 389 | 12:00
BIPTC | 400 | 05:00 | 391 | 13:00
Bogura | 413 | 03:00 | 394 | 12:00
Gopalganj | 408 | 05:00 | 383 | 12:00
Kaliakoir | 382 | 03:00 | 363 | 14:00
Madunaghat | 408 | 06:00 | 397 | 12:00
Meghnaghat | 398 | 05:00 | 374 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 05:00 | 215 | 12:00 | Keranigonj | 230 | 05:00 | 214 | 12:00
AKSML | 234 | 19:30 | 222 | 11:00 | Khulna(S) | 238 | 03:00 | 220 | 12:00
Aminbazar | 230 | 03:00 | 216 | 12:00 | Madunaghat | 234 | 19:00 | 225 | 11:00
Ashuganj | 234 | 03:00 | 224 | 12:00 | Madunaghat-400 | 234 | 20:00 | 224 | 12:00
Ashuganj-400 | 232 | 4:00 | 226 | 12:00 | Maniknagar | 229 | 04:00 | 217 | 12:00
Baghabari | 237 | 19:30 | 226 | 12:00 | Meghnaghat | 238 | 05:00 | 225 | 11:00
Barapukuria | 228 | 16:00 | 219 | 07:00 | Meghnaghat-400 | 233 | 04:00 | 219 | 12:00
Barapukuria-230 | 226 | 15:00 | 218 | 8:00 | Mirsorai | 234 | 19:00 | 222 | 11:00
Barishal | 242 | 05:00 | 232 | 11:00 | Rajshahi | 237 | 20:00 | 221 | 12:00
Bheramara | 235 | 19:30 | 222 | 07:00 | Rampal | 237 | 04:00 | 220 | 11:00
Bhulta | 232 | 03:00 | 218 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 03:00 | 223 | 16:00 | Rampura | 231 | 04:00 | 217 | 12:00
BIPTC | 237 | 03:00 | 224 | 07:00 | Shikalbaha | 236 | 19:00 | 222 | 11:00
Bogura | 239 | 03:00 | 228 | 08:00 | Shyampur | 230 | 04:00 | 216 | 12:00
Bogura-400 | 239 | 23:00 | 227 | 08:00 | Siddhirganj | 230 | 03:00 | 227 | 22:00
Borhanuddin | 245 | 04:00 | 242 | 00:00 | Sirajgonj | 243 | 02:00 | 237 | 11:00
BSRM | 232 | 19:00 | 221 | 12:00 | Sreepur | 238 | 04:00 | 227 | 12:00
Cumilla(N) | 228 | 04:00 | 218 | 12:00 | Tongi | 229 | 05:00 | 215 | 12:00
Faridpur | 241 | 04:00 | 228 | 11:00
Fenchuganj | 235 | 06:00 | 230 | 11:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 231 | 05:00 | 219 | 12:00
Gopalganj | 240 | 04:00 | 226 | 12:00
GPH | 233 | 19:00 | 223 | 11:00
Haripur | 232 | 04:00 | 217 | 12:00
Hasnabad | 230 | 04:00 | 217 | 11:00
Hathazari | 236 | 19:00 | 224 | 11:00
Ishurdi | 237 | 03:00 | 226 | 07:00
Jhenaidah | 235 | 04:00 | 219 | 12:00
Kaliakoir | 230 | 02:00 | 216 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 04:00 | 121 | 12:00 | Madunaghat | 135 | 19:00 | 129 | 10:00
Agargaon | 134 | 05:00 | 123 | 12:00 | Magura | 136 | 04:00 | 125 | 11:00
Agrabad | 134 | 19:00 | 125 | 10:00 | Mahasthangarh | 136 | 07:00 | 125 | 08:00
AKS | 132 | 19:00 | 124 | 11:00 | Manikganj | 133 | 19:00 | 124 | 14:00
Aminbazar | 134 | 02:00 | 124 | 12:00 | Maniknagar | 131 | 05:00 | 122 | 12:00
Amnura | 142 | 19:30 | 126 | 12:00 | Matarbari | 121 | 01:00 | 117 | 12:00
Ashuganj | 137 | 06:00 | 133 | 16:00 | Matuail | 132 | 03:00 | 124 | 12:00
Bagerhat | 136 | 06:00 | 121 | 11:00 | Millgate | 135 | 03:00 | 124 | 11:00
Bajitpur | 132 | 07:00 | 127 | 17:00 | Mirpur | 134 | 03:00 | 122 | 12:00
Bakulia | 134 | 19:00 | 126 | 11:00 | Mirzapur | 135 | 17:00 | 123 | 14:00
Banani | 132 | 05:00 | 121 | 15:00 | Mithapukur | 134 | 21:00 | 123 | 10:00
Bangabhaban | 131 | 04:00 | 122 | 12:00 | MI_Cement | 133 | 03:00 | 124 | 12:00
Barapukuria | 137 | 16:00 | 128 | 07:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 136 | 19:00 | 128 | 11:00 | Mogbazar | 134 | 04:00 | 122 | 12:00
Barishal | 135 | 20:00 | 128 | 11:00 | Mongla | 132 | 04:00 | 122 | 12:00
Barishal-230 | 135 | 05:00 | 128 | 11:00 | Motijheel | 131 | 04:00 | 122 | 12:00
Baroaulia | 135 | 19:00 | 127 | 12:00 | Muktagacha | 130 | 15:00 | 116 | 07:00
Baroirhat | 131 | 19:00 | 120 | 12:00 | Munshiganj | 132 | 03:00 | 124 | 12:00
Bashundhara | 135 | 02:00 | 121 | 12:00 | Muradnagar | 130 | 04:00 | 122 | 12:00
BashundharaCement | 131 | 01:00 | 123 | 12:00 | Mymensingh | 132 | 15:00 | 113 | 18:00
Beanibazar | 134 | 10:00 | 128 | 18:00 | Naogaon | 133 | 04:00 | 120 | 08:00
Benapole | 136 | 03:00 | 121 | 12:00 | Narail | 137 | 05:00 | 124 | 11:00
Bhaluka | 130 | 04:00 | 118 | 18:00 | Narinda | 131 | 5:00 | 122 | 12:00
Bhandaria | 132 | 06:00 | 125 | 12:00 | Narshingdi | 130 | 06:00 | 119 | 18:30
Bhangura | 136 | 03:00 | 128 | 11:00 | Natore | 135 | 20:00 | 126 | 12:00
Bheramara | 135 | 03:00 | 127 | 12:00 | Nawabganj | 138 | 04:00 | 127 | 12:00
Bheramara(GK) | 134 | 03:00 | 128 | 10:00 | Netrakona | 123 | 23:00 | 111 | 13:00
Bhulta | 126 | 09:00 | 120 | 12:00 | New | 135 | 02:00 | 125 | 12:00
Bog-Sherpur | 136 | 05:00 | 126 | 08:00 | Niamatpur | 136 | 23:00 | 129 | 08:00
Bogura | 137 | 23:00 | 127 | 12:00 | Noapara | 137 | 04:00 | 124 | 11:00
Bogura-230 | 137 | 23:00 | 128 | 08:00 | Pabna | 136 | 03:00 | 127 | 21:00
Brahmanbaria | 132 | 09:00 | 125 | 17:00 | Palashbari | 130 | 03:00 | 116 | 08:00
Cantonment | 134 | 05:00 | 123 | 12:00 | Panchagarh | 140 | 23:00 | 121 | 10:00
Chandpur | 136 | 19:30 | 118 | 11:00 | Patuakhali | 136 | 18:00 | 128 | 11:00
Chandraghona | 134 | 19:00 | 129 | 11:00 | Payra | 137 | 18:00 | 132 | 11:00
Chapai | 134 | 23:00 | 127 | 12:00 | PHP | 129 | 20:00 | 120 | 11:00
Charsaidpur | 132 | 02:00 | 32 | 04:00 | Postogola | 135 | 05:00 | 126 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 130 | 19:00 | 121 | 11:00 | Purbachal | 131 | 01:00 | 121 | 12:00
Chhatak | 132 | 01:00 | 126 | 18:30 | Purbasadipur | 135 | 22:00 | 119 | 10:00
Chowmuhani | 128 | 19:30 | 117 | 11:00 | Rahanpur | 137 | 22:00 | 131 | 08:00
Chuadanga | 136 | 04:00 | 122 | 11:00 | Rahanpur-400 | 137 | 02:00 | 131 | 08:00
Coxsbazar | 123 | 06:00 | 118 | 11:00 | Rahim | 131 | 03:00 | 124 | 12:00
Cumilla(N) | 132 | 19:30 | 125 | 12:00 | Rajbari | 135 | 04:00 | 125 | 12:00
Cumilla(S) | 131 | 06:00 | 122 | 11:00 | Rajendrapur | 133 | 19:30 | 125 | 15:00
Daudkandi | 129 | 05:00 | 120 | 12:00 | Rajshahi | 137 | 20:00 | 128 | 11:00
Dhaka | 131 | 02:00 | 122 | 11:00 | Rajshahi-230 | 137 | 23:00 | 121 | 12:00
Dhamrai | 133 | 03:00 | 121 | 12:00 | Ramganj | 130 | 19:00 | 116 | 00:00
Dhanmondi | 132 | 03:00 | 124 | 12:00 | Rampur | 134 | 19:00 | 124 | 11:00
Dohazari | 131 | 20:00 | 124 | 12:00 | Rampura | 132 | 04:00 | 121 | 12:00
Faridpur | 135 | 04:00 | 127 | 14:00 | Rangamati | 134 | 20:00 | 127 | 11:00
Fatullah | 134 | 06:00 | 126 | 11:00 | Rangpur | 132 | 17:00 | 121 | 07:00
Fenchuganj | 136 | 06:00 | 132 | 18:00 | Ruppur | 139 | 03:00 | 131 | 11:00
Feni | 130 | 19:00 | 117 | 12:00 | Saidpur | 134 | 17:00 | 120 | 07:00
Ghatail | 130 | 09:00 | 117 | 07:00 | Satkhira | 136 | 05:00 | 120 | 12:00
Ghorashal | 138 | 04:00 | 132 | 19:30 | Satmasjid | 133 | 05:00 | 123 | 12:00
Goalpara | 139 | 03:00 | 125 | 12:00 | Savar | 133 | 19:00 | 121 | 12:00
Gollamari | 138 | 02:00 | 127 | 11:00 | SevenRings | 139 | 20:00 | 132 | 12:00
Gopalganj | 138 | 04:00 | 127 | 12:00 | ShahCement | 132 | 02:00 | 124 | 11:00
Gopalganj-400 | 139 | 03:00 | 130 | 12:00 | Shahjadpur | 139 | 04:00 | 132 | 12:00
Gulshan | 130 | 08:00 | 121 | 12:00 | Shahjibazar | 134 | 08:00 | 128 | 18:30
Halishahar | 136 | 19:00 | 125 | 11:00 | Shahmirpur | 136 | 19:00 | 126 | 11:00
Haripur | 132 | 05:00 | 124 | 12:00 | Shariatpur | 138 | 04:00 | 127 | 13:00
HaripurSBU | 132 | 05:00 | 124 | 16:00 | Sherpur | 130 | 15:00 | 109 | 05:00
Hasnabad | 134 | 19:30 | 126 | 11:00 | Shikalbaha | 124 | 19:00 | 116 | 10:00
Hathazari | 136 | 18:30 | 130 | 11:00 | Shikalbaha-230 | 136 | 19:30 | 127 | 11:00
Ishurdi | 137 | 20:00 | 131 | 07:00 | Shitalakhya | 133 | 03:00 | 124 | 12:00
Jaldhaka | 132 | 17:00 | 118 | 10:00 | Sholosohor | 134 | 19:00 | 128 | 11:00
Jamalpur | 131 | 15:00 | 113 | 04:00 | Shyampur | 135 | 00:00 | 125 | 12:00
Jashore | 137 | 03:00 | 123 | 12:00 | Shyampur-230 | 134 | 06:00 | 124 | 12:00
Jhenaidah | 136 | 05:00 | 126 | 11:00 | Siddhirganj | 132 | 04:00 | 124 | 12:00
Jhenaidah-230 | 138 | 03:00 | 126 | 12:00 | Sirajganj | 134 | 02:00 | 126 | 12:00
Joydebpur | 135 | 19:30 | 127 | 12:00 | Sonargaon | 130 | 04:00 | 121 | 12:00
Joypurhat | 132 | 03:00 | 117 | 08:00 | Sreemongol | 134 | 04:00 | 128 | 18:00
Juldah | 136 | 19:00 | 126 | 11:00 | Sreepur | 136 | 22:00 | 121 | 18:00
Kabirpur | 135 | 01:00 | 122 | 11:00 | Srinagar | 134 | 00:00 | 128 | 12:00
Kachua | 136 | 15:00 | 119 | 11:00 | SSM | 138 | 19:00 | 130 | 10:00
Kaliakoir | 137 | 19:00 | 124 | 12:00 | Sunamganj | 130 | 02:00 | 125 | 18:00
Kallyanpur | 135 | 01:00 | 125 | 12:00 | Sylhet | 133 | 02:00 | 128 | 18:30
Kalurghat | 135 | 20:00 | 125 | 13:00 | Sylhet-132 | 133 | 03:00 | 129 | 17:00
Kamrangirchar | 137 | 04:00 | 125 | 12:00 | Tangail | 127 | 08:00 | 120 | 14:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 140 | 23:00 | 121 | 07:00
Kazla | 131 | 03:00 | 121 | 13:00 | TK | 136 | 19:00 | 127 | 11:00
Keranigonj | 137 | 04:00 | 126 | 12:00 | Tongi | 159 | 18:00 | 127 | 12:00
Khagrachori | 133 | 19:00 | 128 | 11:00 | Ullahpara | 135 | 04:00 | 127 | 12:00
Khosba | 130 | 05:00 | 122 | 12:00 | Ullon | 132 | 05:00 | 121 | 12:00
Khulna | 133 | 05:00 | 124 | 12:00 | Uttara | 134 | 04:00 | 122 | 12:00
Khulna(S) | 138 | 03:00 | 125 | 12:00 | UttaraNew | 134 | 03:00 | 122 | 12:00
Khulshi | 134 | 19:00 | 126 | 10:00 | Zigatola | 139 | 04:00 | 128 | 12:00
Kishoreganj | 129 | 08:00 | 117 | 13:00
Kodda | 135 | 19:00 | 123 | 11:00
KSRM | 135 | 19:00 | 126 | 11:00
Kulaura | 136 | 04:00 | 131 | 18:30
Kurigram | 132 | 21:00 | 117 | 07:00
Kushtia | 136 | 01:00 | 126 | 11:00
Lalbag | 138 | 04:00 | 127 | 12:00
Lalmonirhat | 130 | 21:00 | 119 | 07:00
Madanganj | 131 | 01:00 | 123 | 12:00
Madaripur | 139 | 05:00 | 129 | 12:00
Madartek | 132 | 05:00 | 120 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division