## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-03-2025 | during | 04-03-2025 | during | 04-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 130 | 130 | 230 | 230 | 150 | 150 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 260 | 260 | 110 | 110 | Reliable test run by OEM
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 403 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 89 | 335 | 335 | 300 | 300 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 320 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 22 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 27 | 27 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 33 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 120 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 50 | 105 | 105 | 70 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 70 | 70 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 25 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 160 | 160 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6189 | 5925.764 | 1964.5 | 2025 | 4935.1 | 5000.1 | 3128.29 | 3193.29
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 158 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 30 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 9 | 6 | 10 | 32 | 10 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 30 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 3.78 | 0 | 3.78 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 35 | 35 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1183 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 6 | 0 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 640 | 898 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2051 | 2379 | 3905.64 | 3910.86 | 3746.64 | 3751.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 235 | 230 | 230 | 230 | 200 | 200 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 35 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 20 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 192 | 163 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 35 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 140 | 140 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 8 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 85 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 80 | 64 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 16 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 38 | 113 | 113 | 9 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 55 | 115 | 115 | 95 | 95 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1062 | 1051 | 1948.97 | 1898.97 | 1657.03 | 1711.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-03-2025 | during | 04-03-2025 | during | 04-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 20 | 21 | 210 | 210 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 97 | 105 | 200 | 200 | 135 | 135 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 89 | 115 | 115 | 100 | 100 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.81 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 250.81 | 227 | 653.6 | 601.5 | 386.6 | 334.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 41 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 113 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 35 | 32 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 198 | 390 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 360 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1344 | 1462 | 1549.5 | 1549.5 | 1513 | 1513
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 43 | 43 | 43 | 43 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71.43 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 628 | 1234.2 | 1234.2 | 610 | 610 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 995.43 | 1505 | 3477.2 | 3397.2 | 1783.02 | 1703.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 425 | 0 | 594 | 594 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 8 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 127 | 114 | 127 | 127 | 127 | 127 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1170 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.33 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 2184.33 | 1819 | 2763.12 | 2762.12 | 2169.12 | 2168.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 159 | 159 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 170 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 320 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.7 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1117 | 1364.38 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.05 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2085.25 | 2018.88 | 3054.08 | 2893.78 | 2792.3 | 2632
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 63 | 62 | 62 | 62 | 62 | 62 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 169 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 100 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 105 | 0 | 103 | 0 | 103 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 415.3 | 401 | 599.6 | 460 | 579.62 | 440.02
System Total |  |  |  |  | 27566.2 | 28375.742 | 12352.62 | 12887.88 | 22886.81 | 22474.03 | 17755.62 | 17446.84
Forecast Scenario (04-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11758 |  | 0 |  | 11758
|  |  |  | 1:00 | 11070 |  | 0 |  | 11070
|  |  |  | 2:00 | 10796 |  | 0 |  | 10796
|  |  |  | 3:00 | 11400 |  | 0 |  | 11400
|  |  |  | 4:00 | 11500 |  | 0 |  | 11500
|  |  |  | 5:00 | 10370 |  | 0 |  | 10370
|  |  |  | 6:00 | 9750 |  | 0 |  | 9750
|  |  |  | 7:00 | 9900 |  | 0 |  | 9900
|  |  |  | 8:00 | 10280 |  | 0 |  | 10280
|  |  |  | 9:00 | 11039 |  | 0 |  | 11039
|  |  |  | 10:00 | 11553 |  | 0 |  | 11553
|  |  |  | 11:00 | 12198 |  | 0 |  | 12198
|  |  |  | 12:00 | 12764 |  | 0 |  | 12764
|  |  |  | 13:00 | 12920 |  | 0 |  | 12920
|  |  |  | 14:00 | 12831 |  | 0 |  | 12831
|  |  |  | 15:00 | 12885 |  | 0 |  | 12885
|  |  |  | 16:00 | 12573 |  | 0 |  | 12573
|  |  |  | 17:00 | 12555 |  | 0 |  | 12555
|  |  |  | 18:00 | 12482 |  | 0 |  | 12482
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 13451 |  | 0 |  | 13451
|  |  |  | 19:30 | 13156 |  | 0 |  | 13156
|  |  |  | 20:00 | 13381 |  | 0 |  | 13381
|  |  |  | 21:00 | 13296 |  | 0 |  | 13296
|  |  |  | 22:00 | 13170 |  | 0 |  | 13170
|  |  |  | 23:00 | 12510 |  | 0 |  | 12510
Probable Maximum Temperature: |  |  | 31.80°C
Probable Maximum Demand at Day Peak: |  |  | 12764.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13451.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13451.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 286.432 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:30 hrs on 04-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-03-2025 | [28 empty] | Date: | 03-03-2025 | [28 empty] | Date: | 03-03-2025 | [28 empty] | Date: | 03-03-2025 | [28 empty] | Date: | 03-03-2025 | [18 empty] | Date: | 03-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 110 | 0 | 131 | 0 | 0 | 402 | 0 | 0 | 17 | 28 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 350 | 0 | 0 | 0 | 0 | 28 | 270 | 0 | 0 | 0 | 160 | 17 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 34 | 40 | 431 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 1180 | 0 | 51 | 0 | 195 | 0 | 220 | 0 | 29 | 216 | 35 | 50 | 50 | 17 | 39 | 16 | 0 | 82 | 0 | 0 | 0 | 300 | 320 | 5 | 35 | 42 | 29 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 49 | 48 | 17 | 0 | 0 | 12 | 5885 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 2.5 | 166 | 61 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 320 | 1120 | 0 | 5407.5 | 11292.5 | 88.81
01:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 385 | 0 | 0 | 0 | 35 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 350 | 0 | 0 | 0 | 0 | 28 | 270 | 0 | 0 | 0 | 160 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 32 | 575 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1020 | 0 | 51 | 0 | 195 | 0 | 220 | 0 | 29 | 183 | 35 | 26 | 50 | 17 | 20 | 16 | 0 | 70 | 0 | 0 | 0 | 305 | 320 | 80 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 49 | 48 | 18 | 0 | 0 | 12 | 5743 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 2.5 | 166 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 319 | 1040 | 0 | 5280.5 | 11023.5 | 88.81
02:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 350 | 0 | 0 | 0 | 35 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 300 | 0 | 0 | 0 | 0 | 28 | 270 | 0 | 0 | 0 | 160 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 700 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 195 | 0 | 220 | 0 | 29 | 183 | 35 | 17 | 50 | 17 | 10 | 16 | 0 | 72 | 0 | 0 | 0 | 295 | 320 | 80 | 32 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 49 | 48 | 20 | 0 | 0 | 12 | 5660 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 320 | 0 | 0 | 2.5 | 170 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 120 | 180 | 0 | 319 | 950 | 0 | 4976.5 | 10636.5 | 88.8
03:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 0 | 41 | 40 | 0 | 0 | 0 | 0 | 30 | 0 | 300 | 0 | 0 | 0 | 0 | 28 | 270 | 0 | 0 | 0 | 160 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 907 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 195 | 0 | 220 | 0 | 29 | 204 | 35 | 17 | 50 | 17 | 19 | 16 | 0 | 68 | 0 | 0 | 0 | 290 | 320 | 80 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 49 | 48 | 20 | 0 | 0 | 12 | 5861 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 2.5 | 165 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 120 | 180 | 0 | 319 | 950 | 0 | 5070.5 | 10931.5 | 88.8
04:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 0 | 35 | 98 | 0 | 0 | 1.7 | 0 | 30 | 0 | 420 | 0 | 0 | 0 | 0 | 30 | 320 | 0 | 0 | 0 | 160 | 18.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 906 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 970 | 0 | 51 | 0 | 195 | 0 | 220 | 0 | 29 | 183 | 34 | 57 | 50 | 17 | 18 | 16 | 0 | 72 | 0 | 0 | 0 | 300 | 320 | 80 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 68 | 95 | 20 | 0 | 0 | 12 | 6214.4 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 192 | 0 | 350 | 0 | 0 | 2.5 | 164 | 61 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 100 | 220 | 0 | 319 | 1060 | 0 | 5101.5 | 11315.9 | 88.8
05:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 0 | 0 | 0 | 0 | 32 | 280 | 0 | 0 | 0 | 160 | 18.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 909 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 830 | 0 | 51 | 0 | 195 | 0 | 220 | 0 | 29 | 205 | 34 | 45 | 50 | 17 | 18 | 16 | 0 | 70 | 0 | 0 | 0 | 310 | 320 | 80 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 68 | 45 | 21 | 0 | 0 | 12 | 5844.7 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 2.5 | 164 | 63 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 80 | 180 | 0 | 320 | 900 | 0 | 4511.5 | 10356.2 | 88.79
06:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 307 | 0 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 340 | 0 | 0 | 0 | 0 | 32 | 250 | 0 | 0 | 0 | 160 | 18.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 907 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 125 | 0 | 220 | 0 | 29 | 184 | 34 | 0 | 50 | 17 | 9 | 16 | 0 | 64 | 0 | 0 | 0 | 300 | 320 | 80 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 32 | 30 | 0 | 18 | 100 | 0 | 69 | 45 | 22 | 0 | 0 | 12 | 5492.7 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 160 | 0 | 300 | 0 | 0 | 2.5 | 160 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 319 | 700 | 0 | 4119.5 | 9612.2 | 88.79
07:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 295 | 0 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 0 | 0 | 0 | 0 | 32 | 305 | 0 | 0 | 2 | 160 | 18.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 907 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 800 | 2 | 51 | 0 | 142 | 0 | 220 | 0 | 29 | 212 | 34 | 0 | 50 | 17 | 9 | 16 | 0 | 58 | 0 | 2 | 0 | 315 | 320 | 80 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 32 | 30 | 0 | 18 | 100 | 0 | 69 | 45 | 22 | 0 | 2.66 | 12 | 5639.36 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.43 | 0 | 0 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.89 | 150 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0.29 | 2.5 | 156 | 63 | 0 | 2 | 0 | 0 | 0 | 0 | 14 | 0.01 | 0 | 155 | 6 | 120 | 220 | 0 | 320 | 645 | 0 | 4289.12 | 9928.48 | 88.79
08:00 | 0 | 50 | 8 | 110 | 0 | 130 | 0 | 0 | 276 | 0 | 0 | 0 | 17 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 0 | 0 | 0 | 0 | 32 | 305 | 0 | 0 | 12 | 160 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 8 | 908 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 900 | 6 | 51 | 0 | 192 | 0 | 220 | 0 | 29 | 182 | 34 | 0 | 50 | 17 | 9 | 16 | 0 | 58 | 0 | 15 | 0 | 300 | 320 | 70 | 35 | 42 | 30 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 69 | 86 | 22 | 1 | 10.61 | 6 | 5871.11 | 881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.55 | 0 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 5.06 | 201 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0.45 | 5.5 | 162 | 63 | 0 | 11 | 0 | 0 | 0 | 1.8 | 66 | 0.09 | 0 | 250 | 5 | 120 | 220 | 0 | 319 | 720 | 0 | 4512.45 | 10383.56 | 88.78
09:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 265 | 0 | 0 | 0 | 17 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 29 | 325 | 0 | 0 | 17 | 160 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 8 | 908 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 960 | 11 | 51 | 0 | 185 | 0 | 220 | 0 | 29 | 215 | 34 | 1 | 50 | 18 | 0 | 16 | 0 | 62 | 0 | 25 | 0 | 320 | 320 | 70 | 35 | 41 | 30 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 69 | 96 | 22 | 2 | 28.91 | 9 | 6168.41 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.55 | 0 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25.89 | 214 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 2.14 | 5.5 | 137 | 63 | 0 | 20 | 15 | 0 | 0 | 3.6 | 100 | 0.26 | 0 | 307 | 5 | 120 | 220 | 0 | 299 | 880 | 0 | 4936.94 | 11105.35 | 88.78
10:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 295 | 0 | 0 | 0 | 17 | 0 | 105 | 16 | 0 | 0 | 0 | 40 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 25 | 160 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3 | 40 | 0 | 7 | 800 | 0 | 0 | 0 | 0 | 6 | 161 | 0 | 0 | 0 | 1100 | 15 | 43 | 0 | 192 | 0 | 225 | 0 | 29 | 182 | 34 | 36 | 50 | 38 | 0 | 16 | 0 | 72 | 0 | 42 | 0 | 310 | 320 | 70 | 35 | 41 | 30 | 2 | 163 | 24 | 0 | 83 | 30 | 0 | 18 | 100 | 0 | 69 | 96 | 22 | 2 | 40.25 | 12 | 6325.25 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.44 | 0 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 50.55 | 214 | 0 | 0 | 0 | 210 | 0 | 414 | 0 | 4.36 | 5.5 | 120 | 62 | 0 | 29 | 30 | 0 | 0 | 5.1 | 102 | 0.38 | 0 | 307 | 5 | 100 | 220 | 0 | 328 | 1040 | 0 | 5427.33 | 11752.58 | 88.78
11:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 105 | 16 | 0 | 0 | 0 | 54 | 30 | 0 | 370 | 0 | 0 | 0 | 0 | 27 | 280 | 0 | 0 | 28 | 160 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 4 | 40 | 16 | 9 | 793 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 1100 | 14 | 43 | 0 | 184 | 0 | 225 | 0 | 29 | 184 | 34 | 68 | 51 | 68 | 7 | 16 | 0 | 70 | 0 | 55 | 0 | 290 | 320 | 76 | 35 | 41 | 30 | 2 | 120 | 24 | 0 | 83 | 30 | 0 | 18 | 100 | 0 | 69 | 97 | 22 | 2 | 49.72 | 12 | 6494.72 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.75 | 0 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 60.42 | 150 | 0 | 0 | 0 | 211 | 0 | 360 | 0 | 5.21 | 5.5 | 169 | 62 | 0 | 34 | 34 | 0 | 0 | 5.8 | 105 | 0 | 0 | 307 | 5 | 100 | 180 | 0 | 362 | 1090 | 0 | 5444.68 | 11939.4 | 88.77
12:00 | 0 | 34 | 25 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 25 | 0 | 105 | 16 | 0 | 0 | 0 | 54 | 30 | 0 | 450 | 0 | 0 | 0 | 0 | 27 | 322 | 0 | 0 | 30 | 160 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 2 | 40 | 17 | 9 | 640 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 1100 | 18 | 43 | 0 | 192 | 0 | 235 | 0 | 29 | 183 | 35 | 72 | 50 | 68 | 0 | 16 | 0 | 80 | 0 | 59 | 0 | 305 | 360 | 198 | 35 | 41 | 30 | 2 | 120 | 24 | 0 | 83 | 30 | 0 | 16 | 100 | 0 | 69 | 97 | 20 | 2 | 50.81 | 12 | 6672.31 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.43 | 0 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 65.05 | 159 | 0 | 0 | 0 | 211 | 0 | 414 | 0 | 5.7 | 5.5 | 170 | 63 | 0 | 37 | 34 | 0 | 0 | 6.3 | 105 | 0.33 | 0 | 307 | 5 | 127 | 220 | 0 | 425 | 1100 | 0 | 5680.31 | 12352.62 | 88.77
13:00 | 0 | 34 | 25 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 54 | 0 | 105 | 16 | 0 | 0 | 0 | 54 | 30 | 0 | 450 | 0 | 0 | 0 | 0 | 27 | 321 | 0 | 0 | 31 | 160 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 0 | 4 | 40 | 17 | 16 | 640 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 1224 | 17 | 43 | 0 | 184 | 0 | 230 | 0 | 29 | 183 | 35 | 68 | 50 | 68 | 0 | 16 | 35 | 86 | 0 | 22 | 0 | 300 | 320 | 281 | 35 | 41 | 29 | 2 | 112 | 24 | 0 | 86 | 30 | 0 | 16 | 100 | 0 | 69 | 97 | 20 | 2 | 51.25 | 12 | 6837.75 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.63 | 0 | 0 | 1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 64.09 | 205 | 0 | 0 | 0 | 210 | 0 | 414 | 0 | 5.56 | 5.5 | 167 | 62 | 0 | 36 | 35 | 0 | 0 | 6.2 | 104 | 0.16 | 0 | 307 | 6 | 127 | 220 | 0 | 492 | 1200 | 0 | 5911.14 | 12748.89 | 88.77
14:00 | 0 | 34 | 16 | 110 | 0 | 130 | 0 | 0 | 381 | 0 | 0 | 0 | 54 | 0 | 105 | 16 | 0 | 0 | 0 | 54 | 30 | 0 | 400 | 0 | 0 | 0 | 0 | 27 | 316 | 0 | 0 | 27 | 160 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 17 | 2 | 640 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 1226 | 14 | 43 | 0 | 190 | 0 | 230 | 0 | 29 | 186 | 35 | 68 | 50 | 68 | 0 | 16 | 35 | 88 | 0 | 45 | 0 | 290 | 320 | 393 | 35 | 40 | 29 | 0 | 113 | 24 | 0 | 86 | 30 | 0 | 16 | 100 | 0 | 79 | 105 | 18 | 2 | 46.39 | 12 | 6874.39 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.69 | 0 | 0 | 1163.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 57.37 | 155 | 0 | 0 | 0 | 210 | 0 | 350 | 0 | 5.07 | 5.5 | 163 | 62 | 0 | 34 | 35 | 0 | 0 | 5.9 | 106 | 0.34 | 0 | 307 | 6 | 122 | 210 | 0 | 326 | 1244 | 0 | 5650.49 | 12524.88 | 88.76
15:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 311 | 0 | 0 | 0 | 54 | 0 | 105 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 420 | 15 | 0 | 0 | 0 | 27 | 317 | 0 | 0 | 21 | 160 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 20 | 0 | 2 | 40 | 17 | 2 | 759 | 0 | 0 | 0 | 0 | 34 | 161 | 0 | 0 | 0 | 1227 | 11 | 43 | 0 | 180 | 0 | 225 | 0 | 29 | 205 | 35 | 56 | 50 | 68 | 0 | 16 | 35 | 59 | 0 | 25 | 0 | 300 | 320 | 392 | 35 | 40 | 28 | 2 | 113 | 24 | 0 | 86 | 30 | 0 | 16 | 100 | 0 | 78 | 106 | 18 | 2 | 36.05 | 0 | 6815.05 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.23 | 30 | 0 | 1173.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 44.68 | 132 | 0 | 0 | 0 | 211 | 0 | 340 | 0 | 3.93 | 5.5 | 164 | 62 | 0 | 28 | 0 | 0 | 0 | 4.4 | 106 | 0.29 | 0 | 307 | 6 | 122 | 219 | 0 | 191 | 1230 | 0 | 5429.17 | 12244.22 | 88.76
16:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 95 | 0 | 0 | 0 | 17 | 0 | 105 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 420 | 20 | 0 | 0 | 0 | 27 | 315 | 0 | 0 | 13 | 160 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 45 | 0 | 1 | 40 | 17 | 9 | 790 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1224 | 7 | 51 | 0 | 180 | 0 | 230 | 0 | 29 | 208 | 35 | 51 | 50 | 81 | 17 | 16 | 35 | 61 | 0 | 16 | 0 | 305 | 320 | 391 | 32 | 40 | 28 | 2 | 113 | 24 | 0 | 86 | 30 | 0 | 16 | 100 | 0 | 79 | 110 | 18 | 1 | 22 | 0 | 6640 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.28 | 268 | 0 | 1257.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 28.26 | 143 | 0 | 0 | 0 | 172 | 0 | 358 | 0 | 2.49 | 2.5 | 162 | 63 | 0 | 18 | 0 | 0 | 0 | 2.8 | 95 | 0.16 | 0 | 307 | 6 | 123 | 220 | 0 | 66 | 1220 | 0 | 5512.22 | 12152.22 | 88.76
17:00 | 0 | 34 | 16 | 110 | 0 | 130 | 0 | 0 | 79 | 0 | 0 | 6 | 17 | 0 | 108 | 16 | 0 | 0 | 0 | 17 | 30 | 0 | 420 | 20 | 0 | 0 | 0 | 27 | 315 | 0 | 0 | 5 | 160 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 17 | 21 | 900 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1224 | 2 | 51 | 0 | 135 | 0 | 230 | 0 | 29 | 183 | 35 | 51 | 50 | 85 | 30 | 16 | 35 | 61 | 0 | 7 | 0 | 300 | 320 | 395 | 35 | 39 | 28 | 2 | 113 | 24 | 0 | 52 | 30 | 0 | 16 | 100 | 0 | 79 | 144 | 16 | 0 | 7.61 | 1 | 6692.61 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.64 | 400 | 0 | 1357.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10.15 | 191 | 0 | 0 | 0 | 184 | 0 | 383 | 0 | 0.89 | 2.5 | 163 | 62 | 0 | 7 | 20 | 0 | 0 | 0.8 | 33 | 0.06 | 0 | 307 | 6 | 100 | 220 | 0 | 0 | 1120 | 0 | 5524.8 | 12217.41 | 88.75
18:00 | 0 | 50 | 16 | 110 | 0 | 130 | 0 | 0 | 338 | 0 | 0 | 35 | 17 | 0 | 111 | 32 | 0 | 20 | 0 | 17 | 30 | 0 | 300 | 51 | 0 | 0 | 0 | 27 | 290 | 0 | 0 | 0 | 160 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 17 | 38 | 900 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1110 | 0 | 20 | 0 | 107 | 0 | 230 | 0 | 29 | 178 | 35 | 51 | 50 | 85 | 36 | 16 | 70 | 62 | 0 | 0 | 0 | 295 | 320 | 360 | 35 | 43 | 30 | 2 | 113 | 24 | 0 | 52 | 30 | 0 | 16 | 100 | 0 | 89 | 154 | 12 | 0 | 0.07 | 12 | 6804.07 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 530 | 0 | 1361.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 174 | 0 | 250 | 0 | 0.02 | 5.5 | 164 | 62 | 75 | 0 | 95 | 0 | 0 | 0 | 1 | 0 | 0 | 220 | 7 | 100 | 180 | 0 | 0 | 1100 | 0 | 5387.95 | 12192.02 | 88.75
19:00 | 0 | 50 | 33 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 0 | 120 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 89 | 0 | 0 | 0 | 27 | 320 | 0 | 0 | 0 | 160 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 6 | 898 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 1183 | 0 | 35 | 0 | 163 | 0 | 230 | 0 | 20 | 182 | 35 | 55 | 50 | 85 | 38 | 16 | 70 | 64 | 0 | 0 | 8 | 280 | 320 | 390 | 32 | 42 | 30 | 2 | 113 | 24 | 0 | 83 | 30 | 0 | 16 | 100 | 0 | 89 | 105 | 21 | 0 | 0 | 12 | 7144 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 0 | 1364.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 170 | 0 | 320 | 0 | 0 | 5.5 | 169 | 62 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 114 | 220 | 0 | 0 | 1170 | 0 | 5743.88 | 12887.88 | 88.75
19:30 | 0 | 50 | 33 | 110 | 0 | 131 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 96 | 0 | 0 | 0 | 27 | 322 | 0 | 0 | 0 | 160 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 26 | 898 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 163 | 0 | 230 | 0 | 29 | 184 | 35 | 72 | 50 | 51 | 38 | 16 | 70 | 56 | 0 | 0 | 16 | 300 | 320 | 391 | 32 | 42 | 30 | 2 | 80 | 24 | 0 | 83 | 30 | 0 | 18 | 100 | 0 | 89 | 105 | 22 | 0 | 0 | 12 | 7162 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 1359.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 157 | 0 | 309 | 0 | 0 | 5.5 | 168 | 62 | 35 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 119 | 220 | 0 | 0 | 1180 | 0 | 5506.15 | 12668.15
20:00 | 0 | 50 | 33 | 110 | 0 | 130 | 0 | 0 | 405 | 0 | 0 | 0 | 17 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 118 | 0 | 0 | 0 | 30 | 324 | 0 | 0 | 0 | 160 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 27 | 898 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 163 | 0 | 230 | 0 | 29 | 182 | 35 | 50 | 50 | 51 | 38 | 16 | 70 | 54 | 0 | 0 | 16 | 275 | 320 | 390 | 35 | 42 | 30 | 2 | 80 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 89 | 85 | 23 | 0 | 0 | 12 | 7118 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 1354.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 155 | 0 | 308 | 0 | 0 | 5.5 | 172 | 62 | 35 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 120 | 213.5 | 0 | 0 | 1212 | 0 | 5534.14 | 12652.14 | 88.74
21:00 | 0 | 17 | 33 | 110 | 0 | 130 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 155 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 160 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 30 | 900 | 0 | 0 | 0 | 12 | 0 | 148 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 165 | 0 | 230 | 0 | 29 | 188 | 35 | 34 | 50 | 51 | 39 | 16 | 70 | 60 | 0 | 0 | 0 | 280 | 320 | 393 | 35 | 42 | 30 | 2 | 80 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 89 | 85 | 24 | 0 | 0 | 12 | 6928 | 918 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 0 | 1258.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 154 | 0 | 313 | 0 | 0 | 5.5 | 171 | 62 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 123 | 218 | 0 | 0 | 1200 | 0 | 5605.96 | 12533.96 | 88.74
22:00 | 0 | 17 | 33 | 110 | 0 | 130 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 152 | 0 | 0 | 0 | 32 | 280 | 0 | 0 | 0 | 160 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 34 | 896 | 0 | 0 | 0 | 16 | 0 | 148 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 194 | 0 | 230 | 0 | 29 | 188 | 35 | 34 | 50 | 51 | 39 | 16 | 70 | 58 | 0 | 0 | 0 | 295 | 320 | 392 | 35 | 43 | 30 | 2 | 80 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 89 | 85 | 23 | 0 | 0 | 12 | 6967 | 919 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566 | 0 | 1159.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 158 | 0 | 302 | 0 | 0 | 2.5 | 170 | 63 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 123 | 220 | 0 | 0 | 1120 | 0 | 5431.87 | 12398.87 | 88.74
23:00 | 0 | 17 | 33 | 110 | 0 | 130 | 0 | 0 | 365 | 0 | 0 | 0 | 11 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 279 | 0 | 0 | 0 | 32 | 280 | 0 | 0 | 0 | 160 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 38 | 896 | 0 | 0 | 0 | 8 | 0 | 142 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 195 | 0 | 230 | 0 | 29 | 182 | 35 | 34 | 50 | 51 | 39 | 16 | 70 | 62 | 0 | 0 | 0 | 280 | 320 | 390 | 35 | 42 | 30 | 2 | 80 | 24 | 0 | 86 | 30 | 0 | 18 | 100 | 0 | 89 | 85 | 22 | 0 | 0 | 12 | 6924 | 919 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563 | 0 | 1008.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 153 | 0 | 309 | 0 | 0 | 2.5 | 169 | 63 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 123 | 215 | 0 | 0 | 980 | 0 | 5041.2 | 11965.2 | 88.73
Total KWH | 0 | 718080 | 434400 | 2639700 | 0 | 3116062 | 0 | 0 | 7894800 | 0 | 0 | 97560 | 612000 | 0 | 2023920 | 424800 | 0 | 46069 | 7586 | 332640 | 721440 | 0 | 9405500 | 1031738 | 0 | 0 | 0 | 686700 | 7140249 | 0 | 0 | 183438 | 3922800 | 458400 | 394200 | 0 | 0 | 0 | 5018 | 0 | 0 | 26400 | 219621 | 0 | 0 | 596160 | 0 | 21242 | 960000 | 204072 | 548160 | 19585454.55 | 0 | 0 | 0 | 52689.6 | 302763 | 3713192 | 0 | 0 | 0 | 25456361 | 118395 | 1085944 | 0 | 4215273 | 0 | 5654200 | 0 | 689280 | 4631000 | 836208 | 1019520 | 1181580 | 11534400 | 461160 | 269.45 | 598500 | 1603200 | 0 | 328064 | 799.2 | 7217500 | 7687900 | 5532000 | 805608 | 977000 | 672240 | 53520 | 2794500 | 551616 | 0 | 1838400 | 703488 | 0 | 406000 | 2389380 | 0 | 1725600 | 2104800 | 467520 | 15800 | 346280 | 264000 | 164494159.8 | 22129454 | 152928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445680 | 4087273 | 0 | 27943637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 695060 | 0 | 422248 | 4529745 | 0 | 0 | 0 | 4442282 | 0 | 8552654 | 0 | 36300 | 96282 | 3967000 | 1455272 | 272767 | 257726 | 894796 | 0 | 0 | 42973.92 | 946800 | 2681 | 0 | 6676000 | 166266 | 2690000 | 5186680 | 0 | 5286744 | 25722181.82 | 0 | 127101430.74 | 291595590.54

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12352.62 | MW | 12:00 Hr. | Energy Generated |  |  | 291.5956 |  | MKWHr.
| Day Peak Demand |  |  | 12352.62 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.04 |  | MKWHr.
| Evening Peak Generation |  |  | 12887.88 | MW | 19:00 Hr. | Energy Demand |  |  | 291.6356 |  | MKWHr.
| Evening Peak Demand |  |  | 12887.88 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.6 |  | °C
| Minimum Generation of the Day |  |  | 9612.2 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 947.26 |  | MMCFD
| Maximum Generation of the Day |  |  | 12887.88 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.3058 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.4888 | 0 | 8.6199 | 0 | 0 | 0.18344 | 0 | 0 | 42.2921 | Gas | 113.9574 | Gas | 412558342.97
| Chattogram Zone |  |  | 4.2614 | 45.0418 | 1.3803 | 0 | 0.96 | 0.13964 | 0 | 0.0264 | 51.8095 | Coal | 92.2363 | Coal | 610832397.9011
| Cumilla Zone |  |  | 18.2938 | 0 | 13.6144 | 0 | 0 | 0.32806 | 1.6032 | 0 | 33.8394 | HFO | 28.8765 | HFO | 458531800.872
| Mymensingh Zone |  |  | 0.46752 | 0 | 4.0944 | 0 | 0 | 0.36208 | 0 | 0 | 4.924 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.6292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6292 | Hydro | 0.96 | Hydro | 96000
| Khulna Zone |  |  | 0.15293 | 4.0873 | 0 | 0 | 0 | 0.44568 | 22.1295 | 0 | 26.8153 | Solar | 3.8627 | Solar | 63021940.6412
| Barishal Zone |  |  | 8.0429 | 37.6849 | 0 | 0 | 0 | 0.002681 | 0 | 0 | 45.7306 | Import | 51.6763 | Import | 293321588.19
| Rajshahi Zone |  |  | 17.621 | 0 | 0 | 0 | 0 | 1.1536 | 27.9436 | 0 | 46.7182 | Wind | 0.0264 | Wind | 386496
| Rangpur Zone |  |  | 0 | 5.4223 | 1.1676 | 0 | 0 | 1.2475 | 0 | 0 | 7.8373
| Total |  |  | 113.9574 | 92.2363 | 28.8765 | 0 | 0.96 | 3.8627 | 51.6763 | 0.0264 | 291.5956
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 412558342.97 |  | Hydro | 96000
|  |  |  | Coal | 610832397.9011 |  | Solar | 63021940.6412
|  |  |  | HFO | 458531800.872 |  | Import | 293321588.19
|  |  |  | HSD | 0 |  | Wind | 386496
[5 empty] | Total: | 183,87,48,566 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1295 | Peak Hr Flow | 877.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 12149200.097 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.9436 | Peak Hr Flow | 1364.38 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 638 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6032 | Peak Hr Flow | 64.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 986 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.6763 | Peak Hr Flow | 2305.38 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4423
|  |  |  | Chattogram |  | 0 |  | 1341
|  |  |  | Cumilla |  | 0 |  | 1176
|  |  |  | Mymensingh |  | 0 |  | 1017
|  |  |  | Sylhet |  | 0 |  | 416
|  |  |  | Khulna |  | 0 |  | 1443
|  |  |  | Barishal |  | 0 |  | 373
|  |  |  | Rajshahi |  | 0 |  | 1212
|  |  |  | Rangpur |  | 0 |  | 794
|  |  |  | Total |  | 0 |  | 12195
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 720.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1512.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:36 | 16:15 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Annual
Maintenance
| 08:46 | 17:20 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to IDRNPP Project work.
| 08:52 | 09:08 | Chowmuhani 132/33kV S/S TR2-425T LT Tripped showing No relay shown relays Due to Don't | [7 empty] | 35.0MW load
|  |  | operate 33 kv companigonj feeder relay . | [7 empty] | interrup.
| 08:52 | 09:08 | Chowmuhani 132/33kV S/S TR3-435T LT Tripped showing E/F Ins. relays Due to Don't operate | [7 empty] | 35.0MW load
|  |  | 33 kv companigonj feeder relay . | [7 empty] | interrup.
| 09:08 | 16:14 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance
| 09:26 | 13:57 | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Maintenance work at Aminbazar End. and from Aminbazar 400/230/132kV end Due to Disc
cleaning work
| 10:48 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
| 10:48 |  | Bibiyana-3 400 MW ST was sync.
| 11:37 | 12:55 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to Due to emergency maintenance
work.
| 11:37 | 12:55 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to Due to emergency maintenance
work.
|  | 11:58 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT is restored.
|  | 11:59 | Kallyanpur 132/33kV S/S GT-1 (132kV) LT is restored.
| 12:00 |  | Day peak Generation is 12349 MW
| 13:59 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning work and from Keranigonj 230/132/33kV end Due to Maintence work at
Aminbazar end.
| 14:25 |  | Haripur 412MW CCPP ST tripped
| 14:31 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to
Reconstrution of boundary wall at Mirpur Grid SS.
| 14:38 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 14:40 | 18:13 | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Scheduled S/D Due to Work for Tripura end.
| 14:50 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 14:50 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- GT-2 synchronized as per NLDC
requirement.
| 16:41 |  | Patuakhali 1320 MW (RNPL) unit-2 was shutdown due to boiler tube leakage.
| 16:50 |  | Haripur 412MW CCPP ST was sync.
|  | 16:52 | Naogaon 132/33kV S/S T-1 HT is restored.
|  | 16:55 | Naogaon 132/33kV S/S T-1 LT is restored.
| 17:26 |  | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- ST synchronized at 17:26 hrs as
per NLDC request
| 17:26 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
| 18:14 |  | BIPTC S/S 20DF24 Tripped showing 20DF24 relays.
| 18:33 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is ON with remarks:- As per instruction of NLDC at
15:10 hrs.
| 19:00 |  | Evening peak Generation is 12887 MW
| 20:07 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- None
| 20:07 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
| 20:35 |  | Bheramara 410MW GT was sync.
| 02:44 |  | Bheramara 410MW ST was sync.
| 06:00 |  | Minimum Generation: 9305 MW.
| 06:16 | 07:17 | Bhaluka-Mymensingh 132 kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to 132kV | [7 empty] | 70.0MW load
|  |  | Mym-Bh Ckt-2 S/D due High Temperature in CT nut of Bhaluka SS end | [7 empty] | interrup.
Mymensingh 132/33kV
end
| 07:01 |  | Keranigonj 230/132/33kV S/S ATR-1 LT Scheduled S/D Due to Maintenance work at Keraniganj
end for high temperature.
| 07:02 |  | Keranigonj 230/132/33kV S/S ATR-1 HT Scheduled S/D Due to Maintenance work at Keraniganj
end for high temperature.
| 07:37 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 130 | 3116062 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2639700 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 7894800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9405500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 89 | 1031738 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 46069 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7140249 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 97560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 424800 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 7586 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 458400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 394200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 721440 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 27 | 686700 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 434400 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 120 | 2023920 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 718080 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 332640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 183438 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 612000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 160 | 3922800 | -
Dhaka Area Total |  |  |  |  | 5925.764 | 2025 | 42292082
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 52689.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 118395 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 158 | 3713192 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 302763 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 219621 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 596160 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 6 | 548160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 5018 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 204072 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1183 | 25456361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 26400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 898 | 19585454.55 | Coal shortage
Chattogram Area Total |  |  |  |  | 4915.22 | 2379 | 51809528.15
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4631000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 230 | 5654200 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 836208 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 20 | 689280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 163 | 4215273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 35 | 1085944 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 8 | 799.2 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1181580 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 85 | 11534400 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 64 | 1603200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 269.45 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 598500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 461160 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 55 | 1019520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 328064 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1051 | 33839397.65
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 21 | 467520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 105 | 2104800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1725600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 346280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 264000 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 227 | 4924000
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 977000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 672240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2794500 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 805608 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 53520 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 703488 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1838400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 100 | 2389380 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 406000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 551616 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7217500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 5532000 | simple cycle
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7687900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1462 | 31629152
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 22129454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 152928 | Inadequate gas supply to run the plant.
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 445680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 628 | 4087273 | U#1 & U#2 under Force Majeure shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1505 | 26815335
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 5286744 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 166266 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 114 | 2690000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 25722181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5186680 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6676000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2681 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1819 | 45730552.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 159 | 4529745 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 170 | 4442282 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 320 | 8552654 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 96282 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1364.38 | 27943637 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 422248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 695060 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2018.88 | 46718208
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1455272 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 169 | 3967000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 894796 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42973.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 272767 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 257726 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 946800 | -
Rangpur Area Total |  |  |  |  | 950 | 401 | 7837334.92
Eastern Grid Total |  |  |  |  | 16761.242 | 7144 | 164494159.8
Western Grid Total |  |  |  |  | 11614.5 | 5743.88 | 127101430.74
National Grid Total |  |  |  |  | 28375.742 | 12887.88 | 291595590.54
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-03-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8373.28 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3821.9 | MW
i) Dhaka area |  |  | 4423.08 |  | MW | i) Khulna area |  |  |  | 1442.7 | MW
ii) Chattogram area |  |  | 1341.2 |  | MW | ii) Barishal area |  |  |  | 372.7 | MW
iii) Cumilla area |  |  | 1176 |  | MW | iii) Rajshahi area |  |  |  | 1212.5 | MW
iv) Mymensingh area |  |  | 1017 |  | MW | iv) Rangpur area |  |  |  | 794 | MW
v) Sylhet area |  |  | 416 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12195.18 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 72 | 18:00 | 133 | Payra | 24 | 00:00
2 | AKSML | 21 | 11:00 | 68 | Jamalpur | 107 | 18:00 | 134 | Postogola | 68 | 18:00
3 | Aftabnagar | 32 | 19:00 | 69 | Jashore | 122 | 19:00 | 135 | Purbachal | 16 | 19:00
4 | Agargaon | 101 | 13:00 | 70 | Jhenaidah | 105 | 19:00 | 136 | Purbasadipur | 114 | 19:00
5 | Agrabad | 84 | 14:00 | 71 | Joydebpur | 141 | 20:00 | 137 | Rahanpur | 11 | 09:00
6 | Amnura | 48 | 12:00 | 72 | Joypurhat | 70 | 18:00 | 138 | Rahim | 28 | 16:00
7 | Ashuganj | 76 | 19:00 | 73 | Juldah | 11 | 00:00 | 139 | Rajbari | 56 | 03:00
8 | BSRM | 202 | 11:00 | 74 | KSRM | 28 | 22:00 | 140 | Rajendrapur | 114 | 10:00
9 | Bagerhat | 71 | 19:00 | 75 | Kabirpur | 233 | 15:00 | 141 | Rajshahi | 90 | 20:00
10 | Bajitpur | 40 | 13:00 | 76 | Kachua | 67 | 18:00 | 142 | Rajshahi-230 | 60 | 18:00
11 | Bakulia | 85 | 19:00 | 77 | Kallyanpur | 93 | 20:00 | 143 | Ramganj | 100 | 18:00
12 | Banani | 24.4 | 13:00 | 78 | Kalurghat | 38 | 10:00 | 144 | Rampur | 37 | 18:30
13 | Bangabhaban | 13 | 10:00 | 79 | Kamrangirchar | 64 | 13:00 | 145 | Rangamati | 14 | 18:30
14 | Barapukuria | 63 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 123 | 18:00
15 | Barguna | 18 | 21:00 | 81 | Kazla | 103 | 12:00 | 147 | Ruppur | 5.8 | 11:00
16 | Barishal | 92 | 19:00 | 82 | Keranigonj | 70 | 19:00 | 148 | SSM | 15 | 04:00
17 | Barishal-230 | 76 | 19:00 | 83 | Khagrachori | 26 | 18:00 | 149 | Saidpur | 97 | 09:00
18 | Baroaulia | 54 | 14:00 | 84 | Khosba | 28 | 04:00 | 150 | Satkhira | 108 | 18:30
19 | Baroirhat | 53 | 13:00 | 85 | Khulna | 78 | 19:30 | 151 | Satmasjid | 86 | 13:00
20 | Bashundhara | 153 | 19:00 | 86 | Khulshi | 159 | 20:00 | 152 | Savar | 204 | 14:00
21 | BashundharaCement | 13 | 00:00 | 87 | Kishoreganj | 125 | 18:30 | 153 | SevenRings | 18.41 | 13:00
22 | Beanibazar | 48 | 18:30 | 88 | Kodda | 275 | 09:00 | 154 | ShahCement | 32 | 01:00
23 | Benapole | 56 | 19:00 | 89 | Kulaura | 31 | 18:00 | 155 | Shahjadpur | 79 | 10:00
24 | Bhaluka | 130 | 10:00 | 90 | Kurigram | 54 | 18:00 | 156 | Shahjibazar | 97 | 22:00
25 | Bhandaria | 43 | 21:00 | 91 | Kushtia | 120 | 19:00 | 157 | Shahmirpur | 45 | 00:00
26 | Bhangura | 36 | 14:00 | 92 | Lalbag | 74 | 13:00 | 158 | Shariatpur | 62 | 20:00
27 | Bheramara(GK) | 44 | 19:00 | 93 | Lalmonirhat | 49 | 18:00 | 159 | Sherpur | 146 | 18:00
28 | Bhulta | 258 | 00:00 | 94 | MI_Cement | 16.9 | 11:00 | 160 | Shikalbaha | 31 | 12:00
29 | Bog-Sherpur | 70 | 10:00 | 95 | Madanganj | 38 | 20:00 | 161 | Shitalakhya | 74.6 | 12:00
30 | Bogura | 131 | 18:00 | 96 | Madaripur | 81 | 19:00 | 162 | Sholosohor | 40 | 14:00
31 | Borhanuddin | 68 | 21:00 | 97 | Madartek | 80.01 | 21:00 | 163 | Shyampur | 144 | 00:00
32 | Brahmanbaria | 105 | 19:00 | 98 | Madunaghat | 43 | 18:30 | 164 | Siddhirganj | 126 | 12:00
33 | Cantonment | 116 | 14:00 | 99 | Magura | 51 | 19:00 | 165 | Sirajganj | 96 | 10:00
34 | Chandpur | 52 | 19:00 | 100 | Mahasthangarh | 64 | 13:00 | 166 | Sonargaon | 86 | 09:00
35 | Chandraghona | 31 | 19:00 | 101 | Manikganj | 116 | 19:00 | 167 | Sreemongol | 56 | 22:00
36 | Chapai | 67 | 10:00 | 102 | Maniknagar | 62 | 13:00 | 168 | Sreepur | 92 | 09:00
37 | Charsaidpur | 40 | 10:00 | 103 | Matarbari | 42 | 21:00 | 169 | Srinagar | 35.45 | 20:00
38 | Chauddagram | 59 | 13:00 | 104 | Matuail | 64 | 10:00 | 170 | Sunamganj | 40 | 18:00
39 | Chhatak | 28 | 13:00 | 105 | Millgate | 72 | 10:00 | 171 | Sylhet | 26 | 13:00
40 | Chowmuhani | 184 | 21:00 | 106 | Mirpur | 113 | 12:00 | 172 | Sylhet-132 | 97 | 13:00
41 | Chuadanga | 84 | 20:00 | 107 | Mirsorai | 9 | 10:00 | 173 | TK | 26.7 | 18:30
42 | Coxsbazar | 118 | 18:00 | 108 | Mirzapur | 39 | 04:00 | 174 | Tangail | 154 | 05:00
43 | Cumilla(N) | 132 | 19:00 | 109 | Mithapukur | 50 | 03:00 | 175 | Thakurgaon | 80 | 18:00
44 | Cumilla(S) | 169 | 14:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 115 | 12:00
45 | Daudkandi | 132 | 20:00 | 111 | Mogbazar | 126.7 | 14:00 | 177 | Ullahpara | 32 | 13:00
46 | Dhaka | 46 | 11:00 | 112 | Mongla | 39 | 19:30 | 178 | Ullon | 40 | 20:00
47 | Dhamrai | 112 | 15:00 | 113 | Motijheel | 32 | 13:00 | 179 | Uttara | 74 | 13:00
48 | Dhanmondi | 117.8 | 13:00 | 114 | Muktagacha | 31 | 04:00 | 180 | UttaraNew | 41 | 21:00
49 | Dohazari | 82 | 21:00 | 115 | Munshiganj | 78 | 13:00 | 181 | Zigatola | 62 | 13:00
50 | Faridpur | 124 | 19:00 | 116 | Muradnagar | 15 | 18:30
51 | Fatullah | 86 | 15:00 | 117 | Mymensingh | 180 | 18:00
52 | Fenchuganj | 25 | 13:00 | 118 | Naogaon | 112 | 10:00
53 | Feni | 96 | 18:30 | 119 | Narail | 47 | 19:00
54 | GPH | 82 | 09:00 | 120 | Narinda | 62 | 13:00
55 | Ghatail | 68 | 17:00 | 121 | Narshingdi | 151 | 19:30
56 | Ghorashal | 13 | 16:00 | 122 | Natore | 122 | 20:00
57 | Ghorashal-230 | 69 | 01:00 | 123 | Nawabganj | 41.4 | 22:00
58 | Goalpara | 28 | 18:30 | 124 | Netrakona | 131 | 19:30
59 | Gollamari | 52 | 19:00 | 125 | New | 79.8 | 12:00
60 | Gopalganj | 85.6 | 20:00 | 126 | Niamatpur | 96 | 13:00
61 | Gulshan | 98 | 13:00 | 127 | Noapara | 40 | 19:00
62 | Halishahar | 66.5 | 15:00 | 128 | PHP | 9 | 22:00
63 | HaripurSBU | 166 | 14:00 | 129 | Pabna | 92 | 03:00
64 | Hasnabad | 72 | 19:30 | 130 | Palashbari | 100 | 18:00
65 | Hathazari | 70 | 19:00 | 131 | Panchagarh | 48 | 18:00
66 | Ishurdi | 57 | 13:00 | 132 | Patuakhali | 61.9 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11292.5 | 0 |  | 11292.5
1:00 | 11023.5 | 0 |  | 11023.5
2:00 | 10636.5 | 0 |  | 10636.5
3:00 | 10931.5 | 0 |  | 10931.5
4:00 | 11315.9 | 0 |  | 11315.9
5:00 | 10356.2 | 0 |  | 10356.2
6:00 | 9612.2 | 0 |  | 9612.2
7:00 | 9928.48 | 0 |  | 9928.48
8:00 | 10383.56 | 0 |  | 10383.56
9:00 | 11105.35 | 0 |  | 11105.35
10:00 | 11752.58 | 0 |  | 11752.58
11:00 | 11939.4 | 0 |  | 11939.4
12:00 | 12352.62 | 0 |  | 12352.62
13:00 | 12748.89 | 0 |  | 12748.89
14:00 | 12524.88 | 0 |  | 12524.88
15:00 | 12244.22 | 0 |  | 12244.22
16:00 | 12152.22 | 0 |  | 12152.22
17:00 | 12217.41 | 0 |  | 12217.41
18:00 | 12192.02 | 40 |  | 12234.02
19:00 | 12887.88 | 0 |  | 12887.88
19:30 | 12668.15 | 0 |  | 12668.15
20:00 | 12652.14 | 0 |  | 12652.14
21:00 | 12533.96 | 0 |  | 12533.96
22:00 | 12398.87 | 0 |  | 12398.87
23:00 | 11965.2 | 0 |  | 11965.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5885 | 5407.5 | 11292.5 | DAILY GENERATION CURVE
00:30 | 5814 | 5344 | 11158
01:00 | 5743 | 5280.5 | 11023.5 | 03-03-2025
01:30 | 5701.5 | 5128.5 | 10830
02:00 | 5660 | 4976.5 | 10636.5
02:30 | 5760.5 | 5023.5 | 10784
03:00 | 5861 | 5070.5 | 10931.5
03:30 | 6037.7 | 5086 | 11123.7
04:00 | 6214.4 | 5101.5 | 11315.9
04:30 | 6029.55 | 4806.5 | 10836.05
05:00 | 5844.7 | 4511.5 | 10356.2
05:30 | 5668.7 | 4315.5 | 9984.2
06:00 | 5492.7 | 4119.5 | 9612.2
06:30 | 5566.03 | 4204.31 | 9770.34
07:00 | 5639.36 | 4289.12 | 9928.48
07:30 | 5755.235 | 4400.785 | 10156.02
08:00 | 5871.11 | 4512.45 | 10383.56
08:30 | 6019.76 | 4724.695 | 10744.455
09:00 | 6168.41 | 4936.94 | 11105.35
09:30 | 6246.83 | 5182.135 | 11428.965
10:00 | 6325.25 | 5427.33 | 11752.58
10:30 | 6409.985 | 5436.005 | 11845.99
11:00 | 6494.72 | 5444.68 | 11939.4
11:30 | 6583.515 | 5562.495 | 12146.01
12:00 | 6672.31 | 5680.31 | 12352.62
12:30 | 6755.03 | 5795.725 | 12550.755
13:00 | 6837.75 | 5911.14 | 12748.89
13:30 | 6856.07 | 5780.815 | 12636.885
14:00 | 6874.39 | 5650.49 | 12524.88
14:30 | 6844.72 | 5539.83 | 12384.55
15:00 | 6815.05 | 5429.17 | 12244.22
15:30 | 6727.525 | 5470.695 | 12198.22
16:00 | 6640 | 5512.22 | 12152.22
16:30 | 6666.305 | 5518.51 | 12184.815
17:00 | 6692.61 | 5524.8 | 12217.41
17:30 | 6748.34 | 5456.375 | 12204.715
18:00 | 6804.07 | 5387.95 | 12192.02
18:30 | 6974.035 | 5565.915 | 12539.95
19:00 | 7144 | 5743.88 | 12887.88
19:30 | 7162 | 5506.15 | 12668.15
20:00 | 7118 | 5534.14 | 12652.14
20:30 | 7023 | 5570.05 | 12593.05 |  | Executive Engineer
21:00 | 6928 | 5605.96 | 12533.96 |  | Network Operation Division
21:30 | 6947.5 | 5518.915 | 12466.415
22:00 | 6967 | 5431.87 | 12398.87
22:30 | 6945.5 | 5236.535 | 12182.035
23:00 | 6924 | 5041.2 | 11965.2

## En-Curve
QF-LDC-12
Date | 03-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2978 | 1576.5 | 924 | 0 | 82 | 1372 | 40 | 3585 | 0 | 226 | 509 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2991.5 | 1576 | 924.5 | 0 | 76 | 1373 | 40 | 3536 | 0 | 213.5 | 427.5 | 0 | 0 | 0 | 0 | 03-03-2025
01:00 | 3005 | 1575.5 | 925 | 0 | 70 | 1374 | 40 | 3487 | 0 | 201 | 346 | 0 | 0 | 0 | 0
01:30 | 2957 | 1525.5 | 924.5 | 0 | 71 | 1317.5 | 40 | 3474 | 0 | 201 | 319.5 | 0 | 0 | 0 | 0 | Energy Generated | 291.5956 |  | MKWHr
02:00 | 2909 | 1475.5 | 924 | 0 | 72 | 1261 | 40 | 3461 | 0 | 201 | 293 | 0 | 0 | 0 | 0 | Energy not Served | 0.04 |  | MKWHr
02:30 | 2956.5 | 1474.5 | 924.5 | 0 | 70 | 1263 | 40 | 3560 | 0 | 213 | 282.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 291.6356 |  | MKWHr
03:00 | 3004 | 1473.5 | 925 | 0 | 68 | 1265 | 40 | 3659 | 0 | 225 | 272 | 0 | 0 | 0 | 0
03:30 | 3026.5 | 1557.85 | 924.5 | 0 | 70 | 1209 | 40 | 3723 | 0 | 254 | 318.85 | 0 | 0 | 0 | 0
04:00 | 3049 | 1642.2 | 924 | 0 | 72 | 1153 | 40 | 3787 | 0 | 283 | 365.7 | 0 | 0 | 0 | 0
04:30 | 2990.5 | 1588.7 | 923.5 | 0 | 71 | 1042.5 | 40 | 3586.5 | 0 | 250 | 343.35 | 0 | 0 | 0 | 0
05:00 | 2932 | 1535.2 | 923 | 0 | 70 | 932 | 40 | 3386 | 0 | 217 | 321 | 0 | 0 | 0 | 0
05:30 | 2851 | 1460.7 | 923 | 0 | 67 | 929 | 40 | 3242.5 | 0 | 201 | 270 | 0 | 0 | 0 | 0
06:00 | 2770 | 1386.2 | 923 | 0 | 64 | 926 | 40 | 3099 | 0 | 185 | 219 | 0 | 0 | 0 | 0
06:30 | 2883 | 1442.2 | 923 | 0 | 61 | 925.5 | 40 | 3072.5 | 19.14 | 185 | 219 | 0 | 0 | 0 | 0
07:00 | 2996 | 1498.2 | 923 | 0 | 58 | 925 | 40 | 3046 | 38.28 | 185 | 219 | 0 | 0 | 0 | 0
07:30 | 2962 | 1530.6 | 902 | 0 | 58 | 924.5 | 40 | 3184 | 107.92 | 201.5 | 245.5 | 0 | 0 | 0 | 0
08:00 | 2928 | 1563 | 881 | 0 | 58 | 924 | 40 | 3322 | 177.56 | 218 | 272 | 0 | 0 | 0 | 0
08:30 | 2988.5 | 1599.5 | 879 | 0 | 60 | 968.5 | 40 | 3438 | 235.455 | 234.5 | 301 | 0 | 0 | 0 | 0
09:00 | 3049 | 1636 | 877 | 0 | 62 | 1013 | 40 | 3554 | 293.35 | 251 | 330 | 0 | 0 | 0 | 0
09:30 | 3042.5 | 1638.75 | 900 | 0 | 67 | 1066 | 40 | 3655.5 | 375.215 | 251 | 393 | 0 | 0 | 0 | 0
10:00 | 3036 | 1641.5 | 923 | 0 | 72 | 1119 | 40 | 3757 | 457.08 | 251 | 456 | 0 | 0 | 0 | 0
10:30 | 3035 | 1568 | 923 | 0 | 71 | 1118 | 40 | 3820 | 489.49 | 251 | 530.5 | 0 | 0 | 0 | 0
11:00 | 3034 | 1494.5 | 923 | 0 | 70 | 1117 | 40 | 3883 | 521.9 | 251 | 605 | 0 | 0 | 0 | 0
11:30 | 3184.5 | 1566.75 | 923.5 | 0 | 75 | 1117 | 40 | 3844 | 541.26 | 243 | 611 | 0 | 0 | 0 | 0
12:00 | 3335 | 1639 | 924 | 0 | 80 | 1117 | 40 | 3805 | 560.62 | 235 | 617 | 0 | 0 | 0 | 0
12:30 | 3375.5 | 1634 | 924 | 0 | 83 | 1136.5 | 40 | 3948.5 | 534.255 | 235 | 638.5 | 0 | 0 | 1.5 | 0
13:00 | 3416 | 1629 | 924 | 0 | 86 | 1156 | 40 | 4092 | 507.89 | 235 | 660 | 0 | 0 | 3 | 0
13:30 | 3399 | 1588.75 | 924 | 0 | 87 | 1159.81 | 40 | 4030 | 505.825 | 230.5 | 669 | 0 | 0 | 3 | 0
14:00 | 3382 | 1548.5 | 924 | 0 | 88 | 1163.62 | 40 | 3968 | 503.76 | 226 | 678 | 0 | 0 | 3 | 0
14:30 | 3337.5 | 1569.5 | 924 | 0 | 73.5 | 1168.38 | 40 | 3969 | 456.67 | 209.5 | 634 | 0 | 0 | 2.5 | 0
15:00 | 3293 | 1590.5 | 924 | 0 | 59 | 1173.14 | 40 | 3970 | 409.58 | 193 | 590 | 0 | 0 | 2 | 0
15:30 | 3183 | 1602.5 | 923.5 | 0 | 60 | 1215.435 | 40 | 4035 | 345.285 | 193 | 590.5 | 0 | 0 | 10 | 0
16:00 | 3073 | 1614.5 | 923 | 0 | 61 | 1257.73 | 40 | 4100 | 280.99 | 193 | 591 | 0 | 0 | 18 | 0
16:30 | 3084 | 1579 | 923.5 | 0 | 61 | 1307.745 | 40 | 4138 | 193.57 | 209.5 | 639 | 0 | 0 | 9.5 | 0
17:00 | 3095 | 1543.5 | 924 | 0 | 61 | 1357.76 | 40 | 4176 | 106.15 | 226 | 687 | 0 | 0 | 1 | 0
17:30 | 3096 | 1456 | 923 | 0 | 61.5 | 1359.595 | 40 | 4131 | 54.12 | 259 | 824 | 0 | 0 | 0.5 | 20
18:00 | 3097 | 1368.5 | 922 | 0 | 62 | 1361.43 | 40 | 4086 | 2.09 | 292 | 961 | 0 | 0 | 0 | 40
18:30 | 3212.5 | 1504.5 | 899.5 | 0 | 63 | 1362.905 | 40 | 4251.5 | 1.045 | 296.5 | 908.5 | 0 | 0 | 0 | 20
19:00 | 3328 | 1640.5 | 877 | 0 | 64 | 1364.38 | 40 | 4417 | 0 | 301 | 856 | 0 | 0 | 0 | 0
19:30 | 3349 | 1677.5 | 877 | 0 | 56 | 1359.65 | 40 | 4254 | 0 | 309 | 746 | 0 | 0 | 0 | 0
20:00 | 3342 | 1685 | 877 | 0 | 54 | 1354.14 | 40 | 4325 | 0 | 309 | 666 | 0 | 0 | 0 | 0
20:30 | 3328 | 1707.25 | 897.5 | 0 | 57 | 1306.3 | 40 | 4336.5 | 0 | 284.5 | 636 | 0 | 0 | 0 | 0
21:00 | 3314 | 1729.5 | 918 | 0 | 60 | 1258.46 | 40 | 4348 | 0 | 260 | 606 | 0 | 0 | 0 | 0
21:30 | 3309.5 | 1752.5 | 918.5 | 0 | 59 | 1208.915 | 40 | 4310 | 0 | 260 | 608 | 0 | 0 | 0 | 0
22:00 | 3305 | 1775.5 | 919 | 0 | 58 | 1159.37 | 40 | 4272 | 0 | 260 | 610 | 0 | 0 | 0 | 0
22:30 | 3297.5 | 1831 | 919 | 0 | 60 | 1084.035 | 40 | 4096.5 | 0 | 260 | 594 | 0 | 0 | 0 | 0
23:00 | 3290 | 1886.5 | 919 | 0 | 62 | 1008.7 | 40 | 3921 | 0 | 260 | 578 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 396 | 06:00 | 372 | 16:00 | Payra | 415 | 06:00 | 405 | 13:00
Ashuganj | 409 | 14:00 | 392 | 19:00 | Rahanpur | 414 | 05:00 | 399 | 17:00
Bhulta | 410 | 18:00 | 374 | 11:00 | Rampal | 407 | 06:00 | 380 | 13:00
Bibiana | 397 | 04:00 | 384 | 12:00
BIPTC | 398 | 04:00 | 391 | 16:00
Bogura | 410 | 06:00 | 390 | 17:00
Gopalganj | 405 | 06:00 | 381 | 13:00
Kaliakoir | 381 | 18:00 | 359 | 16:00
Madunaghat | 399 | 19:00 | 391 | 10:00
Meghnaghat | 391 | 06:00 | 372 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 214 | 11:00 | Keranigonj | 226 | 06:00 | 212 | 11:00
AKSML | 229 | 18:00 | 219 | 11:00 | Khulna(S) | 238 | 06:00 | 222 | 13:00
Aminbazar | 226 | 03:00 | 216 | 09:00 | Madunaghat | 228 | 18:00 | 222 | 10:00
Ashuganj | 236 | 19:00 | 219 | 15:00 | Madunaghat-400 | 228 | 19:00 | 222 | 10:00
Ashuganj-400 | 234 | 04:00 | 231 | 07:00 | Maniknagar | 225 | 04:00 | 210 | 16:00
Baghabari | 237 | 05:00 | 226 | 12:00 | Meghnaghat | 233 | 00:00 | 219 | 16:00
Barapukuria | 226 | 05:00 | 218 | 09:00 | Meghnaghat-400 | 229 | 06:00 | 214 | 16:00
Barapukuria-230 | 226 | 05:00 | 218 | 09:00 | Mirsorai | 224 | 07:00 | 217 | 10:00
Barishal | 240 | 06:00 | 224 | 13:00 | Rajshahi | 235 | 06:00 | 224 | 09:00
Bheramara | 235 | 05:00 | 222 | 12:00 | Rampal | 235 | 06:00 | 220 | 13:00
Bhulta | 227 | 06:00 | 212 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 220 | 13:00 | Rampura | 227 | 06:00 | 210 | 16:00
BIPTC | 237 | 05:00 | 224 | 09:00 | Shikalbaha | 226 | 07:00 | 220 | 09:00
Bogura | 237 | 05:00 | 226 | 10:00 | Shyampur | 227 | 06:00 | 212 | 16:00
Bogura-400 | 236 | 05:00 | 226 | 10:00 | Siddhirganj | 227 | 04:00 | 214 | 16:00
Borhanuddin | 243 | 07:00 | 232 | 14:00 | Sirajgonj | 243 | 06:00 | 233 | 17:00
BSRM | 225 | 18:30 | 215 | 11:00 | Sreepur | 234 | 05:00 | 220 | 12:00
Cumilla(N) | 223 | 18:00 | 213 | 15:00 | Tongi | 224 | 04:00 | 208 | 11:00
Faridpur | 237 | 05:00 | 216 | 14:00
Fenchuganj | 234 | 06:00 | 225 | 13:00
Ghorashal | 230 | 00:00 | 220 | 14:00
Ghorashal-230 | 227 | 05:00 | 213 | 16:00
Gopalganj | 238 | 06:00 | 214 | 13:00
GPH | 226 | 18:00 | 218 | 11:00
Haripur | 227 | 06:00 | 212 | 16:00
Hasnabad | 226 | 23:00 | 213 | 11:00
Hathazari | 229 | 18:00 | 220 | 11:00
Ishurdi | 236 | 05:00 | 226 | 09:00
Jhenaidah | 235 | 06:00 | 220 | 13:00
Kaliakoir | 228 | 18:00 | 214 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 130 | 23:00 | 118 | 14:00 | Madunaghat | 131 | 18:00 | 126 | 11:00
Agargaon | 136 | 06:00 | 127 | 11:00 | Magura | 138 | 06:00 | 126 | 13:00
Agrabad | 131 | 18:00 | 123 | 14:00 | Mahasthangarh | 133 | 05:00 | 124 | 10:00
AKS | 129 | 18:00 | 123 | 09:00 | Manikganj | 130 | 04:00 | 121 | 16:00
Aminbazar | 132 | 05:00 | 123 | 09:00 | Maniknagar | 127 | 05:00 | 118 | 13:00
Amnura | 136 | 05:00 | 126 | 12:00 | Matarbari | 1145 | 03:00 | 112 | 21:00
Ashuganj | 135 | 23:00 | 130 | 10:00 | Matuail | 132 | 05:00 | 122.6 | 16:00
Bagerhat | 135 | 06:00 | 119 | 13:00 | Millgate | 132 | 06:00 | 120 | 11:00
Bajitpur | 130 | 18:00 | 123 | 11:00 | Mirpur | 132 | 18:00 | 50 | 01:00
Bakulia | 131 | 18:00 | 125 | 11:00 | Mirzapur | 132 | 18:00 | 123 | 16:00
Banani | 130 | 23:00 | 117 | 14:00 | Mithapukur | 136 | 18:30 | 123 | 08:00
Bangabhaban | 127 | 05:00 | 118 | 14:00 | MI_Cement | 132 | 06:00 | 122 | 16:00
Barapukuria | 136 | 15:00 | 128 | 09:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 136 | 07:00 | 131 | 13:00 | Mogbazar | 130 | 02:00 | 119 | 16:00
Barishal | 133 | 05:00 | 35 | 02:00 | Mongla | 133 | 06:00 | 120 | 13:00
Barishal-230 | 134 | 06:00 | 124 | 13:00 | Motijheel | 127 | 05:00 | 118 | 14:00
Baroaulia | 129 | 23:00 | 125 | 03:00 | Muktagacha | 158 | 17:00 | 123 | 09:00
Baroirhat | 123 | 23:00 | 116 | 11:00 | Munshiganj | 133 | 18:00 | 121 | 16:00
Bashundhara | 131 | 04:00 | 117 | 15:00 | Muradnagar | 126 | 06:00 | 118 | 14:00
BashundharaCement | 131 | 18:30 | 122 | 16:00 | Mymensingh | 134 | 23:00 | 110 | 17:00
Beanibazar | 131 | 06:00 | 126 | 14:00 | Naogaon | 131 | 05:00 | 120 | 09:00
Benapole | 135 | 06:00 | 120 | 13:00 | Narail | 136 | 05:00 | 127 | 13:00
Bhaluka | 129 | 05:00 | 117 | 15:00 | Narinda | 127 | 05:00 | 118 | 13:00
Bhandaria | 131 | 06:00 | 119 | 15:00 | Narshingdi | 131 | 18:00 | 118 | 15:00
Bhangura | 135 | 05:00 | 127 | 11:00 | Natore | 135 | 06:00 | 127 | 12:00
Bheramara | 135 | 05:00 | 127 | 12:00 | Nawabganj | 137 | 18:00 | 125 | 11:00
Bheramara(GK) | 135 | 06:00 | 128 | 09:00 | Netrakona | 124 | 05:00 | 108 | 11:00
Bhulta | 127 | 04:00 | 116 | 16:00 | New | 132 | 06:00 | 121 | 11:00
Bog-Sherpur | 133 | 05:00 | 125 | 10:00 | Niamatpur | 136 | 05:00 | 129 | 17:00
Bogura | 135 | 06:00 | 127 | 10:00 | Noapara | 137 | 05:00 | 122 | 13:00
Bogura-230 | 135 | 05:00 | 127 | 10:00 | Pabna | 136 | 06:00 | 128 | 16:00
Brahmanbaria | 130 | 08:00 | 121 | 15:00 | Palashbari | 128 | 05:00 | 12 | 14:00
Cantonment | 136 | 06:00 | 127 | 11:00 | Panchagarh | 142 | 18:30 | 118 | 09:00
Chandpur | 123 | 18:00 | 115 | 01:00 | Patuakhali | 133 | 02:00 | 131 | 00:00
Chandraghona | 138 | 18:00 | 127 | 10:00 | Payra | 136 | 07:00 | 133 | 13:00
Chapai | 134 | 05:00 | 128 | 10:00 | PHP | 122 | 18:00 | 114 | 01:00
Charsaidpur | 132 | 05:00 | 123 | 15:00 | Postogola | 134 | 05:00 | 125 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 123 | 18:00 | 115 | 12:00 | Purbachal | 129 | 06:00 | 117 | 15:00
Chhatak | 130 | 06:00 | 125 | 14:00 | Purbasadipur | 133 | 18:00 | 118 | 08:00
Chowmuhani | 119 | 23:00 | 110 | 12:00 | Rahanpur | 137 | 03:00 | 131 | 11:00
Chuadanga | 136 | 06:00 | 123 | 12:00 | Rahanpur-400 | 137 | 05:00 | 132 | 10:00
Coxsbazar | 121 | 08:00 | 113 | 19:00 | Rahim | 132 | 06:00 | 123 | 16:00
Cumilla(N) | 127 | 18:00 | 121 | 15:00 | Rajbari | 133 | 06:00 | 119 | 13:00
Cumilla(S) | 130 | 21:00 | 119 | 14:00 | Rajendrapur | 135 | 18:30 | 119 | 16:00
Daudkandi | 124 | 04:00 | 117 | 15:00 | Rajshahi | 135 | 05:00 | 128 | 09:00
Dhaka | 130 | 18:00 | 118 | 15:00 | Rajshahi-230 | 135 | 05:00 | 122 | 17:00
Dhamrai | 129 | 01:00 | 119 | 15:00 | Ramganj | 119 | 18:00 | 110 | 00:00
Dhanmondi | 133 | 03:00 | 118 | 15:00 | Rampur | 130 | 18:00 | 123 | 11:00
Dohazari | 125 | 18:00 | 120 | 12:00 | Rampura | 130 | 23:00 | 117 | 16:00
Faridpur | 132 | 05:00 | 123 | 13:00 | Rangamati | 130 | 06:00 | 126 | 11:00
Fatullah | 133 | 06:00 | 124 | 11:00 | Rangpur | 134 | 18:30 | 121 | 09:00
Fenchuganj | 135 | 06:00 | 130 | 13:00 | Ruppur | 137 | 05:00 | 129 | 09:00
Feni | 124 | 18:30 | 116 | 12:00 | Saidpur | 133 | 18:30 | 121 | 08:00
Ghatail | 130 | 18:30 | 122 | 10:00 | Satkhira | 136 | 06:00 | 119 | 16:00
Ghorashal | 136 | 05:00 | 128 | 15:00 | Satmasjid | 135 | 06:00 | 127 | 11:00
Goalpara | 137 | 05:00 | 122 | 13:00 | Savar | 132 | 18:00 | 122 | 08:00
Gollamari | 138 | 06:00 | 124 | 13:00 | SevenRings | 137 | 18:30 | 128 | 15:00
Gopalganj | 137 | 06:00 | 124 | 13:00 | ShahCement | 132 | 05:00 | 123 | 16:00
Gopalganj-400 | 138 | 06:00 | 126 | 13:00 | Shahjadpur | 142 | 10:00 | 130 | 19:00
Gulshan | 129 | 23:00 | 117 | 15:00 | Shahjibazar | 131 | 01:00 | 124 | 18:30
Halishahar | 131 | 06:00 | 124 | 11:00 | Shahmirpur | 132 | 18:00 | 124 | 11:00
Haripur | 132 | 05:00 | 122 | 16:00 | Shariatpur | 136 | 05:00 | 125 | 14:00
HaripurSBU | 132 | 07:00 | 122 | 16:00 | Sherpur | 135 | 18:30 | 121 | 10:00
Hasnabad | 133 | 01:00 | 125 | 11:00 | Shikalbaha | 120 | 18:00 | 114 | 11:00
Hathazari | 133 | 18:00 | 126 | 11:00 | Shikalbaha-230 | 131 | 00:00 | 125 | 09:00
Ishurdi | 137 | 05:00 | 130 | 19:30 | Shitalakhya | 132 | 06:00 | 122 | 16:00
Jaldhaka | 133 | 02:00 | 119 | 10:00 | Sholosohor | 130 | 19:00 | 126 | 10:00
Jamalpur | 138 | 18:30 | 124 | 00:00 | Shyampur | 133 | 18:00 | 130 | 08:00
Jashore | 136 | 06:00 | 122 | 13:00 | Shyampur-230 | 132 | 06:00 | 123 | 16:00
Jhenaidah | 136 | 06:00 | 127 | 12:00 | Siddhirganj | 132 | 05:00 | 123 | 16:00
Jhenaidah-230 | 138 | 06:00 | 126 | 13:00 | Sirajganj | 134 | 01:00 | 125 | 09:00
Joydebpur | 136 | 18:00 | 124 | 14:00 | Sonargaon | 129 | 02:00 | 121 | 16:00
Joypurhat | 129 | 05:00 | 115 | 10:00 | Sreemongol | 136 | 15:00 | 126 | 11:00
Juldah | 131 | 18:00 | 124 | 12:00 | Sreepur | 128 | 02:00 | 119 | 12:00
Kabirpur | 134 | 18:30 | 116 | 15:00 | Srinagar | 138 | 18:00 | 125 | 12:00
Kachua | 123 | 18:00 | 116 | 01:00 | SSM | 135 | 00:00 | 128 | 08:00
Kaliakoir | 137 | 00:00 | 122 | 11:00 | Sunamganj | 129 | 06:00 | 124 | 13:00
Kallyanpur | 134 | 06:00 | 125 | 11:00 | Sylhet | 131 | 04:00 | 127 | 13:00
Kalurghat | 130 | 18:00 | 126 | 11:00 | Sylhet-132 | 132 | 05:00 | 128 | 15:00
Kamrangirchar | 137 | 18:30 | 123 | 11:00 | Tangail | 131 | 18:00 | 121 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 141 | 18:30 | 117 | 09:00
Kazla | 127 | 05:00 | 117 | 13:00 | TK | 131 | 18:00 | 126 | 09:00
Keranigonj | 136 | 18:00 | 124 | 16:00 | Tongi | 132 | 04:00 | 122 | 12:00
Khagrachori | 130 | 06:00 | 125 | 11:00 | Ullahpara | 135 | 05:00 | 127 | 11:00
Khosba | 126 | 06:00 | 118 | 14:00 | Ullon | 131 | 23:00 | 117 | 16:00
Khulna | 135 | 05:00 | 122 | 13:00 | Uttara | 132 | 18:30 | 120 | 12:00
Khulna(S) | 139 | 06:00 | 123 | 13:00 | UttaraNew | 132 | 06:00 | 119 | 16:00
Khulshi | 129 | 18:00 | 122 | 11:00 | Zigatola | 139 | 18:00 | 126 | 11:00
Kishoreganj | 127 | 03:00 | 116 | 14:00
Kodda | 135 | 18:00 | 122 | 15:00
KSRM | 132 | 18:00 | 125 | 14:00
Kulaura | 133 | 03:00 | 129 | 15:00
Kurigram | 133 | 15:00 | 118 | 08:00
Kushtia | 135 | 05:00 | 127 | 12:00
Lalbag | 137 | 18:00 | 125 | 11:00
Lalmonirhat | 130 | 05:00 | 121 | 07:00
Madanganj | 131 | 18:30 | 122 | 16:00
Madaripur | 135 | 06:00 | 127 | 13:00
Madartek | 130 | 23:00 | 117 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division