## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-03-2025 | during | 06-03-2025 | during | 06-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 130 | 130 | 230 | 230 | 130 | 130 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 260 | 260 | 110 | 110 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 362 | 412 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 282 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 305 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 22 | 22.5 | 22.5 | 22.5 | 22.5 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 26 | 23 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 26 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 86 | 85 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 70 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 90 | 90 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 51 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1976 | 2023 | 5268 | 5327 | 3261.1 | 3320.1
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 134 | 134 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 9 | 33 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 30 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.2 | 0 | 4.2 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 35 | 35 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 750 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 7 | 0 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 980 | 965 | 980 | 980 | 980 | 980 | -
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1963 | 2269 | 3766.06 | 3781.86 | 3633.06 | 3648.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 230 | 230 | 230 | 230 | 230 | 230 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 73 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 32 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 0 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 45 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 58 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 19 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 981 | 782 | 1978.97 | 1908.97 | 1759.03 | 1689.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-03-2025 | during | 06-03-2025 | during | 06-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 29 | 13 | 210 | 210 | 33 | 33 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 86 | 135 | 200 | 200 | 130 | 130 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 89 | 89 | 115 | 115 | 100 | 100 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.86 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 259.86 | 249 | 653.7 | 601.5 | 381.7 | 329.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 30 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 113 | 113 | 163 | 163 | 110 | 110 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 34 | 34 | 40 | 40 | 36 | 36 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 103 | 162 | 100 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 340 | 382 | 380 | 380 | 385 | 385 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1435 | 1515 | 1580 | 1640 | 1554 | 1554
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 174 | 205 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 100 | 100 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 93.13 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 380 | 510 | 1234.2 | 1234.2 | 610 | 610 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1571.13 | 1592 | 3486.2 | 3396.2 | 2192.02 | 2102.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 123 | 123 | 127 | 127 | 127 | 127 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 700 | 1100 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 72 | 72 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1355.6 | 1757 | 2169.12 | 2168.12 | 2091.12 | 2090.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 154 | 178 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 145 | 172 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 370 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.59 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 817 | 1084.29 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.66 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1673.75 | 1853.79 | 3111.28 | 2940.78 | 2849.49 | 2678.99
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 63 | 62 | 62 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 | 175 | 175 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 54 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 202 | 0 | 199 | 0 | 199 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 477 | 394 | 729.6 | 494 | 703.62 | 468.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 11692.34 | 12434.79 | 22742.93 | 22258.43 | 18425.14 | 17880.64
Forecast Scenario (06-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11323 |  | 0 |  | 11323
|  |  |  | 1:00 | 10847 |  | 0 |  | 10847
|  |  |  | 2:00 | 10405 |  | 0 |  | 10405
|  |  |  | 3:00 | 10625 |  | 0 |  | 10625
|  |  |  | 4:00 | 11146 |  | 0 |  | 11146
|  |  |  | 5:00 | 10067 |  | 0 |  | 10067
|  |  |  | 6:00 | 9220 |  | 0 |  | 9220
|  |  |  | 7:00 | 9567 |  | 0 |  | 9567
|  |  |  | 8:00 | 10279 |  | 0 |  | 10279
|  |  |  | 9:00 | 10995 |  | 0 |  | 10995
|  |  |  | 10:00 | 11604 |  | 0 |  | 11604
|  |  |  | 11:00 | 11850 |  | 0 |  | 11850
|  |  |  | 12:00 | 12033 |  | 0 |  | 12033
|  |  |  | 13:00 | 12253 |  | 0 |  | 12253
|  |  |  | 14:00 | 12373 |  | 0 |  | 12373
|  |  |  | 15:00 | 12217 |  | 0 |  | 12217
|  |  |  | 16:00 | 12075 |  | 0 |  | 12075
|  |  |  | 17:00 | 12133 |  | 0 |  | 12133
|  |  |  | 18:00 | 12088 |  | 0 |  | 12088
|  |  |  | 18:30 | 12329 |  | 0 |  | 12329
|  |  |  | 19:00 | 12686 |  | 0 |  | 12686
|  |  |  | 19:30 | 12618 |  | 0 |  | 12618
|  |  |  | 20:00 | 12460 |  | 0 |  | 12460
|  |  |  | 21:00 | 12350 |  | 0 |  | 12350
|  |  |  | 22:00 | 12200 |  | 0 |  | 12200
|  |  |  | 23:00 | 11762 |  | 0 |  | 11762
Probable Maximum Temperature: |  |  | 30.10°C
Probable Maximum Demand at Day Peak: |  |  | 12033.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12686.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12686.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 274.558 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:23 hrs on 06-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-03-2025 | [28 empty] | Date: | 05-03-2025 | [28 empty] | Date: | 05-03-2025 | [28 empty] | Date: | 05-03-2025 | [28 empty] | Date: | 05-03-2025 | [18 empty] | Date: | 05-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 292 | 0 | 0 | 0 | 32 | 308 | 0 | 0 | 0 | 160 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 0 | 38 | 805 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 195 | 0 | 230 | 0 | 29 | 184 | 31 | 0 | 50 | 34 | 33 | 17 | 17 | 50 | 0 | 0 | 0 | 300 | 320 | 388 | 35 | 42 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 18 | 20 | 0 | 68 | 56 | 27 | 0 | 0 | 12 | 6489 | 923 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 819.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 153 | 0 | 350 | 0 | 0 | 2.5 | 170 | 62 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 123 | 180 | 0 | 0 | 900 | 0 | 4649.92 | 11138.92 | 88.65
01:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 4 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 289 | 0 | 0 | 0 | 31 | 307 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 0 | 38 | 881 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 735 | 0 | 43 | 0 | 195 | 0 | 230 | 0 | 29 | 183 | 31 | 0 | 50 | 17 | 31 | 17 | 17 | 48 | 0 | 0 | 0 | 290 | 320 | 388 | 35 | 42 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 18 | 22 | 0 | 48 | 48 | 23 | 0 | 0 | 12 | 6244 | 924 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 819.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 151 | 0 | 350 | 0 | 0 | 2.5 | 167 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 123 | 180 | 0 | 0 | 700 | 0 | 4393.49 | 10637.49 | 88.65
02:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 392 | 0 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 296 | 0 | 0 | 0 | 32 | 270 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 0 | 38 | 810 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 708 | 0 | 51 | 0 | 195 | 0 | 230 | 0 | 29 | 197 | 31 | 0 | 50 | 17 | 28 | 17 | 17 | 46 | 0 | 0 | 0 | 295 | 320 | 333 | 35 | 42 | 30 | 5 | 80 | 24 | 0 | 41 | 30 | 0 | 18 | 33 | 0 | 48 | 48 | 23 | 0 | 0 | 12 | 5963 | 923 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 819.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 151 | 0 | 320 | 0 | 0 | 2.5 | 167 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 0 | 700 | 0 | 4334.83 | 10297.83 | 88.64
03:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 0 | 60 | 8 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 298 | 0 | 0 | 0 | 32 | 270 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 0 | 38 | 810 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 760 | 0 | 51 | 0 | 195 | 0 | 230 | 0 | 29 | 194 | 28 | 0 | 50 | 17 | 29 | 17 | 17 | 44 | 0 | 0 | 0 | 310 | 320 | 339 | 35 | 42 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 18 | 49 | 0 | 50 | 55 | 32 | 0 | 0 | 12 | 6191 | 924 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 825.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 2.5 | 168 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 7 | 100 | 180 | 0 | 0 | 710 | 0 | 4410.69 | 10601.69 | 88.64
04:00 | 0 | 20 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 60 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 270 | 0 | 0 | 0 | 32 | 300 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 40 | 0 | 38 | 860 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 906 | 0 | 51 | 0 | 138 | 0 | 230 | 0 | 29 | 183 | 28 | 0 | 50 | 17 | 29 | 17 | 4 | 46 | 0 | 0 | 0 | 300 | 320 | 380 | 35 | 42 | 30 | 5 | 80 | 24 | 0 | 86 | 30 | 0 | 18 | 52 | 0 | 79 | 113 | 32 | 0 | 0 | 12 | 6479 | 923 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 820.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 148 | 0 | 300 | 0 | 0 | 2.5 | 167 | 62 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 7 | 123 | 180 | 0 | 0 | 840 | 0 | 4580.58 | 11059.58 | 88.64
05:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 282 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 40 | 770 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 840 | 0 | 5 | 0 | 73 | 0 | 230 | 0 | 29 | 183 | 28 | 0 | 50 | 0 | 29 | 17 | 0 | 44 | 0 | 0 | 0 | 290 | 320 | 380 | 5 | 42 | 30 | 5 | 80 | 24 | 0 | 11 | 20 | 0 | 18 | 52 | 0 | 79 | 65 | 32 | 0 | 0 | 0 | 5795 | 924 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 822.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 148 | 0 | 300 | 0 | 0 | 2.5 | 166 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 123 | 180 | 0 | 0 | 560 | 0 | 4156.16 | 9951.16 | 88.63
06:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 240 | 0 | 0 | 0 | 29 | 240 | 0 | 0 | 0 | 24 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 40 | 770 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 675 | 0 | 5 | 0 | 73 | 0 | 230 | 0 | 29 | 129 | 30 | 0 | 50 | 0 | 9 | 17 | 0 | 40 | 0 | 0 | 0 | 290 | 320 | 305 | 5 | 42 | 30 | 5 | 80 | 24 | 0 | 11 | 20 | 0 | 18 | 52 | 0 | 55 | 45 | 33 | 0 | 0 | 0 | 5144 | 923 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 819.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 151 | 0 | 250 | 0 | 0 | 2.5 | 165 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 520 | 0 | 4028.49 | 9172.49 | 88.63
07:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 321 | 0 | 0 | 0 | 29 | 240 | 0 | 0 | 2 | 17 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 770 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 660 | 1 | 5 | 0 | 73 | 0 | 230 | 0 | 29 | 218 | 32 | 0 | 50 | 0 | 0 | 6 | 0 | 46 | 0 | 5 | 0 | 310 | 320 | 305 | 5 | 42 | 30 | 5 | 80 | 24 | 0 | 11 | 20 | 0 | 18 | 75 | 0 | 62 | 60 | 33 | 0 | 3.61 | 0 | 5292.61 | 924 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.79 | 384 | 0 | 822.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.97 | 150 | 0 | 0 | 0 | 154 | 0 | 350 | 0 | 0.32 | 2.5 | 164 | 62 | 0 | 2 | 0 | 0 | 0 | 0.3 | 15 | 0.04 | 0 | 150 | 5 | 100 | 180 | 0 | 0 | 500 | 0 | 4144.69 | 9437.3 | 88.63
08:00 | 0 | 8 | 8 | 110 | 0 | 131 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 370 | 319 | 0 | 0 | 0 | 29 | 298 | 0 | 0 | 9 | 17 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 10 | 770 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 660 | 8 | 5 | 0 | 73 | 0 | 230 | 0 | 29 | 203 | 32 | 0 | 50 | 0 | 0 | 10 | 0 | 42 | 0 | 20 | 0 | 310 | 320 | 380 | 11 | 42 | 30 | 5 | 113 | 24 | 0 | 11 | 20 | 0 | 18 | 78 | 0 | 87 | 87 | 32 | 1 | 16.73 | 5 | 5729.73 | 877 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.18 | 383 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 18.76 | 150 | 0 | 0 | 0 | 152 | 0 | 350 | 0 | 1.51 | 2.5 | 162 | 60 | 0 | 11 | 0 | 0 | 0 | 1.6 | 76 | 0.17 | 0 | 150 | 4 | 123 | 220 | 0 | 0 | 540 | 0 | 4337.72 | 10067.45 | 88.62
09:00 | 0 | 17 | 16 | 110 | 0 | 131 | 0 | 0 | 403 | 0 | 0 | 0 | 7 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 287 | 0 | 0 | 0 | 18 | 290 | 0 | 0 | 19 | 22 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 9 | 807 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 750 | 13 | 51 | 0 | 184 | 0 | 230 | 0 | 29 | 185 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 50 | 0 | 42 | 0 | 305 | 320 | 389 | 31 | 42 | 30 | 5 | 80 | 24 | 0 | 83 | 30 | 0 | 18 | 79 | 0 | 86 | 86 | 32 | 1 | 31.44 | 12 | 6175.44 | 878 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.15 | 382 | 0 | 810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 37.25 | 159 | 0 | 0 | 0 | 149 | 0 | 414 | 0 | 3.17 | 5.5 | 163 | 60 | 0 | 23 | 0 | 0 | 0 | 3.2 | 131 | 0.32 | 0 | 220 | 4 | 123 | 220 | 0 | 0 | 580 | 0 | 4649.59 | 10825.03 | 88.62
10:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 391 | 0 | 0 | 0 | 17 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 350 | 270 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 26 | 34 | 24 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 7 | 977 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 750 | 17 | 51 | 0 | 184 | 0 | 230 | 0 | 29 | 180 | 28 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 57 | 0 | 310 | 320 | 383 | 34 | 41 | 30 | 5 | 80 | 24 | 0 | 83 | 30 | 0 | 18 | 93 | 0 | 89 | 86 | 31 | 2 | 43.43 | 12 | 6353.43 | 924 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 382 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 51.54 | 163 | 0 | 0 | 0 | 144 | 0 | 370 | 0 | 4.5 | 5.5 | 167 | 62 | 0 | 32 | 0 | 0 | 0 | 4.5 | 170 | 0.47 | 0 | 307 | 5 | 123 | 180 | 0 | 0 | 660 | 0 | 4885.51 | 11238.94 | 88.62
11:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 293 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 31 | 34 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 7 | 981 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 750 | 8 | 51 | 0 | 182 | 0 | 230 | 0 | 29 | 194 | 30 | 0 | 50 | 0 | 0 | 10 | 0 | 54 | 0 | 66 | 0 | 305 | 320 | 340 | 34 | 41 | 30 | 5 | 80 | 24 | 0 | 83 | 30 | 0 | 0 | 93 | 0 | 98 | 86 | 29 | 2 | 50.75 | 0 | 6284.75 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.44 | 381 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 60.47 | 162 | 0 | 0 | 0 | 148 | 0 | 370 | 0 | 5.32 | 5.5 | 168 | 61 | 0 | 36 | 0 | 0 | 0 | 5.4 | 197 | 0.57 | 0 | 307 | 5 | 123 | 180 | 0 | 0 | 700 | 0 | 5024.7 | 11309.45 | 88.61
12:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 362 | 0 | 0 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 297 | 0 | 0 | 0 | 26 | 310 | 0 | 0 | 33 | 51 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 9 | 980 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 750 | 19 | 43 | 0 | 182 | 0 | 230 | 73 | 29 | 200 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 68 | 0 | 310 | 320 | 340 | 34 | 40 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 103 | 0 | 89 | 86 | 29 | 2 | 53.86 | 0 | 6614.86 | 924 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.13 | 380 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 63.66 | 154 | 0 | 0 | 0 | 145 | 0 | 370 | 0 | 5.59 | 5.5 | 170 | 62 | 0 | 37 | 0 | 0 | 0 | 6 | 202 | 0.6 | 0 | 307 | 5 | 123 | 220 | 0 | 0 | 700 | 0 | 5077.48 | 11692.34 | 88.61
13:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 287 | 0 | 0 | 0 | 26 | 310 | 0 | 0 | 32 | 54 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 19 | 943 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 750 | 19 | 43 | 0 | 182 | 0 | 170 | 121 | 29 | 140 | 31 | 0 | 50 | 0 | 8 | 17 | 0 | 56 | 0 | 65 | 0 | 305 | 320 | 385 | 34 | 40 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 112 | 0 | 45 | 65 | 29 | 2 | 52.3 | 0 | 6551.3 | 924 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.76 | 382 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 61.5 | 145 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 5.48 | 5.5 | 167 | 63 | 0 | 34 | 0 | 0 | 0 | 5.9 | 204 | 0.61 | 0 | 275 | 6 | 123 | 220 | 0 | 0 | 750 | 0 | 5108.75 | 11660.05 | 88.61
14:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 294 | 0 | 0 | 0 | 23 | 310 | 0 | 0 | 28 | 54 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 7 | 907 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 855 | 17 | 43 | 0 | 145 | 0 | 150 | 121 | 21 | 148 | 31 | 0 | 50 | 0 | 8 | 17 | 0 | 62 | 0 | 57 | 0 | 315 | 320 | 385 | 34 | 40 | 30 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 112 | 0 | 45 | 45 | 28 | 2 | 46.7 | 0 | 6531.7 | 924 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.42 | 410 | 0 | 822.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 52.61 | 150 | 0 | 0 | 0 | 137 | 0 | 414 | 0 | 4.82 | 2.5 | 169 | 63 | 0 | 31 | 0 | 0 | 0 | 5.8 | 176 | 0.53 | 0 | 307 | 5 | 123 | 220 | 0 | 0 | 900 | 0 | 5249.3 | 11781 | 88.6
15:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 380 | 307 | 0 | 0 | 0 | 23 | 305 | 0 | 0 | 22 | 54 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 24 | 0 | 2 | 40 | 0 | 9 | 908 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 835 | 13 | 43 | 0 | 82 | 0 | 150 | 235 | 5 | 147 | 31 | 8 | 50 | 23 | 10 | 17 | 0 | 60 | 0 | 43 | 0 | 280 | 320 | 360 | 34 | 28 | 29 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 112 | 0 | 17 | 28 | 22 | 2 | 36.27 | 0 | 6421.77 | 923 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.34 | 494 | 0 | 823.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 43.24 | 165 | 0 | 0 | 0 | 150 | 0 | 367 | 0 | 3.95 | 2.5 | 167 | 65 | 0 | 24 | 0 | 0 | 0 | 4.7 | 139 | 0.39 | 0 | 250 | 5 | 123 | 180 | 0 | 0 | 1000 | 0 | 5229.68 | 11651.45 | 88.6
16:00 | 0 | 34 | 16 | 110 | 0 | 130 | 0 | 0 | 391 | 0 | 0 | 0 | 17 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 294 | 0 | 0 | 0 | 21 | 305 | 0 | 0 | 14 | 54 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 24 | 0 | 1 | 40 | 0 | 15 | 975 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 900 | 9 | 43 | 0 | 35 | 0 | 150 | 240 | 5 | 127 | 30 | 34 | 50 | 34 | 36 | 17 | 0 | 56 | 0 | 26 | 0 | 315 | 320 | 385 | 0 | 28 | 29 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 129 | 0 | 65 | 65 | 16 | 1 | 21.55 | 0 | 6629.55 | 924 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.6 | 465 | 0 | 820.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 26.16 | 166 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 2.33 | 2.5 | 168 | 63 | 0 | 15 | 0 | 0 | 0 | 2.8 | 85 | 0.23 | 0 | 307 | 5 | 123 | 220 | 0 | 0 | 1040 | 0 | 5274.22 | 11903.77 | 88.6
17:00 | 0 | 50 | 16 | 110 | 0 | 130 | 0 | 0 | 404 | 0 | 0 | 0 | 17 | 0 | 149 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 274 | 0 | 0 | 0 | 20 | 305 | 0 | 0 | 5 | 62 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 21 | 974 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 951 | 3 | 43 | 0 | 8 | 0 | 150 | 106 | 0 | 215 | 28 | 34 | 50 | 34 | 36 | 17 | 17 | 54 | 0 | 8 | 0 | 300 | 320 | 385 | 0 | 28 | 29 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 75 | 105 | 11 | 0 | 7.35 | 0 | 6707.85 | 923 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.39 | 512 | 0 | 870.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8.89 | 172 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 0.76 | 2.5 | 168 | 63 | 38 | 5 | 42 | 0 | 0 | 1.1 | 29 | 0.09 | 0 | 307 | 5 | 123 | 220 | 0 | 0 | 1100 | 0 | 5394.9 | 12102.75 | 88.59
18:00 | 0 | 50 | 16 | 110 | 0 | 130 | 0 | 0 | 367 | 0 | 0 | 15 | 24 | 0 | 149 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 370 | 291 | 0 | 0 | 0 | 21 | 280 | 0 | 0 | 0 | 70 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 35 | 903 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 910 | 0 | 43 | 0 | 8 | 0 | 230 | 0 | 0 | 205 | 31 | 34 | 50 | 37 | 38 | 17 | 17 | 56 | 0 | 0 | 0 | 310 | 320 | 352 | 31 | 28 | 29 | 5 | 80 | 24 | 0 | 41 | 20 | 0 | 0 | 163 | 0 | 88 | 135 | 8 | 0 | 0.06 | 0 | 6497.06 | 923 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 504 | 0 | 966.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0.02 | 5.5 | 166 | 63 | 91 | 0 | 95 | 0 | 0 | 0 | 1 | 0 | 0 | 268 | 6 | 100 | 220 | 0 | 0 | 1000 | 0 | 5240.89 | 11737.95 | 88.59
19:00 | 0 | 50 | 26 | 110 | 0 | 130 | 0 | 0 | 411 | 0 | 0 | 37 | 20 | 0 | 149 | 32 | 0 | 0 | 0 | 0 | 25 | 15 | 360 | 275 | 0 | 0 | 0 | 24 | 305 | 0 | 0 | 0 | 70 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 31 | 969 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 43 | 0 | 230 | 0 | 0 | 182 | 32 | 58 | 50 | 57 | 38 | 17 | 22 | 58 | 0 | 0 | 0 | 280 | 320 | 380 | 31 | 29 | 29 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 162 | 0 | 89 | 135 | 12 | 0 | 0 | 11 | 6943 | 876 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 0 | 1127.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 170 | 0 | 350 | 0 | 0 | 5.5 | 170 | 63 | 90 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 7 | 100 | 220 | 0 | 0 | 1020 | 0 | 5448.78 | 12391.78 | 88.59
19:30 | 0 | 34 | 26 | 110 | 0 | 130 | 0 | 0 | 412 | 0 | 0 | 35 | 17 | 0 | 85 | 16 | 0 | 0 | 0 | 0 | 25 | 16 | 400 | 282 | 0 | 0 | 0 | 23 | 305 | 0 | 0 | 0 | 70 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 33 | 965 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 45 | 0 | 230 | 0 | 0 | 182 | 32 | 34 | 50 | 34 | 38 | 17 | 19 | 58 | 0 | 0 | 0 | 300 | 320 | 382 | 34 | 30 | 29 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 162 | 0 | 89 | 135 | 13 | 0 | 0 | 12 | 6838 | 877 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 1084.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 172 | 0 | 414 | 0 | 0 | 5.5 | 170 | 63 | 54 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 123 | 220 | 0 | 0 | 1100 | 0 | 5596.79 | 12434.79 | 88.59
20:00 | 0 | 34 | 26 | 110 | 0 | 130 | 0 | 0 | 411 | 0 | 0 | 35 | 17 | 0 | 98 | 16 | 0 | 0 | 0 | 0 | 25 | 16 | 400 | 282 | 0 | 0 | 0 | 23 | 305 | 0 | 0 | 0 | 54 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 36 | 965 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 45 | 0 | 230 | 0 | 0 | 182 | 34 | 34 | 50 | 34 | 39 | 17 | 17 | 56 | 0 | 0 | 0 | 290 | 320 | 382 | 35 | 30 | 29 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 162 | 0 | 89 | 135 | 17 | 0 | 0 | 12 | 6831 | 876 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 1069.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 172 | 0 | 414 | 0 | 0 | 5.5 | 170 | 63 | 54 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 123 | 220 | 0 | 0 | 1050 | 0 | 5462.32 | 12293.32 | 88.58
21:00 | 0 | 34 | 26 | 110 | 0 | 130 | 0 | 0 | 411 | 0 | 0 | 35 | 0 | 0 | 85 | 16 | 0 | 0 | 0 | 0 | 25 | 16 | 400 | 289 | 0 | 0 | 0 | 23 | 305 | 0 | 0 | 0 | 54 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 34 | 965 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 73 | 0 | 230 | 0 | 10 | 187 | 36 | 34 | 50 | 34 | 39 | 18 | 17 | 60 | 0 | 0 | 0 | 300 | 320 | 382 | 35 | 30 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 162 | 0 | 89 | 115 | 17 | 0 | 0 | 12 | 6847 | 923 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 1067.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 172 | 0 | 360 | 0 | 0 | 2.5 | 170 | 63 | 54 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 123 | 220 | 0 | 0 | 1040 | 0 | 5452.88 | 12299.88 | 88.58
22:00 | 0 | 34 | 25 | 110 | 0 | 130 | 0 | 0 | 407 | 0 | 0 | 35 | 5 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 25 | 5 | 400 | 272 | 0 | 0 | 0 | 23 | 305 | 0 | 0 | 0 | 54 | 21.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 34 | 965 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 73 | 0 | 230 | 0 | 10 | 182 | 36 | 34 | 50 | 34 | 38 | 18 | 0 | 58 | 0 | 0 | 0 | 295 | 320 | 382 | 35 | 30 | 29 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 162 | 0 | 89 | 115 | 15 | 0 | 0 | 12 | 6741.8 | 922 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 1064.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 180 | 0 | 360 | 0 | 0 | 2.5 | 124 | 63 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 123 | 220 | 0 | 0 | 1030 | 0 | 5438.48 | 12180.28 | 88.58
23:00 | 0 | 33 | 25 | 110 | 0 | 130 | 0 | 0 | 404 | 0 | 0 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 294 | 0 | 0 | 0 | 23 | 305 | 0 | 0 | 0 | 54 | 22.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 38 | 965 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 903 | 0 | 43 | 0 | 73 | 0 | 230 | 0 | 13 | 183 | 36 | 34 | 50 | 34 | 39 | 18 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 382 | 35 | 30 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 162 | 0 | 65 | 65 | 13 | 0 | 0 | 12 | 6527.5 | 922 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 909.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 0 | 2.5 | 164 | 63 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 123 | 220 | 0 | 0 | 950 | 0 | 5099.2 | 11626.7 | 88.57
Total KWH | 0 | 564480 | 349920 | 2656600 | 0 | 3124688 | 0 | 0 | 9439200 | 0 | 0 | 186120 | 340920 | 0 | 2132928 | 182880 | 0 | 0 | 0 | 0 | 578600 | 59520 | 9348000 | 6932451 | 0 | 0 | 0 | 602600 | 7004758 | 0 | 0 | 224942 | 1401600 | 526800 | 426600 | 0 | 0 | 0 | 0 | 0 | 0 | 81120 | 0 | 0 | 0 | 720960 | 0 | 25032 | 968000 | 0 | 630240 | 21585454.55 | 0 | 0 | 0 | 0 | 0 | 3791439 | 0 | 0 | 0 | 19816362 | 132570 | 888628 | 0 | 2659636 | 0 | 5295000 | 918000 | 472320 | 4406000 | 746928 | 354240 | 1198700 | 469920 | 545160 | 388730 | 166440 | 1251840 | 0 | 461255 | 0 | 7325500 | 7685700 | 9206000 | 620424 | 863000 | 680760 | 102192 | 2461418 | 529752 | 0 | 1645440 | 658176 | 0 | 0 | 2516950 | 0 | 1672800 | 1929600 | 518400 | 15050 | 363940 | 164400 | 153017083.55 | 22101090 | 4561632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637920 | 10181820 | 0 | 21113669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 781350 | 0 | 431248 | 4071000 | 0 | 0 | 0 | 3907809 | 0 | 8910618 | 0 | 37500 | 87858 | 4035000 | 1445236 | 401353 | 254463 | 719001 | 0 | 0 | 41265.84 | 1437840 | 4011 | 17568 | 5869000 | 149930 | 2824000 | 5126760 | 0 | 0 | 20589090.91 | 0 | 119738032.75 | 272755116.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11692.34 | MW | 12:00 Hr. | Energy Generated |  |  | 272.7551 |  | MKWHr.
| Day Peak Demand |  |  | 11692.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12434.79 | MW | 19:30 Hr. | Energy Demand |  |  | 272.7551 |  | MKWHr.
| Evening Peak Demand |  |  | 12434.79 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.6 |  | °C
| Minimum Generation of the Day |  |  | 9172.49 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 982.09 |  | MMCFD
| Maximum Generation of the Day |  |  | 12434.79 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.7509 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6403 | 0 | 5.2184 | 0 | 0 | 0.22494 | 0 | 0 | 46.0836 | Gas | 126.4892 | Gas | 450958735.14
| Chattogram Zone |  |  | 4.4217 | 41.4018 | 0.72096 | 0 | 0.968 | 0.1576 | 0 | 0.08112 | 47.7512 | Coal | 83.522 | Coal | 594383588.6913
| Cumilla Zone |  |  | 16.9739 | 0 | 1.5358 | 0 | 0 | 0.46126 | 1.2518 | 0 | 20.2228 | HFO | 12.3798 | HFO | 205883273.03
| Mymensingh Zone |  |  | 0.5184 | 0 | 3.7668 | 0 | 0 | 0.37899 | 0 | 0 | 4.6642 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2953 | Hydro | 0.968 | Hydro | 96800
| Khulna Zone |  |  | 4.5616 | 10.1818 | 0 | 0 | 0 | 0.63792 | 22.1011 | 0 | 37.4825 | Solar | 4.8484 | Solar | 79318773.5124
| Barishal Zone |  |  | 8.1007 | 26.4581 | 0.017568 | 0 | 0 | 0.004011 | 0 | 0 | 34.5804 | Import | 44.4666 | Import | 236749690.51
| Rajshahi Zone |  |  | 16.9773 | 0 | 0 | 0 | 0 | 1.2501 | 21.1137 | 0 | 39.3411 | Wind | 0.08112 | Wind | 1187596.8
| Rangpur Zone |  |  | 0 | 5.4802 | 1.1204 | 0 | 0 | 1.7336 | 0 | 0 | 8.3342
| Total |  |  | 126.4892 | 83.522 | 12.3798 | 0 | 0.968 | 4.8484 | 44.4666 | 0.08112 | 272.7551
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 450958735.14 |  | Hydro | 96800
|  |  |  | Coal | 594383588.6913 |  | Solar | 79318773.5124
|  |  |  | HFO | 205883273.03 |  | Import | 236749690.51
|  |  |  | HSD | 0 |  | Wind | 1187596.8
[5 empty] | Total: | 156,85,78,457 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1011 | Peak Hr Flow | 877.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10542290.991 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.1137 | Peak Hr Flow | 1084.29 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 664 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2518 | Peak Hr Flow | 58.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 848 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.4666 | Peak Hr Flow | 2019.29 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4525
|  |  |  | Chattogram |  | 0 |  | 1267
|  |  |  | Cumilla |  | 0 |  | 1082
|  |  |  | Mymensingh |  | 0 |  | 991
|  |  |  | Sylhet |  | 0 |  | 400
|  |  |  | Khulna |  | 0 |  | 1339
|  |  |  | Barishal |  | 0 |  | 348
|  |  |  | Rajshahi |  | 0 |  | 1209
|  |  |  | Rangpur |  | 0 |  | 757
|  |  |  | Total |  | 0 |  | 11918
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Khulna 330 MW CCPP ST |  |  | 110
|  | 6 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 902 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1391.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:16 | 17:08 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
Maintenance Work.
| 08:18 | 16:58 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Bay Extension
| 08:51 |  | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to Oil centrefuging of Trafo-1
| 08:52 |  | Sylhet (South) S/S Trafo-1 HT Scheduled S/D Due to Oil centrefuging of Trafo-1
|  | 08:56 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT is restored.
|  | 08:57 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT is restored.
| 09:01 | 15:46 | Kalurghat 132/33kV S/S TRFO-01(506T) HT Scheduled S/D Due to Annual Maintenance.
| 09:05 | 15:40 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance Work.
| 09:06 | 10:44 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to Hot spot maintenance | [7 empty] | 5.0MW load
|  |  | work | [7 empty] | interrup.
| 09:07 | 10:43 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to Hot spot maintenance | [7 empty] | 5.0MW load
|  |  | work | [7 empty] | interrup.
| 09:43 |  | Tongi 230/132/33kV S/S 230 kV Bus-2 Scheduled S/D
| 10:10 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to As per NLDC's
instruction.
| 10:58 | 12:42 | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to High temperature maintenance at
LT bushing (Y phase).
| 10:58 | 12:42 | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to High temperature maintenance at
LT bushing (Y phase).
| 11:26 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 11:26 |  | Ashuganj (S) CCPP GT was synch.
| 11:26 |  | Ashuganj South 360MW GT was sync.
| 11:42 | 13:13 | Ghorashal 230kV S/S Ghorashal GIS- AIS Ckt-3 Scheduled S/D Due to Due to
Telecommunication works in AIS Ckt-3.
| 11:54 |  | Adani - Rohanpur 400 kv line-2 was switched on.
| 12:00 |  | Day Peak Gen. 11692 MW
| 14:40 | 17:06 | Keranigonj 230/132/33kV S/S TR-2 LT Scheduled S/D Due to Maintenance at high junction
temperature point.
| 14:41 | 17:06 | Keranigonj 230/132/33kV S/S TR-2 HT Scheduled S/D Due to Maintenance at high junction
temperature point.
|  | 15:00 | Kishoreganj-Mymensingh 132kV Ckt-2 is restored.
| 15:52 | 17:09 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance Work.
| 17:29 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 00:18 | 02:18 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Forced S/D Due to red hot
maintenance
| 00:24 | 02:17 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Forced S/D Due to red hot
maintenance
| 02:19 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Barishal
132/33kV end Due to Order by ALDC
| 06:00 |  | Minimum generation is 9120 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 130 | 3124688 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2656600 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 412 | 9439200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9348000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 282 | 6932451 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 305 | 7004758 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 186120 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 182880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 526800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 426600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 578600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 23 | 602600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 26 | 349920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 85 | 2132928 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 564480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 59520 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 224942 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 340920 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1401600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2023 | 46083607
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132570 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 968000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3791439 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 720960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 33 | 630240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25032 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 19816362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 81120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 965 | 21585454.55 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 2269 | 47751177.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4406000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 230 | 5295000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 918000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 32 | 746928 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 472320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 2659636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 888628 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1198700 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 469920 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1251840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 388730 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 19 | 166440 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 545160 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 354240 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 461255 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 782 | 20222797
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 13 | 518400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 135 | 1929600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1672800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 363940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 164400 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 249 | 4664190
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 863000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 680760 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2461418 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 34 | 620424 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 102192 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 658176 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1645440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 162 | 2516950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 529752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7325500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 382 | 9206000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7685700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1515 | 34295312
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 22101090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 205 | 4561632 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 637920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 510 | 10181820 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1592 | 37482462
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 17568 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 149930 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 123 | 2824000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 20589090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5126760 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5869000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4011 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1757 | 34580359.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 4071000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 172 | 3907809 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8910618 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 87858 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Fuel shortage as BPDB payment not done in time
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 37500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1084.29 | 21113669 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 431248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 781350 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1853.79 | 39341052
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 63 | 1445236 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4035000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 719001 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41265.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 54 | 401353 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 254463 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1437840 | -
Rangpur Area Total |  |  |  |  | 950 | 394 | 8334158.84
Eastern Grid Total |  |  |  |  | 16921.242 | 6838 | 153017083.55
Western Grid Total |  |  |  |  | 11614.5 | 5596.79 | 119738032.75
National Grid Total |  |  |  |  | 28535.742 | 12434.79 | 272755116.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-03-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8264.91 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3653.4 | MW
i) Dhaka area |  |  | 4524.51 |  | MW | i) Khulna area |  |  |  | 1339 | MW
ii) Chattogram area |  |  | 1267.4 |  | MW | ii) Barishal area |  |  |  | 348 | MW
iii) Cumilla area |  |  | 1082 |  | MW | iii) Rajshahi area |  |  |  | 1209.4 | MW
iv) Mymensingh area |  |  | 991 |  | MW | iv) Rangpur area |  |  |  | 757 | MW
v) Sylhet area |  |  | 400 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11918.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 64 | 18:00 | 133 | Payra | 24 | 20:00
2 | AKSML | 28 | 17:00 | 68 | Jamalpur | 112 | 18:00 | 134 | Postogola | 45 | 13:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 120 | 19:00 | 135 | Purbachal | 16 | 21:00
4 | Agargaon | 95 | 14:00 | 70 | Jhenaidah | 102 | 19:00 | 136 | Purbasadipur | 113 | 16:00
5 | Agrabad | 82 | 19:00 | 71 | Joydebpur | 147 | 12:00 | 137 | Rahanpur | 12.2 | 12:00
6 | Amnura | 55 | 18:00 | 72 | Joypurhat | 61 | 10:00 | 138 | Rahim | 31 | 14:00
7 | Ashuganj | 75 | 13:00 | 73 | Juldah | 14 | 12:00 | 139 | Rajbari | 54 | 03:00
8 | BSRM | 209 | 23:00 | 74 | KSRM | 32 | 17:00 | 140 | Rajendrapur | 100 | 13:00
9 | Bagerhat | 71 | 19:00 | 75 | Kabirpur | 250 | 12:00 | 141 | Rajshahi | 89 | 04:00
10 | Bajitpur | 37 | 20:00 | 76 | Kachua | 60 | 18:30 | 142 | Rajshahi-230 | 63 | 18:00
11 | Bakulia | 85 | 19:00 | 77 | Kallyanpur | 90 | 19:30 | 143 | Ramganj | 92 | 19:00
12 | Banani | 23.4 | 14:00 | 78 | Kalurghat | 40 | 11:00 | 144 | Rampur | 36 | 00:00
13 | Bangabhaban | 12 | 10:00 | 79 | Kamrangirchar | 64 | 16:00 | 145 | Rangamati | 14 | 18:30
14 | Barapukuria | 59 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 125 | 18:00
15 | Barguna | 16 | 18:30 | 81 | Kazla | 94 | 15:00 | 147 | Ruppur | 5.8 | 12:00
16 | Barishal | 90 | 19:00 | 82 | Keranigonj | 67 | 14:00 | 148 | SSM | 14 | 07:00
17 | Barishal-230 | 72 | 19:00 | 83 | Khagrachori | 26 | 18:00 | 149 | Saidpur | 107 | 17:00
18 | Baroaulia | 62 | 10:00 | 84 | Khosba | 27 | 21:00 | 150 | Satkhira | 108 | 19:00
19 | Baroirhat | 45 | 19:00 | 85 | Khulna | 75 | 19:00 | 151 | Satmasjid | 84 | 13:00
20 | Bashundhara | 150 | 14:00 | 86 | Khulshi | 156 | 14:00 | 152 | Savar | 190 | 12:00
21 | BashundharaCement | 8 | 00:00 | 87 | Kishoreganj | 110 | 19:00 | 153 | SevenRings | 18.13 | 02:00
22 | Beanibazar | 44 | 18:30 | 88 | Kodda | 276 | 16:00 | 154 | ShahCement | 38 | 23:00
23 | Benapole | 54 | 13:00 | 89 | Kulaura | 32 | 18:00 | 155 | Shahjadpur | 73 | 11:00
24 | Bhaluka | 124 | 10:00 | 90 | Kurigram | 58 | 18:00 | 156 | Shahjibazar | 96 | 22:00
25 | Bhandaria | 40 | 21:00 | 91 | Kushtia | 110 | 03:00 | 157 | Shahmirpur | 45 | 08:00
26 | Bhangura | 36 | 14:00 | 92 | Lalbag | 73 | 16:00 | 158 | Shariatpur | 59 | 21:00
27 | Bheramara(GK) | 43 | 19:00 | 93 | Lalmonirhat | 48 | 18:00 | 159 | Sherpur | 130 | 10:00
28 | Bhulta | 243 | 23:00 | 94 | MI_Cement | 16.7 | 12:00 | 160 | Shikalbaha | 26 | 01:00
29 | Bog-Sherpur | 72 | 10:00 | 95 | Madanganj | 36 | 20:00 | 161 | Shitalakhya | 73.7 | 15:00
30 | Bogura | 128 | 03:00 | 96 | Madaripur | 79 | 21:00 | 162 | Sholosohor | 37 | 14:00
31 | Borhanuddin | 62 | 21:00 | 97 | Madartek | 72.88 | 21:00 | 163 | Shyampur | 158 | 11:00
32 | Brahmanbaria | 96 | 00:00 | 98 | Madunaghat | 41 | 21:00 | 164 | Siddhirganj | 116 | 11:00
33 | Cantonment | 112 | 14:00 | 99 | Magura | 50 | 19:00 | 165 | Sirajganj | 94 | 17:00
34 | Chandpur | 50 | 22:00 | 100 | Mahasthangarh | 62 | 09:00 | 166 | Sonargaon | 93 | 12:00
35 | Chandraghona | 29 | 18:00 | 101 | Manikganj | 117 | 19:00 | 167 | Sreemongol | 53 | 18:00
36 | Chapai | 60 | 04:00 | 102 | Maniknagar | 60 | 13:00 | 168 | Sreepur | 87 | 16:00
37 | Charsaidpur | 40 | 07:00 | 103 | Matarbari | 41 | 18:30 | 169 | Srinagar | 33.2 | 20:00
38 | Chauddagram | 56 | 13:00 | 104 | Matuail | 58 | 12:00 | 170 | Sunamganj | 40 | 18:00
39 | Chhatak | 22 | 20:00 | 105 | Millgate | 71 | 09:00 | 171 | Sylhet | 24 | 14:00
40 | Chowmuhani | 167 | 18:00 | 106 | Mirpur | 98 | 21:00 | 172 | Sylhet-132 | 92 | 14:00
41 | Chuadanga | 77 | 19:00 | 107 | Mirsorai | 9 | 12:00 | 173 | TK | 25.4 | 19:00
42 | Coxsbazar | 113 | 19:00 | 108 | Mirzapur | 43 | 04:00 | 174 | Tangail | 152 | 07:00
43 | Cumilla(N) | 129 | 21:00 | 109 | Mithapukur | 54 | 17:00 | 175 | Thakurgaon | 81 | 19:00
44 | Cumilla(S) | 140 | 14:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 114 | 13:00
45 | Daudkandi | 118 | 19:00 | 111 | Mogbazar | 121.4 | 15:00 | 177 | Ullahpara | 31 | 09:00
46 | Dhaka | 42 | 11:00 | 112 | Mongla | 42 | 12:00 | 178 | Ullon | 39 | 19:30
47 | Dhamrai | 106 | 09:00 | 113 | Motijheel | 31 | 13:00 | 179 | Uttara | 72 | 15:00
48 | Dhanmondi | 114.2 | 13:00 | 114 | Muktagacha | 29 | 18:00 | 180 | UttaraNew | 39 | 22:00
49 | Dohazari | 85 | 18:30 | 115 | Munshiganj | 76 | 14:00 | 181 | Zigatola | 62 | 19:00
50 | Faridpur | 121 | 21:00 | 116 | Muradnagar | 20 | 19:00
51 | Fatullah | 86 | 16:00 | 117 | Mymensingh | 190 | 18:00
52 | Fenchuganj | 24 | 18:00 | 118 | Naogaon | 111 | 18:00
53 | Feni | 89 | 18:30 | 119 | Narail | 45 | 19:00
54 | GPH | 16 | 04:00 | 120 | Narinda | 60.5 | 14:00
55 | Ghatail | 64 | 04:00 | 121 | Narshingdi | 152 | 20:00
56 | Ghorashal | 14 | 12:00 | 122 | Natore | 124 | 18:00
57 | Ghorashal-230 | 71 | 19:30 | 123 | Nawabganj | 34.2 | 00:00
58 | Goalpara | 24 | 00:00 | 124 | Netrakona | 130 | 21:00
59 | Gollamari | 66 | 19:00 | 125 | New | 78 | 14:00
60 | Gopalganj | 83 | 20:00 | 126 | Niamatpur | 95 | 10:00
61 | Gulshan | 94 | 12:00 | 127 | Noapara | 39 | 19:00
62 | Halishahar | 60 | 09:00 | 128 | PHP | 9 | 09:00
63 | HaripurSBU | 165 | 11:00 | 129 | Pabna | 91 | 18:00
64 | Hasnabad | 80 | 21:00 | 130 | Palashbari | 100 | 18:00
65 | Hathazari | 66 | 20:00 | 131 | Panchagarh | 46 | 18:00
66 | Ishurdi | 57 | 19:00 | 132 | Patuakhali | 56 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11138.92 | 0 |  | 11138.92
1:00 | 10637.49 | 0 |  | 10637.49
2:00 | 10297.83 | 0 |  | 10297.83
3:00 | 10601.69 | 0 |  | 10601.69
4:00 | 11059.58 | 0 |  | 11059.58
5:00 | 9951.16 | 0 |  | 9951.16
6:00 | 9172.49 | 0 |  | 9172.49
7:00 | 9437.3 | 0 |  | 9437.3
8:00 | 10067.45 | 0 |  | 10067.45
9:00 | 10825.03 | 0 |  | 10825.03
10:00 | 11238.94 | 0 |  | 11238.94
11:00 | 11309.45 | 0 |  | 11309.45
12:00 | 11692.34 | 0 |  | 11692.34
13:00 | 11660.05 | 0 |  | 11660.05
14:00 | 11781 | 0 |  | 11781
15:00 | 11651.45 | 0 |  | 11651.45
16:00 | 11903.77 | 0 |  | 11903.77
17:00 | 12102.75 | 0 |  | 12102.75
18:00 | 11737.95 | 0 |  | 11737.95
19:00 | 12391.78 | 0 |  | 12391.78
19:30 | 12434.79 | 0 |  | 12434.79
20:00 | 12293.32 | 0 |  | 12293.32
21:00 | 12299.88 | 0 |  | 12299.88
22:00 | 12180.28 | 0 |  | 12180.28
23:00 | 11626.7 | 0 |  | 11626.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6489 | 4649.92 | 11138.92 | DAILY GENERATION CURVE
00:30 | 6366.5 | 4521.705 | 10888.205
01:00 | 6244 | 4393.49 | 10637.49 | 05-03-2025
01:30 | 6103.5 | 4364.16 | 10467.66
02:00 | 5963 | 4334.83 | 10297.83
02:30 | 6077 | 4372.76 | 10449.76
03:00 | 6191 | 4410.69 | 10601.69
03:30 | 6335 | 4495.635 | 10830.635
04:00 | 6479 | 4580.58 | 11059.58
04:30 | 6137 | 4368.37 | 10505.37
05:00 | 5795 | 4156.16 | 9951.16
05:30 | 5469.5 | 4092.325 | 9561.825
06:00 | 5144 | 4028.49 | 9172.49
06:30 | 5218.305 | 4086.59 | 9304.895
07:00 | 5292.61 | 4144.69 | 9437.3
07:30 | 5511.17 | 4241.205 | 9752.375
08:00 | 5729.73 | 4337.72 | 10067.45
08:30 | 5952.585 | 4493.655 | 10446.24
09:00 | 6175.44 | 4649.59 | 10825.03
09:30 | 6264.435 | 4767.55 | 11031.985
10:00 | 6353.43 | 4885.51 | 11238.94
10:30 | 6319.09 | 4955.105 | 11274.195
11:00 | 6284.75 | 5024.7 | 11309.45
11:30 | 6449.805 | 5051.09 | 11500.895
12:00 | 6614.86 | 5077.48 | 11692.34
12:30 | 6583.08 | 5093.115 | 11676.195
13:00 | 6551.3 | 5108.75 | 11660.05
13:30 | 6541.5 | 5179.025 | 11720.525
14:00 | 6531.7 | 5249.3 | 11781
14:30 | 6476.735 | 5239.49 | 11716.225
15:00 | 6421.77 | 5229.68 | 11651.45
15:30 | 6525.66 | 5251.95 | 11777.61
16:00 | 6629.55 | 5274.22 | 11903.77
16:30 | 6668.7 | 5334.56 | 12003.26
17:00 | 6707.85 | 5394.9 | 12102.75
17:30 | 6602.455 | 5317.895 | 11920.35
18:00 | 6497.06 | 5240.89 | 11737.95
18:30 | 6720.03 | 5344.835 | 12064.865
19:00 | 6943 | 5448.78 | 12391.78
19:30 | 6838 | 5596.79 | 12434.79
20:00 | 6831 | 5462.32 | 12293.32
20:30 | 6839 | 5457.6 | 12296.6 |  | Executive Engineer
21:00 | 6847 | 5452.88 | 12299.88 |  | Network Operation Division
21:30 | 6794.4 | 5445.68 | 12240.08
22:00 | 6741.8 | 5438.48 | 12180.28
22:30 | 6634.65 | 5268.84 | 11903.49
23:00 | 6527.5 | 5099.2 | 11626.7

## En-Curve
QF-LDC-12
Date | 05-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3422 | 1915.5 | 923 | 0 | 50 | 819.42 | 40 | 3414 | 0 | 185 | 364 | 0 | 0 | 6 | 0 | DAILY ENERGY CURVE
00:30 | 3432 | 1883.5 | 923.5 | 0 | 49 | 819.705 | 40 | 3244 | 0 | 150 | 341.5 | 0 | 0 | 5 | 0 | 05-03-2025
01:00 | 3442 | 1851.5 | 924 | 0 | 48 | 819.99 | 40 | 3074 | 0 | 115 | 319 | 0 | 0 | 4 | 0
01:30 | 3372.5 | 1798 | 923.5 | 0 | 47 | 819.66 | 40 | 3025 | 0 | 115 | 325 | 0 | 0 | 2 | 0 | Energy Generated | 272.7551 |  | MKWHr
02:00 | 3303 | 1744.5 | 923 | 0 | 46 | 819.33 | 40 | 2976 | 0 | 115 | 331 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3299.5 | 1827 | 923.5 | 0 | 45 | 822.26 | 40 | 3037.5 | 0 | 119 | 336 | 0 | 0 | 0 | 0 | Total Energy Requirement | 272.7551 |  | MKWHr
03:00 | 3296 | 1909.5 | 924 | 0 | 44 | 825.19 | 40 | 3099 | 0 | 123 | 341 | 0 | 0 | 0 | 0
03:30 | 3347 | 1845.5 | 923.5 | 0 | 45 | 822.635 | 40 | 3267 | 0 | 144.5 | 395.5 | 0 | 0 | 0 | 0
04:00 | 3398 | 1781.5 | 923 | 0 | 46 | 820.08 | 40 | 3435 | 0 | 166 | 450 | 0 | 0 | 0 | 0
04:30 | 3389 | 1614 | 923.5 | 0 | 45 | 821.37 | 40 | 3182.5 | 0 | 132 | 358 | 0 | 0 | 0 | 0
05:00 | 3380 | 1446.5 | 924 | 0 | 44 | 822.66 | 40 | 2930 | 0 | 98 | 266 | 0 | 0 | 0 | 0
05:30 | 3209 | 1421.5 | 923.5 | 0 | 42 | 821.325 | 40 | 2829 | 0 | 65 | 210.5 | 0 | 0 | 0 | 0
06:00 | 3038 | 1396.5 | 923 | 0 | 40 | 819.99 | 40 | 2728 | 0 | 32 | 155 | 0 | 0 | 0 | 0
06:30 | 3133.5 | 1428 | 923.5 | 0 | 43 | 821.38 | 40 | 2709 | 22.515 | 28.5 | 155.5 | 0 | 0 | 0 | 0
07:00 | 3229 | 1459.5 | 924 | 0 | 46 | 822.77 | 40 | 2690 | 45.03 | 25 | 156 | 0 | 0 | 0 | 0
07:30 | 3343 | 1532.5 | 900.5 | 0 | 44 | 822.385 | 40 | 2707.5 | 135.99 | 29 | 197.5 | 0 | 0 | 0 | 0
08:00 | 3457 | 1605.5 | 877 | 0 | 42 | 822 | 40 | 2725 | 226.95 | 33 | 239 | 0 | 0 | 0 | 0
08:30 | 3501 | 1686 | 877.5 | 0 | 46 | 816 | 40 | 2843.5 | 324.74 | 44 | 267.5 | 0 | 0 | 0 | 0
09:00 | 3545 | 1766.5 | 878 | 0 | 50 | 810 | 40 | 2962 | 422.53 | 55 | 296 | 0 | 0 | 0 | 0
09:30 | 3485.5 | 1749.5 | 901 | 0 | 47 | 814.5 | 40 | 3133.5 | 497.485 | 61 | 302.5 | 0 | 0 | 0 | 0
10:00 | 3426 | 1732.5 | 924 | 0 | 44 | 819 | 40 | 3305 | 572.44 | 67 | 309 | 0 | 0 | 0 | 0
10:30 | 3401 | 1736.5 | 923.5 | 0 | 49 | 818 | 40 | 3326.5 | 614.195 | 63 | 302.5 | 0 | 0 | 0 | 0
11:00 | 3376 | 1740.5 | 923 | 0 | 54 | 817 | 40 | 3348 | 655.95 | 59 | 296 | 0 | 0 | 0 | 0
11:30 | 3445.5 | 1833.5 | 923.5 | 0 | 56 | 817 | 40 | 3348.5 | 678.395 | 71.5 | 287 | 0 | 0 | 0 | 0
12:00 | 3515 | 1926.5 | 924 | 0 | 58 | 817 | 40 | 3349 | 700.84 | 84 | 278 | 0 | 0 | 0 | 0
12:30 | 3536.5 | 1925 | 924 | 0 | 57 | 817.5 | 40 | 3339.5 | 693.695 | 85.5 | 251.5 | 0 | 0 | 6 | 0
13:00 | 3558 | 1923.5 | 924 | 0 | 56 | 818 | 40 | 3330 | 686.55 | 87 | 225 | 0 | 0 | 12 | 0
13:30 | 3544.5 | 1898.5 | 924 | 0 | 59 | 820.31 | 40 | 3470.5 | 646.215 | 87 | 222 | 0 | 0 | 8.5 | 0
14:00 | 3531 | 1873.5 | 924 | 0 | 62 | 822.62 | 40 | 3611 | 605.88 | 87 | 219 | 0 | 0 | 5 | 0
14:30 | 3557 | 1771.25 | 923.5 | 0 | 61 | 823.09 | 40 | 3665 | 541.385 | 87 | 235 | 0 | 0 | 12 | 0
15:00 | 3583 | 1669 | 923 | 0 | 60 | 823.56 | 40 | 3719 | 476.89 | 87 | 251 | 0 | 0 | 19 | 0
15:30 | 3626 | 1655.25 | 923.5 | 0 | 58 | 822.08 | 40 | 3818.5 | 385.78 | 95.5 | 337.5 | 0 | 0 | 15.5 | 0
16:00 | 3669 | 1641.5 | 924 | 0 | 56 | 820.6 | 40 | 3918 | 294.67 | 104 | 424 | 0 | 0 | 12 | 0
16:30 | 3679.5 | 1621.25 | 923.5 | 0 | 55 | 845.385 | 40 | 3996.5 | 199.125 | 132 | 497.5 | 0 | 0 | 13.5 | 0
17:00 | 3690 | 1601 | 923 | 0 | 54 | 870.17 | 40 | 4075 | 103.58 | 160 | 571 | 0 | 0 | 15 | 0
17:30 | 3553 | 1587.75 | 923 | 0 | 55 | 918.27 | 40 | 3944.5 | 52.83 | 164 | 671 | 0 | 0 | 11 | 0
18:00 | 3416 | 1574.5 | 923 | 0 | 56 | 966.37 | 40 | 3814 | 2.08 | 168 | 771 | 0 | 0 | 7 | 0
18:30 | 3479 | 1600.5 | 899.5 | 0 | 57 | 1046.825 | 40 | 3907 | 1.04 | 173 | 857.5 | 0 | 0 | 3.5 | 0
19:00 | 3542 | 1626.5 | 876 | 0 | 58 | 1127.28 | 40 | 4000 | 0 | 178 | 944 | 0 | 0 | 0 | 0
19:30 | 3670 | 1699.5 | 877 | 0 | 58 | 1084.29 | 40 | 4115 | 0 | 146 | 745 | 0 | 0 | 0 | 0
20:00 | 3688 | 1693.5 | 876 | 0 | 56 | 1069.82 | 40 | 4017 | 0 | 130 | 723 | 0 | 0 | 0 | 0
20:30 | 3672.5 | 1719 | 899.5 | 0 | 58 | 1068.6 | 40 | 4012 | 0 | 130 | 697 | 0 | 0 | 0 | 0
21:00 | 3657 | 1744.5 | 923 | 0 | 60 | 1067.38 | 40 | 4007 | 0 | 130 | 671 | 0 | 0 | 0 | 0
21:30 | 3673.5 | 1733.9 | 922.5 | 0 | 59 | 1066.18 | 40 | 3979 | 0 | 129.5 | 636.5 | 0 | 0 | 0 | 0
22:00 | 3690 | 1723.3 | 922 | 0 | 58 | 1064.98 | 40 | 3951 | 0 | 129 | 602 | 0 | 0 | 0 | 0
22:30 | 3670.5 | 1738.15 | 922 | 0 | 57 | 987.34 | 40 | 3855.5 | 0 | 120.5 | 512.5 | 0 | 0 | 0 | 0
23:00 | 3651 | 1753 | 922 | 0 | 56 | 909.7 | 40 | 3760 | 0 | 112 | 423 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 06:00 | 377 | 16:00 | Payra | 420 | 06:00 | 408 | 16:00
Ashuganj | 408 | 4:00 | 380 | 16:00 | Rahanpur | 415 | 01:00 | 390 | 10:00
Bhulta | 403 | 05:00 | 380 | 15:00 | Rampal | 412 | 06:00 | 390 | 14:00
Bibiana | 398 | 05:00 | 388 | 15:00
BIPTC | 398 | 05:00 | 390 | 17:00
Bogura | 409 | 01:00 | 383 | 10:00
Gopalganj | 411 | 06:00 | 388 | 16:00
Kaliakoir | 381 | 05:00 | 361 | 16:00
Madunaghat | 402 | 06:00 | 387 | 15:00
Meghnaghat | 399 | 05:00 | 377 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 05:00 | 219 | 14:00 | Keranigonj | 232 | 06:00 | 217 | 15:00
AKSML | 233 | 05:00 | 222 | 14:00 | Khulna(S) | 240 | 06:00 | 224 | 14:00
Aminbazar | 234 | 05:00 | 219 | 14:00 | Madunaghat | 235 | 06:00 | 222 | 02:00
Ashuganj | 233 | 01:00 | 222 | 16:00 | Madunaghat-400 | 235 | 06:00 | 226 | 15:00
Ashuganj-400 | 233 | 01:00 | 222 | 16:00 | Maniknagar | 229 | 05:00 | 216 | 14:00
Baghabari | 237 | 01:00 | 227 | 10:00 | Meghnaghat | 237 | 05:00 | 224 | 15:00
Barapukuria | 225 | 18:30 | 216 | 09:00 | Meghnaghat-400 | 232 | 05:00 | 219 | 16:00
Barapukuria-230 | 225 | 18:30 | 216 | 09:00 | Mirsorai | 231 | 05:00 | 219 | 14:00
Barishal | 241 | 05:00 | 231 | 14:00 | Rajshahi | 236 | 01:00 | 222 | 10:00
Bheramara | 235 | 01:00 | 223 | 10:00 | Rampal | 237 | 06:00 | 222 | 14:00
Bhulta | 231 | 06:00 | 217 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 06:00 | 222 | 14:00 | Rampura | 230 | 05:00 | 216 | 14:00
BIPTC | 237 | 01:00 | 223 | 14:00 | Shikalbaha | 233 | 05:00 | 222 | 12:00
Bogura | 236 | 00:00 | 223 | 09:00 | Shyampur | 246 | 09:00 | 217 | 15:00
Bogura-400 | 236 | 01:00 | 222 | 10:00 | Siddhirganj | 232 | 04:00 | 219 | 16:00
Borhanuddin | 244 | 06:00 | 237 | 16:00 | Sirajgonj | 242 | 05:00 | 234 | 10:00
BSRM | 231 | 05:00 | 219 | 14:00 | Sreepur | 235 | 00:00 | 224 | 12:00
Cumilla(N) | 227 | 02:00 | 216 | 14:00 | Tongi | 228 | 04:00 | 213 | 15:00
Faridpur | 238 | 06:00 | 226 | 14:00
Fenchuganj | 232 | 19:00 | 227 | 14:00
Ghorashal | 235 | 01:00 | 230 | 00:00
Ghorashal-230 | 231 | 05:00 | 218 | 14:00
Gopalganj | 237 | 06:00 | 224 | 15:00
GPH | 233 | 05:00 | 222 | 14:00
Haripur | 230 | 05:00 | 216 | 14:00
Hasnabad | 229 | 01:00 | 218 | 14:00
Hathazari | 236 | 06:00 | 226 | 13:00
Ishurdi | 237 | 01:00 | 226 | 10:00
Jhenaidah | 236 | 05:00 | 220 | 14:00
Kaliakoir | 232 | 06:00 | 217 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 124 | 14:00 | Madunaghat | 134 | 03:00 | 120 | 02:00
Agargaon | 140 | 05:00 | 130 | 15:00 | Magura | 139 | 05:00 | 126 | 13:00
Agrabad | 133 | 04:00 | 126 | 15:00 | Mahasthangarh | 132 | 01:00 | 122 | 10:00
AKS | 131 | 05:00 | 125 | 11:00 | Manikganj | 133 | 04:00 | 121 | 15:00
Aminbazar | 137 | 05:00 | 126 | 14:00 | Maniknagar | 130 | 05:00 | 121 | 14:00
Amnura | 136 | 05:00 | 123 | 08:00 | Matarbari | 125 | 09:00 | 116 | 20:00
Ashuganj | 136 | 04:00 | 130 | 16:00 | Matuail | 134 | 05:00 | 126 | 12:00
Bagerhat | 137 | 06:00 | 125 | 12:00 | Millgate | 134 | 04:00 | 122 | 15:00
Bajitpur | 134 | 03:00 | 125 | 15:00 | Mirpur | 136 | 06:00 | 124 | 15:00
Bakulia | 134 | 04:00 | 128 | 12:00 | Mirzapur | 133 | 05:00 | 123 | 16:00
Banani | 133 | 02:00 | 124 | 15:00 | Mithapukur | 137 | 18:30 | 123 | 09:00
Bangabhaban | 130 | 01:00 | 121 | 14:00 | MI_Cement | 134 | 04:00 | 125 | 16:00
Barapukuria | 139 | 18:30 | 131 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 05:00 | 132 | 16:00 | Mogbazar | 134 | 05:00 | 125 | 12:00
Barishal | 135 | 06:00 | 127 | 14:00 | Mongla | 139 | 06:00 | 125 | 14:00
Barishal-230 | 136 | 06:00 | 128 | 15:00 | Motijheel | 130 | 05:00 | 121 | 15:00
Baroaulia | 134 | 05:00 | 127 | 14:00 | Muktagacha | 135 | 05:00 | 126 | 15:00
Baroirhat | 127 | 06:00 | 116 | 14:00 | Munshiganj | 134 | 05:00 | 124 | 15:00
Bashundhara | 134 | 05:00 | 120 | 16:00 | Muradnagar | 130 | 06:00 | 120 | 14:00
BashundharaCement | 134 | 05:00 | 124 | 15:00 | Mymensingh | 136 | 05:00 | 111 | 16:00
Beanibazar | 133 | 06:00 | 128 | 15:00 | Naogaon | 130 | 23:00 | 119 | 09:00
Benapole | 138 | 06:00 | 124 | 13:00 | Narail | 140 | 05:00 | 125 | 14:00
Bhaluka | 132 | 00:00 | 120 | 16:00 | Narinda | 130 | 05:00 | 121 | 14:00
Bhandaria | 131 | 04:00 | 125 | 13:00 | Narshingdi | 128 | 18:00 | 120 | 15:00
Bhangura | 135 | 01:00 | 128 | 08:00 | Natore | 135 | 01:00 | 127 | 10:00
Bheramara | 137 | 01:00 | 130 | 10:00 | Nawabganj | 142 | 05:00 | 127 | 14:00
Bheramara(GK) | 138 | 00:00 | 131 | 10:00 | Netrakona | 125 | 00:00 | 112 | 16:00
Bhulta | 129 | 05:00 | 120 | 16:00 | New | 134 | 04:00 | 123 | 15:00
Bog-Sherpur | 132 | 00:00 | 123 | 10:00 | Niamatpur | 134 | 04:00 | 127 | 10:00
Bogura | 134 | 23:00 | 125 | 09:00 | Noapara | 139 | 04:00 | 126 | 14:00
Bogura-230 | 134 | 00:00 | 125 | 10:00 | Pabna | 137 | 01:00 | 129 | 10:00
Brahmanbaria | 130 | 01:00 | 122 | 17:00 | Palashbari | 126 | 05:00 | 112 | 10:00
Cantonment | 140 | 05:00 | 130 | 14:00 | Panchagarh | 136 | 01:00 | 120 | 09:00
Chandpur | 125 | 18:00 | 112 | 14:00 | Patuakhali | 137 | 05:00 | 132 | 14:00
Chandraghona | 135 | 05:00 | 129 | 12:00 | Payra | 137 | 01:00 | 134 | 05:00
Chapai | 133 | 02:00 | 125 | 09:00 | PHP | 126 | 06:00 | 114 | 14:00
Charsaidpur | 134 | 05:00 | 125 | 15:00 | Postogola | 136 | 03:00 | 127 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 128 | 05:00 | 117 | 12:00 | Purbachal | 134 | 03:00 | 123 | 14:00
Chhatak | 131 | 05:00 | 128 | 11:00 | Purbasadipur | 133 | 18:00 | 120 | 10:00
Chowmuhani | 123 | 06:00 | 110 | 14:00 | Rahanpur | 136 | 00:00 | 128 | 10:00
Chuadanga | 137 | 05:00 | 123 | 14:00 | Rahanpur-400 | 137 | 01:00 | 128 | 09:00
Coxsbazar | 126 | 07:00 | 116 | 13:00 | Rahim | 132 | 07:00 | 126 | 12:00
Cumilla(N) | 130 | 02:00 | 122 | 14:00 | Rajbari | 133 | 05:00 | 124 | 15:00
Cumilla(S) | 133 | 01:00 | 120 | 14:00 | Rajendrapur | 137 | 18:30 | 126 | 13:00
Daudkandi | 129 | 06:00 | 119 | 14:00 | Rajshahi | 136 | 01:00 | 128 | 10:00
Dhaka | 134 | 04:00 | 124 | 14:00 | Rajshahi-230 | 137 | 02:00 | 120 | 10:00
Dhamrai | 133 | 05:00 | 122 | 15:00 | Ramganj | 122 | 19:00 | 108 | 13:00
Dhanmondi | 135 | 05:00 | 124 | 15:00 | Rampur | 134 | 05:00 | 126 | 11:00
Dohazari | 131 | 06:00 | 124 | 14:00 | Rampura | 134 | 04:00 | 123 | 19:00
Faridpur | 133 | 03:00 | 127 | 15:00 | Rangamati | 134 | 05:00 | 128 | 12:00
Fatullah | 135 | 05:00 | 126 | 15:00 | Rangpur | 134 | 18:30 | 123 | 09:00
Fenchuganj | 135 | 05:00 | 131 | 17:00 | Ruppur | 138 | 01:00 | 131 | 10:00
Feni | 125 | 05:00 | 114 | 16:00 | Saidpur | 133 | 04:00 | 123 | 09:00
Ghatail | 132 | 04:00 | 121 | 15:00 | Satkhira | 137 | 05:00 | 123 | 17:00
Ghorashal | 138 | 01:00 | 130 | 14:00 | Satmasjid | 139 | 04:00 | 130 | 14:00
Goalpara | 139 | 06:00 | 126 | 14:00 | Savar | 135 | 05:00 | 122 | 15:00
Gollamari | 139 | 05:00 | 128 | 14:00 | SevenRings | 140 | 18:30 | 131 | 14:00
Gopalganj | 138 | 05:00 | 129 | 14:00 | ShahCement | 134 | 05:00 | 125 | 15:00
Gopalganj-400 | 140 | 06:00 | 132 | 14:00 | Shahjadpur | 138 | 01:00 | 131 | 11:00
Gulshan | 134 | 06:00 | 124 | 14:00 | Shahjibazar | 133 | 04:00 | 126 | 18:00
Halishahar | 132 | 21:00 | 127 | 12:00 | Shahmirpur | 133 | 02:00 | 128 | 11:00
Haripur | 134 | 04:00 | 127 | 11:00 | Shariatpur | 138 | 06:00 | 130 | 14:00
HaripurSBU | 137 | 18:30 | 127 | 14:00 | Sherpur | 139 | 18:00 | 126 | 03:00
Hasnabad | 136 | 04:00 | 127 | 16:00 | Shikalbaha | 123 | 06:00 | 118 | 13:00
Hathazari | 136 | 05:00 | 129 | 15:00 | Shikalbaha-230 | 136 | 05:00 | 129 | 14:00
Ishurdi | 139 | 05:00 | 132 | 10:00 | Shitalakhya | 134 | 04:00 | 125 | 16:00
Jaldhaka | 131 | 06:00 | 120 | 09:00 | Sholosohor | 134 | 05:00 | 128 | 14:00
Jamalpur | 139 | 18:00 | 126 | 08:00 | Shyampur | 135 | 06:00 | 127 | 12:00
Jashore | 138 | 06:00 | 125 | 14:00 | Shyampur-230 | 135 | 05:00 | 126 | 15:00
Jhenaidah | 138 | 02:00 | 122 | 14:00 | Siddhirganj | 134 | 02:00 | 126 | 12:00
Jhenaidah-230 | 139 | 05:00 | 128 | 13:00 | Sirajganj | 133 | 00:00 | 124 | 10:00
Joydebpur | 139 | 18:30 | 127 | 12:00 | Sonargaon | 128 | 00:00 | 122 | 13:00
Joypurhat | 128 | 01:00 | 115 | 10:00 | Sreemongol | 132 | 01:00 | 127 | 18:00
Juldah | 134 | 05:00 | 127 | 14:00 | Sreepur | 133 | 00:00 | 124 | 12:00
Kabirpur | 136 | 18:00 | 119 | 15:00 | Srinagar | 142 | 04:00 | 127 | 14:00
Kachua | 126 | 19:00 | 114 | 14:00 | SSM | 139 | 06:00 | 130 | 14:00
Kaliakoir | 138 | 04:00 | 124 | 15:00 | Sunamganj | 131 | 02:00 | 127 | 15:00
Kallyanpur | 136 | 03:00 | 127 | 14:00 | Sylhet | 133 | 01:00 | 128 | 14:00
Kalurghat | 135 | 05:00 | 128 | 13:00 | Sylhet-132 | 132 | 03:00 | 130 | 13:00
Kamrangirchar | 143 | 03:00 | 125 | 15:00 | Tangail | 130 | 03:00 | 122 | 15:00
Kaptai | 135 | 4:00 | 124 | 12:00 | Thakurgaon | 135 | 18:30 | 118 | 09:00
Kazla | 130 | 05:00 | 120 | 15:00 | TK | 134 | 04:00 | 128 | 14:00
Keranigonj | 142 | 04:00 | 127 | 16:00 | Tongi | 136 | 04:00 | 124 | 15:00
Khagrachori | 133 | 05:00 | 126 | 14:00 | Ullahpara | 135 | 00:00 | 127 | 10:00
Khosba | 130 | 06:00 | 120 | 14:00 | Ullon | 134 | 06:00 | 124 | 14:00
Khulna | 137 | 02:00 | 126 | 13:00 | Uttara | 137 | 05:00 | 124 | 15:00
Khulna(S) | 140 | 06:00 | 128 | 16:00 | UttaraNew | 133 | 04:00 | 121 | 15:00
Khulshi | 132 | 06:00 | 125 | 14:00 | Zigatola | 143 | 06:00 | 127 | 15:00
Kishoreganj | 130 | 06:00 | 118 | 16:00
Kodda | 137 | 18:30 | 121 | 15:00
KSRM | 134 | 05:00 | 126 | 13:00
Kulaura | 134 | 02:00 | 131 | 15:00
Kurigram | 132 | 01:00 | 121 | 09:00
Kushtia | 138 | 05:00 | 128 | 14:00
Lalbag | 142 | 05:00 | 127 | 14:00
Lalmonirhat | 132 | 18:30 | 120 | 09:00
Madanganj | 134 | 05:00 | 124 | 15:00
Madaripur | 136 | 07:00 | 132 | 14:00
Madartek | 133 | 03:00 | 123 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division