## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-03-2025 | during | 07-03-2025 | during | 07-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 130 | 130 | 230 | 230 | 130 | 130 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 260 | 260 | 110 | 110 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 323 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 309 | 281 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 289 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 23 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 7 | 25 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 122 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 100 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1878 | 1885 | 5274.5 | 5334.5 | 3343.29 | 3403.29
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 156 | 156 | 134 | 134 | 134 | 134 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 20 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 9 | 26 | 7 | 32 | 7 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.86 | 0 | 3.86 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 609 | 1003 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 2 | 9 | 2 | 9 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 967 | 964 | 965 | 965 | 980 | 980 | -
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1807 | 2209 | 3757.72 | 3784.86 | 3772.72 | 3799.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 193 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 170 | 210 | 230 | 230 | 230 | 230 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 135 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 31 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 14 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 73 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 58 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 54 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 4 | 38 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 763 | 1056 | 1978.97 | 1908.97 | 1840.03 | 1770.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-03-2025 | during | 07-03-2025 | during | 07-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 9 | 10 | 210 | 210 | 33 | 33 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 136 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 89 | 89 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.41 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 227.41 | 247 | 653.7 | 601.5 | 476.7 | 424.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 28 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 113 | 163 | 163 | 113 | 113 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 31 | 34 | 40 | 40 | 36 | 36 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 162 | 162 | 162 | 164 | 164 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 23 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 335 | 385 | 385 | 385 | 385 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1508 | 1490 | 1637 | 1637 | 1551 | 1551
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 921 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 298 | 234 | 410 | 410 | 305 | 305 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96.49 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 429 | 531 | 1234.2 | 1234.2 | 610 | 610 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1744.49 | 1645 | 3600.2 | 3512.2 | 2305.02 | 2217.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 123 | 123 | 127 | 127 | 100 | 100 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 740 | 850 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 286 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1395.58 | 1486 | 2169.12 | 2168.12 | 2142.12 | 2141.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 189 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 164 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 323 | 300 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.68 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 813.87 | 1179 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.21 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 114 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1705.26 | 1834.5 | 3107.53 | 2940.78 | 2845.75 | 2679
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 62 | 62 | 62 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 164 | 170 | 170 | 175 | 175 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.1 | 0 | 6.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 54 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 189 | 0 | 188 | 0 | 188 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 458.4 | 393 | 718.1 | 494 | 692.12 | 468.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 11487.14 | 12245.5 | 22896.84 | 22381.93 | 18968.75 | 18453.84
Forecast Scenario (07-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11460 |  | 0 |  | 11460
|  |  |  | 1:00 | 10990 |  | 0 |  | 10990
|  |  |  | 2:00 | 10750 |  | 0 |  | 10750
|  |  |  | 3:00 | 10900 |  | 0 |  | 10900
|  |  |  | 4:00 | 10800 |  | 0 |  | 10800
|  |  |  | 5:00 | 10960 |  | 0 |  | 10960
|  |  |  | 6:00 | 9013 |  | 0 |  | 9013
|  |  |  | 7:00 | 9110 |  | 0 |  | 9110
|  |  |  | 8:00 | 9245 |  | 0 |  | 9245
|  |  |  | 9:00 | 9875 |  | 0 |  | 9875
|  |  |  | 10:00 | 10030 |  | 0 |  | 10030
|  |  |  | 11:00 | 10265 |  | 0 |  | 10265
|  |  |  | 12:00 | 10750 |  | 0 |  | 10750
|  |  |  | 13:00 | 11010 |  | 0 |  | 11010
|  |  |  | 14:00 | 10520 |  | 0 |  | 10520
|  |  |  | 15:00 | 10720 |  | 0 |  | 10720
|  |  |  | 16:00 | 10625 |  | 0 |  | 10625
|  |  |  | 17:00 | 10775 |  | 0 |  | 10775
|  |  |  | 18:00 | 11200 |  | 0 |  | 11200
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 12000 |  | 0 |  | 12000
|  |  |  | 19:30 | 12000 |  | 0 |  | 12000
|  |  |  | 20:00 | 11990 |  | 0 |  | 11990
|  |  |  | 21:00 | 11800 |  | 0 |  | 11800
|  |  |  | 22:00 | 11700 |  | 0 |  | 11700
|  |  |  | 23:00 | 11600 |  | 0 |  | 11600
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 10750.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 258.088 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:28 hrs on 07-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-03-2025 | [28 empty] | Date: | 06-03-2025 | [28 empty] | Date: | 06-03-2025 | [28 empty] | Date: | 06-03-2025 | [28 empty] | Date: | 06-03-2025 | [18 empty] | Date: | 06-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 33 | 8 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 282 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 0 | 35 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 31 | 965 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 766 | 0 | 43 | 0 | 73 | 0 | 230 | 0 | 29 | 182 | 36 | 34 | 50 | 34 | 39 | 18 | 0 | 50 | 0 | 0 | 0 | 305 | 320 | 380 | 35 | 30 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 161 | 0 | 49 | 65 | 13 | 0 | 0 | 12 | 6230 | 922 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 915.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 0 | 2.5 | 173 | 63 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 0 | 900 | 0 | 4835.18 | 11065.18 | 88.57
01:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 287 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 0 | 17 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 38 | 966 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 702 | 0 | 43 | 0 | 73 | 0 | 230 | 0 | 29 | 183 | 35 | 16 | 50 | 17 | 32 | 18 | 0 | 50 | 0 | 0 | 0 | 305 | 320 | 380 | 35 | 30 | 30 | 5 | 113 | 24 | 0 | 11 | 30 | 0 | 0 | 162 | 0 | 48 | 45 | 13 | 0 | 0 | 12 | 6006 | 922 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 808.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 0 | 2.5 | 166 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 7 | 100 | 180 | 0 | 0 | 800 | 0 | 4543.86 | 10549.86 | 88.57
02:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 285 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 38 | 964 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 703 | 0 | 43 | 0 | 73 | 0 | 230 | 0 | 29 | 182 | 35 | 0 | 50 | 0 | 29 | 18 | 0 | 48 | 0 | 0 | 0 | 290 | 320 | 381 | 35 | 30 | 30 | 5 | 80 | 24 | 0 | 11 | 30 | 0 | 0 | 161 | 0 | 48 | 45 | 13 | 0 | 0 | 12 | 5856 | 923 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 814.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 320 | 0 | 0 | 2.5 | 168 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 0 | 720 | 0 | 4394.83 | 10250.83 | 88.56
03:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 329 | 0 | 0 | 0 | 20 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 300 | 0 | 0 | 0 | 23 | 280 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 39 | 966 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 102 | 0 | 230 | 0 | 29 | 195 | 35 | 0 | 40 | 0 | 29 | 18 | 0 | 44 | 0 | 0 | 0 | 310 | 320 | 325 | 35 | 30 | 30 | 5 | 80 | 24 | 0 | 11 | 30 | 0 | 0 | 161 | 0 | 59 | 60 | 17 | 0 | 0 | 12 | 5948 | 922 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 816.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 170 | 0 | 320 | 0 | 0 | 2.5 | 171 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 740 | 0 | 4500.58 | 10448.58 | 88.56
04:00 | 0 | 25 | 8 | 110 | 0 | 130 | 0 | 0 | 364 | 0 | 0 | 0 | 35 | 0 | 68 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 248 | 0 | 0 | 0 | 23 | 280 | 0 | 0 | 0 | 35 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 40 | 900 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 877 | 0 | 5 | 0 | 130 | 0 | 230 | 0 | 29 | 181 | 35 | 0 | 50 | 0 | 29 | 18 | 0 | 46 | 0 | 0 | 0 | 295 | 303 | 328 | 35 | 30 | 30 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 161 | 0 | 79 | 105 | 16 | 0 | 0 | 12 | 6289 | 923 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 810.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 186 | 0 | 414 | 0 | 0 | 2.5 | 170 | 63 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 100 | 220 | 0 | 0 | 860 | 0 | 4863.93 | 11152.93 | 88.56
05:00 | 0 | 16 | 8 | 110 | 0 | 130 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 340 | 296 | 0 | 0 | 0 | 23 | 280 | 0 | 0 | 0 | 17 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 40 | 811 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 702 | 0 | 5 | 0 | 73 | 0 | 170 | 0 | 7 | 189 | 35 | 0 | 50 | 0 | 0 | 18 | 0 | 44 | 0 | 0 | 0 | 285 | 320 | 328 | 5 | 30 | 30 | 5 | 80 | 24 | 0 | 10 | 30 | 0 | 0 | 161 | 0 | 55 | 55 | 16 | 0 | 0 | 0 | 5495 | 923 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 816.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 182 | 0 | 300 | 0 | 0 | 2.5 | 168 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 220 | 0 | 0 | 750 | 0 | 4421.54 | 9916.54 | 88.55
06:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 230 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 0 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 752 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 610 | 0 | 5 | 0 | 8 | 0 | 170 | 0 | 6 | 181 | 35 | 0 | 50 | 0 | 0 | 18 | 0 | 40 | 0 | 0 | 0 | 285 | 320 | 328 | 5 | 30 | 30 | 5 | 80 | 24 | 0 | 11 | 30 | 0 | 0 | 161 | 0 | 55 | 55 | 18 | 0 | 0 | 0 | 5001 | 922 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 818.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 250 | 0 | 0 | 2.5 | 169 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 100 | 180 | 0 | 0 | 600 | 0 | 4119.68 | 9120.68 | 88.55
07:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 300 | 323 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 3 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 754 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 605 | 3 | 5 | 0 | 8 | 0 | 170 | 0 | 9 | 211 | 35 | 0 | 50 | 0 | 0 | 18 | 0 | 42 | 0 | 6 | 0 | 305 | 320 | 356 | 5 | 30 | 30 | 5 | 80 | 24 | 0 | 11 | 30 | 0 | 0 | 161 | 0 | 55 | 55 | 18 | 0 | 3.43 | 0 | 5146.43 | 922 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.31 | 380 | 0 | 820.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 4.52 | 140 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0.35 | 2.5 | 170 | 63 | 0 | 2 | 0 | 0 | 0 | 0.3 | 15 | 0.04 | 0 | 150 | 5 | 123 | 180 | 0 | 0 | 600 | 0 | 4232.83 | 9379.26 | 88.55
08:00 | 0 | 16 | 8 | 110 | 0 | 130 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 282 | 0 | 0 | 0 | 24 | 305 | 0 | 0 | 11 | 0 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 10 | 753 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 611 | 8 | 28 | 0 | 73 | 0 | 170 | 0 | 29 | 182 | 35 | 0 | 50 | 0 | 0 | 18 | 0 | 42 | 0 | 21 | 0 | 300 | 320 | 380 | 5 | 30 | 30 | 5 | 80 | 24 | 0 | 86 | 30 | 0 | 0 | 161 | 0 | 87 | 95 | 18 | 1 | 17.3 | 5 | 5621.3 | 875 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.88 | 382 | 0 | 816.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 20.51 | 140 | 0 | 0 | 0 | 141 | 0 | 350 | 0 | 1.7 | 2.5 | 170 | 62 | 0 | 0 | 0 | 0 | 0 | 1.8 | 62 | 0.16 | 0 | 200 | 4 | 123 | 180 | 0 | 0 | 630 | 0 | 4530.18 | 10151.48 | 88.54
09:00 | 0 | 16 | 16 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 27 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 302 | 0 | 0 | 0 | 16 | 300 | 0 | 0 | 20 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 8 | 800 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 612 | 13 | 51 | 0 | 73 | 0 | 170 | 0 | 29 | 187 | 36 | 0 | 50 | 0 | 0 | 18 | 0 | 46 | 0 | 39 | 0 | 300 | 320 | 382 | 5 | 30 | 30 | 5 | 80 | 24 | 0 | 86 | 30 | 0 | 0 | 161 | 0 | 96 | 124 | 18 | 2 | 31.5 | 12 | 5886.5 | 876 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.88 | 427 | 0 | 814.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 38.15 | 152 | 0 | 0 | 0 | 195 | 0 | 394 | 0 | 3.31 | 2.5 | 174 | 62 | 0 | 19 | 0 | 0 | 0 | 3.5 | 112 | 0.32 | 0 | 250 | 4 | 123 | 220 | 0 | 0 | 680 | 0 | 4926.75 | 10813.25 | 88.54
10:00 | 0 | 16 | 16 | 110 | 0 | 130 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 303 | 0 | 0 | 0 | 16 | 300 | 0 | 0 | 27 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 8 | 800 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 608 | 17 | 51 | 0 | 73 | 0 | 170 | 0 | 29 | 186 | 34 | 0 | 50 | 0 | 0 | 12 | 0 | 50 | 0 | 54 | 0 | 305 | 320 | 383 | 32 | 30 | 30 | 5 | 80 | 21 | 0 | 83 | 30 | 0 | 16 | 162 | 0 | 99 | 124 | 11 | 2 | 42.31 | 12 | 6022.31 | 921 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.62 | 429 | 0 | 813.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 51.94 | 181 | 0 | 0 | 0 | 195 | 0 | 312 | 0 | 4.6 | 5.5 | 164 | 62 | 0 | 27 | 0 | 0 | 0 | 5.1 | 152 | 0.47 | 0 | 250 | 4 | 123 | 220 | 0 | 0 | 700 | 0 | 5092.62 | 11114.93 | 88.54
11:00 | 0 | 16 | 16 | 110 | 0 | 130 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 308 | 0 | 0 | 0 | 15 | 300 | 0 | 0 | 31 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 8 | 854 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 605 | 19 | 51 | 0 | 73 | 0 | 170 | 0 | 29 | 192 | 35 | 0 | 50 | 0 | 0 | 18 | 0 | 52 | 0 | 64 | 0 | 300 | 320 | 383 | 34 | 30 | 30 | 5 | 80 | 23 | 0 | 83 | 30 | 0 | 16 | 162 | 0 | 99 | 95 | 11 | 2 | 49.39 | 12 | 6082.89 | 921 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.45 | 437 | 0 | 812.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 61.46 | 185 | 0 | 0 | 0 | 198 | 0 | 319 | 0 | 5.34 | 5.5 | 166 | 62 | 0 | 32 | 0 | 0 | 0 | 6 | 179 | 0.55 | 0 | 280 | 4 | 123 | 220 | 0 | 0 | 700 | 0 | 5218.5 | 11301.39 | 88.53
12:00 | 0 | 0 | 16 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 309 | 0 | 0 | 0 | 7 | 300 | 0 | 0 | 34 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 9 | 967 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 609 | 20 | 51 | 0 | 73 | 0 | 170 | 0 | 29 | 193 | 35 | 0 | 50 | 17 | 4 | 18 | 0 | 56 | 0 | 67 | 0 | 310 | 320 | 385 | 31 | 28 | 30 | 5 | 80 | 23 | 0 | 86 | 30 | 0 | 16 | 164 | 0 | 89 | 65 | 9 | 2 | 50.41 | 12 | 6183.41 | 921 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.49 | 429 | 0 | 813.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 64.21 | 182 | 0 | 0 | 0 | 200 | 0 | 323 | 0 | 5.68 | 2.5 | 167 | 62 | 0 | 34 | 0 | 0 | 0 | 6.4 | 189 | 0.58 | 0 | 307 | 5 | 123 | 220 | 0 | 0 | 740 | 0 | 5303.73 | 11487.14 | 88.53
13:00 | 0 | 0 | 16 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 2 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 279 | 0 | 0 | 0 | 15 | 300 | 0 | 0 | 33 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 18 | 965 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 700 | 19 | 51 | 0 | 73 | 0 | 170 | 0 | 29 | 184 | 32 | 0 | 50 | 61 | 9 | 18 | 17 | 48 | 0 | 68 | 0 | 310 | 320 | 385 | 30 | 28 | 30 | 5 | 80 | 0 | 0 | 86 | 30 | 0 | 16 | 163 | 0 | 79 | 95 | 7 | 2 | 49.7 | 12 | 6320.7 | 920 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.92 | 428 | 0 | 813.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 62.12 | 183 | 0 | 0 | 0 | 220 | 0 | 414 | 0 | 5.47 | 2.5 | 167 | 62 | 0 | 34 | 0 | 0 | 0 | 5.9 | 185 | 0.55 | 0 | 307 | 5 | 123 | 200 | 0 | 0 | 930 | 0 | 5568.39 | 11889.09 | 88.53
14:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 420 | 301 | 0 | 0 | 0 | 15 | 295 | 0 | 0 | 29 | 46 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 8 | 965 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 800 | 18 | 51 | 0 | 128 | 0 | 220 | 0 | 29 | 182 | 35 | 0 | 50 | 68 | 9 | 18 | 23 | 60 | 0 | 32 | 0 | 305 | 320 | 386 | 30 | 28 | 29 | 5 | 80 | 23 | 0 | 86 | 30 | 0 | 16 | 163 | 0 | 55 | 95 | 7 | 2 | 43.72 | 12 | 6534.72 | 921 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1 | 460 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 55.64 | 182 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 4.97 | 2.5 | 170 | 62 | 0 | 29 | 0 | 0 | 0 | 5.5 | 156 | 0.52 | 0 | 307 | 5 | 123 | 220 | 0 | 0 | 980 | 0 | 5574.23 | 12108.95 | 88.52
15:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 420 | 309 | 0 | 0 | 0 | 15 | 295 | 0 | 0 | 23 | 54 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 9 | 965 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 800 | 14 | 51 | 0 | 158 | 0 | 230 | 0 | 29 | 210 | 35 | 0 | 51 | 51 | 16 | 18 | 17 | 58 | 0 | 47 | 0 | 300 | 320 | 389 | 32 | 28 | 29 | 5 | 80 | 16 | 0 | 86 | 30 | 0 | 16 | 163 | 0 | 55 | 95 | 8 | 2 | 33.44 | 12 | 6608.94 | 920 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.57 | 410 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 43.67 | 193 | 0 | 0 | 0 | 182 | 0 | 414 | 0 | 4.01 | 2.5 | 163 | 61 | 0 | 22 | 0 | 0 | 0 | 3.1 | 122 | 0.4 | 0 | 250 | 5 | 123 | 220 | 0 | 0 | 900 | 0 | 5279.25 | 11888.19 | 88.52
16:00 | 0 | 10 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 450 | 310 | 0 | 0 | 0 | 15 | 295 | 0 | 0 | 14 | 54 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 16 | 965 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 852 | 9 | 51 | 0 | 180 | 0 | 230 | 0 | 29 | 202 | 35 | 0 | 51 | 34 | 37 | 18 | 17 | 58 | 0 | 29 | 0 | 320 | 320 | 389 | 32 | 28 | 30 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 16 | 164 | 0 | 55 | 95 | 6 | 1 | 20.12 | 12 | 6744.62 | 920 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.03 | 413 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 28.22 | 201 | 0 | 0 | 0 | 173 | 0 | 414 | 0 | 2.61 | 2.5 | 166 | 63 | 0 | 13 | 7 | 0 | 0 | 2.4 | 71 | 0.25 | 0 | 250 | 5 | 123 | 220 | 0 | 0 | 900 | 0 | 5243.01 | 11987.63 | 88.51
17:00 | 0 | 34 | 8 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 0 | 109 | 32 | 0 | 0 | 0 | 0 | 33 | 0 | 450 | 307 | 0 | 0 | 0 | 15 | 289 | 0 | 0 | 5 | 60 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 9 | 965 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 852 | 3 | 51 | 0 | 190 | 0 | 230 | 0 | 29 | 187 | 35 | 0 | 51 | 17 | 37 | 18 | 34 | 56 | 0 | 9 | 0 | 315 | 320 | 387 | 33 | 28 | 30 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 16 | 162 | 0 | 55 | 95 | 5 | 0 | 6.51 | 12 | 6729.01 | 921 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.55 | 408 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9.93 | 201 | 0 | 0 | 0 | 168 | 0 | 414 | 0 | 0.91 | 2.5 | 165 | 61 | 35 | 5 | 103 | 0 | 0 | 1 | 25 | 0.09 | 0 | 250 | 5 | 123 | 220 | 0 | 0 | 900 | 0 | 5328.98 | 12057.99 | 88.51
18:00 | 0 | 50 | 16 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 32 | 0 | 124 | 62 | 0 | 0 | 0 | 0 | 33 | 0 | 330 | 288 | 0 | 0 | 0 | 10 | 289 | 0 | 0 | 0 | 100 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 965 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 142 | 0 | 225 | 0 | 28 | 187 | 35 | 6 | 50 | 17 | 37 | 18 | 52 | 62 | 0 | 0 | 0 | 320 | 320 | 334 | 5 | 28 | 30 | 5 | 80 | 22 | 0 | 22 | 30 | 0 | 18 | 162 | 0 | 89 | 135 | 5 | 0 | 0 | 12 | 6630 | 920 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.11 | 392 | 0 | 992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0.02 | 2.5 | 167 | 63 | 71 | 0 | 113 | 0 | 0 | 0 | 1 | 0 | 0 | 204 | 6 | 100 | 220 | 0 | 0 | 840 | 0 | 5056.63 | 11686.63 | 88.5
19:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 323 | 0 | 0 | 0 | 35 | 0 | 122 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 281 | 0 | 0 | 0 | 25 | 289 | 0 | 0 | 0 | 100 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 40 | 0 | 26 | 964 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 1003 | 0 | 51 | 0 | 182 | 0 | 210 | 135 | 14 | 182 | 31 | 16 | 50 | 17 | 38 | 18 | 54 | 58 | 0 | 0 | 0 | 305 | 320 | 335 | 34 | 30 | 30 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 18 | 162 | 0 | 89 | 136 | 10 | 0 | 0 | 12 | 6887 | 880 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531 | 0 | 1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 164 | 0 | 300 | 0 | 0 | 2.5 | 164 | 62 | 54 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 7 | 123 | 220 | 0 | 0 | 850 | 0 | 5358.5 | 12245.5 | 88.5
19:30 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 362 | 0 | 0 | 0 | 35 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 312 | 0 | 0 | 0 | 25 | 288 | 0 | 0 | 0 | 90 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 30 | 950 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 960 | 0 | 51 | 0 | 182 | 0 | 205 | 240 | 10 | 140 | 31 | 0 | 50 | 0 | 38 | 18 | 52 | 52 | 0 | 0 | 0 | 325 | 320 | 381 | 34 | 30 | 30 | 5 | 80 | 22 | 0 | 84 | 30 | 0 | 18 | 162 | 0 | 89 | 105 | 13 | 0 | 0 | 12 | 6959 | 869 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 168 | 0 | 310 | 0 | 0 | 2.5 | 163 | 62 | 35 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 7 | 123 | 220 | 0 | 0 | 900 | 0 | 5265.5 | 12224.5
20:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 353 | 0 | 0 | 0 | 35 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 284 | 0 | 0 | 0 | 25 | 288 | 0 | 0 | 0 | 90 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 26 | 954 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 45 | 0 | 170 | 250 | 19 | 144 | 35 | 0 | 50 | 0 | 38 | 18 | 52 | 54 | 0 | 0 | 0 | 295 | 320 | 382 | 34 | 29 | 30 | 5 | 80 | 22 | 0 | 84 | 30 | 0 | 18 | 160 | 0 | 89 | 105 | 13 | 0 | 0 | 12 | 6790 | 868 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 0 | 1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 168 | 0 | 414 | 0 | 0 | 2.5 | 163 | 63 | 35 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 7 | 123 | 220 | 0 | 0 | 900 | 0 | 5378.5 | 12168.5 | 88.49
21:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 314 | 0 | 0 | 0 | 24 | 288 | 0 | 0 | 0 | 90 | 21.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 30 | 954 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 853 | 0 | 51 | 0 | 45 | 0 | 170 | 250 | 10 | 137 | 35 | 0 | 50 | 0 | 38 | 18 | 52 | 54 | 0 | 0 | 0 | 305 | 320 | 383 | 35 | 30 | 30 | 5 | 80 | 22 | 0 | 86 | 30 | 0 | 18 | 162 | 0 | 89 | 105 | 13 | 0 | 0 | 12 | 6745.5 | 916 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 1070.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 168 | 0 | 414 | 0 | 0 | 2.5 | 165 | 63 | 35 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 7 | 123 | 220 | 0 | 0 | 900 | 0 | 5282.21 | 12027.71 | 88.49
22:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 287 | 0 | 0 | 0 | 23 | 295 | 0 | 0 | 0 | 90 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 30 | 921 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 834 | 0 | 51 | 0 | 8 | 0 | 170 | 150 | 10 | 169 | 35 | 0 | 50 | 0 | 38 | 18 | 52 | 60 | 0 | 0 | 0 | 315 | 320 | 382 | 35 | 30 | 30 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 18 | 162 | 0 | 89 | 105 | 11 | 0 | 0 | 12 | 6642.5 | 915 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 1043.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 0 | 2.5 | 167 | 61 | 35 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 7 | 123 | 220 | 0 | 0 | 910 | 0 | 5252.67 | 11895.17 | 88.48
23:00 | 0 | 34 | 25 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 277 | 0 | 0 | 0 | 23 | 295 | 0 | 0 | 0 | 90 | 21.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 34 | 920 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 8 | 0 | 170 | 0 | 10 | 182 | 35 | 0 | 50 | 0 | 38 | 18 | 34 | 58 | 0 | 0 | 0 | 295 | 320 | 382 | 35 | 30 | 30 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 18 | 162 | 0 | 89 | 88 | 11 | 0 | 0 | 9 | 6376.5 | 915 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 964.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 165 | 0 | 414 | 0 | 0 | 2.5 | 163 | 61 | 7 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 7 | 121 | 220 | 0 | 0 | 950 | 0 | 5159.65 | 11536.15 | 88.48
Total KWH | 0 | 564019 | 335520 | 2625800 | 0 | 3120906 | 0 | 0 | 9273600 | 0 | 0 | 0 | 478440 | 0 | 1880640 | 258240 | 0 | 0 | 0 | 0 | 631800 | 0 | 9169000 | 7098385 | 0 | 0 | 0 | 471300 | 6836021 | 0 | 0 | 231618 | 894000 | 487200 | 272520 | 0 | 0 | 0 | 0 | 0 | 0 | 20160 | 0 | 0 | 0 | 369600 | 0 | 27000 | 964000 | 0 | 607200 | 21767272.73 | 0 | 0 | 0 | 0 | 0 | 3716505 | 0 | 0 | 0 | 18136362 | 144450 | 1019348 | 0 | 2007273 | 0 | 4887000 | 802000 | 533760 | 4553000 | 830592 | 70080 | 1115360 | 358560 | 523320 | 403930 | 434340 | 1210560 | 0 | 433445 | 0 | 7364500 | 7689200 | 9251000 | 642456 | 700000 | 690720 | 114240 | 2303345 | 505992 | 0 | 1554240 | 715776 | 0 | 238000 | 4404810 | 0 | 1796400 | 2210400 | 270720 | 16000 | 348780 | 259200 | 150639905.73 | 22106181 | 6351264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657360 | 9985455 | 0 | 21431854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816570 | 0 | 443248 | 4411818 | 0 | 0 | 0 | 4279328 | 0 | 8949090.9 | 0 | 38580 | 68112 | 4069000 | 1475345 | 286243 | 229793 | 726835 | 0 | 0 | 41844.84 | 1269360 | 3966 | 0 | 5673000 | 144578 | 2779000 | 5209680 | 0 | 0 | 20126545.45 | 0 | 121574051.19 | 272213956.92

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11487.14 | MW | 12:00 Hr. | Energy Generated |  |  | 272.214 |  | MKWHr.
| Day Peak Demand |  |  | 11519.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.11 |  | MKWHr.
| Evening Peak Generation |  |  | 12245.5 | MW | 19:00 Hr. | Energy Demand |  |  | 272.324 |  | MKWHr.
| Evening Peak Demand |  |  | 12245.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 9120.68 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 989.5 |  | MMCFD
| Maximum Generation of the Day |  |  | 12245.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.7151 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.9865 | 0 | 4.4109 | 0 | 0 | 0.23162 | 0 | 0 | 44.629 | Gas | 129.1004 | Gas | 461811882.615
| Chattogram Zone |  |  | 4.3237 | 39.9036 | 0.3696 | 0 | 0.964 | 0.17145 | 0 | 0.02016 | 45.7525 | Coal | 81.233 | Coal | 578910353.1239
| Cumilla Zone |  |  | 16.1523 | 0 | 1.3863 | 0 | 0 | 0.43345 | 1.2106 | 0 | 19.1826 | HFO | 11.4458 | HFO | 199228120.83
| Mymensingh Zone |  |  | 0.27072 | 0 | 4.266 | 0 | 0 | 0.36478 | 0 | 0 | 4.9015 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1743 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 6.3513 | 9.9855 | 0 | 0 | 0 | 0.65736 | 22.1062 | 0 | 39.1003 | Solar | 4.702 | Solar | 76531462.2024
| Barishal Zone |  |  | 8.1333 | 25.7995 | 0 | 0 | 0 | 0.003966 | 0 | 0 | 33.9368 | Import | 44.7486 | Import | 238855920.2
| Rajshahi Zone |  |  | 17.7083 | 0 | 0 | 0 | 0 | 1.2984 | 21.4319 | 0 | 40.4386 | Wind | 0.02016 | Wind | 295142.4
| Rangpur Zone |  |  | 0 | 5.5443 | 1.0131 | 0 | 0 | 1.541 | 0 | 0 | 8.0984
| Total |  |  | 129.1004 | 81.233 | 11.4458 | 0 | 0.964 | 4.702 | 44.7486 | 0.02016 | 272.214
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 461811882.615 |  | Hydro | 96400
|  |  |  | Coal | 578910353.1239 |  | Solar | 76531462.2024
|  |  |  | HFO | 199228120.83 |  | Import | 238855920.2
|  |  |  | HSD | 0 |  | Wind | 295142.4
[5 empty] | Total: | 155,57,29,281 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1062 | Peak Hr Flow | 880.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9179972000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.4319 | Peak Hr Flow | 1179.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 706 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2106 | Peak Hr Flow | 58.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 844 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.7486 | Peak Hr Flow | 2117.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4415
|  |  |  | Chattogram |  | 0 |  | 1313
|  |  |  | Cumilla |  | 0 |  | 1082
|  |  |  | Mymensingh |  | 0 |  | 1025
|  |  |  | Sylhet |  | 0 |  | 398
|  |  |  | Khulna |  | 0 |  | 1327
|  |  |  | Barishal |  | 0 |  | 327
|  |  |  | Rajshahi |  | 0 |  | 1166
|  |  |  | Rangpur |  | 0 |  | 776
|  |  |  | Total |  | 0 |  | 11829
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 792 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1281.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:52 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to bus 2 extension
| 10:25 | 10:55 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Tr-3 33kV GCB gas refilling
work.
| 10:25 | 10:55 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to Tr-3 33kV GCB gas refilling
work.
| 10:26 | 10:54 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to Tr-3 33kV GCB gas refilling
work.
| 10:26 | 10:54 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Tr-3 33kV GCB gas refilling
work.
| 12:00 |  | Day Peak Generation: 11483 MW.
| 15:09 |  | BIPTC S/S 10CF15 Tripped showing 87.1 Differential realay relays Due to Tripped by
Capacitor unbalance 60/61 instant L2
| 18:10 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 18:10 |  | Ashuganj South 360MW GT was sync.
| 19:00 |  | Evening Peak Gen. 12245 MW
| 20:25 | 20:39 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Tripped showing K86-1,k86-2 relays Due to | [7 empty] | 9.0MW load
|  |  | 33 kv amirpur feeder fault | [7 empty] | interrup.
| 22:33 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 01:02 | 02:44 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to high temperature at 33kv T-2 bus section | [7 empty] | 75.0MW load
interrup.
| 01:03 | 02:43 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to high temperature at 33kv T-2 bus section | [7 empty] | 75.0MW load
interrup.
| 07:00 | 07:29 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing 50/51 ,.50N/51N relays Due to 33 kv Bus | [7 empty] | 22.0MW load
|  |  | fault | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 8665 MW
| 07:00 | 07:29 | Jaldhaka 132/33kV S/S 416T-2 LT Tripped showing 50/51 ,.50N/51N relays Due to 33 kv Bus | [7 empty] | 22.0MW load
|  |  | fault | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 130 | 3120906 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2625800 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 323 | 9273600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 9169000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 7098385 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 289 | 6836021 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 258240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 487200 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 272520 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 631800 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 471300 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 335520 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 122 | 1880640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 564019 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 231618 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 478440 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 100 | 894000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 1885 | 44629009
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 144450 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 156 | 3716505 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 20 | 369600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 26 | 607200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 27000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1003 | 18136362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 20160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 964 | 21767272.73 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 2209 | 45752549.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4553000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 210 | 4887000 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 135 | 802000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 31 | 830592 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 14 | 533760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 2007273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1019348 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1115360 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 358560 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1210560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 403930 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 54 | 434340 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 523320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 70080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 433445 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1056 | 19182568
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 270720 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 16000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 136 | 2210400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1796400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 348780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 259200 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 247 | 4901500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 700000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 690720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2303345 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 34 | 642456 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 114240 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 715776 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1554240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 162 | 4404810 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 238000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 505992 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7364500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 9251000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7689200 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2368.568 | 1490 | 36174279
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 22106181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 234 | 6351264 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 657360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 531 | 9985455 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1645 | 39100260
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 144578 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 123 | 2779000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 850 | 20126545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5209680 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 286 | 5673000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3966 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1486 | 33936769.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 189 | 4411818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 164 | 4279328 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 300 | 8949090.9 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 68112 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Compressor Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1179 | 21431854 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 443248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 816570 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1834.5 | 40438600.9
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1475345 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 4069000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 726835 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41844.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 54 | 286243 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 229793 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1269360 | -
Rangpur Area Total |  |  |  |  | 950 | 393 | 8098420.84
Eastern Grid Total |  |  |  |  | 16921.242 | 6887 | 150639905.73
Western Grid Total |  |  |  |  | 11614.5 | 5358.5 | 121574051.19
National Grid Total |  |  |  |  | 28535.742 | 12245.5 | 272213956.92
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-03-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8232.71 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3595.7 | MW
i) Dhaka area |  |  | 4414.71 |  | MW | i) Khulna area |  |  |  | 1327 | MW
ii) Chattogram area |  |  | 1313 |  | MW | ii) Barishal area |  |  |  | 327 | MW
iii) Cumilla area |  |  | 1082 |  | MW | iii) Rajshahi area |  |  |  | 1165.7 | MW
iv) Mymensingh area |  |  | 1025 |  | MW | iv) Rangpur area |  |  |  | 776 | MW
v) Sylhet area |  |  | 398 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11828.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 68 | 17:00 | 133 | Payra | 22 | 14:00
2 | AKSML | 15 | 21:00 | 68 | Jamalpur | 103 | 18:00 | 134 | Postogola | 44 | 13:00
3 | Aftabnagar | 28 | 00:00 | 69 | Jashore | 112 | 19:00 | 135 | Purbachal | 15 | 19:00
4 | Agargaon | 85 | 14:00 | 70 | Jhenaidah | 96 | 19:00 | 136 | Purbasadipur | 123 | 17:00
5 | Agrabad | 82 | 19:00 | 71 | Joydebpur | 144 | 16:00 | 137 | Rahanpur | 12.1 | 09:00
6 | Amnura | 54 | 19:00 | 72 | Joypurhat | 64 | 09:00 | 138 | Rahim | 29 | 08:00
7 | Ashuganj | 74 | 13:00 | 73 | Juldah | 14 | 13:00 | 139 | Rajbari | 52 | 19:00
8 | BSRM | 192 | 21:00 | 74 | KSRM | 31 | 19:00 | 140 | Rajendrapur | 100 | 15:00
9 | Bagerhat | 68 | 19:00 | 75 | Kabirpur | 243 | 12:00 | 141 | Rajshahi | 86 | 04:00
10 | Bajitpur | 38 | 18:00 | 76 | Kachua | 59 | 18:00 | 142 | Rajshahi-230 | 62 | 18:00
11 | Bakulia | 85 | 19:00 | 77 | Kallyanpur | 87 | 13:00 | 143 | Ramganj | 88 | 18:30
12 | Banani | 22.6 | 15:00 | 78 | Kalurghat | 38 | 10:00 | 144 | Rampur | 37 | 19:00
13 | Bangabhaban | 11 | 10:00 | 79 | Kamrangirchar | 63 | 17:00 | 145 | Rangamati | 13 | 18:00
14 | Barapukuria | 58 | 10:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 129 | 17:00
15 | Barguna | 14 | 00:00 | 81 | Kazla | 90 | 17:00 | 147 | Ruppur | 5.6 | 11:00
16 | Barishal | 85 | 19:00 | 82 | Keranigonj | 78 | 14:00 | 148 | SSM | 13 | 04:00
17 | Barishal-230 | 68 | 19:00 | 83 | Khagrachori | 26 | 18:30 | 149 | Saidpur | 111 | 17:00
18 | Baroaulia | 54 | 13:00 | 84 | Khosba | 26 | 18:30 | 150 | Satkhira | 99 | 18:30
19 | Baroirhat | 45 | 14:00 | 85 | Khulna | 73 | 19:00 | 151 | Satmasjid | 82 | 13:00
20 | Bashundhara | 147 | 13:00 | 86 | Khulshi | 160 | 22:00 | 152 | Savar | 196 | 15:00
21 | BashundharaCement | 8 | 00:00 | 87 | Kishoreganj | 109 | 19:00 | 153 | SevenRings | 19.45 | 17:00
22 | Beanibazar | 47 | 18:30 | 88 | Kodda | 271 | 10:00 | 154 | ShahCement | 38 | 00:00
23 | Benapole | 52 | 13:00 | 89 | Kulaura | 29 | 18:00 | 155 | Shahjadpur | 75 | 08:00
24 | Bhaluka | 126 | 16:00 | 90 | Kurigram | 60 | 18:00 | 156 | Shahjibazar | 96 | 22:00
25 | Bhandaria | 38 | 22:00 | 91 | Kushtia | 112 | 19:30 | 157 | Shahmirpur | 47 | 00:00
26 | Bhangura | 36 | 13:00 | 92 | Lalbag | 72 | 13:00 | 158 | Shariatpur | 56 | 21:00
27 | Bheramara(GK) | 42 | 18:00 | 93 | Lalmonirhat | 50 | 18:00 | 159 | Sherpur | 142 | 09:00
28 | Bhulta | 243 | 01:00 | 94 | MI_Cement | 17.1 | 12:00 | 160 | Shikalbaha | 27 | 22:00
29 | Bog-Sherpur | 70 | 04:00 | 95 | Madanganj | 35 | 00:00 | 161 | Shitalakhya | 71.8 | 15:00
30 | Bogura | 126 | 04:00 | 96 | Madaripur | 74 | 19:30 | 162 | Sholosohor | 37 | 10:00
31 | Borhanuddin | 60 | 21:00 | 97 | Madartek | 68.95 | 21:00 | 163 | Shyampur | 166 | 12:00
32 | Brahmanbaria | 96 | 19:00 | 98 | Madunaghat | 41 | 21:00 | 164 | Siddhirganj | 116 | 14:00
33 | Cantonment | 104 | 14:00 | 99 | Magura | 48 | 19:00 | 165 | Sirajganj | 92 | 09:00
34 | Chandpur | 48 | 04:00 | 100 | Mahasthangarh | 64 | 04:00 | 166 | Sonargaon | 94 | 10:00
35 | Chandraghona | 30 | 19:00 | 101 | Manikganj | 118 | 20:00 | 167 | Sreemongol | 52 | 18:30
36 | Chapai | 54 | 12:00 | 102 | Maniknagar | 58 | 13:00 | 168 | Sreepur | 90 | 12:00
37 | Charsaidpur | 41 | 04:00 | 103 | Matarbari | 42 | 19:00 | 169 | Srinagar | 31.7 | 21:00
38 | Chauddagram | 56 | 18:30 | 104 | Matuail | 60 | 12:00 | 170 | Sunamganj | 38 | 18:00
39 | Chhatak | 26 | 13:00 | 105 | Millgate | 71 | 14:00 | 171 | Sylhet | 29 | 18:00
40 | Chowmuhani | 160 | 18:30 | 106 | Mirpur | 109 | 14:00 | 172 | Sylhet-132 | 89 | 14:00
41 | Chuadanga | 75 | 03:00 | 107 | Mirsorai | 9 | 13:00 | 173 | TK | 25 | 19:00
42 | Coxsbazar | 113 | 19:30 | 108 | Mirzapur | 42 | 19:00 | 174 | Tangail | 152 | 18:00
43 | Cumilla(N) | 131 | 19:00 | 109 | Mithapukur | 52 | 17:00 | 175 | Thakurgaon | 78 | 18:00
44 | Cumilla(S) | 137 | 14:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 110 | 15:00
45 | Daudkandi | 118 | 19:30 | 111 | Mogbazar | 116.9 | 13:00 | 177 | Ullahpara | 31 | 08:00
46 | Dhaka | 42 | 12:00 | 112 | Mongla | 39 | 13:00 | 178 | Ullon | 38 | 19:30
47 | Dhamrai | 100 | 14:00 | 113 | Motijheel | 30 | 13:00 | 179 | Uttara | 70 | 13:00
48 | Dhanmondi | 110 | 13:00 | 114 | Muktagacha | 28 | 04:00 | 180 | UttaraNew | 37 | 18:30
49 | Dohazari | 85 | 18:00 | 115 | Munshiganj | 74 | 13:00 | 181 | Zigatola | 62 | 21:00
50 | Faridpur | 115 | 19:00 | 116 | Muradnagar | 20 | 18:30
51 | Fatullah | 87 | 15:00 | 117 | Mymensingh | 187 | 18:00
52 | Fenchuganj | 26 | 14:00 | 118 | Naogaon | 114 | 13:00
53 | Feni | 90 | 18:30 | 119 | Narail | 44 | 19:00
54 | GPH | 29 | 23:00 | 120 | Narinda | 60 | 13:00
55 | Ghatail | 78 | 03:00 | 121 | Narshingdi | 147 | 19:30
56 | Ghorashal | 11 | 10:00 | 122 | Natore | 121 | 04:00
57 | Ghorashal-230 | 77 | 22:00 | 123 | Nawabganj | 37.8 | 13:00
58 | Goalpara | 22 | 18:00 | 124 | Netrakona | 134 | 18:30
59 | Gollamari | 56 | 19:00 | 125 | New | 77 | 14:00
60 | Gopalganj | 80 | 19:30 | 126 | Niamatpur | 101 | 09:00
61 | Gulshan | 92 | 14:00 | 127 | Noapara | 38 | 19:00
62 | Halishahar | 62 | 12:00 | 128 | PHP | 9 | 18:30
63 | HaripurSBU | 170 | 11:00 | 129 | Pabna | 85 | 18:00
64 | Hasnabad | 74 | 00:00 | 130 | Palashbari | 98 | 14:00
65 | Hathazari | 93 | 18:00 | 131 | Panchagarh | 48 | 18:00
66 | Ishurdi | 55 | 20:00 | 132 | Patuakhali | 53 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11065.18 | 0 |  | 11065.18
1:00 | 10549.86 | 0 |  | 10549.86
2:00 | 10250.83 | 0 |  | 10250.83
3:00 | 10448.58 | 0 |  | 10448.58
4:00 | 11152.93 | 0 |  | 11152.93
5:00 | 9916.54 | 0 |  | 9916.54
6:00 | 9120.68 | 0 |  | 9120.68
7:00 | 9379.26 | 0 |  | 9379.26
8:00 | 10151.48 | 0 |  | 10151.48
9:00 | 10813.25 | 0 |  | 10813.25
10:00 | 11114.93 | 0 |  | 11114.93
11:00 | 11301.39 | 26 |  | 11328.39
12:00 | 11487.14 | 31 |  | 11519.14
13:00 | 11889.09 | 53 |  | 11944.09
14:00 | 12108.95 | 0 |  | 12108.95
15:00 | 11888.19 | 0 |  | 11888.19
16:00 | 11987.63 | 0 |  | 11987.63
17:00 | 12057.99 | 0 |  | 12057.99
18:00 | 11686.63 | 0 |  | 11686.63
19:00 | 12245.5 | 0 |  | 12245.5
19:30 | 12224.5 | 0 |  | 12224.5
20:00 | 12168.5 | 0 |  | 12168.5
21:00 | 12027.71 | 0 |  | 12027.71
22:00 | 11895.17 | 0 |  | 11895.17
23:00 | 11536.15 | 0 |  | 11536.15
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6230 | 4835.18 | 11065.18 | DAILY GENERATION CURVE
00:30 | 6118 | 4689.52 | 10807.52
01:00 | 6006 | 4543.86 | 10549.86 | 06-03-2025
01:30 | 5931 | 4469.345 | 10400.345
02:00 | 5856 | 4394.83 | 10250.83
02:30 | 5902 | 4447.705 | 10349.705
03:00 | 5948 | 4500.58 | 10448.58
03:30 | 6118.5 | 4682.255 | 10800.755
04:00 | 6289 | 4863.93 | 11152.93
04:30 | 5892 | 4642.735 | 10534.735
05:00 | 5495 | 4421.54 | 9916.54
05:30 | 5248 | 4270.61 | 9518.61
06:00 | 5001 | 4119.68 | 9120.68
06:30 | 5073.715 | 4176.255 | 9249.97
07:00 | 5146.43 | 4232.83 | 9379.26
07:30 | 5383.865 | 4381.505 | 9765.37
08:00 | 5621.3 | 4530.18 | 10151.48
08:30 | 5753.9 | 4728.465 | 10482.365
09:00 | 5886.5 | 4926.75 | 10813.25
09:30 | 5954.405 | 5009.685 | 10964.09
10:00 | 6022.31 | 5092.62 | 11114.93
10:30 | 6052.6 | 5155.56 | 11208.16
11:00 | 6082.89 | 5218.5 | 11301.39
11:30 | 6133.15 | 5261.115 | 11394.265
12:00 | 6183.41 | 5303.73 | 11487.14
12:30 | 6252.055 | 5436.06 | 11688.115
13:00 | 6320.7 | 5568.39 | 11889.09
13:30 | 6427.71 | 5571.31 | 11999.02
14:00 | 6534.72 | 5574.23 | 12108.95
14:30 | 6571.83 | 5426.74 | 11998.57
15:00 | 6608.94 | 5279.25 | 11888.19
15:30 | 6676.78 | 5261.13 | 11937.91
16:00 | 6744.62 | 5243.01 | 11987.63
16:30 | 6736.815 | 5285.995 | 12022.81
17:00 | 6729.01 | 5328.98 | 12057.99
17:30 | 6679.505 | 5192.805 | 11872.31
18:00 | 6630 | 5056.63 | 11686.63
18:30 | 6758.5 | 5207.565 | 11966.065
19:00 | 6887 | 5358.5 | 12245.5
19:30 | 6959 | 5265.5 | 12224.5
20:00 | 6790 | 5378.5 | 12168.5
20:30 | 6767.75 | 5330.355 | 12098.105 |  | Executive Engineer
21:00 | 6745.5 | 5282.21 | 12027.71 |  | Network Operation Division
21:30 | 6694 | 5267.44 | 11961.44
22:00 | 6642.5 | 5252.67 | 11895.17
22:30 | 6509.5 | 5206.16 | 11715.66
23:00 | 6376.5 | 5159.65 | 11536.15

## En-Curve
QF-LDC-12
Date | 06-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3576 | 1669.5 | 922 | 0 | 50 | 915.68 | 40 | 3445 | 0 | 76 | 371 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3576.5 | 1637 | 922 | 0 | 50 | 862.02 | 40 | 3338.5 | 0 | 59 | 322.5 | 0 | 0 | 0 | 0 | 06-03-2025
01:00 | 3577 | 1604.5 | 922 | 0 | 50 | 808.36 | 40 | 3232 | 0 | 42 | 274 | 0 | 0 | 0 | 0
01:30 | 3537.5 | 1564.5 | 922.5 | 0 | 49 | 811.345 | 40 | 3191 | 0 | 33.5 | 251 | 0 | 0 | 0 | 0 | Energy Generated | 272.214 |  | MKWHr
02:00 | 3498 | 1524.5 | 923 | 0 | 48 | 814.33 | 40 | 3150 | 0 | 25 | 228 | 0 | 0 | 0 | 0 | Energy not Served | 0.11 |  | MKWHr
02:30 | 3470 | 1553 | 922.5 | 0 | 46 | 815.205 | 40 | 3235.5 | 0 | 25 | 242.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 272.324 |  | MKWHr
03:00 | 3442 | 1581.5 | 922 | 0 | 44 | 816.08 | 40 | 3321 | 0 | 25 | 257 | 0 | 0 | 0 | 0
03:30 | 3494.5 | 1661.5 | 922.5 | 0 | 45 | 813.255 | 40 | 3410.5 | 0 | 70.5 | 343 | 0 | 0 | 0 | 0
04:00 | 3547 | 1741.5 | 923 | 0 | 46 | 810.43 | 40 | 3500 | 0 | 116 | 429 | 0 | 0 | 0 | 0
04:30 | 3451.5 | 1619.5 | 923 | 0 | 45 | 813.235 | 40 | 3262.5 | 0 | 78.5 | 301.5 | 0 | 0 | 0 | 0
05:00 | 3356 | 1497.5 | 923 | 0 | 44 | 816.04 | 40 | 3025 | 0 | 41 | 174 | 0 | 0 | 0 | 0
05:30 | 3251 | 1391.5 | 922.5 | 0 | 42 | 817.11 | 40 | 2874.5 | 0 | 24.5 | 155.5 | 0 | 0 | 0 | 0
06:00 | 3146 | 1285.5 | 922 | 0 | 40 | 818.18 | 40 | 2724 | 0 | 8 | 137 | 0 | 0 | 0 | 0
06:30 | 3206.5 | 1332.5 | 922 | 0 | 41 | 819.495 | 40 | 2723 | 25.975 | 8 | 131.5 | 0 | 0 | 0 | 0
07:00 | 3267 | 1379.5 | 922 | 0 | 42 | 820.81 | 40 | 2722 | 51.95 | 8 | 126 | 0 | 0 | 0 | 0
07:30 | 3408 | 1469.5 | 898.5 | 0 | 42 | 818.72 | 40 | 2765 | 132.15 | 16 | 175.5 | 0 | 0 | 0 | 0
08:00 | 3549 | 1559.5 | 875 | 0 | 42 | 816.63 | 40 | 2808 | 212.35 | 24 | 225 | 0 | 0 | 0 | 0
08:30 | 3590 | 1590 | 875.5 | 0 | 44 | 815.36 | 40 | 2906.5 | 310.005 | 28 | 283 | 0 | 0 | 0 | 0
09:00 | 3631 | 1620.5 | 876 | 0 | 46 | 814.09 | 40 | 3005 | 407.66 | 32 | 341 | 0 | 0 | 0 | 0
09:30 | 3634 | 1667.5 | 898.5 | 0 | 48 | 813.74 | 40 | 3009 | 480.85 | 32 | 340.5 | 0 | 0 | 0 | 0
10:00 | 3637 | 1714.5 | 921 | 0 | 50 | 813.39 | 40 | 3013 | 554.04 | 32 | 340 | 0 | 0 | 0 | 0
10:30 | 3648.5 | 1716.75 | 921 | 0 | 51 | 812.795 | 40 | 3058.5 | 602.115 | 32 | 325.5 | 0 | 0 | 0 | 13
11:00 | 3660 | 1719 | 921 | 0 | 52 | 812.2 | 40 | 3104 | 650.19 | 32 | 311 | 0 | 0 | 0 | 26
11:30 | 3656.5 | 1721.75 | 921 | 0 | 54 | 813.035 | 40 | 3192.5 | 668.98 | 24 | 301.5 | 0 | 0 | 1 | 28.5
12:00 | 3653 | 1724.5 | 921 | 0 | 56 | 813.87 | 40 | 3281 | 687.77 | 16 | 292 | 0 | 0 | 2 | 31
12:30 | 3700.5 | 1696.5 | 920.5 | 0 | 52 | 813.9 | 40 | 3420 | 680.215 | 23.5 | 337.5 | 0 | 0 | 3.5 | 42
13:00 | 3748 | 1668.5 | 920 | 0 | 48 | 813.93 | 40 | 3559 | 672.66 | 31 | 383 | 0 | 0 | 5 | 53
13:30 | 3750 | 1724.5 | 920.5 | 0 | 54 | 815.465 | 40 | 3651.5 | 618.055 | 42.5 | 378.5 | 0 | 0 | 4 | 26.5
14:00 | 3752 | 1780.5 | 921 | 0 | 60 | 817 | 40 | 3744 | 563.45 | 54 | 374 | 0 | 0 | 3 | 0
14:30 | 3769.5 | 1800.75 | 920.5 | 0 | 59 | 818 | 40 | 3646.5 | 513.82 | 58 | 371 | 0 | 0 | 1.5 | 0
15:00 | 3787 | 1821 | 920 | 0 | 58 | 819 | 40 | 3549 | 464.19 | 62 | 368 | 0 | 0 | 0 | 0
15:30 | 3778 | 1880.5 | 920 | 0 | 58 | 863 | 40 | 3579 | 375.91 | 67 | 373.5 | 0 | 0 | 3 | 0
16:00 | 3769 | 1940 | 920 | 0 | 58 | 907 | 40 | 3609 | 287.63 | 72 | 379 | 0 | 0 | 6 | 0
16:30 | 3746.5 | 1940 | 920.5 | 0 | 57 | 965.5 | 40 | 3605 | 194.81 | 103 | 446.5 | 0 | 0 | 4 | 0
17:00 | 3724 | 1940 | 921 | 0 | 56 | 1024 | 40 | 3601 | 101.99 | 134 | 514 | 0 | 0 | 2 | 0
17:30 | 3649 | 1793.75 | 920.5 | 0 | 59 | 1008 | 40 | 3566 | 52.06 | 181 | 601 | 0 | 0 | 2 | 0
18:00 | 3574 | 1647.5 | 920 | 0 | 62 | 992 | 40 | 3531 | 2.13 | 228 | 688 | 0 | 0 | 2 | 0
18:30 | 3567.5 | 1701 | 900 | 0 | 60 | 1085.5 | 40 | 3695.5 | 1.065 | 217.5 | 697 | 0 | 0 | 1 | 0
19:00 | 3561 | 1754.5 | 880 | 0 | 58 | 1179 | 40 | 3860 | 0 | 207 | 706 | 0 | 0 | 0 | 0
19:30 | 3734 | 1870.5 | 869 | 0 | 52 | 1162 | 40 | 3765 | 0 | 181 | 551 | 0 | 0 | 0 | 0
20:00 | 3812 | 1680.5 | 868 | 0 | 54 | 1161 | 40 | 3818 | 0 | 181 | 554 | 0 | 0 | 0 | 0
20:30 | 3834.5 | 1710.75 | 892 | 0 | 54 | 1115.855 | 40 | 3717.5 | 0 | 181 | 552.5 | 0 | 0 | 0 | 0
21:00 | 3857 | 1741 | 916 | 0 | 54 | 1070.71 | 40 | 3617 | 0 | 181 | 551 | 0 | 0 | 0 | 0
21:30 | 3826.5 | 1745.5 | 915.5 | 0 | 57 | 1056.94 | 40 | 3589 | 0 | 181 | 550 | 0 | 0 | 0 | 0
22:00 | 3796 | 1750 | 915 | 0 | 60 | 1043.17 | 40 | 3561 | 0 | 181 | 549 | 0 | 0 | 0 | 0
22:30 | 3725.5 | 1731.5 | 915 | 0 | 59 | 1003.66 | 40 | 3552 | 0 | 173 | 516 | 0 | 0 | 0 | 0
23:00 | 3655 | 1713 | 915 | 0 | 58 | 964.15 | 40 | 3543 | 0 | 165 | 483 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 06:00 | 378 | 14:00 | Payra | 420 | 06:00 | 411 | 14:00
Ashuganj | 410 | 18:00 | 381 | 13:00 | Rahanpur | 411 | 00:00 | 393 | 16:00
Bhulta | 402 | 18:00 | 381 | 15:00 | Rampal | 410 | 06:00 | 396 | 13:00
Bibiana | 398 | 06:00 | 387 | 14:00
BIPTC | 397 | 02:00 | 388 | 13:00
Bogura | 403 | 01:00 | 378 | 16:00
Gopalganj | 409 | 06:00 | 392 | 14:00
Kaliakoir | 381 | 04:00 | 364 | 14:00
Madunaghat | 402 | 06:00 | 390 | 15:00
Meghnaghat | 398 | 06:00 | 380 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 04:00 | 220 | 14:00 | Keranigonj | 231 | 04:00 | 218 | 14:00
AKSML | 232 | 06:00 | 223 | 16:00 | Khulna(S) | 239 | 06:00 | 226 | 14:00
Aminbazar | 233 | 05:00 | 220 | 14:00 | Madunaghat | 234 | 06:00 | 226 | 13:00
Ashuganj | 232 | 03:00 | 222 | 12:00 | Madunaghat-400 | 235 | 05:00 | 226 | 15:00
Ashuganj-400 | 234 | 18:00 | 216 | 13:00 | Maniknagar | 229 | 06:00 | 216 | 14:00
Baghabari | 237 | 04:00 | 227 | 17:00 | Meghnaghat | 236 | 02:00 | 225 | 14:00
Barapukuria | 225 | 06:00 | 216 | 16:00 | Meghnaghat-400 | 231 | 04:00 | 220 | 12:00
Barapukuria-230 | 226 | 7:00 | 216 | 15:00 | Mirsorai | 230 | 04:00 | 219 | 17:00
Barishal | 241 | 04:00 | 232 | 13:00 | Rajshahi | 237 | 02:00 | 224 | 17:00
Bheramara | 235 | 04:00 | 225 | 16:00 | Rampal | 237 | 06:00 | 225 | 13:00
Bhulta | 230 | 04:00 | 217 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 06:00 | 222 | 13:00 | Rampura | 229 | 04:00 | 216 | 14:00
BIPTC | 238 | 06:00 | 225 | 17:00 | Shikalbaha | 233 | 07:00 | 222 | 16:00
Bogura | 238 | 01:00 | 228 | 16:00 | Shyampur | 230 | 04:00 | 218 | 14:00
Bogura-400 | 237 | 01:00 | 228 | 16:00 | Siddhirganj | 229 | 00:00 | 219 | 14:00
Borhanuddin | 243 | 08:00 | 233 | 19:30 | Sirajgonj | 242 | 05:00 | 236 | 14:00
BSRM | 230 | 04:00 | 219 | 14:00 | Sreepur | 231 | 01:00 | 223 | 12:00
Cumilla(N) | 229 | 06:00 | 217 | 14:00 | Tongi | 232 | 18:30 | 212 | 15:00
Faridpur | 236 | 05:00 | 228 | 14:00
Fenchuganj | 234 | 04:00 | 227 | 14:00
Ghorashal | 235 | 01:00 | 220 | 21:00
Ghorashal-230 | 230 | 04:00 | 217 | 14:00
Gopalganj | 236 | 06:00 | 226 | 14:00
GPH | 232 | 04:00 | 222 | 14:00
Haripur | 229 | 04:00 | 216 | 15:00
Hasnabad | 230 | 03:00 | 220 | 15:00
Hathazari | 236 | 03:00 | 226 | 15:00
Ishurdi | 238 | 06:00 | 227 | 16:00
Jhenaidah | 237 | 05:00 | 224 | 14:00
Kaliakoir | 230 | 04:00 | 217 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 124 | 14:00 | Madunaghat | 134 | 06:00 | 128 | 14:00
Agargaon | 140 | 04:00 | 131 | 14:00 | Magura | 138 | 05:00 | 128 | 13:00
Agrabad | 133 | 06:00 | 126 | 13:00 | Mahasthangarh | 133 | 00:00 | 125 | 16:00
AKS | 130 | 00:00 | 125 | 13:00 | Manikganj | 132 | 18:30 | 123 | 12:00
Aminbazar | 136 | 05:00 | 130 | 11:00 | Maniknagar | 130 | 06:00 | 121 | 14:00
Amnura | 138 | 04:00 | 129 | 00:00 | Matarbari | 129 | 01:00 | 113 | 19:00
Ashuganj | 136 | 18:30 | 130 | 14:00 | Matuail | 133 | 04:00 | 120 | 17:00
Bagerhat | 137 | 06:00 | 125 | 12:00 | Millgate | 133 | 04:00 | 122 | 14:00
Bajitpur | 131 | 03:00 | 123 | 16:00 | Mirpur | 135 | 02:00 | 127 | 13:00
Bakulia | 135 | 07:00 | 128 | 14:00 | Mirzapur | 133 | 18:30 | 124 | 14:00
Banani | 135 | 07:00 | 124 | 13:00 | Mithapukur | 138 | 18:30 | 123 | 13:00
Bangabhaban | 130 | 03:00 | 121 | 13:00 | MI_Cement | 134 | 05:00 | 126 | 14:00
Barapukuria | 140 | 18:30 | 130 | 16:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 137 | 06:00 | 133 | 14:00 | Mogbazar | 134 | 05:00 | 125 | 13:00
Barishal | 135 | 06:00 | 129 | 14:00 | Mongla | 137 | 06:00 | 126 | 14:00
Barishal-230 | 136 | 06:00 | 129 | 15:00 | Motijheel | 130 | 03:00 | 121 | 13:00
Baroaulia | 134 | 06:00 | 129 | 12:00 | Muktagacha | 132 | 18:00 | 123 | 15:00
Baroirhat | 128 | 06:00 | 118 | 15:00 | Munshiganj | 133 | 04:00 | 124 | 15:00
Bashundhara | 134 | 05:00 | 122 | 15:00 | Muradnagar | 130 | 06:00 | 121 | 14:00
BashundharaCement | 132 | 00:00 | 125 | 14:00 | Mymensingh | 133 | 18:30 | 112 | 16:00
Beanibazar | 132 | 04:00 | 128 | 13:00 | Naogaon | 132 | 05:00 | 123 | 09:00
Benapole | 136 | 05:00 | 126 | 14:00 | Narail | 139 | 05:00 | 127 | 14:00
Bhaluka | 128 | 04:00 | 115 | 23:00 | Narinda | 130 | 6:00 | 121 | 14:00
Bhandaria | 130 | 06:00 | 125 | 00:00 | Narshingdi | 130 | 18:00 | 120 | 17:00
Bhangura | 144 | 07:00 | 129 | 12:00 | Natore | 136 | 06:00 | 129 | 16:00
Bheramara | 138 | 05:00 | 133 | 16:00 | Nawabganj | 137 | 04:00 | 127 | 13:00
Bheramara(GK) | 138 | 05:00 | 132 | 17:00 | Netrakona | 124 | 05:00 | 107 | 17:00
Bhulta | 129 | 18:30 | 121 | 13:00 | New | 134 | 04:00 | 123 | 15:00
Bog-Sherpur | 134 | 01:00 | 127 | 16:00 | Niamatpur | 136 | 05:00 | 133 | 16:00
Bogura | 135 | 05:00 | 129 | 09:00 | Noapara | 139 | 05:00 | 130 | 12:00
Bogura-230 | 135 | 00:00 | 128 | 16:00 | Pabna | 137 | 02:00 | 130 | 17:00
Brahmanbaria | 129 | 04:00 | 124 | 12:00 | Palashbari | 129 | 01:00 | 117 | 14:00
Cantonment | 140 | 06:00 | 130 | 14:00 | Panchagarh | 142 | 18:30 | 118 | 13:00
Chandpur | 122 | 00:00 | 115 | 15:00 | Patuakhali | 135 | 05:00 | 127 | 01:00
Chandraghona | 135 | 04:00 | 129 | 14:00 | Payra | 138 | 08:00 | 128 | 01:00
Chapai | 135 | 01:00 | 131 | 00:00 | PHP | 126 | 06:00 | 117 | 15:00
Charsaidpur | 133 | 04:00 | 125 | 15:00 | Postogola | 136 | 05:00 | 128 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 06:00 | 117 | 13:00 | Purbachal | 133 | 02:00 | 124 | 14:00
Chhatak | 132 | 02:00 | 128 | 13:00 | Purbasadipur | 135 | 18:00 | 117 | 16:00
Chowmuhani | 121 | 06:00 | 113 | 13:00 | Rahanpur | 138 | 01:00 | 135 | 00:00
Chuadanga | 137 | 05:00 | 126 | 16:00 | Rahanpur-400 | 138 | 03:00 | 134 | 17:00
Coxsbazar | 125 | 08:00 | 114 | 21:00 | Rahim | 132 | 07:00 | 125 | 13:00
Cumilla(N) | 132 | 06:00 | 123 | 14:00 | Rajbari | 131 | 05:00 | 126 | 14:00
Cumilla(S) | 132 | 01:00 | 120 | 14:00 | Rajendrapur | 137 | 18:30 | 123 | 13:00
Daudkandi | 128 | 05:00 | 119 | 14:00 | Rajshahi | 137 | 05:00 | 130 | 16:00
Dhaka | 134 | 05:00 | 125 | 12:00 | Rajshahi-230 | 137 | 01:00 | 124 | 11:00
Dhamrai | 132 | 05:00 | 123 | 14:00 | Ramganj | 120 | 06:00 | 112 | 13:00
Dhanmondi | 135 | 03:00 | 127 | 14:00 | Rampur | 133 | 06:00 | 126 | 15:00
Dohazari | 131 | 08:00 | 123 | 17:00 | Rampura | 134 | 06:00 | 124 | 14:00
Faridpur | 134 | 07:00 | 128 | 14:00 | Rangamati | 134 | 05:00 | 128 | 14:00
Fatullah | 135 | 05:00 | 127 | 13:00 | Rangpur | 135 | 18:30 | 122 | 13:00
Fenchuganj | 137 | 22:00 | 132 | 13:00 | Ruppur | 139 | 06:00 | 133 | 16:00
Feni | 124 | 08:00 | 115 | 13:00 | Saidpur | 136 | 18:30 | 120 | 13:00
Ghatail | 130 | 19:00 | 121 | 07:00 | Satkhira | 137 | 06:00 | 126 | 17:00
Ghorashal | 139 | 18:30 | 132 | 15:00 | Satmasjid | 139 | 04:00 | 130 | 14:00
Goalpara | 140 | 06:00 | 130 | 14:00 | Savar | 134 | 04:00 | 125 | 15:00
Gollamari | 137 | 04:00 | 130 | 14:00 | SevenRings | 140 | 18:30 | 130 | 14:00
Gopalganj | 138 | 05:00 | 131 | 14:00 | ShahCement | 133 | 04:00 | 125 | 15:00
Gopalganj-400 | 139 | 04:00 | 133 | 14:00 | Shahjadpur | 140 | 04:00 | 133 | 12:00
Gulshan | 134 | 04:00 | 124 | 14:00 | Shahjibazar | 132 | 04:00 | 127 | 15:00
Halishahar | 134 | 04:00 | 128 | 14:00 | Shahmirpur | 135 | 05:00 | 128 | 14:00
Haripur | 134 | 04:00 | 127 | 13:00 | Shariatpur | 138 | 06:00 | 131 | 13:00
HaripurSBU | 134 | 04:00 | 127 | 12:00 | Sherpur | 133 | 18:00 | 122 | 13:00
Hasnabad | 136 | 03:00 | 128 | 15:00 | Shikalbaha | 125 | 06:00 | 117 | 14:00
Hathazari | 136 | 05:00 | 130 | 18:30 | Shikalbaha-230 | 136 | 05:00 | 129 | 15:00
Ishurdi | 140 | 06:00 | 133 | 17:00 | Shitalakhya | 134 | 05:00 | 126 | 14:00
Jaldhaka | 134 | 18:30 | 117 | 16:00 | Sholosohor | 135 | 06:00 | 128 | 14:00
Jamalpur | 137 | 19:00 | 122 | 07:00 | Shyampur | 133 | 05:00 | 125 | 15:00
Jashore | 138 | 06:00 | 127 | 14:00 | Shyampur-230 | 134 | 04:00 | 126 | 14:00
Jhenaidah | 140 | 05:00 | 130 | 14:00 | Siddhirganj | 134 | 04:00 | 126 | 12:00
Jhenaidah-230 | 139 | 06:00 | 130 | 13:00 | Sirajganj | 133 | 01:00 | 127 | 12:00
Joydebpur | 138 | 18:30 | 124 | 14:00 | Sonargaon | 133 | 18:00 | 123 | 15:00
Joypurhat | 130 | 02:00 | 119 | 09:00 | Sreemongol | 131 | 00:00 | 128 | 13:00
Juldah | 134 | 05:00 | 127 | 13:00 | Sreepur | 129 | 00:00 | 123 | 12:00
Kabirpur | 136 | 07:00 | 119 | 14:00 | Srinagar | 137 | 06:00 | 127 | 14:00
Kachua | 124 | 06:00 | 117 | 14:00 | SSM | 138 | 05:00 | 132 | 00:00
Kaliakoir | 137 | 18:00 | 125 | 14:00 | Sunamganj | 131 | 06:00 | 127 | 13:00
Kallyanpur | 137 | 06:00 | 128 | 13:00 | Sylhet | 133 | 08:00 | 128 | 13:00
Kalurghat | 135 | 08:00 | 129 | 13:00 | Sylhet-132 | 132 | 00:00 | 130 | 13:00
Kamrangirchar | 137 | 05:00 | 127 | 14:00 | Tangail | 129 | 18:30 | 122 | 14:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 141 | 18:30 | 116 | 13:00
Kazla | 130 | 05:00 | 121 | 13:00 | TK | 135 | 05:00 | 129 | 14:00
Keranigonj | 137 | 04:00 | 127 | 14:00 | Tongi | 135 | 04:00 | 125 | 15:00
Khagrachori | 134 | 08:00 | 127 | 16:00 | Ullahpara | 136 | 05:00 | 129 | 12:00
Khosba | 130 | 06:00 | 120 | 13:00 | Ullon | 134 | 04:00 | 124 | 14:00
Khulna | 138 | 06:00 | 128 | 13:00 | Uttara | 136 | 06:00 | 126 | 14:00
Khulna(S) | 139 | 06:00 | 130 | 14:00 | UttaraNew | 133 | 06:00 | 122 | 15:00
Khulshi | 133 | 06:00 | 125 | 15:00 | Zigatola | 138 | 05:00 | 128 | 12:00
Kishoreganj | 129 | 06:00 | 114 | 18:00
Kodda | 138 | 18:30 | 121 | 14:00
KSRM | 134 | 01:00 | 128 | 14:00
Kulaura | 134 | 04:00 | 131 | 12:00
Kurigram | 135 | 18:30 | 119 | 07:00
Kushtia | 139 | 06:00 | 131 | 16:00
Lalbag | 137 | 06:00 | 127 | 14:00
Lalmonirhat | 132 | 18:00 | 120 | 16:00
Madanganj | 132 | 01:00 | 125 | 14:00
Madaripur | 139 | 06:00 | 133 | 14:00
Madartek | 133 | 04:00 | 130 | 08:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division