## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-03-2025 | [28 empty] | Date: | 07-03-2025 | [28 empty] | Date: | 07-03-2025 | [28 empty] | Date: | 07-03-2025 | [28 empty] | Date: | 07-03-2025 | [18 empty] | Date: | 07-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 16 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 400 | 265 | 0 | 0 | 0 | 23 | 293 | 0 | 0 | 0 | 35 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 35 | 857 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 803 | 0 | 51 | 0 | 8 | 0 | 170 | 0 | 14 | 181 | 35 | 0 | 50 | 0 | 38 | 18 | 17 | 52 | 0 | 0 | 0 | 280 | 320 | 382 | 32 | 30 | 30 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 18 | 162 | 0 | 89 | 67 | 11 | 0 | 0 | 12 | 6080.5 | 915 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 910.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 161 | 0 | 370 | 0 | 0 | 2.5 | 163 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 7 | 123 | 220 | 0 | 0 | 900 | 0 | 4958.77 | 11039.27 | 88.47
01:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 360 | 260 | 0 | 0 | 0 | 23 | 292 | 0 | 0 | 0 | 35 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 35 | 803 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 802 | 0 | 51 | 0 | 8 | 0 | 170 | 0 | 20 | 182 | 32 | 0 | 50 | 0 | 30 | 18 | 17 | 46 | 0 | 0 | 0 | 285 | 320 | 382 | 35 | 30 | 30 | 5 | 113 | 21 | 0 | 50 | 30 | 0 | 18 | 162 | 0 | 58 | 55 | 11 | 0 | 0 | 12 | 5879.5 | 916 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 822.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 161 | 0 | 370 | 0 | 0 | 2.5 | 165 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 123 | 190 | 0 | 0 | 800 | 0 | 4676.21 | 10555.71 | 88.45
02:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 320 | 254 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 0 | 35 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 35 | 800 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 803 | 0 | 51 | 0 | 8 | 0 | 170 | 0 | 20 | 182 | 32 | 0 | 50 | 0 | 28 | 18 | 0 | 42 | 0 | 0 | 0 | 270 | 320 | 322 | 35 | 30 | 30 | 5 | 80 | 21 | 0 | 50 | 30 | 0 | 18 | 162 | 0 | 58 | 55 | 13 | 0 | 0 | 0 | 5575.5 | 918 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 816.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 164 | 0 | 320 | 0 | 0 | 2.5 | 166 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 80 | 190 | 0 | 0 | 760 | 0 | 4543.46 | 10118.96 | 88.45
03:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 360 | 293 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 0 | 35 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 35 | 807 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 839 | 0 | 51 | 0 | 8 | 0 | 170 | 0 | 20 | 201 | 32 | 0 | 50 | 0 | 29 | 18 | 0 | 42 | 0 | 0 | 0 | 285 | 320 | 322 | 35 | 30 | 30 | 5 | 80 | 21 | 0 | 50 | 30 | 0 | 18 | 162 | 0 | 62 | 60 | 13 | 0 | 0 | 0 | 5731.5 | 919 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 815.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 170 | 0 | 300 | 0 | 0 | 2.5 | 163 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 80 | 220 | 0 | 0 | 700 | 0 | 4504.12 | 10235.62 | 88.45
04:00 | 0 | 25 | 8 | 110 | 0 | 130 | 0 | 0 | 378 | 0 | 0 | 0 | 17 | 0 | 51 | 63 | 0 | 0 | 0 | 0 | 23 | 0 | 400 | 245 | 0 | 0 | 0 | 23 | 260 | 0 | 0 | 0 | 27 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 35 | 850 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 36 | 0 | 200 | 0 | 20 | 230 | 29 | 0 | 50 | 0 | 29 | 18 | 0 | 44 | 0 | 0 | 0 | 290 | 320 | 368 | 35 | 30 | 30 | 5 | 80 | 21 | 0 | 86 | 30 | 0 | 18 | 162 | 0 | 88 | 115 | 16 | 0 | 0 | 7 | 6142.5 | 919 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 815.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 154 | 0 | 350 | 0 | 0 | 2.5 | 168 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 114 | 220 | 0 | 0 | 800 | 0 | 4792.51 | 10935.01 | 88.45
05:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 340 | 259 | 0 | 0 | 0 | 25 | 240 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 752 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 700 | 0 | 17 | 0 | 36 | 0 | 200 | 0 | 20 | 182 | 29 | 0 | 50 | 0 | 0 | 18 | 0 | 44 | 0 | 0 | 0 | 280 | 320 | 320 | 32 | 30 | 30 | 5 | 80 | 16 | 0 | 22 | 30 | 0 | 18 | 161 | 0 | 45 | 55 | 17 | 0 | 0 | 12 | 5298 | 919 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 815.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 2.5 | 169 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 120 | 180 | 0 | 0 | 720 | 0 | 4423.28 | 9721.28 | 88.45
06:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 25 | 180 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 757 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 609 | 0 | 10 | 0 | 8 | 0 | 100 | 0 | 12 | 181 | 10 | 0 | 50 | 0 | 0 | 18 | 0 | 40 | 0 | 0 | 0 | 265 | 291 | 300 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 20 | 0 | 18 | 161 | 0 | 45 | 45 | 19 | 0 | 0 | 0 | 4774 | 926 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 814.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 260 | 0 | 0 | 2.5 | 170 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 65 | 180 | 0 | 0 | 600 | 0 | 4087.25 | 8861.25 | 88.44
07:00 | 0 | 10 | 0 | 110 | 0 | 130 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 273 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 3 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 755 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 608 | 2 | 10 | 0 | 8 | 0 | 100 | 0 | 5 | 181 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 42 | 0 | 7 | 0 | 275 | 291 | 300 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 20 | 0 | 18 | 161 | 0 | 45 | 45 | 21 | 0 | 4.22 | 0 | 4551.22 | 918 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 383 | 0 | 817.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 4.45 | 140 | 0 | 0 | 0 | 140 | 0 | 280 | 0 | 0.38 | 2.5 | 169 | 61 | 0 | 2 | 0 | 0 | 0 | 0.3 | 14 | 0.04 | 0 | 150 | 4 | 65 | 180 | 0 | 0 | 580 | 0 | 4117.2 | 8668.42 | 88.44
08:00 | 0 | 17 | 0 | 110 | 0 | 130 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 12 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 36 | 757 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 609 | 9 | 10 | 0 | 8 | 0 | 100 | 0 | 5 | 194 | 10 | 0 | 50 | 0 | 0 | 16 | 0 | 42 | 0 | 27 | 0 | 290 | 291 | 300 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 20 | 0 | 18 | 161 | 0 | 45 | 45 | 22 | 1 | 16.98 | 0 | 4688.98 | 869 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.49 | 385 | 0 | 819.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 19.32 | 140 | 0 | 0 | 0 | 140 | 0 | 280 | 0 | 1.62 | 2.5 | 169 | 63 | 0 | 10 | 0 | 0 | 0 | 1.6 | 54 | 0.02 | 0 | 150 | 4 | 65 | 180 | 0 | 0 | 600 | 0 | 4212.2 | 8901.18 | 88.43
09:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 21 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 39 | 757 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 605 | 14 | 10 | 0 | 8 | 0 | 170 | 0 | 5 | 196 | 29 | 0 | 50 | 0 | 0 | 5 | 0 | 38 | 0 | 47 | 0 | 310 | 300 | 350 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 20 | 0 | 18 | 162 | 0 | 45 | 45 | 23 | 1 | 29.3 | 0 | 4946.3 | 868 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.52 | 379 | 0 | 815.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 35.67 | 140 | 0 | 0 | 0 | 143 | 0 | 331 | 0 | 0 | 2.5 | 125 | 63 | 0 | 18 | 0 | 0 | 0 | 3.2 | 102 | 0.36 | 0 | 150 | 4 | 65 | 180 | 0 | 0 | 600 | 0 | 4341.18 | 9287.48 | 88.42
10:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 310 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 28 | 17 | 17.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 31 | 764 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 608 | 18 | 10 | 0 | 8 | 0 | 170 | 0 | 25 | 222 | 35 | 0 | 50 | 0 | 0 | 12 | 0 | 44 | 0 | 62 | 0 | 310 | 300 | 353 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 20 | 0 | 18 | 162 | 0 | 55 | 55 | 23 | 2 | 39.29 | 0 | 5156.09 | 915 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.16 | 379 | 0 | 816.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 59.99 | 140 | 0 | 0 | 0 | 160 | 0 | 358 | 0 | 4.55 | 5.5 | 130 | 63 | 0 | 27 | 0 | 0 | 0 | 4.8 | 144 | 0.54 | 0 | 150 | 4 | 65 | 180 | 0 | 0 | 600 | 0 | 4564.78 | 9720.87 | 88.41
11:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 380 | 310 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 33 | 17 | 17.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 31 | 760 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 608 | 20 | 20 | 0 | 8 | 0 | 210 | 0 | 29 | 205 | 34 | 0 | 50 | 0 | 0 | 9 | 0 | 52 | 0 | 68 | 0 | 315 | 320 | 353 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 20 | 0 | 18 | 162 | 0 | 45 | 35 | 23 | 2 | 47.64 | 0 | 5295.44 | 916 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.92 | 373 | 0 | 814.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 59.56 | 145 | 0 | 0 | 0 | 165 | 0 | 351 | 0 | 5.31 | 5.5 | 170 | 62 | 0 | 31 | 0 | 0 | 0 | 5.8 | 168 | 0.62 | 0 | 150 | 5 | 65 | 180 | 0 | 0 | 600 | 0 | 4660.47 | 9955.91 | 88.4
12:00 | 0 | 0 | 13 | 110 | 0 | 130 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 380 | 290 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 34 | 35 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 34 | 765 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 610 | 20 | 51 | 0 | 55 | 0 | 230 | 0 | 29 | 183 | 34 | 0 | 50 | 0 | 1 | 18 | 0 | 56 | 0 | 74 | 0 | 310 | 320 | 366 | 23 | 30 | 30 | 5 | 80 | 16 | 0 | 86 | 30 | 0 | 18 | 163 | 0 | 50 | 35 | 23 | 2 | 50.23 | 0 | 5547.23 | 916 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.04 | 378 | 0 | 816.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 64.07 | 163 | 0 | 0 | 0 | 156 | 0 | 392 | 0 | 5.92 | 5.5 | 168 | 65 | 0 | 33 | 34 | 0 | 0 | 6.2 | 176 | 0.65 | 0 | 150 | 5 | 65 | 220 | 0 | 0 | 600 | 0 | 4969.66 | 10516.89 | 88.39
13:00 | 0 | 0 | 17 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 256 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 32 | 51 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 4 | 40 | 0 | 40 | 850 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 650 | 19 | 51 | 0 | 83 | 0 | 205 | 0 | 29 | 183 | 34 | 0 | 50 | 0 | 18 | 18 | 0 | 54 | 0 | 71 | 0 | 295 | 320 | 354 | 28 | 30 | 30 | 5 | 113 | 16 | 0 | 86 | 30 | 0 | 16 | 163 | 0 | 65 | 55 | 23 | 2 | 47.56 | 0 | 5768.56 | 916 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.57 | 461 | 0 | 812.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 63.97 | 185 | 0 | 0 | 0 | 179 | 0 | 390 | 0 | 5.52 | 5.5 | 168 | 64 | 0 | 32 | 38 | 0 | 0 | 6.2 | 164 | 0.65 | 0 | 200 | 5 | 65 | 220 | 0 | 0 | 630 | 0 | 5113.56 | 10882.12 | 88.38
14:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 310 | 0 | 0 | 0 | 30 | 28 | 0 | 0 | 29 | 35 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 0 | 39 | 755 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 609 | 18 | 10 | 0 | 45 | 0 | 105 | 0 | 21 | 211 | 33 | 0 | 50 | 0 | 27 | 12 | 0 | 50 | 0 | 63 | 0 | 300 | 320 | 335 | 5 | 30 | 30 | 5 | 80 | 16 | 0 | 11 | 30 | 0 | 16 | 163 | 0 | 65 | 55 | 23 | 2 | 42.19 | 0 | 5137.19 | 916 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.29 | 385 | 0 | 813.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 52.2 | 150 | 0 | 0 | 0 | 150 | 0 | 404 | 0 | 4.82 | 2.5 | 170 | 62 | 0 | 29 | 0 | 0 | 0 | 5.5 | 157 | 0.56 | 0 | 150 | 5 | 65 | 180 | 0 | 0 | 500 | 0 | 4607.61 | 9744.8 | 88.37
15:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 302 | 0 | 0 | 0 | 30 | 24 | 0 | 0 | 23 | 25 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 0 | 26 | 752 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 609 | 14 | 10 | 0 | 83 | 0 | 230 | 0 | 5 | 195 | 33 | 0 | 50 | 0 | 27 | 16 | 0 | 48 | 0 | 51 | 0 | 310 | 320 | 384 | 5 | 29 | 30 | 5 | 113 | 16 | 0 | 11 | 30 | 0 | 16 | 163 | 0 | 45 | 45 | 23 | 2 | 35 | 0 | 5363 | 915 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.19 | 382 | 0 | 812.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 44.4 | 150 | 0 | 0 | 0 | 150 | 0 | 405 | 0 | 3.71 | 2.5 | 170 | 63 | 0 | 22 | 0 | 0 | 0 | 4.2 | 80 | 0.45 | 0 | 180 | 5 | 63 | 180 | 0 | 0 | 560 | 0 | 4566.28 | 9929.28 | 88.36
16:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 380 | 273 | 0 | 0 | 0 | 32 | 121 | 0 | 0 | 14 | 17 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 28 | 761 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 607 | 8 | 18 | 0 | 122 | 0 | 230 | 0 | 12 | 182 | 33 | 0 | 50 | 0 | 36 | 8 | 0 | 42 | 0 | 31 | 0 | 310 | 320 | 384 | 25 | 29 | 30 | 5 | 113 | 21 | 0 | 50 | 30 | 0 | 16 | 163 | 0 | 50 | 65 | 10 | 1 | 21.02 | 0 | 5581.02 | 916 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.11 | 380 | 0 | 814.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 25.14 | 161 | 0 | 0 | 0 | 175 | 0 | 357 | 0 | 2.32 | 2.5 | 170 | 62 | 0 | 14 | 0 | 0 | 0 | 2.5 | 50 | 0.27 | 0 | 180 | 5 | 63 | 205 | 0 | 0 | 560 | 0 | 4556.96 | 10137.98 | 88.35
17:00 | 0 | 20 | 8 | 110 | 0 | 130 | 0 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 312 | 0 | 0 | 0 | 32 | 319 | 0 | 0 | 5 | 25 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 0 | 1 | 40 | 0 | 28 | 780 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 606 | 3 | 51 | 0 | 163 | 0 | 230 | 0 | 29 | 185 | 33 | 0 | 50 | 0 | 42 | 18 | 0 | 42 | 0 | 11 | 0 | 305 | 320 | 340 | 34 | 29 | 30 | 5 | 113 | 21 | 0 | 86 | 30 | 0 | 16 | 163 | 0 | 88 | 70 | 18 | 0 | 7.67 | 1 | 6021.67 | 916 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.37 | 380 | 0 | 812.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 7 | 200 | 0 | 0 | 0 | 176 | 0 | 395 | 0 | 0.73 | 2.5 | 172 | 62 | 35 | 5 | 80 | 0 | 0 | 0.9 | 22 | 0.1 | 0 | 150 | 5 | 63 | 220 | 0 | 0 | 560 | 0 | 4621.26 | 10642.93 | 88.34
18:00 | 0 | 50 | 17 | 110 | 0 | 130 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 36 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 278 | 0 | 0 | 0 | 30 | 319 | 0 | 0 | 0 | 64 | 11.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 30 | 821 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 652 | 0 | 51 | 0 | 167 | 0 | 220 | 0 | 29 | 182 | 33 | 22 | 50 | 0 | 38 | 18 | 34 | 46 | 0 | 0 | 0 | 300 | 320 | 340 | 34 | 29 | 30 | 5 | 80 | 21 | 0 | 86 | 30 | 0 | 16 | 162 | 0 | 89 | 130 | 11 | 0 | 0.1 | 12 | 6092.6 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 429 | 0 | 810.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 175 | 0 | 329 | 0 | 0.01 | 2.5 | 170 | 62 | 70 | 0 | 113 | 0 | 0 | 0 | 1 | 0 | 0 | 200 | 6 | 63 | 220 | 0 | 0 | 580 | 0 | 4605.01 | 10697.61 | 88.33
19:00 | 0 | 17 | 25 | 110 | 0 | 130 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 293 | 0 | 0 | 0 | 24 | 323 | 0 | 0 | 0 | 70 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 30 | 825 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 700 | 0 | 31 | 0 | 120 | 0 | 230 | 0 | 10 | 183 | 33 | 41 | 50 | 0 | 38 | 18 | 0 | 46 | 0 | 0 | 0 | 280 | 320 | 383 | 25 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 16 | 162 | 0 | 87 | 85 | 23 | 0 | 0 | 12 | 6036 | 876 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 922.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 393 | 0 | 0 | 2.5 | 168 | 62 | 35 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 60 | 220 | 0 | 0 | 640 | 0 | 4774.9 | 10810.9 | 88.32
19:30 | 0 | 17 | 25 | 110 | 0 | 130 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 264 | 0 | 0 | 0 | 24 | 326 | 0 | 0 | 0 | 44 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 30 | 825 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 720 | 0 | 51 | 0 | 180 | 0 | 230 | 0 | 14 | 182 | 33 | 16 | 50 | 0 | 38 | 13 | 0 | 46 | 0 | 0 | 0 | 260 | 320 | 383 | 34 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 16 | 162 | 0 | 89 | 85 | 31 | 0 | 0 | 12 | 6188 | 876 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 920.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 174 | 0 | 391 | 0 | 0 | 2.5 | 169 | 62 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 63 | 220 | 0 | 0 | 700 | 0 | 4782.66 | 10970.66
20:00 | 0 | 17 | 17 | 110 | 0 | 131 | 0 | 0 | 407 | 0 | 0 | 0 | 10 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 302 | 0 | 0 | 0 | 32 | 326 | 0 | 0 | 0 | 35 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 36 | 825 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 677 | 0 | 51 | 0 | 185 | 0 | 230 | 30 | 26 | 183 | 33 | 0 | 50 | 0 | 39 | 18 | 0 | 46 | 0 | 0 | 0 | 280 | 320 | 384 | 35 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 18 | 162 | 0 | 89 | 65 | 32 | 0 | 0 | 12 | 6237 | 876 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 822.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 168 | 0 | 393 | 0 | 0 | 2.5 | 169 | 62 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 63 | 220 | 0 | 0 | 700 | 0 | 4647.78 | 10884.78 | 88.31
21:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 313 | 0 | 0 | 0 | 32 | 326 | 0 | 0 | 0 | 35 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 36 | 823 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 601 | 0 | 51 | 0 | 182 | 0 | 230 | 95 | 29 | 203 | 33 | 0 | 50 | 0 | 38 | 18 | 0 | 46 | 0 | 0 | 0 | 310 | 320 | 385 | 35 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 18 | 162 | 0 | 89 | 65 | 43 | 0 | 0 | 0 | 6255.5 | 922 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 827.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 167 | 0 | 414 | 0 | 0 | 2.5 | 167 | 62 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 63 | 220 | 0 | 0 | 700 | 0 | 4714.21 | 10969.71 | 88.3
22:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 282 | 0 | 0 | 0 | 32 | 332 | 0 | 0 | 0 | 35 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 36 | 900 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 601 | 0 | 51 | 0 | 151 | 0 | 230 | 100 | 29 | 151 | 34 | 0 | 50 | 0 | 39 | 18 | 0 | 48 | 0 | 0 | 0 | 310 | 320 | 385 | 35 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 18 | 162 | 0 | 89 | 65 | 47 | 0 | 0 | 0 | 6267.5 | 922 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 826.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 165 | 0 | 371 | 0 | 0 | 2.5 | 170 | 61 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 65 | 220 | 0 | 0 | 700 | 0 | 4663.74 | 10931.24 | 88.29
23:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 389 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 298 | 0 | 0 | 0 | 32 | 333 | 0 | 0 | 0 | 17 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 37 | 810 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 602 | 0 | 51 | 0 | 16 | 0 | 230 | 18 | 29 | 221 | 34 | 0 | 50 | 0 | 38 | 18 | 0 | 46 | 0 | 0 | 0 | 295 | 320 | 385 | 33 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 18 | 162 | 0 | 65 | 45 | 45 | 0 | 0 | 2 | 5926.5 | 923 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 826.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 164 | 0 | 376 | 0 | 0 | 2.5 | 171 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 65 | 220 | 0 | 0 | 700 | 0 | 4584.29 | 10510.79 | 88.28
Total KWH | 0 | 280320 | 204960 | 2597700 | 0 | 3118938 | 0 | 0 | 8899200 | 0 | 0 | 0 | 165960 | 0 | 706464 | 69600 | 0 | 0 | 0 | 0 | 482040 | 0 | 8760000 | 6943156 | 0 | 0 | 0 | 693500 | 4218411 | 0 | 0 | 233750 | 661200 | 391800 | 415800 | 0 | 0 | 0 | 0 | 0 | 0 | 53760 | 0 | 0 | 0 | 356160 | 0 | 28441 | 964000 | 0 | 839520 | 19112727.27 | 0 | 0 | 0 | 0 | 0 | 3456847 | 0 | 0 | 0 | 15932726 | 143100 | 885348 | 0 | 1472000 | 0 | 4703500 | 282000 | 490560 | 4688000 | 728064 | 93120 | 1256790 | 0 | 546840 | 337000 | 74100 | 1093440 | 0 | 515827 | 0 | 7200500 | 7585600 | 8812000 | 548568 | 711000 | 699720 | 115296 | 2363564 | 397692 | 0 | 1174080 | 591456 | 0 | 420000 | 3404230 | 0 | 1590000 | 1524000 | 527040 | 15450 | 339560 | 95520 | 135011945.27 | 22013090 | 6302304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685440 | 9476364 | 0 | 19796467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769610 | 0 | 426000 | 4330273 | 0 | 0 | 0 | 4076509 | 0 | 8577745.5 | 0 | 36300 | 76914 | 4058000 | 1445236 | 245940 | 220820 | 702796 | 0 | 0 | 41317.44 | 1162800 | 4440 | 0 | 4473000 | 133946 | 1728000 | 5123240 | 0 | 0 | 16110545.45 | 0 | 112017097.39 | 247029042.66

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-03-2025 | during | 08-03-2025 | during | 08-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 130 | 130 | 230 | 230 | 130 | 130 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 110 | 110 | 110 | 110 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 406 | 409 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 290 | 264 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 15 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 24 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 13 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 44 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1510 | 1857 | 5124.5 | 5184.5 | 3343.29 | 3403.29
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 146 | 142 | 134 | 134 | 134 | 134 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 34 | 30 | 2 | 16 | 2 | 16 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.05 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 610 | 720 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 2 | 8 | 2 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 765 | 825 | 965 | 965 | 965 | 965 | -
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1619 | 1781 | 3753.91 | 3767.86 | 3753.9 | 3767.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 230 | 230 | 230 | 230 | 230 | 230 | Partial Shutdown due to maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 14 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 55 | 180 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 13 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 38 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 781 | 853 | 1978.97 | 1908.97 | 1840.03 | 1770.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-03-2025 | during | 08-03-2025 | during | 08-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 23 | 31 | 210 | 210 | 33 | 33 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 85 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 50 | 89 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.23 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 160.23 | 217 | 652.7 | 601.5 | 475.7 | 424.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 113 | 163 | 163 | 113 | 113 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 23 | 34 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 20 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 163 | 162 | 162 | 162 | 164 | 164 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 260 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 383 | 400 | 400 | 385 | 385 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Machine Problem
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1477 | 1480 | 1652 | 1652 | 1551 | 1551
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 340 | 306 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.04 | 0 | 89 | 0 | 89 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 378 | 382 | 1234.2 | 1234.2 | 610 | 610 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1732.04 | 1564 | 3601.2 | 3512.2 | 2351.02 | 2262.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 0 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 65 | 63 | 67 | 67 | 67 | 67 | GT-02 air filter change
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 700 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 230 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1040.65 | 1213 | 2109.12 | 2108.12 | 2069.12 | 2068.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 163 | 182 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 156 | 174 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 392 | 391 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.92 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 816.28 | 920.16 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.07 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1714.77 | 1669.66 | 3107.48 | 2940.78 | 2845.7 | 2679
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 65 | 62 | 62 | 62 | 62 | 62 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 168 | 169 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 176 | 0 | 189 | 0 | 189 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 482.2 | 336 | 705.6 | 480 | 685.62 | 460.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 10516.89 | 10970.66 | 22685.48 | 22155.93 | 18915.38 | 18385.84
Forecast Scenario (08-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11570 |  | 0 |  | 11570
|  |  |  | 1:00 | 11070 |  | 0 |  | 11070
|  |  |  | 2:00 | 10850 |  | 0 |  | 10850
|  |  |  | 3:00 | 10900 |  | 0 |  | 10900
|  |  |  | 4:00 | 11110 |  | 0 |  | 11110
|  |  |  | 5:00 | 10100 |  | 0 |  | 10100
|  |  |  | 6:00 | 9300 |  | 0 |  | 9300
|  |  |  | 7:00 | 9400 |  | 0 |  | 9400
|  |  |  | 8:00 | 9950 |  | 0 |  | 9950
|  |  |  | 9:00 | 10200 |  | 0 |  | 10200
|  |  |  | 10:00 | 10725 |  | 0 |  | 10725
|  |  |  | 11:00 | 10900 |  | 0 |  | 10900
|  |  |  | 12:00 | 11350 |  | 0 |  | 11350
|  |  |  | 13:00 | 11850 |  | 0 |  | 11850
|  |  |  | 14:00 | 11800 |  | 0 |  | 11800
|  |  |  | 15:00 | 11900 |  | 0 |  | 11900
|  |  |  | 16:00 | 11750 |  | 0 |  | 11750
|  |  |  | 17:00 | 11500 |  | 0 |  | 11500
|  |  |  | 18:00 | 11950 |  | 0 |  | 11950
|  |  |  | 18:30 | 12400 |  | 0 |  | 12400
|  |  |  | 19:00 | 12500 |  | 0 |  | 12500
|  |  |  | 19:30 | 12400 |  | 0 |  | 12400
|  |  |  | 20:00 | 12350 |  | 0 |  | 12350
|  |  |  | 21:00 | 12200 |  | 0 |  | 12200
|  |  |  | 22:00 | 12000 |  | 0 |  | 12000
|  |  |  | 23:00 | 11800 |  | 0 |  | 11800
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 11350.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 269.025 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:30 hrs on 08-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10516.89 | MW | 12:00 Hr. | Energy Generated |  |  | 247.029 |  | MKWHr.
| Day Peak Demand |  |  | 10516.89 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10970.66 | MW | 19:30 Hr. | Energy Demand |  |  | 247.029 |  | MKWHr.
| Evening Peak Demand |  |  | 10970.66 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 8668.42 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 944.94 |  | MMCFD
| Maximum Generation of the Day |  |  | 11039.27 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.5153 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.5205 | 0 | 2.0885 | 0 | 0 | 0.23375 | 0 | 0 | 38.8428 | Gas | 120.5599 | Gas | 431389931.625
| Chattogram Zone |  |  | 4.2964 | 35.0455 | 0.35616 | 0 | 0.964 | 0.17154 | 0 | 0.05376 | 40.8873 | Coal | 70.6086 | Coal | 506468547.7981
| Cumilla Zone |  |  | 14.8433 | 0 | 0.71406 | 0 | 0 | 0.51583 | 1.0934 | 0 | 17.1666 | HFO | 7.317 | HFO | 124295427.44
| Mymensingh Zone |  |  | 0.52704 | 0 | 3.2095 | 0 | 0 | 0.35501 | 0 | 0 | 4.0916 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.0237 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 6.3023 | 9.4764 | 0 | 0 | 0 | 0.68544 | 22.0131 | 0 | 38.4772 | Solar | 4.6229 | Solar | 74641251.0084
| Barishal Zone |  |  | 6.9852 | 20.5835 | 0 | 0 | 0 | 0.00444 | 0 | 0 | 27.5732 | Import | 42.903 | Import | 224764942.93
| Rajshahi Zone |  |  | 17.0614 | 0 | 0 | 0 | 0 | 1.2319 | 19.7965 | 0 | 38.0898 | Wind | 0.05376 | Wind | 787046.4
| Rangpur Zone |  |  | 0 | 5.5032 | 0.94874 | 0 | 0 | 1.4249 | 0 | 0 | 7.8769
| Total |  |  | 120.5599 | 70.6086 | 7.317 | 0 | 0.964 | 4.6229 | 42.903 | 0.05376 | 247.029
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431389931.625 |  | Hydro | 96400
|  |  |  | Coal | 506468547.7981 |  | Solar | 74641251.0084
|  |  |  | HFO | 124295427.44 |  | Import | 224764942.93
|  |  |  | HSD | 0 |  | Wind | 787046.4
[5 empty] | Total: | 136,24,43,547 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0131 | Peak Hr Flow | 876.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10730127 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 19.7965 | Peak Hr Flow | 920.16 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 612 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0934 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 962 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.903 | Peak Hr Flow | 1842.16 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3767
|  |  |  | Chattogram |  | 0 |  | 1088
|  |  |  | Cumilla |  | 0 |  | 944
|  |  |  | Mymensingh |  | 0 |  | 955
|  |  |  | Sylhet |  | 0 |  | 380
|  |  |  | Khulna |  | 0 |  | 1231
|  |  |  | Barishal |  | 0 |  | 299
|  |  |  | Rajshahi |  | 0 |  | 1111
|  |  |  | Rangpur |  | 0 |  | 702
|  |  |  | Total |  | 0 |  | 10477
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1281.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:20 |  | Bakulia 132/33kV S/S T-4 (432T) HT Project Work S/D Due to Installation of AVR at 132KV
RTCC panel & Tr. Differential Relay (P-642) at Relay panel.
| 09:20 |  | Bakulia 132/33kV S/S T-4 (432T) HT Project Work S/D Due to Installation of AVR at 132KV
RTCC panel & Tr. Differential Relay (P-642) at Relay panel.
| 09:38 | 12:53 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Scheduled S/D Due to To Connect Rajendrapur Line
Conductor With Bus-1.
| 10:21 | 11:17 | BIPTC S/S 10CF15 Forced S/D Due to Shutdown is taken for emergency maintenance work
| 11:06 | 16:18 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Forced S/D from Cumilla(N) 230/132/33kV end Due to
Isulator (Q89L) T-Phase Red hot.
| 11:20 |  | Ishwardi-Natore 132kV Ckt-1 Project Work S/D from Natore 132/33kV end Due to
Reconductoring. and from Ishurdi 132/33kV end Due to Re-conductoring Work
| 11:43 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:- FGMO Minimum @10:48 hrs
| 12:00 |  | Day peak Generation is 10514 MW
| 14:21 | 15:40 | Jaldhaka 132/33kV S/S 406T-1 LT Scheduled S/D Due to 33kv Bus Section-1 maintenance by | [7 empty] | 25.0MW load
|  |  | PBS | [7 empty] | interrup.
| 14:22 | 15:40 | Jaldhaka 132/33kV S/S 406T-1 HT Scheduled S/D Due to 33kv Bus Section-1 maintenance by | [7 empty] | 25.0MW load
|  |  | PBS | [7 empty] | interrup.
| 15:43 | 20:41 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D Due to Work at Power
Station End.
| 15:43 |  | Siddhirganj CCPP 335 MW ST was sync.
| 19:30 |  | Evening Peak Generation: 10970 MW.
| 19:43 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 06:00 |  | Min. Gen. 8360 MW
| 06:18 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 06:18 |  | Ashuganj South 360MW GT tripped.
| 07:24 | 07:37 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing OC/EF, ABC inst. fault relays Due to
Pran Jamuna-2, 33 kv feeder CT blust B phase
| 07:24 | 07:37 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Trip relay-1, OC/EF relays Due to Pran
Jamuna-2 33 kv feeder CT blust B phase
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 130 | 3118938 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2597700 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 409 | 8899200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8760000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 264 | 6943156 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 4218411 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 69600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 391800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 415800 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 482040 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 693500 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 204960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 706464 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 280320 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 233750 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 165960 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 44 | 661200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 1857 | 38842799
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 143100 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 142 | 3456847 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 356160 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 839520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 28441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Fuel shortage as BPDB payment not done in time
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 720 | 15932726 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 53760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 825 | 19112727.27 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 1781 | 40887281.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4688000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 230 | 4703500 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 282000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 728064 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 14 | 490560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 1472000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 885348 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1256790 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1093440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 337000 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 74100 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 546840 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 93120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 515827 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 853 | 17166589
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 31 | 527040 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 85 | 1524000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1590000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 339560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 95520 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 217 | 4091570
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 711000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 699720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2363564 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 34 | 548568 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 115296 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 20 | 591456 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1174080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 162 | 3404230 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 420000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 397692 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7200500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 8812000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7585600 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1480 | 34023706
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 22013090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 306 | 6302304 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 685440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 382 | 9476364 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1564 | 38477198
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 0 | 133946 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 63 | 1728000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 700 | 16110545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5123240 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 230 | 4473000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4440 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1213 | 27573171.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4330273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 174 | 4076509 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 391 | 8577745.5 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 76914 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 920.16 | 19796467 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 426000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 769610 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1669.66 | 38089818.5
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1445236 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 169 | 4058000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 702796 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41317.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 245940 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 220820 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1162800 | -
Rangpur Area Total |  |  |  |  | 950 | 336 | 7876909.44
Eastern Grid Total |  |  |  |  | 16921.242 | 6188 | 135011945.27
Western Grid Total |  |  |  |  | 11614.5 | 4782.66 | 112017097.39
National Grid Total |  |  |  |  | 28535.742 | 10970.66 | 247029042.66
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-03-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7133.79 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3343.2 | MW
i) Dhaka area |  |  | 3766.89 |  | MW | i) Khulna area |  |  |  | 1231 | MW
ii) Chattogram area |  |  | 1087.9 |  | MW | ii) Barishal area |  |  |  | 299 | MW
iii) Cumilla area |  |  | 944 |  | MW | iii) Rajshahi area |  |  |  | 1111.2 | MW
iv) Mymensingh area |  |  | 955 |  | MW | iv) Rangpur area |  |  |  | 702 | MW
v) Sylhet area |  |  | 380 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10476.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 74 | 18:00 | 133 | Payra | 20 | 00:00
2 | AKSML | 15 | 00:00 | 68 | Jamalpur | 104 | 04:00 | 134 | Postogola | 39 | 00:00
3 | Aftabnagar | 27 | 21:00 | 69 | Jashore | 107 | 18:30 | 135 | Purbachal | 14 | 00:00
4 | Agargaon | 76 | 20:00 | 70 | Jhenaidah | 97 | 18:00 | 136 | Purbasadipur | 121 | 12:00
5 | Agrabad | 76 | 00:00 | 71 | Joydebpur | 117 | 00:00 | 137 | Rahanpur | 11.5 | 10:00
6 | Amnura | 50 | 09:00 | 72 | Joypurhat | 61 | 09:00 | 138 | Rahim | 25 | 00:00
7 | Ashuganj | 72 | 00:00 | 73 | Juldah | 17 | 19:00 | 139 | Rajbari | 50 | 03:00
8 | BSRM | 191 | 11:00 | 74 | KSRM | 32 | 20:00 | 140 | Rajendrapur | 94 | 18:00
9 | Bagerhat | 65 | 19:00 | 75 | Kabirpur | 193 | 00:00 | 141 | Rajshahi | 85 | 04:00
10 | Bajitpur | 35 | 18:30 | 76 | Kachua | 58 | 18:30 | 142 | Rajshahi-230 | 57 | 22:00
11 | Bakulia | 80 | 00:00 | 77 | Kallyanpur | 81 | 21:00 | 143 | Ramganj | 86 | 20:00
12 | Banani | 18 | 19:00 | 78 | Kalurghat | 30 | 00:00 | 144 | Rampur | 36 | 00:00
13 | Bangabhaban | 4 | 11:00 | 79 | Kamrangirchar | 60 | 00:00 | 145 | Rangamati | 13 | 18:30
14 | Barapukuria | 56 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 120 | 18:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 81 | 00:00 | 147 | Ruppur | 5.2 | 11:00
16 | Barishal | 74 | 19:00 | 82 | Keranigonj | 65 | 00:00 | 148 | SSM | 11 | 07:00
17 | Barishal-230 | 64 | 19:00 | 83 | Khagrachori | 26 | 18:30 | 149 | Saidpur | 94 | 13:00
18 | Baroaulia | 48 | 00:00 | 84 | Khosba | 27 | 13:00 | 150 | Satkhira | 97 | 18:30
19 | Baroirhat | 40 | 18:30 | 85 | Khulna | 66 | 19:00 | 151 | Satmasjid | 74 | 13:00
20 | Bashundhara | 132 | 13:00 | 86 | Khulshi | 148 | 00:00 | 152 | Savar | 136 | 00:00
21 | BashundharaCement | 8 | 07:00 | 87 | Kishoreganj | 108 | 13:00 | 153 | SevenRings | 20.63 | 09:00
22 | Beanibazar | 44 | 18:30 | 88 | Kodda | 239 | 00:00 | 154 | ShahCement | 38 | 11:00
23 | Benapole | 50 | 09:00 | 89 | Kulaura | 30 | 18:00 | 155 | Shahjadpur | 63 | 07:00
24 | Bhaluka | 110 | 18:00 | 90 | Kurigram | 62 | 17:00 | 156 | Shahjibazar | 93 | 22:00
25 | Bhandaria | 37 | 22:00 | 91 | Kushtia | 104 | 19:30 | 157 | Shahmirpur | 37 | 01:00
26 | Bhangura | 33 | 09:00 | 92 | Lalbag | 67 | 00:00 | 158 | Shariatpur | 53 | 21:00
27 | Bheramara(GK) | 42 | 18:00 | 93 | Lalmonirhat | 46 | 18:00 | 159 | Sherpur | 146 | 17:00
28 | Bhulta | 242 | 00:00 | 94 | MI_Cement | 16.7 | 19:30 | 160 | Shikalbaha | 26 | 00:00
29 | Bog-Sherpur | 70 | 04:00 | 95 | Madanganj | 38 | 16:00 | 161 | Shitalakhya | 50.6 | 00:00
30 | Bogura | 122 | 04:00 | 96 | Madaripur | 72 | 19:00 | 162 | Sholosohor | 33 | 00:00
31 | Borhanuddin | 57 | 22:00 | 97 | Madartek | 65.69 | 22:00 | 163 | Shyampur | 166 | 10:00
32 | Brahmanbaria | 91 | 21:00 | 98 | Madunaghat | 39 | 00:00 | 164 | Siddhirganj | 96 | 00:00
33 | Cantonment | 90 | 19:30 | 99 | Magura | 45 | 19:00 | 165 | Sirajganj | 82 | 07:00
34 | Chandpur | 46 | 04:00 | 100 | Mahasthangarh | 62 | 04:00 | 166 | Sonargaon | 95 | 00:00
35 | Chandraghona | 28 | 18:30 | 101 | Manikganj | 109 | 19:30 | 167 | Sreemongol | 47 | 00:00
36 | Chapai | 54 | 04:00 | 102 | Maniknagar | 48 | 00:00 | 168 | Sreepur | 67 | 09:00
37 | Charsaidpur | 39 | 03:00 | 103 | Matarbari | 39 | 04:00 | 169 | Srinagar | 33.31 | 13:00
38 | Chauddagram | 57 | 13:00 | 104 | Matuail | 50 | 01:00 | 170 | Sunamganj | 38 | 19:00
39 | Chhatak | 26 | 20:00 | 105 | Millgate | 60 | 00:00 | 171 | Sylhet | 30 | 13:00
40 | Chowmuhani | 152 | 18:00 | 106 | Mirpur | 99 | 13:00 | 172 | Sylhet-132 | 74 | 22:00
41 | Chuadanga | 73 | 03:00 | 107 | Mirsorai | 8 | 00:00 | 173 | TK | 24 | 01:00
42 | Coxsbazar | 108 | 21:00 | 108 | Mirzapur | 40 | 04:00 | 174 | Tangail | 141 | 12:00
43 | Cumilla(N) | 120 | 13:00 | 109 | Mithapukur | 53 | 17:00 | 175 | Thakurgaon | 80 | 17:00
44 | Cumilla(S) | 115 | 00:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 85 | 11:00
45 | Daudkandi | 108 | 00:00 | 111 | Mogbazar | 95.4 | 13:00 | 177 | Ullahpara | 31 | 08:00
46 | Dhaka | 22 | 11:00 | 112 | Mongla | 38 | 00:00 | 178 | Ullon | 36 | 19:00
47 | Dhamrai | 84 | 00:00 | 113 | Motijheel | 26 | 21:00 | 179 | Uttara | 61 | 19:30
48 | Dhanmondi | 92 | 12:00 | 114 | Muktagacha | 32 | 17:00 | 180 | UttaraNew | 35 | 13:00
49 | Dohazari | 79 | 18:30 | 115 | Munshiganj | 70 | 00:00 | 181 | Zigatola | 58 | 13:00
50 | Faridpur | 101 | 19:00 | 116 | Muradnagar | 17 | 04:00
51 | Fatullah | 69 | 00:00 | 117 | Mymensingh | 180 | 18:00
52 | Fenchuganj | 24 | 04:00 | 118 | Naogaon | 116 | 04:00
53 | Feni | 81 | 18:30 | 119 | Narail | 42 | 18:30
54 | GPH | 34 | 01:00 | 120 | Narinda | 45 | 12:00
55 | Ghatail | 66 | 17:00 | 121 | Narshingdi | 140 | 00:00
56 | Ghorashal | 10 | 21:00 | 122 | Natore | 117 | 18:00
57 | Ghorashal-230 | 74 | 00:00 | 123 | Nawabganj | 39.8 | 13:00
58 | Goalpara | 22 | 02:00 | 124 | Netrakona | 136 | 18:00
59 | Gollamari | 50 | 19:00 | 125 | New | 61 | 00:00
60 | Gopalganj | 77 | 21:00 | 126 | Niamatpur | 96 | 08:00
61 | Gulshan | 66 | 19:00 | 127 | Noapara | 30 | 19:00
62 | Halishahar | 45 | 09:00 | 128 | PHP | 8 | 08:00
63 | HaripurSBU | 139 | 06:00 | 129 | Pabna | 82 | 03:00
64 | Hasnabad | 55 | 00:00 | 130 | Palashbari | 100 | 10:00
65 | Hathazari | 59 | 19:00 | 131 | Panchagarh | 45 | 18:00
66 | Ishurdi | 54 | 19:00 | 132 | Patuakhali | 53 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11039.27 | 0 |  | 11039.27
1:00 | 10555.71 | 0 |  | 10555.71
2:00 | 10118.96 | 0 |  | 10118.96
3:00 | 10235.62 | 0 |  | 10235.62
4:00 | 10935.01 | 0 |  | 10935.01
5:00 | 9721.28 | 0 |  | 9721.28
6:00 | 8861.25 | 0 |  | 8861.25
7:00 | 8668.42 | 0 |  | 8668.42
8:00 | 8901.18 | 0 |  | 8901.18
9:00 | 9287.48 | 0 |  | 9287.48
10:00 | 9720.87 | 0 |  | 9720.87
11:00 | 9955.91 | 0 |  | 9955.91
12:00 | 10516.89 | 0 |  | 10516.89
13:00 | 10882.12 | 0 |  | 10882.12
14:00 | 9744.8 | 0 |  | 9744.8
15:00 | 9929.28 | 0 |  | 9929.28
16:00 | 10137.98 | 0 |  | 10137.98
17:00 | 10642.93 | 0 |  | 10642.93
18:00 | 10697.61 | 0 |  | 10697.61
19:00 | 10810.9 | 0 |  | 10810.9
19:30 | 10970.66 | 0 |  | 10970.66
20:00 | 10884.78 | 0 |  | 10884.78
21:00 | 10969.71 | 0 |  | 10969.71
22:00 | 10931.24 | 0 |  | 10931.24
23:00 | 10510.79 | 0 |  | 10510.79
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6080.5 | 4958.77 | 11039.27 | DAILY GENERATION CURVE
00:30 | 5980 | 4817.49 | 10797.49
01:00 | 5879.5 | 4676.21 | 10555.71 | 07-03-2025
01:30 | 5727.5 | 4609.835 | 10337.335
02:00 | 5575.5 | 4543.46 | 10118.96
02:30 | 5653.5 | 4523.79 | 10177.29
03:00 | 5731.5 | 4504.12 | 10235.62
03:30 | 5937 | 4648.315 | 10585.315
04:00 | 6142.5 | 4792.51 | 10935.01
04:30 | 5720.25 | 4607.895 | 10328.145
05:00 | 5298 | 4423.28 | 9721.28
05:30 | 5036 | 4255.265 | 9291.265
06:00 | 4774 | 4087.25 | 8861.25
06:30 | 4662.61 | 4102.225 | 8764.835
07:00 | 4551.22 | 4117.2 | 8668.42
07:30 | 4620.1 | 4164.7 | 8784.8
08:00 | 4688.98 | 4212.2 | 8901.18
08:30 | 4817.64 | 4276.69 | 9094.33
09:00 | 4946.3 | 4341.18 | 9287.48
09:30 | 5051.195 | 4452.98 | 9504.175
10:00 | 5156.09 | 4564.78 | 9720.87
10:30 | 5225.765 | 4612.625 | 9838.39
11:00 | 5295.44 | 4660.47 | 9955.91
11:30 | 5421.335 | 4815.065 | 10236.4
12:00 | 5547.23 | 4969.66 | 10516.89
12:30 | 5657.895 | 5041.61 | 10699.505
13:00 | 5768.56 | 5113.56 | 10882.12
13:30 | 5452.875 | 4860.585 | 10313.46
14:00 | 5137.19 | 4607.61 | 9744.8
14:30 | 5250.095 | 4586.945 | 9837.04
15:00 | 5363 | 4566.28 | 9929.28
15:30 | 5472.01 | 4561.62 | 10033.63
16:00 | 5581.02 | 4556.96 | 10137.98
16:30 | 5801.345 | 4589.11 | 10390.455
17:00 | 6021.67 | 4621.26 | 10642.93
17:30 | 6057.135 | 4613.135 | 10670.27
18:00 | 6092.6 | 4605.01 | 10697.61
18:30 | 6064.3 | 4689.955 | 10754.255
19:00 | 6036 | 4774.9 | 10810.9
19:30 | 6188 | 4782.66 | 10970.66
20:00 | 6237 | 4647.78 | 10884.78
20:30 | 6246.25 | 4680.995 | 10927.245 |  | Executive Engineer
21:00 | 6255.5 | 4714.21 | 10969.71 |  | Network Operation Division
21:30 | 6261.5 | 4688.975 | 10950.475
22:00 | 6267.5 | 4663.74 | 10931.24
22:30 | 6097 | 4624.015 | 10721.015
23:00 | 5926.5 | 4584.29 | 10510.79

## En-Curve
QF-LDC-12
Date | 07-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3605 | 1650 | 915 | 0 | 52 | 910.27 | 40 | 3432 | 0 | 68 | 367 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3603.5 | 1599 | 915.5 | 0 | 49 | 866.49 | 40 | 3321.5 | 0 | 64 | 338.5 | 0 | 0 | 0 | 0 | 07-03-2025
01:00 | 3602 | 1548 | 916 | 0 | 46 | 822.71 | 40 | 3211 | 0 | 60 | 310 | 0 | 0 | 0 | 0
01:30 | 3471.5 | 1499.5 | 917 | 0 | 44 | 819.835 | 40 | 3191 | 0 | 60 | 294.5 | 0 | 0 | 0 | 0 | Energy Generated | 247.029 |  | MKWHr
02:00 | 3341 | 1451 | 918 | 0 | 42 | 816.96 | 40 | 3171 | 0 | 60 | 279 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3318.5 | 1511.5 | 918.5 | 0 | 42 | 816.29 | 40 | 3186.5 | 0 | 60 | 284 | 0 | 0 | 0 | 0 | Total Energy Requirement | 247.029 |  | MKWHr
03:00 | 3296 | 1572 | 919 | 0 | 42 | 815.62 | 40 | 3202 | 0 | 60 | 289 | 0 | 0 | 0 | 0
03:30 | 3433.5 | 1603 | 919 | 0 | 43 | 815.315 | 40 | 3309 | 0 | 91.5 | 329 | 0 | 0 | 2 | 0
04:00 | 3571 | 1634 | 919 | 0 | 44 | 815.01 | 40 | 3416 | 0 | 123 | 369 | 0 | 0 | 4 | 0
04:30 | 3449 | 1533.25 | 919 | 0 | 44 | 815.395 | 40 | 3199 | 0 | 61.5 | 263.5 | 0 | 0 | 3.5 | 0
05:00 | 3327 | 1432.5 | 919 | 0 | 44 | 815.78 | 40 | 2982 | 0 | 0 | 158 | 0 | 0 | 3 | 0
05:30 | 3106.5 | 1368 | 922.5 | 0 | 42 | 815.265 | 40 | 2856 | 0 | 0 | 139 | 0 | 0 | 2 | 0
06:00 | 2886 | 1303.5 | 926 | 0 | 40 | 814.75 | 40 | 2730 | 0 | 0 | 120 | 0 | 0 | 1 | 0
06:30 | 2795 | 1287 | 922 | 0 | 41 | 816.265 | 40 | 2718 | 26.57 | 5 | 113.5 | 0 | 0 | 0.5 | 0
07:00 | 2704 | 1270.5 | 918 | 0 | 42 | 817.78 | 40 | 2706 | 53.14 | 10 | 107 | 0 | 0 | 0 | 0
07:30 | 2710 | 1303 | 893.5 | 0 | 42 | 818.715 | 40 | 2719.5 | 137.585 | 13.5 | 107 | 0 | 0 | 0 | 0
08:00 | 2716 | 1335.5 | 869 | 0 | 42 | 819.65 | 40 | 2733 | 222.03 | 17 | 107 | 0 | 0 | 0 | 0
08:30 | 2839.5 | 1343.5 | 868.5 | 0 | 40 | 817.79 | 40 | 2706 | 311.04 | 21 | 107 | 0 | 0 | 0 | 0
09:00 | 2963 | 1351.5 | 868 | 0 | 38 | 815.93 | 40 | 2679 | 400.05 | 25 | 107 | 0 | 0 | 0 | 0
09:30 | 3027 | 1378.9 | 891.5 | 0 | 41 | 816.085 | 40 | 2686.5 | 481.19 | 25 | 117 | 0 | 0 | 0 | 0
10:00 | 3091 | 1406.3 | 915 | 0 | 44 | 816.24 | 40 | 2694 | 562.33 | 25 | 127 | 0 | 0 | 0 | 0
10:30 | 3116.5 | 1454.8 | 915.5 | 0 | 48 | 815.5 | 40 | 2708.5 | 602.59 | 25 | 112 | 0 | 0 | 0 | 0
11:00 | 3142 | 1503.3 | 916 | 0 | 52 | 814.76 | 40 | 2723 | 642.85 | 25 | 97 | 0 | 0 | 0 | 0
11:30 | 3263.5 | 1602.9 | 916 | 0 | 54 | 815.52 | 40 | 2729.5 | 661.48 | 36.5 | 117 | 0 | 0 | 0 | 0
12:00 | 3385 | 1702.5 | 916 | 0 | 56 | 816.28 | 40 | 2736 | 680.11 | 48 | 137 | 0 | 0 | 0 | 0
12:30 | 3365 | 1723.5 | 916 | 0 | 55 | 814.215 | 40 | 2879.5 | 665.29 | 58 | 182.5 | 0 | 0 | 0.5 | 0
13:00 | 3345 | 1744.5 | 916 | 0 | 54 | 812.15 | 40 | 3023 | 650.47 | 68 | 228 | 0 | 0 | 1 | 0
13:30 | 3202 | 1583.5 | 916 | 0 | 52 | 812.945 | 40 | 2827 | 616.015 | 55.5 | 203.5 | 0 | 0 | 5 | 0
14:00 | 3059 | 1422.5 | 916 | 0 | 50 | 813.74 | 40 | 2631 | 581.56 | 43 | 179 | 0 | 0 | 9 | 0
14:30 | 3184 | 1444 | 915.5 | 0 | 49 | 813.285 | 40 | 2673.5 | 503.755 | 38 | 162.5 | 0 | 0 | 13.5 | 0
15:00 | 3309 | 1465.5 | 915 | 0 | 48 | 812.83 | 40 | 2716 | 425.95 | 33 | 146 | 0 | 0 | 18 | 0
15:30 | 3385.5 | 1560.5 | 915.5 | 0 | 45 | 813.475 | 40 | 2718 | 345.155 | 37 | 157 | 0 | 0 | 16.5 | 0
16:00 | 3462 | 1655.5 | 916 | 0 | 42 | 814.12 | 40 | 2720 | 264.36 | 41 | 168 | 0 | 0 | 15 | 0
16:30 | 3576.5 | 1773 | 916 | 0 | 42 | 813.39 | 40 | 2715 | 182.065 | 55 | 267 | 0 | 0 | 10.5 | 0
17:00 | 3691 | 1890.5 | 916 | 0 | 42 | 812.66 | 40 | 2710 | 99.77 | 69 | 366 | 0 | 0 | 6 | 0
17:30 | 3608 | 1805.75 | 919.5 | 0 | 44 | 811.57 | 40 | 2812 | 50.95 | 108 | 467 | 0 | 0 | 3.5 | 0
18:00 | 3525 | 1721 | 923 | 0 | 46 | 810.48 | 40 | 2914 | 2.13 | 147 | 568 | 0 | 0 | 1 | 0
18:30 | 3555 | 1688.75 | 899.5 | 0 | 46 | 866.44 | 40 | 3012 | 1.065 | 129.5 | 515.5 | 0 | 0 | 0.5 | 0
19:00 | 3585 | 1656.5 | 876 | 0 | 46 | 922.4 | 40 | 3110 | 0 | 112 | 463 | 0 | 0 | 0 | 0
19:30 | 3720 | 1791.5 | 876 | 0 | 46 | 920.16 | 40 | 3088 | 0 | 86 | 403 | 0 | 0 | 0 | 0
20:00 | 3763 | 1895.5 | 876 | 0 | 46 | 822.28 | 40 | 3020 | 0 | 69 | 353 | 0 | 0 | 0 | 0
20:30 | 3821 | 1916.75 | 899 | 0 | 46 | 824.995 | 40 | 2979 | 0 | 64.5 | 336 | 0 | 0 | 0 | 0
21:00 | 3879 | 1938 | 922 | 0 | 46 | 827.71 | 40 | 2938 | 0 | 60 | 319 | 0 | 0 | 0 | 0
21:30 | 3836.5 | 1922 | 922 | 0 | 47 | 826.975 | 40 | 2976.5 | 0 | 60 | 319.5 | 0 | 0 | 0 | 0
22:00 | 3794 | 1906 | 922 | 0 | 48 | 826.24 | 40 | 3015 | 0 | 60 | 320 | 0 | 0 | 0 | 0
22:30 | 3781 | 1836.5 | 922.5 | 0 | 47 | 826.515 | 40 | 2948 | 0 | 38.5 | 281 | 0 | 0 | 0 | 0
23:00 | 3768 | 1767 | 923 | 0 | 46 | 826.79 | 40 | 2881 | 0 | 17 | 242 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 06:00 | 391 | 12:00 | Payra | 420 | 05:00 | 415 | 13:00
Ashuganj | 412 | 18:00 | 393 | 13:00 | Rahanpur | 405 | 02:00 | 399 | 09:00
Bhulta | 408 | 18:00 | 394 | 14:00 | Rampal | 412 | 06:00 | 402 | 16:00
Bibiana | 401 | 19:30 | 392 | 00:00
BIPTC | 398 | 04:00 | 389 | 12:00
Bogura | 394 | 02:00 | 385 | 10:00
Gopalganj | 412 | 07:00 | 402 | 14:00
Kaliakoir | 388 | 18:00 | 374 | 16:00
Madunaghat | 403 | 07:00 | 396 | 00:00
Meghnaghat | 400 | 06:00 | 392 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 05:00 | 229 | 11:00 | Keranigonj | 233 | 06:00 | 227 | 12:00
AKSML | 235 | 09:00 | 228 | 01:00 | Khulna(S) | 240 | 05:00 | 231 | 13:00
Aminbazar | 235 | 05:00 | 230 | 00:00 | Madunaghat | 235 | 05:00 | 230 | 00:00
Ashuganj | 236 | 19:00 | 228 | 00:00 | Madunaghat-400 | 236 | 08:00 | 231 | 00:00
Ashuganj-400 | 236 | 19:00 | 228 | 00:00 | Maniknagar | 231 | 18:00 | 224 | 11:00
Baghabari | 239 | 07:00 | 232 | 10:00 | Meghnaghat | 238 | 21:00 | 231 | 00:00
Barapukuria | 227 | 18:30 | 218 | 16:00 | Meghnaghat-400 | 233 | 18:30 | 228 | 00:00
Barapukuria-230 | 227 | 18:30 | 218 | 16:00 | Mirsorai | 232 | 07:00 | 225 | 00:00
Barishal | 241 | 06:00 | 236 | 12:00 | Rajshahi | 237 | 06:00 | 230 | 11:00
Bheramara | 237 | 05:00 | 230 | 11:00 | Rampal | 238 | 05:00 | 230 | 12:00
Bhulta | 234 | 18:00 | 226 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 18:30 | 225 | 01:00 | Rampura | 232 | 19:30 | 224 | 11:00
BIPTC | 239 | 05:00 | 230 | 11:00 | Shikalbaha | 233 | 09:00 | 227 | 00:00
Bogura | 239 | 02:00 | 233 | 10:00 | Shyampur | 232 | 05:00 | 227 | 00:00
Bogura-400 | 238 | 02:00 | 233 | 09:00 | Siddhirganj | 239 | 09:00 | 226 | 00:00
Borhanuddin | 245 | 06:00 | 238 | 19:00 | Sirajgonj | 243 | 05:00 | 238 | 11:00
BSRM | 232 | 19:30 | 226 | 00:00 | Sreepur | 236 | 18:30 | 227 | 11:00
Cumilla(N) | 229 | 07:00 | 223 | 13:00 | Tongi | 229 | 04:00 | 223 | 00:00
Faridpur | 240 | 06:00 | 233 | 13:00
Fenchuganj | 235 | 19:30 | 229 | 17:00
Ghorashal | 235 | 01:00 | 220 | 00:00
Ghorashal-230 | 233 | 18:30 | 226 | 11:00
Gopalganj | 238 | 06:00 | 232 | 11:00
GPH | 233 | 05:00 | 228 | 00:00
Haripur | 232 | 18:30 | 226 | 00:00
Hasnabad | 233 | 05:00 | 228 | 00:00
Hathazari | 235 | 06:00 | 229 | 00:00
Ishurdi | 239 | 05:00 | 233 | 10:00
Jhenaidah | 238 | 05:00 | 227 | 13:00
Kaliakoir | 235 | 18:00 | 227 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 19:30 | 131 | 11:00 | Madunaghat | 135 | 07:00 | 132 | 00:00
Agargaon | 142 | 21:00 | 130 | 17:00 | Magura | 139 | 05:00 | 131 | 13:00
Agrabad | 134 | 05:00 | 131 | 00:00 | Mahasthangarh | 135 | 06:00 | 128 | 10:00
AKS | 132 | 18:00 | 128 | 00:00 | Manikganj | 134 | 18:00 | 127 | 03:00
Aminbazar | 138 | 05:00 | 134 | 11:00 | Maniknagar | 131 | 05:00 | 127 | 11:00
Amnura | 138 | 05:00 | 131 | 17:00 | Matarbari | 126 | 06:00 | 118 | 13:00
Ashuganj | 139 | 18:30 | 135 | 00:00 | Matuail | 135.5 | 18:30 | 131 | 00:00
Bagerhat | 137 | 05:00 | 130 | 19:00 | Millgate | 135 | 06:00 | 130 | 00:00
Bajitpur | 133 | 18:00 | 129 | 09:00 | Mirpur | 138 | 04:00 | 133 | 11:00
Bakulia | 136 | 07:00 | 132 | 00:00 | Mirzapur | 134 | 18:30 | 125 | 09:00
Banani | 135 | 05:00 | 131 | 11:00 | Mithapukur | 139 | 18:30 | 123 | 16:00
Bangabhaban | 132 | 18:30 | 127 | 00:00 | MI_Cement | 136 | 06:00 | 132 | 01:00
Barapukuria | 141 | 18:30 | 132 | 16:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 138 | 05:00 | 135 | 15:00 | Mogbazar | 136 | 06:00 | 132 | 11:00
Barishal | 137 | 06:00 | 132 | 12:00 | Mongla | 137 | 05:00 | 130 | 13:00
Barishal-230 | 137 | 06:00 | 132 | 13:00 | Motijheel | 132 | 18:30 | 127 | 00:00
Baroaulia | 133 | 20:00 | 130 | 00:00 | Muktagacha | 134 | 18:00 | 120 | 09:00
Baroirhat | 128 | 06:00 | 123 | 04:00 | Munshiganj | 135 | 18:00 | 130 | 00:00
Bashundhara | 136 | 18:00 | 129 | 13:00 | Muradnagar | 132 | 07:00 | 125 | 13:00
BashundharaCement | 135 | 18:30 | 130 | 00:00 | Mymensingh | 136 | 18:30 | 117 | 13:00
Beanibazar | 133 | 06:00 | 130 | 10:00 | Naogaon | 133 | 02:00 | 126 | 10:00
Benapole | 139 | 05:00 | 126 | 13:00 | Narail | 138 | 05:00 | 130 | 11:00
Bhaluka | 130 | 02:00 | 123 | 09:00 | Narinda | 131 | 18:00 | 127 | 12:00
Bhandaria | 135 | 05:00 | 129 | 13:00 | Narshingdi | 134 | 18:00 | 125 | 11:00
Bhangura | 137 | 02:00 | 131 | 11:00 | Natore | 137 | 06:00 | 131 | 16:00
Bheramara | 138 | 01:00 | 135 | 10:00 | Nawabganj | 138 | 03:00 | 133 | 12:00
Bheramara(GK) | 138 | 02:00 | 135 | 10:00 | Netrakona | 124 | 00:00 | 115 | 11:00
Bhulta | 131 | 18:00 | 124 | 00:00 | New | 136 | 05:00 | 131 | 11:00
Bog-Sherpur | 135 | 02:00 | 130 | 10:00 | Niamatpur | 138 | 05:00 | 135 | 07:00
Bogura | 136 | 05:00 | 131 | 10:00 | Noapara | 138 | 01:00 | 131 | 13:00
Bogura-230 | 136 | 01:00 | 131 | 10:00 | Pabna | 138 | 02:00 | 134 | 10:00
Brahmanbaria | 133 | 23:00 | 126 | 14:00 | Palashbari | 129 | 01:00 | 119 | 10:00
Cantonment | 141 | 05:00 | 137 | 11:00 | Panchagarh | 138 | 18:00 | 122 | 16:00
Chandpur | 128 | 18:00 | 116 | 12:00 | Patuakhali | 137 | 05:00 | 134 | 15:00
Chandraghona | 136 | 06:00 | 132 | 00:00 | Payra | 139 | 06:00 | 136 | 13:00
Chapai | 135 | 01:00 | 131 | 07:00 | PHP | 128 | 07:00 | 119 | 13:00
Charsaidpur | 136 | 18:30 | 131 | 11:00 | Postogola | 138 | 06:00 | 133 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 129 | 07:00 | 121 | 12:00 | Purbachal | 137 | 19:00 | 130 | 13:00
Chhatak | 133 | 06:00 | 130 | 00:00 | Purbasadipur | 134 | 18:30 | 121 | 10:00
Chowmuhani | 123 | 18:00 | 116 | 00:00 | Rahanpur | 139 | 06:00 | 136 | 09:00
Chuadanga | 138 | 01:00 | 129 | 17:00 | Rahanpur-400 | 139 | 01:00 | 136 | 10:00
Coxsbazar | 125 | 08:00 | 117 | 00:00 | Rahim | 134 | 07:00 | 130 | 00:00
Cumilla(N) | 133 | 07:00 | 127 | 13:00 | Rajbari | 135 | 06:00 | 129 | 12:00
Cumilla(S) | 132 | 04:00 | 126 | 12:00 | Rajendrapur | 136 | 18:30 | 127 | 00:00
Daudkandi | 131 | 06:00 | 125 | 00:00 | Rajshahi | 138 | 05:00 | 132 | 17:00
Dhaka | 136 | 05:00 | 131 | 11:00 | Rajshahi-230 | 137 | 02:00 | 123 | 10:00
Dhamrai | 135 | 18:00 | 130 | 10:00 | Ramganj | 123 | 06:00 | 115 | 14:00
Dhanmondi | 136 | 06:00 | 132 | 00:00 | Rampur | 134 | 07:00 | 130 | 00:00
Dohazari | 132 | 06:00 | 126 | 00:00 | Rampura | 135 | 05:00 | 131 | 11:00
Faridpur | 135 | 07:00 | 130 | 13:00 | Rangamati | 135 | 06:00 | 131 | 00:00
Fatullah | 137 | 18:30 | 132 | 00:00 | Rangpur | 133 | 06:00 | 123 | 16:00
Fenchuganj | 136 | 19:30 | 132 | 02:00 | Ruppur | 140 | 05:00 | 136 | 10:00
Feni | 126 | 06:00 | 120 | 00:00 | Saidpur | 135 | 18:30 | 123 | 09:00
Ghatail | 133 | 18:30 | 120 | 16:00 | Satkhira | 137 | 05:00 | 129 | 18:00
Ghorashal | 141 | 19:30 | 134 | 13:00 | Satmasjid | 141 | 06:00 | 137 | 11:00
Goalpara | 139 | 05:00 | 131 | 18:00 | Savar | 136 | 02:00 | 132 | 11:00
Gollamari | 140 | 06:00 | 133 | 13:00 | SevenRings | 141 | 18:30 | 136 | 00:00
Gopalganj | 140 | 06:00 | 134 | 11:00 | ShahCement | 136 | 18:30 | 131 | 11:00
Gopalganj-400 | 141 | 06:00 | 136 | 11:00 | Shahjadpur | 138 | 00:00 | 135 | 06:00
Gulshan | 135 | 05:00 | 130 | 11:00 | Shahjibazar | 133 | 19:30 | 126 | 14:00
Halishahar | 135 | 07:00 | 129 | 01:00 | Shahmirpur | 135 | 10:00 | 132 | 00:00
Haripur | 136 | 18:30 | 132 | 00:00 | Shariatpur | 140 | 05:00 | 133 | 13:00
HaripurSBU | 136 | 18:30 | 132 | 01:00 | Sherpur | 136 | 04:00 | 118 | 11:00
Hasnabad | 137 | 04:00 | 133 | 00:00 | Shikalbaha | 125 | 07:00 | 120 | 00:00
Hathazari | 137 | 08:00 | 132 | 00:00 | Shikalbaha-230 | 137 | 07:00 | 129 | 04:00
Ishurdi | 140 | 01:00 | 136 | 11:00 | Shitalakhya | 136 | 06:00 | 131 | 00:00
Jaldhaka | 133 | 18:30 | 121 | 10:00 | Sholosohor | 135 | 06:00 | 131 | 00:00
Jamalpur | 139 | 18:30 | 121 | 09:00 | Shyampur | 136 | 18:00 | 128 | 10:00
Jashore | 140 | 05:00 | 129 | 13:00 | Shyampur-230 | 136 | 06:00 | 132 | 00:00
Jhenaidah | 140 | 05:00 | 131 | 10:00 | Siddhirganj | 136 | 18:30 | 131 | 00:00
Jhenaidah-230 | 139 | 02:00 | 132 | 13:00 | Sirajganj | 135 | 06:00 | 130 | 07:00
Joydebpur | 139 | 18:00 | 130 | 10:00 | Sonargaon | 136 | 18:00 | 129 | 00:00
Joypurhat | 132 | 02:00 | 123 | 09:00 | Sreemongol | 133 | 19:00 | 128 | 11:00
Juldah | 135 | 08:00 | 131 | 13:00 | Sreepur | 133 | 18:30 | 126 | 11:00
Kabirpur | 135 | 18:30 | 127 | 16:00 | Srinagar | 138 | 05:00 | 133 | 13:00
Kachua | 128 | 06:00 | 118 | 13:00 | SSM | 136 | 18:30 | 134 | 00:00
Kaliakoir | 139 | 18:00 | 131 | 16:00 | Sunamganj | 131 | 05:00 | 128 | 12:00
Kallyanpur | 138 | 04:00 | 134 | 00:00 | Sylhet | 133 | 07:00 | 130 | 11:00
Kalurghat | 134 | 07:00 | 131 | 00:00 | Sylhet-132 | 133 | 03:00 | 131 | 12:00
Kamrangirchar | 138 | 03:00 | 132 | 12:00 | Tangail | 132 | 18:30 | 123 | 11:00
Kaptai | 137 | 8:00 | 134 | 5:00 | Thakurgaon | 137 | 18:00 | 120 | 16:00
Kazla | 132 | 19:00 | 126 | 00:00 | TK | 135 | 07:00 | 131 | 00:00
Keranigonj | 138 | 05:00 | 134 | 00:00 | Tongi | 137 | 04:00 | 132 | 15:00
Khagrachori | 134 | 06:00 | 131 | 00:00 | Ullahpara | 137 | 03:00 | 133 | 09:00
Khosba | 131 | 06:00 | 125 | 00:00 | Ullon | 135 | 05:00 | 131 | 11:00
Khulna | 138 | 05:00 | 130 | 13:00 | Uttara | 138 | 06:00 | 133 | 12:00
Khulna(S) | 140 | 05:00 | 132 | 13:00 | UttaraNew | 135 | 06:00 | 130 | 00:00
Khulshi | 133 | 04:00 | 129 | 00:00 | Zigatola | 138 | 06:00 | 134 | 00:00
Kishoreganj | 131 | 21:00 | 121 | 09:00
Kodda | 136 | 19:00 | 126 | 15:00
KSRM | 135 | 19:30 | 132 | 00:00
Kulaura | 134 | 02:00 | 132 | 11:00
Kurigram | 134 | 18:30 | 119 | 16:00
Kushtia | 138 | 01:00 | 134 | 11:00
Lalbag | 138 | 06:00 | 134 | 00:00
Lalmonirhat | 134 | 18:00 | 122 | 16:00
Madanganj | 135 | 18:30 | 130 | 00:00
Madaripur | 138 | 01:00 | 135 | 13:00
Madartek | 134 | 05:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division