## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-03-2025 | during | 09-03-2025 | during | 09-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 150 | 150 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 110 | 110 | 110 | 110 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 310 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 319 | 322 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25 | 21 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 32 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 88 | 121 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 70 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 30 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1983 | 2211 | 5124.5 | 5184.5 | 3443.29 | 3503.29
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 134 | 134 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 6 | 16 | 7 | 32 | 7 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.05 | 0 | 4.05 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 145 | 145 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 720 | 1150 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 0 | 8 | 0 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 635 | 343 | 575 | 575 | 300 | 300 | -
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1587 | 1758 | 3366.91 | 3393.86 | 3117.91 | 3144.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 213 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 230 | 225 | 230 | 230 | 230 | 230 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 90 | 250 | 356.56 | 356.56 | 320 | 320 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 9 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 45 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 46 | 50 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 855 | 1082 | 2335.53 | 2265.53 | 2080.03 | 2010.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-03-2025 | during | 09-03-2025 | during | 09-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 28 | 210 | 210 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 105 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 89 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.22 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 171.22 | 234 | 651.7 | 601.5 | 476.7 | 426.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 29 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 21 | 49 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 34 | 29 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 163 | 163 | 162 | 162 | 164 | 164 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 353 | 400 | 400 | 400 | 400 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1439 | 1411 | 1650 | 1650 | 1614 | 1614
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 922 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 281 | 236 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 422 | 582 | 1234.2 | 1234.2 | 610 | 610 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1716 | 1694 | 3565.2 | 3470.2 | 2215.02 | 2120.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 55 | 55 | 67 | 67 | 67 | 67 | GT-02 air filter change
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 660 | 1100 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 275 | 303 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.63 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1105.63 | 1575 | 2109.12 | 2108.12 | 2069.12 | 2068.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 214 | 149 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 136 | 144 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.63 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 820.18 | 1259.5 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.87 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1771.18 | 1969 | 3107.28 | 2940.78 | 2845.5 | 2679
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 65 | 64 | 62 | 62 | 62 | 62 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 172 | 170 | 170 | 120 | 120 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.3 | 0 | 6.1 | 0 | 6.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 54 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 180 | 0 | 192 | 0 | 192 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 450.3 | 360 | 722.1 | 494 | 638.12 | 410.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 11078.33 | 12294 | 22632.34 | 22108.49 | 18499.69 | 17975.84
Forecast Scenario (09-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11600 |  | 0 |  | 11600
|  |  |  | 1:00 | 10720 |  | 0 |  | 10720
|  |  |  | 2:00 | 10446 |  | 0 |  | 10446
|  |  |  | 3:00 | 10848 |  | 0 |  | 10848
|  |  |  | 4:00 | 10870 |  | 0 |  | 10870
|  |  |  | 5:00 | 10020 |  | 0 |  | 10020
|  |  |  | 6:00 | 9338 |  | 0 |  | 9338
|  |  |  | 7:00 | 9323 |  | 0 |  | 9323
|  |  |  | 8:00 | 9930 |  | 0 |  | 9930
|  |  |  | 9:00 | 10689 |  | 0 |  | 10689
|  |  |  | 10:00 | 11203 |  | 0 |  | 11203
|  |  |  | 11:00 | 11698 |  | 0 |  | 11698
|  |  |  | 12:00 | 12064 |  | 0 |  | 12064
|  |  |  | 13:00 | 12220 |  | 0 |  | 12220
|  |  |  | 14:00 | 12231 |  | 0 |  | 12231
|  |  |  | 15:00 | 11985 |  | 0 |  | 11985
|  |  |  | 16:00 | 11973 |  | 0 |  | 11973
|  |  |  | 17:00 | 11955 |  | 0 |  | 11955
|  |  |  | 18:00 | 11822 |  | 0 |  | 11822
|  |  |  | 18:30 | 12700 |  | 0 |  | 12700
|  |  |  | 19:00 | 12800 |  | 0 |  | 12800
|  |  |  | 19:30 | 12750 |  | 0 |  | 12750
|  |  |  | 20:00 | 12700 |  | 0 |  | 12700
|  |  |  | 21:00 | 12645 |  | 0 |  | 12645
|  |  |  | 22:00 | 12519 |  | 0 |  | 12519
|  |  |  | 23:00 | 11859 |  | 0 |  | 11859
Probable Maximum Temperature: |  |  | 31.80°C
Probable Maximum Demand at Day Peak: |  |  | 12064.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 273.458 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:21 hrs on 09-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-03-2025 | [28 empty] | Date: | 08-03-2025 | [28 empty] | Date: | 08-03-2025 | [28 empty] | Date: | 08-03-2025 | [28 empty] | Date: | 08-03-2025 | [18 empty] | Date: | 08-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 288 | 0 | 0 | 0 | 32 | 333 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 732 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 601 | 0 | 51 | 0 | 8 | 0 | 230 | 55 | 29 | 182 | 34 | 0 | 50 | 0 | 37 | 18 | 0 | 44 | 0 | 0 | 0 | 295 | 320 | 385 | 35 | 30 | 30 | 5 | 80 | 21 | 0 | 86 | 20 | 0 | 18 | 162 | 0 | 45 | 8 | 56 | 0 | 0 | 0 | 5590.5 | 923 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 826.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 140 | 0 | 340 | 0 | 0 | 2.5 | 172 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 65 | 220 | 0 | 0 | 620 | 0 | 4400.65 | 9991.15 | 88.27
01:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 374 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 278 | 0 | 0 | 0 | 32 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 640 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 601 | 0 | 10 | 0 | 8 | 0 | 230 | 60 | 29 | 182 | 34 | 0 | 50 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 300 | 320 | 385 | 35 | 30 | 30 | 5 | 80 | 21 | 0 | 5 | 20 | 0 | 18 | 162 | 0 | 8 | 8 | 71 | 0 | 0 | 0 | 5223.5 | 922 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 825.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 314 | 0 | 0 | 2.5 | 168 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 65 | 220 | 0 | 0 | 600 | 0 | 4201.89 | 9425.39 | 88.26
02:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 289 | 0 | 0 | 0 | 32 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 638 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 603 | 0 | 10 | 0 | 8 | 0 | 150 | 60 | 18 | 182 | 34 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 295 | 320 | 321 | 5 | 30 | 30 | 5 | 80 | 21 | 0 | 5 | 20 | 0 | 18 | 162 | 0 | 8 | 8 | 68 | 0 | 0 | 0 | 4930.5 | 922 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 821.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 314 | 0 | 0 | 2.5 | 168 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 65 | 180 | 0 | 0 | 600 | 0 | 4157.72 | 9088.22 | 88.25
03:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 304 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 320 | 0 | 0 | 0 | 33 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 638 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 606 | 0 | 10 | 0 | 8 | 0 | 150 | 60 | 10 | 211 | 32 | 0 | 50 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 300 | 320 | 322 | 5 | 30 | 30 | 5 | 113 | 21 | 0 | 5 | 20 | 0 | 18 | 162 | 0 | 24 | 24 | 67 | 0 | 0 | 0 | 5150.5 | 923 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 822.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 148 | 0 | 378 | 0 | 0 | 2.5 | 166 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 65 | 180 | 0 | 0 | 600 | 0 | 4247.69 | 9398.19 | 88.24
04:00 | 0 | 5 | 0 | 110 | 0 | 130 | 0 | 0 | 362 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 340 | 280 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 583 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 605 | 0 | 25 | 0 | 8 | 0 | 230 | 60 | 20 | 186 | 34 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 310 | 320 | 381 | 32 | 30 | 30 | 5 | 113 | 21 | 0 | 86 | 20 | 0 | 18 | 161 | 0 | 75 | 75 | 68 | 0 | 0 | 0 | 5515.5 | 923 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 818.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 165 | 0 | 346 | 0 | 0 | 2.5 | 171 | 62 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 65 | 220 | 0 | 0 | 650 | 0 | 4568.36 | 10083.86 | 88.23
05:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 298 | 0 | 0 | 0 | 33 | 280 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 602 | 0 | 10 | 0 | 8 | 0 | 170 | 60 | 19 | 202 | 5 | 0 | 30 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 305 | 320 | 288 | 5 | 10 | 30 | 5 | 80 | 21 | 0 | 5 | 20 | 0 | 18 | 161 | 0 | 45 | 0 | 68 | 0 | 0 | 0 | 4840.5 | 923 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 821.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 353 | 0 | 0 | 2.5 | 155 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 55 | 180 | 0 | 0 | 560 | 0 | 4243.63 | 9084.13 | 88.21
06:00 | 0 | 0 | 0 | 110 | 0 | 100 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 240 | 0 | 0 | 0 | 33 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 603 | 0 | 10 | 0 | 8 | 0 | 150 | 80 | 5 | 155 | 5 | 0 | 30 | 0 | 0 | 11 | 0 | 38 | 0 | 0 | 0 | 255 | 300 | 287 | 5 | 10 | 20 | 5 | 80 | 8 | 0 | 5 | 8 | 0 | 18 | 161 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 4409.5 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 822.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 250 | 0 | 0 | 2.5 | 155 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 55 | 180 | 0 | 0 | 500 | 0 | 3951.29 | 8360.79 | 88.2
07:00 | 0 | 0 | 0 | 110 | 0 | 130 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 240 | 0 | 0 | 0 | 33 | 240 | 0 | 0 | 2 | 0 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 605 | 3 | 10 | 0 | 45 | 0 | 150 | 0 | 5 | 195 | 5 | 0 | 30 | 0 | 0 | 11 | 0 | 34 | 0 | 7 | 0 | 175 | 320 | 380 | 5 | 10 | 20 | 5 | 80 | 8 | 0 | 5 | 8 | 0 | 18 | 161 | 0 | 4 | 3 | 69 | 0 | 3.78 | 0 | 4458.28 | 923 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.95 | 388 | 0 | 821.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 4.07 | 146 | 0 | 0 | 0 | 140 | 0 | 280 | 0 | 0.34 | 2.5 | 157 | 64 | 0 | 2 | 0 | 0 | 0 | 0.3 | 13 | 0.05 | 0 | 150 | 5 | 55 | 220 | 0 | 0 | 500 | 0 | 4085.58 | 8543.86 | 88.2
08:00 | 0 | 0 | 8 | 110 | 0 | 131 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 306 | 0 | 0 | 0 | 25 | 240 | 0 | 0 | 10 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 602 | 9 | 10 | 0 | 45 | 0 | 230 | 0 | 18 | 208 | 31 | 0 | 50 | 0 | 0 | 11 | 0 | 34 | 0 | 24 | 0 | 255 | 320 | 380 | 5 | 10 | 20 | 5 | 80 | 8 | 0 | 5 | 20 | 0 | 18 | 161 | 0 | 24 | 19 | 62 | 1 | 16.68 | 0 | 4956.18 | 876 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.58 | 383 | 0 | 825.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 16.47 | 205 | 0 | 0 | 0 | 140 | 0 | 330 | 0 | 1.39 | 2.5 | 155 | 65 | 0 | 8 | 0 | 0 | 0 | 1.6 | 54 | 0.18 | 0 | 150 | 4 | 55 | 220 | 0 | 0 | 500 | 0 | 4284.27 | 9240.45 | 88.19
09:00 | 0 | 0 | 17 | 110 | 0 | 130 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 288 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 19 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 3 | 510 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 600 | 15 | 28 | 0 | 45 | 0 | 230 | 20 | 28 | 194 | 28 | 0 | 50 | 0 | 0 | 11 | 0 | 36 | 0 | 42 | 0 | 315 | 320 | 332 | 31 | 30 | 30 | 5 | 113 | 16 | 0 | 83 | 20 | 0 | 18 | 162 | 0 | 24 | 24 | 62 | 1 | 28.18 | 0 | 5364.68 | 875 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.99 | 381 | 0 | 818.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 30.78 | 214 | 0 | 0 | 0 | 140 | 0 | 370 | 0 | 2.77 | 2.5 | 153 | 66 | 0 | 17 | 0 | 0 | 0 | 2.8 | 101 | 0.34 | 0 | 200 | 4 | 55 | 180 | 0 | 0 | 540 | 0 | 4600.15 | 9964.83 | 88.18
10:00 | 0 | 0 | 17 | 110 | 0 | 130 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 288 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 25 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 5 | 517 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 600 | 18 | 51 | 0 | 45 | 0 | 230 | 60 | 28 | 187 | 28 | 0 | 50 | 0 | 0 | 11 | 0 | 40 | 0 | 55 | 0 | 310 | 320 | 335 | 34 | 30 | 30 | 0 | 113 | 16 | 0 | 86 | 20 | 0 | 18 | 163 | 0 | 45 | 45 | 28 | 2 | 38.43 | 0 | 5455.43 | 921 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 381 | 0 | 816.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 46.02 | 214 | 0 | 0 | 0 | 140 | 0 | 370 | 0 | 4.06 | 5.5 | 160 | 64 | 0 | 24 | 0 | 0 | 0 | 4.6 | 140 | 0.5 | 0 | 200 | 4 | 55 | 180 | 0 | 0 | 600 | 0 | 4806.98 | 10262.41 | 88.17
11:00 | 0 | 0 | 17 | 110 | 0 | 150 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 297 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 29 | 17 | 27 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 6 | 534 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 700 | 20 | 51 | 0 | 45 | 0 | 230 | 70 | 28 | 191 | 29 | 0 | 50 | 0 | 0 | 18 | 0 | 40 | 0 | 63 | 0 | 310 | 320 | 384 | 34 | 29 | 30 | 2 | 40 | 16 | 0 | 83 | 30 | 0 | 18 | 163 | 0 | 45 | 45 | 30 | 2 | 46.28 | 0 | 5787.28 | 922 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 380 | 0 | 814.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 56.16 | 214 | 0 | 0 | 0 | 152 | 0 | 414 | 0 | 4.84 | 5.5 | 168 | 65 | 0 | 29 | 0 | 0 | 0 | 5.5 | 165 | 0.59 | 0 | 250 | 4 | 55 | 150 | 0 | 0 | 630 | 0 | 4959.55 | 10746.83 | 88.16
12:00 | 0 | 0 | 17 | 110 | 0 | 150 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 305 | 0 | 0 | 0 | 16 | 319 | 0 | 0 | 30 | 30 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 6 | 635 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 720 | 20 | 51 | 0 | 45 | 0 | 230 | 90 | 29 | 213 | 32 | 0 | 50 | 0 | 0 | 5 | 0 | 46 | 0 | 64 | 0 | 305 | 320 | 387 | 34 | 29 | 30 | 5 | 21 | 16 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 45 | 45 | 30 | 2 | 49.22 | 0 | 6035.22 | 922 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 422 | 0 | 820.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 62.87 | 214 | 0 | 0 | 0 | 136 | 0 | 414 | 0 | 5.63 | 5.5 | 170 | 65 | 0 | 32 | 0 | 0 | 0 | 3.3 | 180 | 0.63 | 0 | 275 | 5 | 55 | 110 | 0 | 0 | 660 | 0 | 5043.11 | 11078.33 | 88.15
13:00 | 0 | 0 | 17 | 110 | 0 | 150 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 0 | 0 | 0 | 30 | 316 | 0 | 0 | 30 | 51 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 10 | 635 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 872 | 20 | 51 | 0 | 45 | 0 | 230 | 80 | 29 | 206 | 32 | 0 | 50 | 0 | 0 | 18 | 0 | 50 | 0 | 66 | 0 | 320 | 320 | 387 | 34 | 29 | 30 | 0 | 20 | 16 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 45 | 45 | 28 | 2 | 43.75 | 0 | 6202.75 | 923 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.79 | 423 | 0 | 907.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 60.62 | 205 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 5.53 | 5.5 | 174 | 65 | 0 | 30 | 0 | 0 | 0 | 6.3 | 172 | 0.61 | 0 | 307 | 5 | 55 | 110 | 0 | 0 | 790 | 0 | 5264.63 | 11467.38 | 88.14
14:00 | 0 | 0 | 8 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 285 | 0 | 0 | 0 | 30 | 314 | 0 | 0 | 26 | 51 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 8 | 690 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 952 | 18 | 51 | 0 | 45 | 0 | 225 | 95 | 28 | 197 | 33 | 0 | 50 | 0 | 0 | 15 | 0 | 50 | 0 | 60 | 0 | 305 | 320 | 387 | 34 | 29 | 30 | 0 | 20 | 16 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 45 | 48 | 28 | 2 | 37.54 | 0 | 6310.54 | 922 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.47 | 501 | 0 | 918.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 54.22 | 194 | 0 | 0 | 0 | 167 | 0 | 414 | 0 | 4.97 | 2.5 | 174 | 64 | 0 | 21 | 0 | 0 | 0 | 5.4 | 152 | 0.54 | 0 | 307 | 5 | 55 | 110 | 0 | 0 | 970 | 0 | 5427.61 | 11738.15 | 88.13
15:00 | 0 | 5 | 8 | 110 | 0 | 150 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 282 | 0 | 0 | 0 | 30 | 315 | 0 | 0 | 12 | 54 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 10 | 583 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 930 | 14 | 51 | 0 | 45 | 0 | 220 | 105 | 29 | 183 | 33 | 0 | 50 | 34 | 11 | 11 | 17 | 50 | 0 | 46 | 0 | 290 | 320 | 388 | 34 | 29 | 30 | 0 | 20 | 16 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 77 | 75 | 27 | 2 | 28.88 | 0 | 6251.88 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.11 | 505 | 0 | 914.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 38.11 | 181 | 0 | 0 | 0 | 165 | 0 | 414 | 0 | 3.72 | 2.5 | 170 | 63 | 0 | 16 | 0 | 0 | 0 | 4 | 119 | 0.42 | 0 | 307 | 5 | 55 | 110 | 0 | 0 | 1040 | 0 | 5428.67 | 11680.55 | 88.12
16:00 | 0 | 17 | 8 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 101 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 299 | 0 | 0 | 0 | 28 | 313 | 0 | 0 | 12 | 54 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 14 | 560 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 908 | 9 | 51 | 0 | 45 | 0 | 225 | 110 | 29 | 212 | 30 | 0 | 50 | 34 | 36 | 17 | 17 | 48 | 0 | 28 | 0 | 315 | 320 | 390 | 34 | 29 | 30 | 0 | 20 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 88 | 75 | 27 | 1 | 18.32 | 1 | 6326.32 | 922 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 440 | 0 | 950.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 25.5 | 173 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 2.24 | 2.5 | 142 | 64 | 0 | 12 | 0 | 0 | 0 | 2.6 | 66 | 0.24 | 0 | 307 | 5 | 55 | 110 | 0 | 0 | 1060 | 0 | 5217.67 | 11543.99 | 88.11
17:00 | 0 | 34 | 8 | 110 | 0 | 150 | 0 | 0 | 403 | 0 | 0 | 0 | 5 | 0 | 105 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 380 | 277 | 0 | 0 | 0 | 27 | 318 | 0 | 0 | 3 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 20 | 560 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1019 | 3 | 51 | 0 | 45 | 0 | 225 | 140 | 23 | 182 | 30 | 19 | 50 | 34 | 37 | 17 | 34 | 46 | 0 | 10 | 0 | 300 | 320 | 387 | 32 | 29 | 30 | 0 | 20 | 16 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 89 | 96 | 25 | 0 | 6.21 | 12 | 6443.21 | 922 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.19 | 545 | 0 | 1113.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8.09 | 168 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0.74 | 2.5 | 130 | 65 | 35 | 5 | 33 | 0 | 0 | 1.2 | 21 | 0.09 | 0 | 217 | 5 | 55 | 110 | 0 | 0 | 1180 | 0 | 5444.82 | 11888.03 | 88.1
18:00 | 0 | 70 | 16 | 110 | 0 | 150 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 0 | 123 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 380 | 250 | 0 | 0 | 0 | 28 | 300 | 0 | 0 | 0 | 90 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 20 | 492 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1063 | 0 | 51 | 0 | 8 | 0 | 195 | 170 | 27 | 174 | 35 | 34 | 50 | 34 | 38 | 17 | 52 | 48 | 0 | 0 | 0 | 315 | 320 | 350 | 10 | 29 | 29 | 5 | 22 | 16 | 0 | 50 | 20 | 0 | 16 | 163 | 0 | 89 | 125 | 22 | 0 | 0.09 | 12 | 6399.09 | 922 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 613 | 0 | 1111.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0.02 | 2.5 | 171 | 63 | 50 | 0 | 70 | 0 | 0 | 0 | 1 | 0 | 0 | 230 | 6 | 55 | 110 | 0 | 0 | 1100 | 0 | 5450.82 | 11849.91 | 88.09
19:00 | 0 | 70 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 121 | 48 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 310 | 0 | 0 | 0 | 32 | 322 | 0 | 0 | 0 | 90 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 16 | 343 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 45 | 0 | 225 | 250 | 9 | 192 | 35 | 34 | 50 | 34 | 38 | 17 | 52 | 50 | 0 | 0 | 0 | 290 | 320 | 353 | 29 | 30 | 29 | 5 | 49 | 16 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 89 | 105 | 28 | 0 | 0 | 12 | 6696 | 876 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 0 | 1259.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 0 | 2.5 | 172 | 64 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 7 | 55 | 110 | 0 | 0 | 1100 | 0 | 5598 | 12294 | 88.08
19:30 | 0 | 70 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 265 | 0 | 0 | 0 | 32 | 325 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 20 | 341 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 45 | 0 | 230 | 290 | 9 | 182 | 35 | 34 | 50 | 34 | 38 | 17 | 34 | 50 | 0 | 0 | 0 | 270 | 320 | 354 | 32 | 30 | 29 | 5 | 49 | 21 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 87 | 85 | 33 | 0 | 0 | 12 | 6599 | 876 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 1257.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 145 | 0 | 414 | 0 | 0 | 2.5 | 173 | 64 | 35 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 55 | 110 | 0 | 0 | 1180 | 0 | 5669.47 | 12268.47
20:00 | 0 | 50 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 300 | 0 | 0 | 0 | 32 | 328 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 25 | 342 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 45 | 0 | 230 | 330 | 29 | 188 | 35 | 27 | 50 | 17 | 39 | 18 | 34 | 50 | 0 | 0 | 0 | 280 | 320 | 353 | 34 | 30 | 29 | 5 | 70 | 21 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 89 | 85 | 33 | 0 | 0 | 12 | 6701 | 876 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524 | 0 | 1261.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 145 | 0 | 414 | 0 | 0 | 2.5 | 167 | 63 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 55 | 110 | 0 | 0 | 1210 | 0 | 5580.48 | 12281.48 | 88.07
21:00 | 0 | 34 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 62 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 280 | 0 | 0 | 0 | 32 | 333 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 26 | 331 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 63 | 0 | 230 | 305 | 29 | 182 | 35 | 0 | 50 | 17 | 38 | 18 | 34 | 52 | 0 | 0 | 0 | 285 | 320 | 370 | 35 | 30 | 30 | 5 | 106 | 21 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 89 | 85 | 34 | 0 | 0 | 12 | 6638 | 922 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523 | 0 | 1268.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 145 | 0 | 414 | 0 | 0 | 2.5 | 167 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 55 | 110 | 0 | 0 | 1244 | 0 | 5633.18 | 12271.18 | 88.06
22:00 | 0 | 34 | 25 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 281 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 60 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 26 | 333 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1068 | 0 | 51 | 0 | 63 | 0 | 230 | 245 | 29 | 182 | 35 | 0 | 50 | 17 | 39 | 18 | 17 | 52 | 0 | 0 | 0 | 285 | 320 | 382 | 35 | 30 | 30 | 5 | 163 | 21 | 0 | 81 | 30 | 0 | 18 | 163 | 0 | 89 | 85 | 34 | 0 | 0 | 12 | 6516 | 922 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 1124.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 0 | 2.5 | 173 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 8 | 55 | 110 | 0 | 0 | 1120 | 0 | 5219.89 | 11735.89 | 88.05
23:00 | 0 | 34 | 25 | 110 | 0 | 150 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 282 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 35 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 33 | 323 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1052 | 0 | 51 | 0 | 8 | 0 | 230 | 280 | 29 | 195 | 35 | 0 | 50 | 0 | 38 | 18 | 0 | 50 | 0 | 0 | 0 | 300 | 320 | 382 | 35 | 30 | 30 | 5 | 163 | 21 | 0 | 81 | 30 | 0 | 18 | 163 | 0 | 89 | 45 | 32 | 0 | 0 | 12 | 6357 | 923 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 1062.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 149 | 0 | 414 | 0 | 0 | 2.5 | 171 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 65 | 119 | 0 | 0 | 1110 | 0 | 5105.22 | 11462.22 | 88.05
Total KWH | 0 | 397440 | 265440 | 2666800 | 0 | 3362406 | 0 | 0 | 9039600 | 0 | 0 | 0 | 207000 | 0 | 1326240 | 231840 | 0 | 0 | 0 | 0 | 495360 | 0 | 9199000 | 6915055 | 0 | 0 | 0 | 673400 | 7300621 | 0 | 0 | 201202 | 816000 | 511200 | 505080 | 0 | 0 | 0 | 0 | 0 | 0 | 41280 | 0 | 0 | 0 | 319680 | 0 | 28199 | 848000 | 0 | 558240 | 12632727.27 | 0 | 0 | 0 | 0 | 0 | 3630032 | 0 | 0 | 0 | 19619998 | 148500 | 943512 | 0 | 769455 | 0 | 5305300 | 2970000 | 557760 | 4619000 | 716040 | 129600 | 1144070 | 248160 | 374640 | 352370 | 265620 | 1063680 | 0 | 469618 | 0 | 7114500 | 7664500 | 9086000 | 625464 | 635000 | 647400 | 76512 | 1800900 | 399744 | 0 | 1389120 | 582912 | 0 | 410000 | 4406130 | 0 | 1316400 | 1291200 | 999360 | 14600 | 310190 | 102960 | 140742057.27 | 22085818 | 6090336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604080 | 10596360 | 0 | 22668979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780400 | 0 | 405000 | 4450827 | 0 | 0 | 0 | 3807136 | 0 | 9225090 | 0 | 36300 | 77436 | 4007000 | 1455272 | 160584 | 199071 | 270422 | 0 | 0 | 37604.52 | 1172160 | 4126 | 0 | 5542000 | 144195 | 1384000 | 3747600 | 0 | 0 | 20340363.64 | 0 | 119292160.16 | 260034217.43

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11078.33 | MW | 12:00 Hr. | Energy Generated |  |  | 260.0342 |  | MKWHr.
| Day Peak Demand |  |  | 11078.33 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.02 |  | MKWHr.
| Evening Peak Generation |  |  | 12294 | MW | 19:00 Hr. | Energy Demand |  |  | 260.0542 |  | MKWHr.
| Evening Peak Demand |  |  | 12294 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.8 |  | °C
| Minimum Generation of the Day |  |  | 8360.79 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 993.37 |  | MMCFD
| Maximum Generation of the Day |  |  | 12294 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.5148 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6685 | 0 | 3.244 | 0 | 0 | 0.2012 | 0 | 0 | 44.1137 | Gas | 126.9985 | Gas | 452569804.38
| Chattogram Zone |  |  | 4.1883 | 32.2527 | 0.31968 | 0 | 0.848 | 0.1767 | 0 | 0.04128 | 37.8267 | Coal | 74.1937 | Coal | 532093513.2063
| Cumilla Zone |  |  | 17.3775 | 0 | 1.018 | 0 | 0 | 0.46962 | 1.0637 | 0 | 19.9288 | HFO | 7.7232 | HFO | 130356110.14
| Mymensingh Zone |  |  | 0.99936 | 0 | 2.7106 | 0 | 0 | 0.32479 | 0 | 0 | 4.0347 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.8382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8382 | Hydro | 0.848 | Hydro | 84800
| Khulna Zone |  |  | 6.0903 | 10.5964 | 0 | 0 | 0 | 0.60408 | 22.0858 | 0 | 39.3766 | Solar | 4.4111 | Solar | 71271075.1972
| Barishal Zone |  |  | 5.2758 | 25.8824 | 0 | 0 | 0 | 0.004126 | 0 | 0 | 31.1623 | Import | 45.8185 | Import | 247062532.53
| Rajshahi Zone |  |  | 17.5605 | 0 | 0 | 0 | 0 | 1.2217 | 22.669 | 0 | 41.4512 | Wind | 0.04128 | Wind | 604339.2
| Rangpur Zone |  |  | 0 | 5.4623 | 0.43101 | 0 | 0 | 1.4088 | 0 | 0 | 7.3021
| Total |  |  | 126.9985 | 74.1937 | 7.7232 | 0 | 0.848 | 4.4111 | 45.8185 | 0.04128 | 260.0342
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 452569804.38 |  | Hydro | 84800
|  |  |  | Coal | 532093513.2063 |  | Solar | 71271075.1972
|  |  |  | HFO | 130356110.14 |  | Import | 247062532.53
|  |  |  | HSD | 0 |  | Wind | 604339.2
[5 empty] | Total: | 143,40,42,174 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0858 | Peak Hr Flow | 876.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 13231436.478 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.669 | Peak Hr Flow | 1259.50 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 800 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0637 | Peak Hr Flow | 50.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 904 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.8185 | Peak Hr Flow | 2185.50 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4428
|  |  |  | Chattogram |  | 0 |  | 1293
|  |  |  | Cumilla |  | 0 |  | 1040
|  |  |  | Mymensingh |  | 0 |  | 1027
|  |  |  | Sylhet |  | 0 |  | 393
|  |  |  | Khulna |  | 0 |  | 1367
|  |  |  | Barishal |  | 0 |  | 334
|  |  |  | Rajshahi |  | 0 |  | 1168
|  |  |  | Rangpur |  | 0 |  | 764
|  |  |  | Total |  | 0 |  | 11814
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1227.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 08:15 |  | Ashuganj South 360 MW GT was sync. at 08:15 hours.
| 08:24 | 15:00 | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to Annual maintenance
| 08:25 | 13:59 | Chandraghona 132/33kV S/S TR-01(406T) HT Scheduled S/D Due to Annual maintenance
| 08:28 | 17:32 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Insulator Disc cleaning
| 09:41 | 15:28 | Sreepur 230/132/33kV S/S 132 kV BUS-2 Scheduled S/D
| 09:48 | 12:19 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
PT Maintenance works by Meghnaghat S/S End. and from Meghnaghat 230/132kV end Due to PT
Oil Leakage maintenance
| 10:22 |  | Bhola Natun Biddut BD LTD GT-12 tripped.
| 11:36 | 13:04 | Rajbari 132/33kV S/S Transformer-2 LT Scheduled S/D Due to SAS INTEGRATION.
| 11:36 | 13:04 | Rajbari 132/33kV S/S Transformer-2 HT Scheduled S/D Due to SAS INTEGRATION.
|  | 11:55 | Tongi 230/132/33kV S/S 230 kV Bus-2 is restored.
| 12:12 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:- FGMO OFF @11:21 hrs on 07.03.2025
| 12:19 | 15:06 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
CVT Oil leakage Maintenance works Meghnaghat S/S end and from Meghnaghat 230/132kV end
Due to CVT oil laekage maintenance
| 12:21 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 12:21 |  | Ashuganj South 360 MW ST was sync.
|  | 16:11 | Mahasthangar-Palashbari 132kV Ckt-1 is restored.
| 17:36 |  | Kushiara 163MW CCPP ST was sync.
| 18:50 |  | Matarbari 2*600 MW (CPGCBL) Shutdown with remarks:- U2
| 18:52 |  | Matarbari 2*600 MW (CPGCBL) Synchronized
| 19:00 |  | Evening peak Generation is 12293 MW
| 22:10 |  | Sonargaon 132/33kV S/S Bashundhara Line Tripped showing 87T Trip P- 632 87N Trip
P-632 REF-2 relays Due to Transformer Tripped.
| 22:12 | 00:34 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing DIR O/C & E/F Relay relays Due to 33 kv | [7 empty] | 12.0MW load
|  |  | Langolbandh and Norsingdhi feeder fault. Auxiliary transformer T-2 fuse R -Y -B phase | [7 empty] | interrup.
burn
| 22:15 | 00:15 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing DIR O/C and E/F Relay. relays Due to 33 kv | [7 empty] | 27.0MW load
|  |  | Astha feed feeder fault. | [7 empty] | interrup.
| 22:21 | 22:27 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Tripped showing O/C relays Due to Fault | [7 empty] | 13.0MW load
interrup.
| 22:21 | 22:27 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Tripped showing O/C and E/F relays Due to fault | [7 empty] | 13.0MW load
interrup.
| 22:21 | 22:26 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Tripped showing o/c relays Due to fault | [7 empty] | 13.0MW load
interrup.
| 22:21 | 22:26 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Tripped showing over current relays Due to fault | [7 empty] | 13.0MW load
interrup.
| 22:30 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT12
| 04:39 | 04:51 | Jamalpur-Mymensingh 132kV Ckt-2 Tripped from Jamalpur 132/33kV end showing Micom relays
Due to Trip
| 06:00 |  | Minimum Generation: 9195 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 150 | 3362406 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2666800 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9039600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9199000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 310 | 6915055 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7300621 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 231840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 511200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 505080 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 495360 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 673400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 265440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 121 | 1326240 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 397440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 201202 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 207000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 816000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2211 | 44113684
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 148500 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 848000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3630032 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 48 | 319680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 16 | 558240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 28199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 19619998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 41280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 343 | 12632727.27 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 1758 | 37826656.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 192 | 4619000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 225 | 5305300 | Partial Shutdown due to maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 250 | 2970000 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 716040 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 9 | 557760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 769455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 943512 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1144070 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 248160 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 50 | 1063680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 352370 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 265620 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 374640 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 129600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 469618 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1082 | 19928825
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 28 | 999360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 105 | 1291200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1316400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 310190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 102960 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 234 | 4034710
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 635000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 647400 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 49 | 1800900 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 29 | 625464 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 76512 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 582912 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1389120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 163 | 4406130 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 410000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 399744 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7114500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 353 | 9086000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7664500 | Machine Problem
Sylhet Area Total |  |  |  |  | 2368.568 | 1411 | 34838182
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 22085818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 236 | 6090336 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 604080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 582 | 10596360 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1694 | 39376594
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 144195 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 55 | 1384000 | GT-02 air filter change
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 20340363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 3747600 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 303 | 5542000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4126 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1575 | 31162284.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 149 | 4450827 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 144 | 3807136 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9225090 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 77436 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1259.5 | 22668979 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 405000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 780400 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1969 | 41451168
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 64 | 1455272 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 172 | 4007000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 270422 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37604.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 54 | 160584 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199071 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1172160 | -
Rangpur Area Total |  |  |  |  | 950 | 360 | 7302113.52
Eastern Grid Total |  |  |  |  | 16921.242 | 6696 | 140742057.27
Western Grid Total |  |  |  |  | 11614.5 | 5598 | 119292160.16
National Grid Total |  |  |  |  | 28535.742 | 12294 | 260034217.43
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-03-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8180.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3633.6 | MW
i) Dhaka area |  |  | 4428.12 |  | MW | i) Khulna area |  |  |  | 1367.2 | MW
ii) Chattogram area |  |  | 1292.8 |  | MW | ii) Barishal area |  |  |  | 334 | MW
iii) Cumilla area |  |  | 1040 |  | MW | iii) Rajshahi area |  |  |  | 1168.4 | MW
iv) Mymensingh area |  |  | 1027 |  | MW | iv) Rangpur area |  |  |  | 764 | MW
v) Sylhet area |  |  | 393 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11814.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 70 | 17:00 | 133 | Payra | 22 | 19:00
2 | AKSML | 18.7 | 14:00 | 68 | Jamalpur | 109 | 18:00 | 134 | Postogola | 44 | 13:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jashore | 117 | 18:00 | 135 | Purbachal | 16 | 22:00
4 | Agargaon | 83 | 21:00 | 70 | Jhenaidah | 100 | 19:00 | 136 | Purbasadipur | 117 | 17:00
5 | Agrabad | 70 | 00:00 | 71 | Joydebpur | 139 | 15:00 | 137 | Rahanpur | 12 | 11:00
6 | Amnura | 50 | 19:30 | 72 | Joypurhat | 59 | 09:00 | 138 | Rahim | 22 | 08:00
7 | Ashuganj | 75 | 14:00 | 73 | Juldah | 13 | 10:00 | 139 | Rajbari | 54 | 19:00
8 | BSRM | 191 | 05:00 | 74 | KSRM | 28 | 23:00 | 140 | Rajendrapur | 100 | 09:00
9 | Bagerhat | 71 | 19:00 | 75 | Kabirpur | 234 | 17:00 | 141 | Rajshahi | 82 | 04:00
10 | Bajitpur | 37 | 17:00 | 76 | Kachua | 61 | 18:30 | 142 | Rajshahi-230 | 66 | 18:00
11 | Bakulia | 83 | 19:00 | 77 | Kallyanpur | 90 | 21:00 | 143 | Ramganj | 100 | 19:00
12 | Banani | 20.4 | 15:00 | 78 | Kalurghat | 62 | 14:00 | 144 | Rampur | 34 | 19:00
13 | Bangabhaban | 5 | 11:00 | 79 | Kamrangirchar | 61.4 | 16:00 | 145 | Rangamati | 12 | 18:00
14 | Barapukuria | 54 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 125 | 18:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 89 | 13:00 | 147 | Ruppur | 4.4 | 15:00
16 | Barishal | 75 | 19:30 | 82 | Keranigonj | 78 | 13:00 | 148 | SSM | 12 | 03:00
17 | Barishal-230 | 82 | 19:00 | 83 | Khagrachori | 28 | 18:00 | 149 | Saidpur | 107 | 17:00
18 | Baroaulia | 52 | 14:00 | 84 | Khosba | 28 | 13:00 | 150 | Satkhira | 103 | 18:30
19 | Baroirhat | 43 | 18:00 | 85 | Khulna | 65 | 19:00 | 151 | Satmasjid | 84 | 20:00
20 | Bashundhara | 148 | 21:00 | 86 | Khulshi | 168 | 15:00 | 152 | Savar | 190 | 14:00
21 | BashundharaCement | 8 | 15:00 | 87 | Kishoreganj | 118 | 18:00 | 153 | SevenRings | 19.99 | 12:00
22 | Beanibazar | 44 | 18:30 | 88 | Kodda | 268 | 15:00 | 154 | ShahCement | 38 | 00:00
23 | Benapole | 53 | 21:00 | 89 | Kulaura | 30 | 18:00 | 155 | Shahjadpur | 71 | 12:00
24 | Bhaluka | 136 | 16:00 | 90 | Kurigram | 53 | 18:00 | 156 | Shahjibazar | 100 | 20:00
25 | Bhandaria | 38 | 21:00 | 91 | Kushtia | 108 | 19:00 | 157 | Shahmirpur | 42 | 01:00
26 | Bhangura | 36 | 13:00 | 92 | Lalbag | 72 | 13:00 | 158 | Shariatpur | 59 | 21:00
27 | Bheramara(GK) | 44 | 19:30 | 93 | Lalmonirhat | 48 | 18:00 | 159 | Sherpur | 146 | 17:00
28 | Bhulta | 239 | 19:30 | 94 | MI_Cement | 16.8 | 15:00 | 160 | Shikalbaha | 16 | 00:00
29 | Bog-Sherpur | 68 | 10:00 | 95 | Madanganj | 37 | 13:00 | 161 | Shitalakhya | 69.4 | 14:00
30 | Bogura | 119 | 19:00 | 96 | Madaripur | 79 | 21:00 | 162 | Sholosohor | 36 | 15:00
31 | Borhanuddin | 58 | 21:00 | 97 | Madartek | 72.32 | 22:00 | 163 | Shyampur | 174 | 12:00
32 | Brahmanbaria | 94 | 22:00 | 98 | Madunaghat | 40 | 18:30 | 164 | Siddhirganj | 116 | 12:00
33 | Cantonment | 121 | 18:30 | 99 | Magura | 48 | 18:00 | 165 | Sirajganj | 86 | 15:00
34 | Chandpur | 49 | 19:00 | 100 | Mahasthangarh | 62 | 12:00 | 166 | Sonargaon | 83 | 15:00
35 | Chandraghona | 27 | 18:30 | 101 | Manikganj | 117 | 19:00 | 167 | Sreemongol | 46 | 18:30
36 | Chapai | 56 | 11:00 | 102 | Maniknagar | 50 | 13:00 | 168 | Sreepur | 87 | 16:00
37 | Charsaidpur | 37 | 02:00 | 103 | Matarbari | 45 | 19:30 | 169 | Srinagar | 35.68 | 20:00
38 | Chauddagram | 56 | 18:00 | 104 | Matuail | 54 | 09:00 | 170 | Sunamganj | 39 | 20:00
39 | Chhatak | 23 | 00:00 | 105 | Millgate | 75 | 15:00 | 171 | Sylhet | 30 | 22:00
40 | Chowmuhani | 164 | 20:00 | 106 | Mirpur | 113 | 21:00 | 172 | Sylhet-132 | 82 | 17:00
41 | Chuadanga | 79 | 18:00 | 107 | Mirsorai | 9 | 11:00 | 173 | TK | 24 | 00:00
42 | Coxsbazar | 116 | 20:00 | 108 | Mirzapur | 41 | 18:00 | 174 | Tangail | 152 | 18:00
43 | Cumilla(N) | 135 | 18:00 | 109 | Mithapukur | 54 | 04:00 | 175 | Thakurgaon | 82 | 18:00
44 | Cumilla(S) | 117 | 14:00 | 110 | Modern | 0 | 00:00 | 176 | Tongi | 113 | 13:00
45 | Daudkandi | 122 | 21:00 | 111 | Mogbazar | 106.3 | 13:00 | 177 | Ullahpara | 29 | 18:00
46 | Dhaka | 34 | 12:00 | 112 | Mongla | 36 | 14:00 | 178 | Ullon | 39 | 19:00
47 | Dhamrai | 100 | 10:00 | 113 | Motijheel | 29 | 21:00 | 179 | Uttara | 67 | 13:00
48 | Dhanmondi | 103 | 13:00 | 114 | Muktagacha | 36 | 18:00 | 180 | UttaraNew | 39 | 21:00
49 | Dohazari | 78 | 14:00 | 115 | Munshiganj | 80 | 22:00 | 181 | Zigatola | 62 | 21:00
50 | Faridpur | 121 | 19:00 | 116 | Muradnagar | 19 | 19:00
51 | Fatullah | 87 | 15:00 | 117 | Mymensingh | 187 | 18:00
52 | Fenchuganj | 25 | 23:00 | 118 | Naogaon | 115 | 13:00
53 | Feni | 86 | 19:00 | 119 | Narail | 46 | 19:00
54 | GPH | 97 | 14:00 | 120 | Narinda | 59 | 15:00
55 | Ghatail | 70 | 17:00 | 121 | Narshingdi | 154 | 19:00
56 | Ghorashal | 12 | 08:00 | 122 | Natore | 119 | 18:00
57 | Ghorashal-230 | 75 | 19:30 | 123 | Nawabganj | 38.8 | 13:00
58 | Goalpara | 24 | 18:00 | 124 | Netrakona | 135 | 18:30
59 | Gollamari | 68 | 19:00 | 125 | New | 80.3 | 14:00
60 | Gopalganj | 83 | 21:00 | 126 | Niamatpur | 95 | 09:00
61 | Gulshan | 76 | 13:00 | 127 | Noapara | 37 | 19:00
62 | Halishahar | 57 | 12:00 | 128 | PHP | 3 | 02:00
63 | HaripurSBU | 162 | 14:00 | 129 | Pabna | 88 | 18:00
64 | Hasnabad | 77 | 18:30 | 130 | Palashbari | 99 | 18:00
65 | Hathazari | 64 | 13:00 | 131 | Panchagarh | 46 | 18:00
66 | Ishurdi | 58 | 19:30 | 132 | Patuakhali | 54 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9991.15 | 0 |  | 9991.15
1:00 | 9425.39 | 0 |  | 9425.39
2:00 | 9088.22 | 0 |  | 9088.22
3:00 | 9398.19 | 0 |  | 9398.19
4:00 | 10083.86 | 0 |  | 10083.86
5:00 | 9084.13 | 0 |  | 9084.13
6:00 | 8360.79 | 0 |  | 8360.79
7:00 | 8543.86 | 0 |  | 8543.86
8:00 | 9240.45 | 0 |  | 9240.45
9:00 | 9964.83 | 0 |  | 9964.83
10:00 | 10262.41 | 0 |  | 10262.41
11:00 | 10746.83 | 0 |  | 10746.83
12:00 | 11078.33 | 0 |  | 11078.33
13:00 | 11467.38 | 20 |  | 11488.38
14:00 | 11738.15 | 0 |  | 11738.15
15:00 | 11680.55 | 0 |  | 11680.55
16:00 | 11543.99 | 0 |  | 11543.99
17:00 | 11888.03 | 0 |  | 11888.03
18:00 | 11849.91 | 0 |  | 11849.91
19:00 | 12294 | 0 |  | 12294
19:30 | 12268.47 | 0 |  | 12268.47
20:00 | 12281.48 | 0 |  | 12281.48
21:00 | 12271.18 | 0 |  | 12271.18
22:00 | 11735.89 | 0 |  | 11735.89
23:00 | 11462.22 | 0 |  | 11462.22
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5590.5 | 4400.65 | 9991.15 | DAILY GENERATION CURVE
00:30 | 5407 | 4301.27 | 9708.27
01:00 | 5223.5 | 4201.89 | 9425.39 | 08-03-2025
01:30 | 5077 | 4179.805 | 9256.805
02:00 | 4930.5 | 4157.72 | 9088.22
02:30 | 5040.5 | 4202.705 | 9243.205
03:00 | 5150.5 | 4247.69 | 9398.19
03:30 | 5333 | 4408.025 | 9741.025
04:00 | 5515.5 | 4568.36 | 10083.86
04:30 | 5178 | 4405.995 | 9583.995
05:00 | 4840.5 | 4243.63 | 9084.13
05:30 | 4625 | 4097.46 | 8722.46
06:00 | 4409.5 | 3951.29 | 8360.79
06:30 | 4433.89 | 4018.435 | 8452.325
07:00 | 4458.28 | 4085.58 | 8543.86
07:30 | 4707.23 | 4184.925 | 8892.155
08:00 | 4956.18 | 4284.27 | 9240.45
08:30 | 5160.43 | 4442.21 | 9602.64
09:00 | 5364.68 | 4600.15 | 9964.83
09:30 | 5410.055 | 4703.565 | 10113.62
10:00 | 5455.43 | 4806.98 | 10262.41
10:30 | 5621.355 | 4883.265 | 10504.62
11:00 | 5787.28 | 4959.55 | 10746.83
11:30 | 5911.25 | 5001.33 | 10912.58
12:00 | 6035.22 | 5043.11 | 11078.33
12:30 | 6118.985 | 5153.87 | 11272.855
13:00 | 6202.75 | 5264.63 | 11467.38
13:30 | 6256.645 | 5346.12 | 11602.765
14:00 | 6310.54 | 5427.61 | 11738.15
14:30 | 6281.21 | 5428.14 | 11709.35
15:00 | 6251.88 | 5428.67 | 11680.55
15:30 | 6289.1 | 5323.17 | 11612.27
16:00 | 6326.32 | 5217.67 | 11543.99
16:30 | 6384.765 | 5331.245 | 11716.01
17:00 | 6443.21 | 5444.82 | 11888.03
17:30 | 6421.15 | 5447.82 | 11868.97
18:00 | 6399.09 | 5450.82 | 11849.91
18:30 | 6547.545 | 5524.41 | 12071.955
19:00 | 6696 | 5598 | 12294
19:30 | 6599 | 5669.47 | 12268.47
20:00 | 6701 | 5580.48 | 12281.48
20:30 | 6669.5 | 5606.83 | 12276.33 |  | Executive Engineer
21:00 | 6638 | 5633.18 | 12271.18 |  | Network Operation Division
21:30 | 6577 | 5426.535 | 12003.535
22:00 | 6516 | 5219.89 | 11735.89
22:30 | 6436.5 | 5162.555 | 11599.055
23:00 | 6357 | 5105.22 | 11462.22

## En-Curve
QF-LDC-12
Date | 08-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3696 | 1618 | 923 | 0 | 44 | 826.15 | 40 | 2720 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3582.5 | 1554 | 922.5 | 0 | 43 | 825.77 | 40 | 2662 | 0 | 0 | 78.5 | 0 | 0 | 0 | 0 | 08-03-2025
01:00 | 3469 | 1490 | 922 | 0 | 42 | 825.39 | 40 | 2604 | 0 | 0 | 33 | 0 | 0 | 0 | 0
01:30 | 3363.5 | 1429.5 | 922 | 0 | 41 | 823.305 | 40 | 2604.5 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | Energy Generated | 260.0342 |  | MKWHr
02:00 | 3258 | 1369 | 922 | 0 | 40 | 821.22 | 40 | 2605 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | Energy not Served | 0.02 |  | MKWHr
02:30 | 3304.5 | 1450 | 922.5 | 0 | 41 | 821.705 | 40 | 2614.5 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | Total Energy Requirement | 260.0542 |  | MKWHr
03:00 | 3351 | 1531 | 923 | 0 | 42 | 822.19 | 40 | 2624 | 0 | 0 | 65 | 0 | 0 | 0 | 0
03:30 | 3550.5 | 1573 | 923 | 0 | 45 | 820.525 | 40 | 2642.5 | 0 | 10.5 | 136 | 0 | 0 | 0 | 0
04:00 | 3750 | 1615 | 923 | 0 | 48 | 818.86 | 40 | 2661 | 0 | 21 | 207 | 0 | 0 | 0 | 0
04:30 | 3581 | 1481.5 | 923 | 0 | 45 | 819.995 | 20 | 2577 | 0 | 10.5 | 126 | 0 | 0 | 0 | 0
05:00 | 3412 | 1348 | 923 | 0 | 42 | 821.13 | 0 | 2493 | 0 | 0 | 45 | 0 | 0 | 0 | 0
05:30 | 3183.5 | 1277 | 923 | 0 | 40 | 821.96 | 0 | 2454.5 | 0 | 0 | 22.5 | 0 | 0 | 0 | 0
06:00 | 2955 | 1206 | 923 | 0 | 38 | 822.79 | 0 | 2416 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 3041.5 | 1206 | 923 | 0 | 36 | 822.08 | 0 | 2395 | 25.245 | 0 | 3.5 | 0 | 0 | 0 | 0
07:00 | 3128 | 1206 | 923 | 0 | 34 | 821.37 | 0 | 2374 | 50.49 | 0 | 7 | 0 | 0 | 0 | 0
07:30 | 3286.5 | 1282.5 | 899.5 | 0 | 34 | 823.46 | 20 | 2373 | 128.195 | 4 | 41 | 0 | 0 | 0 | 0
08:00 | 3445 | 1359 | 876 | 0 | 34 | 825.55 | 40 | 2372 | 205.9 | 8 | 75 | 0 | 0 | 0 | 0
08:30 | 3557.5 | 1472.5 | 875.5 | 0 | 35 | 822.26 | 40 | 2411 | 292.38 | 12.5 | 84 | 0 | 0 | 0 | 0
09:00 | 3670 | 1586 | 875 | 0 | 36 | 818.97 | 40 | 2450 | 378.86 | 17 | 93 | 0 | 0 | 0 | 0
09:30 | 3663.5 | 1586.75 | 898 | 0 | 38 | 817.635 | 40 | 2486 | 449.735 | 17 | 117 | 0 | 0 | 0 | 0
10:00 | 3657 | 1587.5 | 921 | 0 | 40 | 816.3 | 40 | 2522 | 520.61 | 17 | 141 | 0 | 0 | 0 | 0
10:30 | 3736 | 1579 | 921.5 | 0 | 40 | 815.63 | 40 | 2624.5 | 566.99 | 25.5 | 155.5 | 0 | 0 | 0 | 0
11:00 | 3815 | 1570.5 | 922 | 0 | 40 | 814.96 | 40 | 2727 | 613.37 | 34 | 170 | 0 | 0 | 0 | 0
11:30 | 3839.5 | 1563 | 922 | 0 | 43 | 817.57 | 40 | 2837 | 635.51 | 40.5 | 174 | 0 | 0 | 0.5 | 0
12:00 | 3864 | 1555.5 | 922 | 0 | 46 | 820.18 | 40 | 2947 | 657.65 | 47 | 178 | 0 | 0 | 1 | 0
12:30 | 3851 | 1564 | 922.5 | 0 | 48 | 863.73 | 40 | 3106.5 | 639.625 | 57.5 | 178 | 0 | 0 | 2 | 10
13:00 | 3838 | 1572.5 | 923 | 0 | 50 | 907.28 | 40 | 3266 | 621.6 | 68 | 178 | 0 | 0 | 3 | 20
13:30 | 3832.5 | 1568 | 922.5 | 0 | 50 | 912.895 | 40 | 3462 | 566.37 | 63.5 | 179.5 | 0 | 0 | 5.5 | 10
14:00 | 3827 | 1563.5 | 922 | 0 | 50 | 918.51 | 40 | 3658 | 511.14 | 59 | 181 | 0 | 0 | 8 | 0
14:30 | 3813 | 1554 | 922.5 | 0 | 50 | 916.66 | 40 | 3628 | 469.69 | 63 | 241.5 | 0 | 0 | 11 | 0
15:00 | 3799 | 1544.5 | 923 | 0 | 50 | 914.81 | 40 | 3598 | 428.24 | 67 | 302 | 0 | 0 | 14 | 0
15:30 | 3796 | 1568.5 | 922.5 | 0 | 49 | 932.7 | 40 | 3539.5 | 343.07 | 81 | 327 | 0 | 0 | 13 | 0
16:00 | 3793 | 1592.5 | 922 | 0 | 48 | 950.59 | 40 | 3481 | 257.9 | 95 | 352 | 0 | 0 | 12 | 0
16:30 | 3789.5 | 1537.5 | 922 | 0 | 47 | 1031.8 | 40 | 3598.5 | 174.71 | 129.5 | 437.5 | 0 | 0 | 8 | 0
17:00 | 3786 | 1482.5 | 922 | 0 | 46 | 1113.01 | 40 | 3716 | 91.52 | 164 | 523 | 0 | 0 | 4 | 0
17:30 | 3741 | 1436.5 | 922 | 0 | 47 | 1112.155 | 40 | 3724 | 46.815 | 202 | 595.5 | 0 | 0 | 2 | 0
18:00 | 3696 | 1390.5 | 922 | 0 | 48 | 1111.3 | 40 | 3732 | 2.11 | 240 | 668 | 0 | 0 | 0 | 0
18:30 | 3779.5 | 1487.5 | 899 | 0 | 49 | 1185.4 | 40 | 3723 | 1.055 | 236.5 | 671 | 0 | 0 | 0 | 0
19:00 | 3863 | 1584.5 | 876 | 0 | 50 | 1259.5 | 40 | 3714 | 0 | 233 | 674 | 0 | 0 | 0 | 0
19:30 | 3927 | 1532.5 | 876 | 0 | 50 | 1257.97 | 40 | 3798 | 0 | 217 | 570 | 0 | 0 | 0 | 0
20:00 | 3975 | 1626.5 | 876 | 0 | 50 | 1261.98 | 40 | 3763 | 0 | 197 | 492 | 0 | 0 | 0 | 0
20:30 | 3971.5 | 1647.5 | 899 | 0 | 51 | 1265.33 | 40 | 3774 | 0 | 181 | 447 | 0 | 0 | 0 | 0
21:00 | 3968 | 1668.5 | 922 | 0 | 52 | 1268.68 | 40 | 3785 | 0 | 165 | 402 | 0 | 0 | 0 | 0
21:30 | 3943.5 | 1698 | 922 | 0 | 52 | 1196.535 | 40 | 3613 | 0 | 150 | 388.5 | 0 | 0 | 0 | 0
22:00 | 3919 | 1727.5 | 922 | 0 | 52 | 1124.39 | 40 | 3441 | 0 | 135 | 375 | 0 | 0 | 0 | 0
22:30 | 3929 | 1715.5 | 922.5 | 0 | 51 | 1093.555 | 40 | 3397 | 0 | 114.5 | 336 | 0 | 0 | 0 | 0
23:00 | 3939 | 1703.5 | 923 | 0 | 50 | 1062.72 | 40 | 3353 | 0 | 94 | 297 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 405 | 06:00 | 382 | 14:00 | Payra | 422 | 06:00 | 409 | 16:00
Ashuganj | 411 | 6:00 | 389 | 14:00 | Rahanpur | 405 | 02:00 | 392 | 17:00
Bhulta | 408 | 06:00 | 387 | 14:00 | Rampal | 414 | 06:00 | 394 | 14:00
Bibiana | 399 | 04:00 | 388 | 14:00
BIPTC | 397 | 00:00 | 387 | 12:00
Bogura | 394 | 02:00 | 377 | 17:00
Gopalganj | 413 | 06:00 | 392 | 14:00
Kaliakoir | 386 | 04:00 | 365 | 14:00
Madunaghat | 404 | 07:00 | 395 | 15:00
Meghnaghat | 405 | 06:00 | 383 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 222 | 14:00 | Keranigonj | 236 | 06:00 | 220 | 14:00
AKSML | 238 | 06:00 | 227 | 14:00 | Khulna(S) | 241 | 06:00 | 224 | 14:00
Aminbazar | 236 | 04:00 | 223 | 14:00 | Madunaghat | 237 | 07:00 | 230 | 14:00
Ashuganj | 234 | 01:00 | 225 | 14:00 | Madunaghat-400 | 237 | 07:00 | 230 | 15:00
Ashuganj-400 | 234 | 01:00 | 225 | 14:00 | Maniknagar | 232 | 04:00 | 220 | 14:00
Baghabari | 238 | 05:00 | 227 | 17:00 | Meghnaghat | 241 | 05:00 | 228 | 15:00
Barapukuria | 227 | 06:00 | 218 | 16:00 | Meghnaghat-400 | 235 | 06:00 | 223 | 14:00
Barapukuria-230 | 227 | 06:00 | 218 | 16:00 | Mirsorai | 234 | 07:00 | 224 | 14:00
Barishal | 243 | 06:00 | 231 | 14:00 | Rajshahi | 238 | 06:00 | 223 | 17:00
Bheramara | 237 | 06:00 | 223 | 17:00 | Rampal | 239 | 06:00 | 223 | 17:00
Bhulta | 234 | 05:00 | 220 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 00:00 | 221 | 14:00 | Rampura | 235 | 06:00 | 220 | 14:00
BIPTC | 239 | 06:00 | 224 | 17:00 | Shikalbaha | 234 | 06:00 | 225 | 14:00
Bogura | 240 | 06:00 | 228 | 17:00 | Shyampur | 235 | 06:00 | 222 | 14:00
Bogura-400 | 239 | 06:00 | 228 | 17:00 | Siddhirganj | 235 | 04:00 | 223 | 14:00
Borhanuddin | 244 | 06:00 | 236 | 14:00 | Sirajgonj | 244 | 06:00 | 236 | 17:00
BSRM | 235 | 06:00 | 223 | 14:00 | Sreepur | 235 | 06:00 | 225 | 14:00
Cumilla(N) | 231 | 06:00 | 217 | 14:00 | Tongi | 231 | 03:00 | 218 | 15:00
Faridpur | 240 | 06:00 | 227 | 14:00
Fenchuganj | 234 | 06:00 | 225 | 14:00
Ghorashal | 235 | 00:00 | 230 | 01:00
Ghorashal-230 | 234 | 06:00 | 220 | 14:00
Gopalganj | 238 | 06:00 | 226 | 16:00
GPH | 236 | 06:00 | 226 | 14:00
Haripur | 234 | 06:00 | 221 | 14:00
Hasnabad | 236 | 06:00 | 220 | 14:00
Hathazari | 238 | 09:00 | 229 | 14:00
Ishurdi | 239 | 06:00 | 226 | 17:00
Jhenaidah | 237 | 06:00 | 222 | 13:00
Kaliakoir | 233 | 04:00 | 220 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 127 | 14:00 | Madunaghat | 136 | 06:00 | 131 | 14:00
Agargaon | 143 | 06:00 | 132 | 13:00 | Magura | 138 | 02:00 | 126 | 14:00
Agrabad | 136 | 08:00 | 128 | 14:00 | Mahasthangarh | 134 | 02:00 | 125 | 15:00
AKS | 133 | 05:00 | 128 | 15:00 | Manikganj | 133 | 18:30 | 123 | 14:00
Aminbazar | 137 | 00:00 | 130 | 14:00 | Maniknagar | 132 | 04:00 | 123 | 16:00
Amnura | 137 | 05:00 | 128 | 13:00 | Matarbari | 132 | 09:00 | 116 | 18:30
Ashuganj | 140 | 04:00 | 133 | 14:00 | Matuail | 135.8 | 05:00 | 128 | 14:00
Bagerhat | 136 | 06:00 | 124 | 17:00 | Millgate | 135 | 01:00 | 124 | 14:00
Bajitpur | 134 | 04:00 | 127 | 12:00 | Mirpur | 138 | 00:00 | 128 | 14:00
Bakulia | 136 | 09:00 | 131 | 14:00 | Mirzapur | 133 | 18:30 | 125 | 14:00
Banani | 136 | 02:00 | 126 | 16:00 | Mithapukur | 135 | 06:00 | 124 | 16:00
Bangabhaban | 133 | 06:00 | 123 | 15:00 | MI_Cement | 137 | 05:00 | 128 | 14:00
Barapukuria | 140 | 06:00 | 132 | 16:00 | Modern | 0 | 00:00 | N/A | N/A
Barguna | 139 | 06:00 | 133 | 14:00 | Mogbazar | 136 | 06:00 | 128 | 13:00
Barishal | 135 | 03:00 | 128 | 14:00 | Mongla | 135 | 05:00 | 125 | 14:00
Barishal-230 | 136 | 06:00 | 128 | 14:00 | Motijheel | 133 | 06:00 | 123 | 15:00
Baroaulia | 136 | 09:00 | 130 | 14:00 | Muktagacha | 136 | 18:30 | 124 | 07:00
Baroirhat | 131 | 06:00 | 117 | 14:00 | Munshiganj | 136 | 06:00 | 127 | 14:00
Bashundhara | 136 | 04:00 | 123 | 14:00 | Muradnagar | 133 | 06:00 | 121 | 14:00
BashundharaCement | 136 | 06:00 | 126 | 16:00 | Mymensingh | 136 | 18:30 | 115 | 12:00
Beanibazar | 134 | 01:00 | 128 | 17:00 | Naogaon | 133 | 06:00 | 123 | 12:00
Benapole | 136 | 06:00 | 122 | 13:00 | Narail | 138 | 06:00 | 125 | 13:00
Bhaluka | 129 | 18:30 | 120 | 12:00 | Narinda | 132 | 04:00 | 123 | 16:00
Bhandaria | 132 | 04:00 | 124 | 16:00 | Narshingdi | 133 | 04:00 | 123 | 19:00
Bhangura | 136 | 00:00 | 129 | 16:00 | Natore | 136 | 06:00 | 127 | 13:00
Bheramara | 138 | 01:00 | 131 | 17:00 | Nawabganj | 139 | 04:00 | 128 | 14:00
Bheramara(GK) | 138 | 00:00 | 132 | 16:00 | Netrakona | 124 | 05:00 | 112 | 16:00
Bhulta | 131 | 01:00 | 122 | 16:00 | New | 136 | 02:00 | 124 | 14:00
Bog-Sherpur | 136 | 06:00 | 127 | 17:00 | Niamatpur | 137 | 00:00 | 132 | 17:00
Bogura | 136 | 06:00 | 128 | 17:00 | Noapara | 141 | 10:00 | 126 | 13:00
Bogura-230 | 136 | 01:00 | 128 | 17:00 | Pabna | 138 | 01:00 | 130 | 17:00
Brahmanbaria | 133 | 00:00 | 126 | 16:00 | Palashbari | 129 | 06:00 | 119 | 12:00
Cantonment | 143 | 06:00 | 132 | 14:00 | Panchagarh | 137 | 18:30 | 120 | 08:00
Chandpur | 125 | 19:30 | 113 | 14:00 | Patuakhali | 136 | 00:00 | 132 | 13:00
Chandraghona | 137 | 07:00 | 132 | 13:00 | Payra | 139 | 06:00 | 134 | 16:00
Chapai | 135 | 03:00 | 131 | 12:00 | PHP | 129 | 06:00 | 116 | 14:00
Charsaidpur | 137 | 05:00 | 127 | 14:00 | Postogola | 138 | 05:00 | 130 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 130 | 06:00 | 116 | 14:00 | Purbachal | 136 | 04:00 | 127 | 14:00
Chhatak | 133 | 05:00 | 128 | 12:00 | Purbasadipur | 133 | 06:00 | 120 | 09:00
Chowmuhani | 123 | 07:00 | 112 | 13:00 | Rahanpur | 139 | 06:00 | 134 | 17:00
Chuadanga | 137 | 05:00 | 125 | 14:00 | Rahanpur-400 | 139 | 00:00 | 134 | 17:00
Coxsbazar | 129 | 08:00 | 117 | 18:30 | Rahim | 135 | 04:00 | 128 | 13:00
Cumilla(N) | 134 | 05:00 | 123 | 14:00 | Rajbari | 134 | 06:00 | 126 | 13:00
Cumilla(S) | 133 | 06:00 | 120 | 14:00 | Rajendrapur | 139 | 18:30 | 124 | 15:00
Daudkandi | 132 | 06:00 | 120 | 14:00 | Rajshahi | 138 | 06:00 | 129 | 14:00
Dhaka | 136 | 03:00 | 127 | 14:00 | Rajshahi-230 | 138 | 06:00 | 125 | 13:00
Dhamrai | 135 | 06:00 | 125 | 14:00 | Ramganj | 125 | 07:00 | 108 | 14:00
Dhanmondi | 136.5 | 06:00 | 128 | 13:00 | Rampur | 136 | 06:00 | 129 | 14:00
Dohazari | 136 | 09:00 | 126 | 18:30 | Rampura | 137 | 06:00 | 127 | 14:00
Faridpur | 135 | 06:00 | 128 | 14:00 | Rangamati | 136 | 06:00 | 131 | 13:00
Fatullah | 138 | 06:00 | 128 | 14:00 | Rangpur | 132 | 06:00 | 122 | 16:00
Fenchuganj | 136 | 10:00 | 131 | 14:00 | Ruppur | 141 | 04:00 | 132 | 16:00
Feni | 128 | 06:00 | 116 | 14:00 | Saidpur | 135 | 18:30 | 123 | 16:00
Ghatail | 132 | 18:30 | 123 | 14:00 | Satkhira | 137 | 06:00 | 124 | 13:00
Ghorashal | 140 | 06:00 | 133 | 16:00 | Satmasjid | 142 | 06:00 | 132 | 13:00
Goalpara | 139 | 06:00 | 126 | 17:00 | Savar | 138 | 06:00 | 127 | 13:00
Gollamari | 140 | 06:00 | 128 | 16:00 | SevenRings | 140 | 06:00 | 132 | 14:00
Gopalganj | 139 | 06:00 | 130 | 14:00 | ShahCement | 137 | 05:00 | 127 | 16:00
Gopalganj-400 | 140 | 06:00 | 132 | 14:00 | Shahjadpur | 140 | 00:00 | 131 | 13:00
Gulshan | 136 | 06:00 | 127 | 13:00 | Shahjibazar | 134 | 04:00 | 128 | 14:00
Halishahar | 136 | 09:00 | 130 | 12:00 | Shahmirpur | 137 | 09:00 | 130 | 14:00
Haripur | 137 | 06:00 | 128 | 14:00 | Shariatpur | 139 | 05:00 | 130 | 16:00
HaripurSBU | 137 | 06:00 | 128 | 16:00 | Sherpur | 135 | 18:30 | 118 | 06:00
Hasnabad | 136 | 00:00 | 130 | 13:00 | Shikalbaha | 127 | 08:00 | 120 | 16:00
Hathazari | 138 | 09:00 | 132 | 14:00 | Shikalbaha-230 | 138 | 06:00 | 132 | 13:00
Ishurdi | 140 | 02:00 | 132 | 17:00 | Shitalakhya | 137 | 05:00 | 128 | 14:00
Jaldhaka | 133 | 06:00 | 121 | 16:00 | Sholosohor | 136 | 07:00 | 131 | 14:00
Jamalpur | 139 | 18:30 | 120 | 06:00 | Shyampur | 137 | 06:00 | 129 | 14:00
Jashore | 137 | 06:00 | 124 | 13:00 | Shyampur-230 | 137 | 06:00 | 127 | 14:00
Jhenaidah | 139 | 06:00 | 127 | 14:00 | Siddhirganj | 136 | 04:00 | 128 | 14:00
Jhenaidah-230 | 139 | 06:00 | 128 | 13:00 | Sirajganj | 135 | 06:00 | 126 | 17:00
Joydebpur | 139 | 18:30 | 126 | 15:00 | Sonargaon | 135 | 05:00 | 126 | 12:00
Joypurhat | 132 | 02:00 | 120 | 12:00 | Sreemongol | 133 | 00:00 | 128 | 13:00
Juldah | 136 | 09:00 | 128 | 12:00 | Sreepur | 131 | 00:00 | 125 | 12:00
Kabirpur | 135 | 01:00 | 120 | 16:00 | Srinagar | 139 | 05:00 | 129 | 14:00
Kachua | 128 | 06:00 | 116 | 13:00 | SSM | 140 | 08:00 | 132 | 13:00
Kaliakoir | 138 | 18:00 | 126 | 14:00 | Sunamganj | 131 | 05:00 | 127 | 13:00
Kallyanpur | 138 | 06:00 | 129 | 14:00 | Sylhet | 133 | 10:00 | 128 | 16:00
Kalurghat | 135 | 02:00 | 131 | 00:00 | Sylhet-132 | 133 | 05:00 | 130 | 14:00
Kamrangirchar | 139 | 04:00 | 127 | 16:00 | Tangail | 130 | 18:00 | 123 | 14:00
Kaptai | 139 | 8:00 | 135 | 1:00 | Thakurgaon | 136 | 18:30 | 119 | 09:00
Kazla | 132 | 05:00 | 123 | 15:00 | TK | 138 | 06:00 | 132 | 00:00
Keranigonj | 140 | 06:00 | 129 | 14:00 | Tongi | 137 | 05:00 | 127 | 15:00
Khagrachori | 136 | 06:00 | 131 | 14:00 | Ullahpara | 137 | 00:00 | 129 | 12:00
Khosba | 133 | 06:00 | 121 | 14:00 | Ullon | 137 | 06:00 | 127 | 14:00
Khulna | 138 | 06:00 | 126 | 16:00 | Uttara | 138 | 03:00 | 128 | 14:00
Khulna(S) | 140 | 06:00 | 129 | 13:00 | UttaraNew | 136 | 06:00 | 123 | 14:00
Khulshi | 135 | 06:00 | 128 | 14:00 | Zigatola | 139 | 05:00 | 129 | 14:00
Kishoreganj | 131 | 03:00 | 123 | 14:00
Kodda | 135 | 06:00 | 122 | 15:00
KSRM | 137 | 10:00 | 131 | 12:00
Kulaura | 135 | 04:00 | 128 | 14:00
Kurigram | 133 | 06:00 | 119 | 16:00
Kushtia | 138 | 02:00 | 125 | 12:00
Lalbag | 139 | 06:00 | 129 | 14:00
Lalmonirhat | 132 | 06:00 | 121 | 15:00
Madanganj | 136 | 06:00 | 126 | 16:00
Madaripur | 137 | 06:00 | 132 | 14:00
Madartek | 137 | 06:00 | 127 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division