## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-03-2025 | during | 11-03-2025 | during | 11-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 130 | 130 | 230 | 230 | 150 | 150 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 110 | 110 | 110 | 110 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 403 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 304 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 324 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 22 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 28 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 101 | 103 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 68 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 50 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 14 | 82 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2110 | 2289 | 5124.5 | 5184.5 | 3363.29 | 3423.29
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 219 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 8 | 30 | 2 | 36 | 2 | 36 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.35 | 0 | 4.35 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1065 | 1154 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 30 | 5 | 4 | 18 | 4 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 361 | 362 | 360 | 360 | 300 | 300 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1741 | 1914 | 3182.07 | 3223.72 | 3122.07 | 3163.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 213 | 218 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 230 | 225 | 0 | 0 | 230 | 230 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 356.56 | 356.56 | 356.56 | 356.56 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 10 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 60 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 15 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 28 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 68 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1071 | 1156 | 2095.53 | 2035.53 | 2186.59 | 2126.59
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-03-2025 | during | 11-03-2025 | during | 11-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 24 | 22 | 210 | 210 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 144 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 98 | 107 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.15 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 275.15 | 285 | 652.7 | 601.5 | 477.7 | 426.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 28 | 30 | 28 | 28 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 31 | 32 | 40 | 40 | 36 | 36 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 164 | 162 | 162 | 162 | 162 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 348 | 400 | 400 | 400 | 400 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1549 | 1545 | 1650 | 1650 | 1614 | 1614
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 170 | 227 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91.61 | 0 | 89 | 0 | 89 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 510 | 581 | 1234.2 | 1234.2 | 610 | 610 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1695.61 | 1680 | 3601.2 | 3512.2 | 2251.02 | 2162.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 8 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 100 | 135 | 135 | 135 | 135 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1040 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1703.61 | 1879 | 2177.12 | 2176.12 | 2177.12 | 2176.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 128 | 186 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 220 | 154 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 330 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 4 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.81 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 916 | 1307 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.68 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1756.99 | 2065 | 3109.83 | 2943.53 | 3068.04 | 2901.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 63 | 62 | 62 | 62 | 62 | 62 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 164 | 178 | 150 | 150 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.8 | 0 | 6.1 | 0 | 6.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 184 | 0 | 174 | 0 | 174 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 451.8 | 325 | 684.1 | 474 | 670.12 | 460.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12354.16 | 13138 | 22277.05 | 21801.1 | 18929.95 | 18454
Forecast Scenario (11-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11700 |  | 0 |  | 11700
|  |  |  | 1:00 | 11100 |  | 0 |  | 11100
|  |  |  | 2:00 | 10650 |  | 0 |  | 10650
|  |  |  | 3:00 | 10850 |  | 0 |  | 10850
|  |  |  | 4:00 | 11400 |  | 0 |  | 11400
|  |  |  | 5:00 | 10150 |  | 0 |  | 10150
|  |  |  | 6:00 | 9500 |  | 0 |  | 9500
|  |  |  | 7:00 | 9900 |  | 0 |  | 9900
|  |  |  | 8:00 | 10500 |  | 0 |  | 10500
|  |  |  | 9:00 | 11300 |  | 0 |  | 11300
|  |  |  | 10:00 | 11700 |  | 0 |  | 11700
|  |  |  | 11:00 | 12000 |  | 0 |  | 12000
|  |  |  | 12:00 | 12400 |  | 0 |  | 12400
|  |  |  | 13:00 | 12800 |  | 0 |  | 12800
|  |  |  | 14:00 | 13100 |  | 0 |  | 13100
|  |  |  | 15:00 | 13000 |  | 0 |  | 13000
|  |  |  | 16:00 | 12800 |  | 0 |  | 12800
|  |  |  | 17:00 | 12900 |  | 0 |  | 12900
|  |  |  | 18:00 | 12400 |  | 0 |  | 12400
|  |  |  | 18:30 | 12600 |  | 0 |  | 12600
|  |  |  | 19:00 | 13100 |  | 0 |  | 13100
|  |  |  | 19:30 | 13500 |  | 0 |  | 13500
|  |  |  | 20:00 | 13500 |  | 0 |  | 13500
|  |  |  | 21:00 | 13400 |  | 0 |  | 13400
|  |  |  | 22:00 | 13000 |  | 0 |  | 13000
|  |  |  | 23:00 | 12600 |  | 0 |  | 12600
Probable Maximum Temperature: |  |  | 34.40°C
Probable Maximum Demand at Day Peak: |  |  | 12400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 285.75 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:23 hrs on 11-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-03-2025 | [28 empty] | Date: | 10-03-2025 | [28 empty] | Date: | 10-03-2025 | [28 empty] | Date: | 10-03-2025 | [28 empty] | Date: | 10-03-2025 | [18 empty] | Date: | 10-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 273 | 0 | 0 | 0 | 25 | 333 | 0 | 0 | 0 | 70 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 38 | 362 | 0 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1060 | 0 | 51 | 0 | 8 | 0 | 230 | 285 | 8 | 174 | 36 | 0 | 50 | 17 | 29 | 18 | 17 | 60 | 0 | 0 | 0 | 285 | 320 | 370 | 35 | 30 | 30 | 5 | 163 | 22 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 75 | 65 | 27 | 0 | 0 | 8 | 6430 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 0 | 1158.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 136 | 0 | 300 | 0 | 0 | 2.5 | 165 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 65 | 220 | 0 | 0 | 1120 | 0 | 5230.52 | 11660.52 | 87.92
01:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 276 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 0 | 70 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 38 | 360 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 0 | 0 | 200 | 290 | 5 | 198 | 36 | 0 | 50 | 0 | 29 | 18 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 371 | 35 | 30 | 30 | 5 | 120 | 22 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 55 | 45 | 30 | 0 | 0 | 12 | 6198 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1067.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 131 | 0 | 250 | 0 | 0 | 2.5 | 166 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 7 | 65 | 220 | 0 | 0 | 1020 | 0 | 4860.29 | 11058.29 | 87.92
02:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 400 | 300 | 0 | 0 | 0 | 25 | 331 | 0 | 0 | 0 | 70 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 39 | 362 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 0 | 0 | 200 | 290 | 5 | 212 | 36 | 0 | 51 | 0 | 29 | 18 | 0 | 52 | 0 | 0 | 0 | 315 | 320 | 369 | 35 | 30 | 30 | 5 | 120 | 16 | 0 | 11 | 30 | 0 | 16 | 162 | 0 | 45 | 45 | 30 | 0 | 0 | 12 | 5981 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 917.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 126 | 0 | 250 | 0 | 0 | 2.5 | 167 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 65 | 220 | 0 | 0 | 1000 | 0 | 4630.49 | 10611.49 | 87.9
03:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 0 | 70 | 22 | 0 | 0 | 0 | 0 | 30 | 0 | 400 | 306 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 0 | 70 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 34 | 362 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 0 | 0 | 200 | 290 | 5 | 220 | 36 | 0 | 50 | 0 | 28 | 18 | 0 | 50 | 0 | 0 | 0 | 325 | 320 | 323 | 35 | 30 | 30 | 5 | 163 | 16 | 0 | 11 | 30 | 0 | 16 | 162 | 0 | 79 | 45 | 30 | 0 | 0 | 12 | 6080 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 0 | 963.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 128 | 0 | 250 | 0 | 0 | 2.5 | 166 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 50 | 180 | 0 | 0 | 1040 | 0 | 4728.03 | 10808.03 | 87.9
04:00 | 0 | 17 | 8 | 110 | 0 | 130 | 0 | 0 | 377 | 0 | 0 | 0 | 17 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 420 | 278 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 0 | 54 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 34 | 362 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 0 | 5 | 0 | 0 | 0 | 210 | 290 | 5 | 199 | 36 | 0 | 50 | 0 | 29 | 18 | 0 | 52 | 0 | 0 | 0 | 305 | 320 | 345 | 5 | 30 | 30 | 5 | 163 | 16 | 0 | 70 | 20 | 0 | 16 | 163 | 0 | 79 | 105 | 30 | 0 | 0 | 12 | 6265 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 0 | 1107.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 128 | 0 | 250 | 0 | 0 | 2.5 | 165 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 65 | 220 | 0 | 0 | 1140 | 0 | 5131.79 | 11396.79 | 87.9
05:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 350 | 290 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 15 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 362 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 960 | 0 | 5 | 0 | 0 | 0 | 100 | 290 | 5 | 183 | 36 | 0 | 50 | 0 | 0 | 18 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 345 | 5 | 30 | 30 | 5 | 120 | 16 | 0 | 70 | 20 | 0 | 16 | 162 | 0 | 45 | 45 | 30 | 0 | 0 | 0 | 5561 | 922 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 834.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 126 | 0 | 250 | 0 | 0 | 2.5 | 167 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 7 | 66 | 180 | 0 | 0 | 1000 | 0 | 4568.21 | 10129.21 | 87.9
06:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 300 | 306 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 0 | 0 | 19.4 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 362 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 810 | 0 | 5 | 0 | 0 | 0 | 100 | 250 | 5 | 193 | 36 | 0 | 50 | 0 | 0 | 15 | 0 | 48 | 0 | 0 | 0 | 300 | 320 | 345 | 5 | 30 | 30 | 5 | 120 | 16 | 0 | 11 | 20 | 0 | 16 | 162 | 0 | 38 | 45 | 30 | 0 | 0 | 0 | 5225.4 | 922 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 823.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 126 | 0 | 240 | 0 | 0 | 2.5 | 167 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 67 | 180 | 0 | 0 | 800 | 0 | 4243.18 | 9468.58 | 87.89
07:00 | 0 | 0 | 8 | 110 | 0 | 130 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 300 | 280 | 0 | 0 | 0 | 28 | 331 | 0 | 0 | 2 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 11 | 362 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 0 | 11 | 0 | 0 | 0 | 210 | 250 | 5 | 182 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 8 | 0 | 300 | 320 | 345 | 28 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 162 | 0 | 65 | 65 | 31 | 0 | 3.39 | 1 | 5540.39 | 923 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.98 | 387 | 0 | 819.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.19 | 131 | 0 | 0 | 0 | 167 | 0 | 240 | 0 | 0.29 | 2.5 | 168 | 64 | 0 | 2 | 0 | 0 | 0 | 0.4 | 14 | 0.05 | 0 | 150 | 5 | 100 | 220 | 0 | 0 | 750 | 0 | 4321.49 | 9861.88 | 87.89
08:00 | 0 | 22 | 8 | 110 | 0 | 130 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 380 | 301 | 0 | 0 | 0 | 28 | 333 | 0 | 0 | 9 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 6 | 361 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 806 | 8 | 51 | 0 | 8 | 0 | 230 | 285 | 5 | 197 | 36 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 28 | 0 | 300 | 320 | 345 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 162 | 0 | 88 | 65 | 29 | 1 | 12.14 | 12 | 5888.14 | 878 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.25 | 461 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 13.52 | 127 | 0 | 0 | 0 | 212 | 0 | 240 | 0 | 1.18 | 2.5 | 166 | 63 | 0 | 10 | 0 | 0 | 0 | 1.9 | 53 | 0.19 | 0 | 200 | 0 | 130 | 220 | 0 | 0 | 760 | 0 | 4576.54 | 10464.68 | 87.88
09:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 299 | 0 | 0 | 0 | 26 | 330 | 0 | 0 | 17 | 8 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 10 | 363 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 902 | 14 | 51 | 0 | 8 | 0 | 230 | 285 | 5 | 207 | 36 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 48 | 0 | 315 | 320 | 360 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 98 | 65 | 29 | 1 | 23.37 | 12 | 6240.37 | 878 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 456 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 27.08 | 126 | 0 | 0 | 0 | 226 | 0 | 270 | 0 | 2.4 | 5.5 | 122 | 63 | 0 | 20 | 0 | 0 | 0 | 3.7 | 97 | 0.36 | 0 | 307 | 0 | 130 | 220 | 0 | 0 | 830 | 0 | 4963.04 | 11203.41 | 87.87
10:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 283 | 0 | 0 | 0 | 24 | 331 | 0 | 0 | 24 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 9 | 360 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1000 | 17 | 51 | 0 | 8 | 0 | 230 | 285 | 5 | 182 | 33 | 0 | 50 | 0 | 0 | 18 | 0 | 48 | 0 | 61 | 0 | 310 | 320 | 350 | 29 | 28 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 97 | 65 | 26 | 2 | 33.15 | 12 | 6312.15 | 924 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4 | 505 | 0 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 41.94 | 126 | 0 | 0 | 0 | 220 | 0 | 300 | 0 | 3.59 | 5.5 | 120 | 63 | 0 | 27 | 0 | 0 | 0 | 5.1 | 139 | 0.5 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 930 | 0 | 5295.03 | 11607.18 | 87.87
11:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 309 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 28 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 8 | 362 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1000 | 20 | 51 | 0 | 8 | 0 | 230 | 285 | 5 | 204 | 36 | 0 | 50 | 0 | 10 | 12 | 0 | 52 | 0 | 68 | 0 | 310 | 320 | 350 | 29 | 28 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 98 | 95 | 26 | 2 | 40.1 | 12 | 6468.1 | 924 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.76 | 513 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 50.78 | 126 | 0 | 0 | 0 | 220 | 0 | 300 | 0 | 4.32 | 5.5 | 170 | 63 | 0 | 31 | 0 | 0 | 0 | 6.3 | 169 | 0.61 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 990 | 0 | 5485.27 | 11953.37 | 87.87
12:00 | 0 | 50 | 50 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 50 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 306 | 0 | 0 | 0 | 24 | 321 | 0 | 0 | 31 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 8 | 361 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1065 | 18 | 51 | 0 | 8 | 0 | 230 | 285 | 28 | 213 | 35 | 0 | 50 | 0 | 37 | 9 | 0 | 54 | 0 | 71 | 0 | 315 | 320 | 350 | 31 | 28 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 98 | 95 | 24 | 2 | 44.15 | 12 | 6746.15 | 924 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.61 | 510 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 53.68 | 128 | 0 | 0 | 0 | 220 | 0 | 330 | 0 | 4.81 | 5.5 | 164 | 63 | 0 | 34 | 0 | 0 | 0 | 6.8 | 184 | 0.61 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1040 | 0 | 5608.01 | 12354.16 | 87.87
13:00 | 0 | 50 | 40 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 54 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 267 | 0 | 0 | 0 | 24 | 325 | 0 | 0 | 30 | 44 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 16 | 362 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1224 | 17 | 51 | 0 | 26 | 0 | 228 | 285 | 29 | 183 | 35 | 5 | 50 | 7 | 37 | 15 | 0 | 56 | 0 | 65 | 0 | 300 | 320 | 350 | 31 | 28 | 30 | 5 | 84 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 98 | 95 | 24 | 2 | 41.81 | 12 | 6794.81 | 924 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.71 | 622 | 0 | 1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 33.53 | 127 | 0 | 0 | 0 | 220 | 0 | 320 | 0 | 4.74 | 2.5 | 168 | 62 | 0 | 33 | 0 | 0 | 0 | 6.4 | 173 | 0.39 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1210 | 0 | 5956.27 | 12751.08 | 87.86
14:00 | 0 | 33 | 25 | 110 | 0 | 130 | 0 | 0 | 401 | 0 | 0 | 0 | 54 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 293 | 0 | 0 | 0 | 16 | 320 | 0 | 0 | 25 | 60 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 21 | 0 | 4 | 40 | 0 | 8 | 362 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 26 | 0 | 227 | 285 | 29 | 184 | 35 | 36 | 50 | 34 | 39 | 14 | 0 | 62 | 0 | 54 | 0 | 310 | 320 | 350 | 31 | 28 | 28 | 5 | 36 | 16 | 0 | 80 | 30 | 0 | 16 | 164 | 0 | 108 | 101 | 23 | 2 | 37.69 | 12 | 6816.69 | 925 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.96 | 621 | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 39.04 | 128 | 0 | 0 | 0 | 220 | 0 | 414 | 0 | 3.87 | 2.5 | 168 | 61 | 0 | 29 | 0 | 0 | 0 | 5.5 | 152 | 0.49 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1244 | 0 | 6234.36 | 13051.05 | 87.86
15:00 | 0 | 33 | 25 | 110 | 0 | 130 | 0 | 0 | 369 | 0 | 0 | 0 | 35 | 0 | 105 | 32 | 0 | 0 | 21 | 17 | 30 | 0 | 450 | 281 | 0 | 0 | 45 | 16 | 320 | 0 | 0 | 18 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 24 | 0 | 3 | 40 | 0 | 7 | 362 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1224 | 12 | 51 | 0 | 26 | 0 | 225 | 285 | 29 | 183 | 35 | 50 | 50 | 51 | 38 | 14 | 34 | 68 | 0 | 43 | 0 | 300 | 320 | 324 | 31 | 28 | 28 | 5 | 50 | 16 | 0 | 80 | 30 | 0 | 16 | 162 | 0 | 107 | 124 | 24 | 1 | 28.08 | 12 | 6904.08 | 925 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.78 | 604 | 0 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 33.33 | 130 | 0 | 0 | 0 | 202 | 0 | 370 | 0 | 3.03 | 2.5 | 170 | 61 | 0 | 23 | 0 | 0 | 0 | 3.8 | 121 | 0.18 | 0 | 307 | 6 | 130 | 190 | 0 | 0 | 1120 | 0 | 6007.62 | 12911.7 | 87.85
16:00 | 0 | 33 | 25 | 110 | 0 | 130 | 0 | 0 | 385 | 0 | 0 | 0 | 35 | 0 | 105 | 32 | 0 | 0 | 55 | 17 | 30 | 0 | 450 | 301 | 0 | 0 | 55 | 24 | 320 | 0 | 0 | 10 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 2 | 40 | 0 | 10 | 362 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1150 | 8 | 51 | 0 | 26 | 0 | 228 | 285 | 29 | 209 | 35 | 50 | 50 | 51 | 35 | 14 | 34 | 60 | 0 | 25 | 0 | 310 | 320 | 350 | 31 | 28 | 28 | 5 | 120 | 16 | 0 | 80 | 30 | 0 | 16 | 163 | 0 | 107 | 124 | 23 | 1 | 18.78 | 12 | 7014.78 | 924 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.96 | 552 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 19.53 | 130 | 0 | 0 | 0 | 162 | 0 | 370 | 0 | 1.95 | 2.5 | 175 | 61 | 0 | 15 | 0 | 0 | 0 | 2.8 | 80 | 0.22 | 0 | 250 | 6 | 130 | 190 | 0 | 0 | 1120 | 0 | 5685.96 | 12700.74 | 87.84
17:00 | 0 | 33 | 25 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 35 | 0 | 105 | 64 | 0 | 0 | 55 | 17 | 30 | 0 | 450 | 290 | 0 | 0 | 55 | 24 | 322 | 0 | 0 | 4 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 24 | 0 | 1 | 40 | 0 | 18 | 362 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1157 | 3 | 51 | 0 | 8 | 0 | 220 | 285 | 29 | 216 | 35 | 50 | 50 | 51 | 27 | 14 | 34 | 66 | 0 | 9 | 0 | 310 | 320 | 348 | 31 | 28 | 28 | 5 | 163 | 16 | 0 | 80 | 30 | 0 | 16 | 162 | 0 | 107 | 155 | 11 | 0 | 6.28 | 12 | 7064.28 | 924 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.27 | 547 | 0 | 1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 6.3 | 177 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 0.59 | 4 | 177 | 62 | 25 | 6 | 55 | 0 | 0 | 1 | 27 | 0.08 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1120 | 0 | 5818.24 | 12882.52 | 87.84
18:00 | 0 | 50 | 25 | 110 | 0 | 130 | 0 | 0 | 404 | 0 | 0 | 0 | 35 | 0 | 105 | 82 | 0 | 0 | 55 | 35 | 30 | 0 | 350 | 285 | 0 | 0 | 55 | 24 | 320 | 0 | 0 | 0 | 90 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 2 | 31 | 362 | 0 | 0 | 0 | 0 | 4 | 215 | 0 | 0 | 0 | 1123 | 0 | 51 | 0 | 8 | 0 | 220 | 285 | 29 | 209 | 35 | 56 | 50 | 56 | 29 | 15 | 52 | 64 | 0 | 0 | 0 | 325 | 320 | 348 | 32 | 28 | 28 | 5 | 120 | 16 | 0 | 50 | 20 | 0 | 16 | 164 | 0 | 107 | 160 | 11 | 0 | 0.1 | 12 | 7003.1 | 924 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 505 | 0 | 1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 157 | 0 | 300 | 0 | 0.01 | 4 | 178 | 62 | 35 | 0 | 70 | 0 | 0 | 0 | 1 | 0 | 0 | 255 | 7 | 130 | 220 | 0 | 0 | 1040 | 0 | 5582.01 | 12585.11 | 87.83
19:00 | 0 | 55 | 25 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 0 | 105 | 81 | 0 | 0 | 55 | 35 | 30 | 0 | 450 | 305 | 0 | 0 | 17 | 28 | 324 | 0 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 16 | 30 | 362 | 0 | 0 | 0 | 0 | 17 | 218 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 8 | 0 | 230 | 285 | 12 | 218 | 35 | 68 | 50 | 68 | 28 | 15 | 52 | 66 | 0 | 0 | 0 | 295 | 320 | 348 | 32 | 30 | 28 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 107 | 160 | 18 | 0 | 0 | 12 | 7244 | 878 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 4 | 177 | 62 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 100 | 220 | 0 | 0 | 1070 | 0 | 5790 | 13034 | 87.83
19:30 | 0 | 68 | 25 | 110 | 0 | 130 | 0 | 0 | 403 | 0 | 0 | 0 | 35 | 0 | 103 | 64 | 0 | 0 | 55 | 17 | 30 | 0 | 450 | 304 | 0 | 0 | 17 | 28 | 324 | 0 | 0 | 0 | 82 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 17 | 30 | 362 | 0 | 0 | 0 | 0 | 17 | 219 | 0 | 0 | 0 | 1154 | 0 | 51 | 0 | 8 | 0 | 225 | 285 | 10 | 218 | 35 | 68 | 50 | 51 | 28 | 15 | 52 | 60 | 0 | 0 | 0 | 310 | 320 | 348 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 107 | 144 | 22 | 0 | 0 | 12 | 7189 | 872 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 0 | 1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 4 | 178 | 62 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 100 | 220 | 0 | 0 | 1244 | 0 | 5949 | 13138 | 87.83
20:00 | 0 | 68 | 25 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 0 | 95 | 64 | 0 | 0 | 17 | 0 | 30 | 0 | 450 | 308 | 0 | 0 | 0 | 28 | 322 | 0 | 0 | 0 | 70 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 34 | 360 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1195 | 0 | 51 | 0 | 8 | 0 | 225 | 285 | 10 | 216 | 35 | 65 | 50 | 51 | 29 | 10 | 52 | 64 | 0 | 0 | 0 | 310 | 320 | 348 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 107 | 130 | 30 | 0 | 0 | 12 | 7095 | 877 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 0 | 4 | 176 | 62 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 100 | 220 | 0 | 0 | 1244 | 0 | 5993 | 13088 | 87.82
21:00 | 0 | 68 | 25 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 0 | 86 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 310 | 0 | 0 | 0 | 28 | 327 | 0 | 0 | 0 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 34 | 361 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1202 | 0 | 51 | 0 | 16 | 0 | 225 | 285 | 10 | 187 | 35 | 51 | 50 | 51 | 29 | 18 | 52 | 58 | 0 | 0 | 0 | 315 | 320 | 348 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 86 | 130 | 30 | 0 | 0 | 12 | 7011 | 924 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 1365.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 0 | 4 | 177 | 62 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 1244 | 0 | 6091.71 | 13102.71 | 87.82
22:00 | 0 | 68 | 25 | 110 | 0 | 130 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 0 | 86 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 304 | 0 | 0 | 0 | 28 | 326 | 0 | 0 | 0 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 34 | 361 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 16 | 0 | 225 | 285 | 10 | 185 | 35 | 50 | 50 | 51 | 29 | 18 | 52 | 58 | 0 | 0 | 0 | 300 | 320 | 348 | 32 | 30 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 86 | 130 | 28 | 0 | 0 | 12 | 6894 | 924 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 1359.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 153 | 0 | 360 | 0 | 0 | 4 | 170 | 62 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 1160 | 0 | 5936.94 | 12830.94 | 87.81
23:00 | 0 | 68 | 25 | 110 | 0 | 130 | 0 | 0 | 382 | 0 | 0 | 0 | 18 | 0 | 86 | 48 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 314 | 0 | 0 | 0 | 28 | 328 | 0 | 0 | 0 | 70 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 38 | 363 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1111 | 0 | 51 | 0 | 16 | 0 | 225 | 285 | 10 | 196 | 36 | 34 | 50 | 51 | 29 | 18 | 34 | 62 | 0 | 0 | 0 | 310 | 320 | 348 | 32 | 30 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 86 | 85 | 30 | 0 | 0 | 12 | 6733 | 924 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 0 | 1246.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 153 | 0 | 360 | 0 | 0 | 4 | 175 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 1110 | 0 | 5644.92 | 12377.92 | 87.81
Total KWH | 0 | 849600 | 472320 | 2618200 | 0 | 3166571 | 0 | 0 | 9273600 | 0 | 0 | 0 | 627480 | 0 | 1995552 | 571200 | 0 | 0 | 294390 | 135360 | 754200 | 0 | 9999000 | 7225513 | 0 | 0 | 238623 | 586300 | 7544421 | 0 | 0 | 197712 | 1144800 | 471000 | 507600 | 0 | 0 | 0 | 0 | 0 | 0 | 349440 | 0 | 0 | 0 | 710400 | 0 | 30121 | 954540 | 28400 | 580320 | 8501818.18 | 0 | 0 | 0 | 5531.4 | 37636 | 4469403 | 0 | 0 | 0 | 25358179 | 117585 | 1036948 | 0 | 250909 | 0 | 5215100 | 6862000 | 324960 | 4883000 | 861840 | 558720 | 1203150 | 605280 | 562800 | 367290 | 432060 | 1345920 | 0 | 481118 | 0 | 7506000 | 7691400 | 8699000 | 693504 | 697000 | 698520 | 115392 | 3249900 | 383136 | 0 | 1656960 | 676512 | 0 | 385000 | 4419160 | 0 | 2078400 | 2318400 | 573120 | 13000 | 289470 | 267600 | 157219384.58 | 21988363 | 4860000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624240 | 12203640 | 0 | 25831637 | 0 | 0 | 0 | 0 | 0 | 2570 | 0 | 0 | 0 | 661470 | 0 | 334504 | 3565000 | 0 | 0 | 0 | 4316964 | 0 | 8004000 | 0 | 30240 | 93744 | 4039000 | 1465309 | 128866 | 233397 | 355209 | 0 | 0 | 44456.04 | 1200240 | 3746 | 0 | 6502000 | 144500 | 2568000 | 5199390 | 0 | 0 | 25643636.36 | 0 | 130044121.4 | 287263505.98

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12354.16 | MW | 12:00 Hr. | Energy Generated |  |  | 287.2635 |  | MKWHr.
| Day Peak Demand |  |  | 12385.16 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.03 |  | MKWHr.
| Evening Peak Generation |  |  | 13138 | MW | 19:30 Hr. | Energy Demand |  |  | 287.2935 |  | MKWHr.
| Evening Peak Demand |  |  | 13138 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.8 |  | °C
| Minimum Generation of the Day |  |  | 9468.58 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1020.36 |  | MMCFD
| Maximum Generation of the Day |  |  | 13138 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.8341 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.1464 | 0 | 6.3293 | 0 | 0 | 0.19771 | 0 | 0 | 48.6734 | Gas | 134.3975 | Gas | 479500180.49
| Chattogram Zone |  |  | 5.0497 | 33.86 | 0.78197 | 0 | 0.95454 | 0.14771 | 0 | 0.34944 | 41.1434 | Coal | 83.7136 | Coal | 598657863.7722
| Cumilla Zone |  |  | 21.0052 | 0 | 2.1589 | 0 | 0 | 0.48112 | 1.3459 | 0 | 24.9911 | HFO | 14.4212 | HFO | 249175097.948
| Mymensingh Zone |  |  | 0.57312 | 0 | 4.6644 | 0 | 0 | 0.30247 | 0 | 0 | 5.54 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8715 | Hydro | 0.95454 | Hydro | 95454
| Khulna Zone |  |  | 4.86 | 12.2036 | 0 | 0 | 0 | 0.62424 | 21.9884 | 0 | 39.6762 | Solar | 4.2613 | Solar | 69291287.2444
| Barishal Zone |  |  | 7.9119 | 32.1456 | 0 | 0 | 0 | 0.003746 | 0 | 0 | 40.0613 | Import | 49.1659 | Import | 274074378.05
| Rajshahi Zone |  |  | 15.9797 | 0 | 0.00257 | 0 | 0 | 1.0262 | 25.8316 | 0 | 42.8401 | Wind | 0.34944 | Wind | 5115801.6
| Rangpur Zone |  |  | 0 | 5.5043 | 0.48407 | 0 | 0 | 1.4781 | 0 | 0 | 7.4665
| Total |  |  | 134.3975 | 83.7136 | 14.4212 | 0 | 0.95454 | 4.2613 | 49.1659 | 0.34944 | 287.2635
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 479500180.49 |  | Hydro | 95454
|  |  |  | Coal | 598657863.7722 |  | Solar | 69291287.2444
|  |  |  | HFO | 249175097.948 |  | Import | 274074378.05
|  |  |  | HSD | 0 |  | Wind | 5115801.6
[5 empty] | Total: | 167,59,10,063 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9884 | Peak Hr Flow | 872.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8704429000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.8316 | Peak Hr Flow | 1307.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 750 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3459 | Peak Hr Flow | 60.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 932 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.1659 | Peak Hr Flow | 2239.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4772
|  |  |  | Chattogram |  | 0 |  | 1310
|  |  |  | Cumilla |  | 0 |  | 1154
|  |  |  | Mymensingh |  | 0 |  | 1041
|  |  |  | Sylhet |  | 0 |  | 440
|  |  |  | Khulna |  | 0 |  | 1494
|  |  |  | Barishal |  | 0 |  | 356
|  |  |  | Rajshahi |  | 0 |  | 1262
|  |  |  | Rangpur |  | 0 |  | 750
|  |  |  | Total |  | 0 |  | 12579
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 15:41 | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D
| 08:02 | 15:40 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Tank colour work
| 08:17 | 13:11 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance (Deep Cleaning).
| 08:39 | 13:19 | Chandraghona 132/33kV S/S MAIN BUS-1 Scheduled S/D Due to Annual Maintenance
| 08:41 |  | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Piling work of
Boundary wall
| 09:36 | 12:51 | Rangpur-Saidpur 132kV Ckt-1 Project Work S/D from Saidpur 132/33kV end Due to Project
work. and from Rangpur 132/33kV end Due to Project work
| 10:01 |  | Tongi 230/132/33kV S/S 230 kV Bus-1 Scheduled S/D Due to R-conductoring
| 10:22 |  | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Re
conductoring
|  | 11:31 | Sonargaon 132/33kV S/S Bashundhara Line is restored.
| 12:00 |  | Day Peak Gen. 12354 MW
| 12:06 |  | Kushiara 163MW CCPP ST tripped.
|  | 13:05 | Mongla 132/33kV S/S T-1 LT is restored.
| 13:10 | 18:04 | Rajbari 132/33kV S/S 132 kV Bus-I Project Work S/D
| 14:18 |  | Kushiara 163MW CCPP ST was sync.
| 14:20 |  | Mongla 132/33kV S/S T-2 LT Project Work S/D Due to Due to T-1 transformer load test.
| 14:21 |  | Mongla 132/33kV S/S T-2 HT Project Work S/D Due to Due to T-1 transformer load test.
| 14:21 | 17:03 | Rangpur-Saidpur 132kV Ckt-2 Project Work S/D from Saidpur 132/33kV end Due to As the
instruction of ALDC, Bogura (499264) and from Rangpur 132/33kV end Due to TARAGONJ LILO
Line work
|  | 21:54 | Chandpur 132/33kV S/S 402T LT is restored.
| 21:55 |  | Chandpur 132/33kV S/S 412T LT Forced S/D
| 01:07 |  | Ghorashal GT-4 was shutdown due to LNG problem.
| 01:07 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 130 | 3166571 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2618200 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9273600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9999000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7225513 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7544421 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 571200 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 294390 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 238623 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 471000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 507600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 754200 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 586300 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 472320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 103 | 1995552 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 68 | 849600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 135360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 197712 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 627480 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 82 | 1144800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2289 | 48673442
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 5531.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117585 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 954540 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 4469403 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 37636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 710400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 580320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 30121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 28400 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1154 | 25358179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 349440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 362 | 8501818.18 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1914 | 41143373.58
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 218 | 4883000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 225 | 5215100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6862000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 861840 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 324960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 250909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1036948 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1203150 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 605280 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 60 | 1345920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 367290 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 432060 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 562800 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 558720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 481118 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1156 | 24991095
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 22 | 573120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 144 | 2318400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 2078400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 289470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 267600 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 285 | 5539990
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 697000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 698520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3249900 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 693504 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 115392 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 676512 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1656960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 4419160 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 385000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 383136 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7506000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8699000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7691400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1545 | 36871484
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 21988363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 227 | 4860000 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 624240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 581 | 12203640 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1680 | 39676243
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 144500 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 100 | 2568000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 25643636.36 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5199390 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6502000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3746 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1879 | 40061272.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 3565000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 154 | 4316964 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8004000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 4 | 93744 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 2570 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30240 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1307 | 25831637 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 334504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 661470 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2065 | 42840129
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1465309 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 178 | 4039000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 50 | 355209 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44456.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 128866 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 233397 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1200240 | -
Rangpur Area Total |  |  |  |  | 950 | 325 | 7466477.04
Eastern Grid Total |  |  |  |  | 16921.242 | 7189 | 157219384.58
Western Grid Total |  |  |  |  | 11614.5 | 5949 | 130044121.4
National Grid Total |  |  |  |  | 28535.742 | 13138 | 287263505.98
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-03-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8716.44 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3861.5 | MW
i) Dhaka area |  |  | 4771.54 |  | MW | i) Khulna area |  |  |  | 1493.5 | MW
ii) Chattogram area |  |  | 1309.9 |  | MW | ii) Barishal area |  |  |  | 356 | MW
iii) Cumilla area |  |  | 1154 |  | MW | iii) Rajshahi area |  |  |  | 1262 | MW
iv) Mymensingh area |  |  | 1041 |  | MW | iv) Rangpur area |  |  |  | 750 | MW
v) Sylhet area |  |  | 440 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12577.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 68 | 18:00 | 133 | Payra | 24 | 19:00
2 | AKSML | 20 | 16:00 | 68 | Jamalpur | 112 | 18:00 | 134 | Postogola | 48 | 13:00
3 | Aftabnagar | 32 | 13:00 | 69 | Jashore | 128 | 19:00 | 135 | Purbachal | 17 | 22:00
4 | Agargaon | 96 | 13:00 | 70 | Jhenaidah | 107 | 18:00 | 136 | Purbasadipur | 118 | 13:00
5 | Agrabad | 84 | 19:30 | 71 | Joydebpur | 151 | 15:00 | 137 | Rahanpur | 24 | 18:30
6 | Amnura | 50 | 03:00 | 72 | Joypurhat | 60 | 10:00 | 138 | Rahim | 28 | 11:00
7 | Ashuganj | 82 | 15:00 | 73 | Juldah | 13 | 10:00 | 139 | Rajbari | 62.5 | 19:30
8 | BSRM | 202 | 20:00 | 74 | KSRM | 28 | 21:00 | 140 | Rajendrapur | 122 | 16:00
9 | Bagerhat | 74 | 20:00 | 75 | Kabirpur | 252 | 11:00 | 141 | Rajshahi | 86 | 19:30
10 | Bajitpur | 41 | 19:30 | 76 | Kachua | 66 | 18:30 | 142 | Rajshahi-230 | 73 | 18:00
11 | Bakulia | 83 | 19:00 | 77 | Kallyanpur | 96 | 19:00 | 143 | Ramganj | 108 | 18:00
12 | Banani | 26 | 12:00 | 78 | Kalurghat | 38 | 14:00 | 144 | Rampur | 35 | 18:30
13 | Bangabhaban | 13 | 10:00 | 79 | Kamrangirchar | 65.2 | 20:00 | 145 | Rangamati | 14 | 19:00
14 | Barapukuria | 55 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 128 | 18:00
15 | Barguna | 16 | 19:00 | 81 | Kazla | 96 | 15:00 | 147 | Ruppur | 6 | 15:00
16 | Barishal | 90 | 19:00 | 82 | Keranigonj | 73 | 19:30 | 148 | SSM | 12 | 02:00
17 | Barishal-230 | 74 | 18:30 | 83 | Khagrachori | 26 | 18:00 | 149 | Saidpur | 107 | 14:00
18 | Baroaulia | 51 | 14:00 | 84 | Khosba | 28 | 18:30 | 150 | Satkhira | 118 | 19:00
19 | Baroirhat | 46 | 19:00 | 85 | Khulna | 77 | 19:30 | 151 | Satmasjid | 90 | 19:00
20 | Bashundhara | 165 | 14:00 | 86 | Khulshi | 163 | 13:00 | 152 | Savar | 204 | 12:00
21 | BashundharaCement | 8 | 23:00 | 87 | Kishoreganj | 122 | 18:00 | 153 | SevenRings | 19.15 | 03:00
22 | Beanibazar | 48 | 18:30 | 88 | Kodda | 267 | 17:00 | 154 | ShahCement | 30 | 16:00
23 | Benapole | 58 | 18:30 | 89 | Kulaura | 32 | 18:00 | 155 | Shahjadpur | 80 | 11:00
24 | Bhaluka | 136 | 14:00 | 90 | Kurigram | 61 | 17:00 | 156 | Shahjibazar | 106 | 22:00
25 | Bhandaria | 41 | 21:00 | 91 | Kushtia | 120 | 19:30 | 157 | Shahmirpur | 50 | 15:00
26 | Bhangura | 35 | 13:00 | 92 | Lalbag | 74 | 13:00 | 158 | Shariatpur | 63 | 21:00
27 | Bheramara(GK) | 49 | 19:00 | 93 | Lalmonirhat | 52 | 18:00 | 159 | Sherpur | 152 | 17:00
28 | Bhulta | 261 | 16:00 | 94 | MI_Cement | 17 | 19:30 | 160 | Shikalbaha | 25 | 20:00
29 | Bog-Sherpur | 74 | 04:00 | 95 | Madanganj | 38 | 14:00 | 161 | Shitalakhya | 77 | 15:00
30 | Bogura | 126 | 17:00 | 96 | Madaripur | 87 | 21:00 | 162 | Sholosohor | 37 | 15:00
31 | Borhanuddin | 62 | 19:00 | 97 | Madartek | 76.6 | 21:00 | 163 | Shyampur | 166 | 00:00
32 | Brahmanbaria | 111 | 18:00 | 98 | Madunaghat | 45 | 18:00 | 164 | Siddhirganj | 120 | 11:00
33 | Cantonment | 118 | 14:00 | 99 | Magura | 54 | 18:30 | 165 | Sirajganj | 96 | 19:30
34 | Chandpur | 54 | 21:00 | 100 | Mahasthangarh | 62 | 04:00 | 166 | Sonargaon | 103 | 00:00
35 | Chandraghona | 24 | 17:00 | 101 | Manikganj | 122 | 19:00 | 167 | Sreemongol | 56 | 19:00
36 | Chapai | 59 | 09:00 | 102 | Maniknagar | 64 | 14:00 | 168 | Sreepur | 84 | 17:00
37 | Charsaidpur | 40 | 15:00 | 103 | Matarbari | 41 | 18:30 | 169 | Srinagar | 37.2 | 20:00
38 | Chauddagram | 59 | 14:00 | 104 | Matuail | 60 | 09:00 | 170 | Sunamganj | 42 | 19:30
39 | Chhatak | 25 | 05:00 | 105 | Millgate | 81 | 15:00 | 171 | Sylhet | 31 | 18:00
40 | Chowmuhani | 170 | 20:00 | 106 | Mirpur | 153 | 15:00 | 172 | Sylhet-132 | 88 | 13:00
41 | Chuadanga | 87 | 19:30 | 107 | Mirsorai | 9 | 09:00 | 173 | TK | 25.4 | 19:00
42 | Coxsbazar | 117 | 18:00 | 108 | Mirzapur | 46 | 14:00 | 174 | Tangail | 164 | 03:00
43 | Cumilla(N) | 144 | 19:00 | 109 | Mithapukur | 52 | 03:00 | 175 | Thakurgaon | 83 | 17:00
44 | Cumilla(S) | 151 | 15:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 110 | 13:00
45 | Daudkandi | 129 | 22:00 | 111 | Mogbazar | 136 | 14:00 | 177 | Ullahpara | 30 | 13:00
46 | Dhaka | 50 | 12:00 | 112 | Mongla | 36 | 04:00 | 178 | Ullon | 42 | 21:00
47 | Dhamrai | 118 | 15:00 | 113 | Motijheel | 33 | 12:00 | 179 | Uttara | 79 | 13:00
48 | Dhanmondi | 127 | 13:00 | 114 | Muktagacha | 34 | 18:00 | 180 | UttaraNew | 43 | 21:00
49 | Dohazari | 86 | 19:00 | 115 | Munshiganj | 84 | 14:00 | 181 | Zigatola | 68 | 21:00
50 | Faridpur | 132 | 19:00 | 116 | Muradnagar | 22 | 20:00
51 | Fatullah | 90 | 12:00 | 117 | Mymensingh | 182 | 18:00
52 | Fenchuganj | 25 | 18:00 | 118 | Naogaon | 114 | 13:00
53 | Feni | 91 | 19:00 | 119 | Narail | 48 | 19:00
54 | GPH | 93 | 20:00 | 120 | Narinda | 67.5 | 13:00
55 | Ghatail | 74 | 17:00 | 121 | Narshingdi | 153 | 20:00
56 | Ghorashal | 14 | 10:00 | 122 | Natore | 125 | 19:00
57 | Ghorashal-230 | 76 | 22:00 | 123 | Nawabganj | 44.8 | 21:00
58 | Goalpara | 28 | 13:00 | 124 | Netrakona | 139 | 17:00
59 | Gollamari | 62 | 19:00 | 125 | New | 84.4 | 14:00
60 | Gopalganj | 90 | 19:00 | 126 | Niamatpur | 96 | 13:00
61 | Gulshan | 106 | 13:00 | 127 | Noapara | 40 | 19:00
62 | Halishahar | 64.5 | 14:00 | 128 | PHP | 8 | 03:00
63 | HaripurSBU | 190 | 11:00 | 129 | Pabna | 96 | 18:00
64 | Hasnabad | 91 | 18:00 | 130 | Palashbari | 100 | 18:00
65 | Hathazari | 61 | 19:00 | 131 | Panchagarh | 48 | 18:00
66 | Ishurdi | 64 | 19:30 | 132 | Patuakhali | 56 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11660.52 | 0 |  | 11660.52
1:00 | 11058.29 | 0 |  | 11058.29
2:00 | 10611.49 | 0 |  | 10611.49
3:00 | 10808.03 | 0 |  | 10808.03
4:00 | 11396.79 | 0 |  | 11396.79
5:00 | 10129.21 | 0 |  | 10129.21
6:00 | 9468.58 | 0 |  | 9468.58
7:00 | 9861.88 | 0 |  | 9861.88
8:00 | 10464.68 | 0 |  | 10464.68
9:00 | 11203.41 | 0 |  | 11203.41
10:00 | 11607.18 | 0 |  | 11607.18
11:00 | 11953.37 | 0 |  | 11953.37
12:00 | 12354.16 | 30 |  | 12385.16
13:00 | 12751.08 | 0 |  | 12751.08
14:00 | 13051.05 | 0 |  | 13051.05
15:00 | 12911.7 | 0 |  | 12911.7
16:00 | 12700.74 | 0 |  | 12700.74
17:00 | 12882.52 | 0 |  | 12882.52
18:00 | 12585.11 | 0 |  | 12585.11
19:00 | 13034 | 0 |  | 13034
19:30 | 13138 | 0 |  | 13138
20:00 | 13088 | 0 |  | 13088
21:00 | 13102.71 | 0 |  | 13102.71
22:00 | 12830.94 | 0 |  | 12830.94
23:00 | 12377.92 | 0 |  | 12377.92
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6430 | 5230.52 | 11660.52 | DAILY GENERATION CURVE
00:30 | 6314 | 5045.405 | 11359.405
01:00 | 6198 | 4860.29 | 11058.29 | 10-03-2025
01:30 | 6089.5 | 4745.39 | 10834.89
02:00 | 5981 | 4630.49 | 10611.49
02:30 | 6030.5 | 4679.26 | 10709.76
03:00 | 6080 | 4728.03 | 10808.03
03:30 | 6172.5 | 4929.91 | 11102.41
04:00 | 6265 | 5131.79 | 11396.79
04:30 | 5913 | 4850 | 10763
05:00 | 5561 | 4568.21 | 10129.21
05:30 | 5393.2 | 4405.695 | 9798.895
06:00 | 5225.4 | 4243.18 | 9468.58
06:30 | 5382.895 | 4282.335 | 9665.23
07:00 | 5540.39 | 4321.49 | 9861.88
07:30 | 5714.265 | 4449.015 | 10163.28
08:00 | 5888.14 | 4576.54 | 10464.68
08:30 | 6064.255 | 4769.79 | 10834.045
09:00 | 6240.37 | 4963.04 | 11203.41
09:30 | 6276.26 | 5129.035 | 11405.295
10:00 | 6312.15 | 5295.03 | 11607.18
10:30 | 6390.125 | 5390.15 | 11780.275
11:00 | 6468.1 | 5485.27 | 11953.37
11:30 | 6607.125 | 5546.64 | 12153.765
12:00 | 6746.15 | 5608.01 | 12354.16
12:30 | 6770.48 | 5782.14 | 12552.62
13:00 | 6794.81 | 5956.27 | 12751.08
13:30 | 6805.75 | 6095.315 | 12901.065
14:00 | 6816.69 | 6234.36 | 13051.05
14:30 | 6860.385 | 6120.99 | 12981.375
15:00 | 6904.08 | 6007.62 | 12911.7
15:30 | 6959.43 | 5846.79 | 12806.22
16:00 | 7014.78 | 5685.96 | 12700.74
16:30 | 7039.53 | 5752.1 | 12791.63
17:00 | 7064.28 | 5818.24 | 12882.52
17:30 | 7033.69 | 5700.125 | 12733.815
18:00 | 7003.1 | 5582.01 | 12585.11
18:30 | 7123.55 | 5686.005 | 12809.555
19:00 | 7244 | 5790 | 13034
19:30 | 7189 | 5949 | 13138
20:00 | 7095 | 5993 | 13088
20:30 | 7053 | 6042.355 | 13095.355 |  | Executive Engineer
21:00 | 7011 | 6091.71 | 13102.71 |  | Network Operation Division
21:30 | 6952.5 | 6014.325 | 12966.825
22:00 | 6894 | 5936.94 | 12830.94
22:30 | 6813.5 | 5790.93 | 12604.43
23:00 | 6733 | 5644.92 | 12377.92

## En-Curve
QF-LDC-12
Date | 10-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3708 | 1766.5 | 924 | 0 | 60 | 1158.02 | 40 | 3528 | 0 | 95 | 376 | 0 | 0 | 5 | 0 | DAILY ENERGY CURVE
00:30 | 3682.5 | 1740.5 | 923.5 | 0 | 57 | 1112.905 | 40 | 3386 | 0 | 86.5 | 326 | 0 | 0 | 4.5 | 0 | 10-03-2025
01:00 | 3657 | 1714.5 | 923 | 0 | 54 | 1067.79 | 40 | 3244 | 0 | 78 | 276 | 0 | 0 | 4 | 0
01:30 | 3648 | 1676.5 | 923 | 0 | 53 | 992.89 | 40 | 3157.5 | 0 | 78 | 259 | 0 | 0 | 7 | 0 | Energy Generated | 287.2635 |  | MKWHr
02:00 | 3639 | 1638.5 | 923 | 0 | 52 | 917.99 | 40 | 3071 | 0 | 78 | 242 | 0 | 0 | 10 | 0 | Energy not Served | 0.03 |  | MKWHr
02:30 | 3573.5 | 1645.5 | 923 | 0 | 51 | 940.76 | 40 | 3173 | 0 | 89 | 258.5 | 0 | 0 | 15.5 | 0 | Total Energy Requirement | 287.2935 |  | MKWHr
03:00 | 3508 | 1652.5 | 923 | 0 | 50 | 963.53 | 40 | 3275 | 0 | 100 | 275 | 0 | 0 | 21 | 0
03:30 | 3556.5 | 1650.5 | 923.5 | 0 | 51 | 1035.41 | 40 | 3427.5 | 0 | 97.5 | 299.5 | 0 | 0 | 21 | 0
04:00 | 3605 | 1648.5 | 924 | 0 | 52 | 1107.29 | 40 | 3580 | 0 | 95 | 324 | 0 | 0 | 21 | 0
04:30 | 3509.5 | 1570.5 | 923 | 0 | 53 | 971 | 40 | 3385 | 0 | 59 | 229.5 | 0 | 0 | 22.5 | 0
05:00 | 3414 | 1492.5 | 922 | 0 | 54 | 834.71 | 40 | 3190 | 0 | 23 | 135 | 0 | 0 | 24 | 0
05:30 | 3372.5 | 1451.7 | 922 | 0 | 51 | 829.195 | 40 | 2964 | 0 | 15.5 | 126 | 0 | 0 | 27 | 0
06:00 | 3331 | 1410.9 | 922 | 0 | 48 | 823.68 | 40 | 2738 | 0 | 8 | 117 | 0 | 0 | 30 | 0
06:30 | 3437.5 | 1477.2 | 922.5 | 0 | 51 | 821.38 | 40 | 2709.5 | 23.65 | 8 | 143 | 0 | 0 | 31.5 | 0
07:00 | 3544 | 1543.5 | 923 | 0 | 54 | 819.08 | 40 | 2681 | 47.3 | 8 | 169 | 0 | 0 | 33 | 0
07:30 | 3613.5 | 1617 | 900.5 | 0 | 50 | 820.04 | 40 | 2749 | 121.74 | 19 | 204.5 | 0 | 0 | 28 | 0
08:00 | 3683 | 1690.5 | 878 | 0 | 46 | 821 | 40 | 2817 | 196.18 | 30 | 240 | 0 | 0 | 23 | 0
08:30 | 3740 | 1734.5 | 878 | 0 | 45 | 867.5 | 40 | 2930 | 279.045 | 56.5 | 244 | 0 | 0 | 19.5 | 0
09:00 | 3797 | 1778.5 | 878 | 0 | 44 | 914 | 40 | 3043 | 361.91 | 83 | 248 | 0 | 0 | 16 | 0
09:30 | 3806 | 1747 | 901 | 0 | 46 | 913.5 | 40 | 3164 | 433.795 | 79 | 256 | 0 | 0 | 19 | 0
10:00 | 3815 | 1715.5 | 924 | 0 | 48 | 913 | 40 | 3285 | 505.68 | 75 | 264 | 0 | 0 | 22 | 0
10:30 | 3829.5 | 1725 | 924 | 0 | 50 | 914 | 40 | 3345 | 551.775 | 75 | 292 | 0 | 0 | 34 | 0
11:00 | 3844 | 1734.5 | 924 | 0 | 52 | 915 | 40 | 3405 | 597.87 | 75 | 320 | 0 | 0 | 46 | 0
11:30 | 3888 | 1765.5 | 924 | 0 | 53 | 915.5 | 40 | 3457.5 | 621.265 | 94.5 | 356.5 | 0 | 0 | 38 | 15
12:00 | 3932 | 1796.5 | 924 | 0 | 54 | 916 | 40 | 3510 | 644.66 | 114 | 393 | 0 | 0 | 30 | 30
12:30 | 3920 | 1745 | 924 | 0 | 55 | 963.5 | 40 | 3732.5 | 623.12 | 124 | 403 | 0 | 0 | 22.5 | 15
13:00 | 3908 | 1693.5 | 924 | 0 | 56 | 1011 | 40 | 3955 | 601.58 | 134 | 413 | 0 | 0 | 15 | 0
13:30 | 3953.5 | 1678.5 | 924.5 | 0 | 59 | 1105.5 | 40 | 3971 | 560.565 | 138.5 | 461.5 | 0 | 0 | 8.5 | 0
14:00 | 3999 | 1663.5 | 925 | 0 | 62 | 1200 | 40 | 3987 | 519.55 | 143 | 510 | 0 | 0 | 2 | 0
14:30 | 3975.5 | 1644 | 925 | 0 | 65 | 1208.5 | 40 | 3917.5 | 465.875 | 151.5 | 586.5 | 0 | 0 | 2 | 0
15:00 | 3952 | 1624.5 | 925 | 0 | 68 | 1217 | 40 | 3848 | 412.2 | 160 | 663 | 0 | 0 | 2 | 0
15:30 | 3965.5 | 1680 | 924.5 | 0 | 64 | 1187 | 40 | 3759 | 335.22 | 160 | 683.5 | 0 | 0 | 7.5 | 0
16:00 | 3979 | 1735.5 | 924 | 0 | 60 | 1157 | 40 | 3670 | 258.24 | 160 | 704 | 0 | 0 | 13 | 0
16:30 | 4023 | 1762.25 | 924 | 0 | 63 | 1160.5 | 40 | 3701 | 175.38 | 176 | 755.5 | 0 | 0 | 11 | 0
17:00 | 4067 | 1789 | 924 | 0 | 66 | 1164 | 40 | 3732 | 92.52 | 192 | 807 | 0 | 0 | 9 | 0
17:30 | 3995.5 | 1715.5 | 924 | 0 | 65 | 1216.5 | 40 | 3628.5 | 47.315 | 219.5 | 872.5 | 0 | 0 | 9.5 | 0
18:00 | 3924 | 1642 | 924 | 0 | 64 | 1269 | 40 | 3525 | 2.11 | 247 | 938 | 0 | 0 | 10 | 0
18:30 | 3969.5 | 1717.5 | 901 | 0 | 65 | 1294 | 40 | 3620.5 | 1.055 | 249 | 944 | 0 | 0 | 8 | 0
19:00 | 4015 | 1793 | 878 | 0 | 66 | 1319 | 40 | 3716 | 0 | 251 | 950 | 0 | 0 | 6 | 0
19:30 | 4040 | 1809 | 872 | 0 | 60 | 1307 | 40 | 3888 | 0 | 239 | 878 | 0 | 0 | 5 | 0
20:00 | 4041 | 1814 | 877 | 0 | 64 | 1318 | 40 | 3956 | 0 | 227 | 747 | 0 | 0 | 4 | 0
20:30 | 4045 | 1822.5 | 900.5 | 0 | 61 | 1341.855 | 40 | 3964 | 0 | 227 | 690 | 0 | 0 | 3.5 | 0
21:00 | 4049 | 1831 | 924 | 0 | 58 | 1365.71 | 40 | 3972 | 0 | 227 | 633 | 0 | 0 | 3 | 0
21:30 | 4016 | 1799 | 924 | 0 | 58 | 1362.825 | 40 | 3904.5 | 0 | 227 | 632.5 | 0 | 0 | 3 | 0
22:00 | 3983 | 1767 | 924 | 0 | 58 | 1359.94 | 40 | 3837 | 0 | 227 | 632 | 0 | 0 | 3 | 0
22:30 | 3944 | 1781 | 924 | 0 | 60 | 1303.43 | 40 | 3759 | 0 | 219 | 568.5 | 0 | 0 | 5.5 | 0
23:00 | 3905 | 1795 | 924 | 0 | 62 | 1246.92 | 40 | 3681 | 0 | 211 | 505 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 06:00 | 382 | 10:00 | Payra | 418 | 06:00 | 407 | 13:00
Ashuganj | 408 | 4:00 | 380 | 16:00 | Rahanpur | 403 | 23:00 | 395 | 04:00
Bhulta | 400 | 07:00 | 373 | 12:00 | Rampal | 409 | 07:00 | 389 | 14:00
Bibiana | 397 | 00:00 | 382 | 13:00
BIPTC | 397 | 02:00 | 387 | 13:00
Bogura | 395 | 18:30 | 383 | 04:00
Gopalganj | 406 | 06:00 | 384 | 14:00
Kaliakoir | 377 | 04:00 | 351 | 14:00
Madunaghat | 404 | 07:00 | 388 | 14:00
Meghnaghat | 397 | 06:00 | 372 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 06:00 | 215 | 14:00 | Keranigonj | 230 | 06:00 | 213 | 14:00
AKSML | 233 | 08:00 | 221 | 13:00 | Khulna(S) | 237 | 06:00 | 222 | 14:00
Aminbazar | 231 | 04:00 | 215 | 13:00 | Madunaghat | 235 | 06:00 | 225 | 13:00
Ashuganj | 233 | 04:00 | 218 | 13:00 | Madunaghat-400 | 236 | 07:00 | 225 | 13:00
Ashuganj-400 | 232 | 4:00 | 216 | 16:00 | Maniknagar | 226 | 03:00 | 211 | 14:00
Baghabari | 237 | 05:00 | 224 | 11:00 | Meghnaghat | 234 | 01:00 | 221 | 14:00
Barapukuria | 225 | 05:00 | 216 | 09:00 | Meghnaghat-400 | 231 | 07:00 | 216 | 14:00
Barapukuria-230 | 225 | 6:00 | 217 | 10:00 | Mirsorai | 232 | 07:00 | 217 | 13:00
Barishal | 239 | 06:00 | 228 | 14:00 | Rajshahi | 235 | 00:00 | 221 | 09:00
Bheramara | 235 | 00:00 | 222 | 09:00 | Rampal | 235 | 06:00 | 220 | 14:00
Bhulta | 228 | 04:00 | 211 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 02:00 | 218 | 14:00 | Rampura | 228 | 06:00 | 209 | 14:00
BIPTC | 237 | 01:00 | 222 | 09:00 | Shikalbaha | 233 | 07:00 | 222 | 13:00
Bogura | 238 | 05:00 | 223 | 14:00 | Shyampur | 229 | 06:00 | 213 | 14:00
Bogura-400 | 237 | 05:00 | 222 | 14:00 | Siddhirganj | 230 | 04:00 | 214 | 14:00
Borhanuddin | 241 | 03:00 | 236 | 13:00 | Sirajgonj | 242 | 05:00 | 230 | 14:00
BSRM | 232 | 07:00 | 216 | 14:00 | Sreepur | 233 | 01:00 | 218 | 14:00
Cumilla(N) | 227 | 06:00 | 213 | 14:00 | Tongi | 226 | 04:00 | 210 | 11:00
Faridpur | 236 | 06:00 | 223 | 13:00
Fenchuganj | 234 | 06:00 | 222 | 14:00
Ghorashal | 230 | 01:00 | 220 | 09:00
Ghorashal-230 | 228 | 04:00 | 213 | 14:00
Gopalganj | 235 | 06:00 | 221 | 14:00
GPH | 234 | 07:00 | 220 | 14:00
Haripur | 229 | 07:00 | 213 | 14:00
Hasnabad | 228 | 04:00 | 213 | 14:00
Hathazari | 236 | 06:00 | 225 | 13:00
Ishurdi | 238 | 01:00 | 225 | 09:00
Jhenaidah | 235 | 06:00 | 219 | 14:00
Kaliakoir | 231 | 18:00 | 216 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 04:00 | 120 | 12:00 | Madunaghat | 135 | 06:00 | 128 | 12:00
Agargaon | 139 | 06:00 | 128 | 12:00 | Magura | 136 | 02:00 | 124 | 13:00
Agrabad | 134 | 05:00 | 125 | 14:00 | Mahasthangarh | 133 | 05:00 | 122 | 13:00
AKS | 132 | 05:00 | 125 | 12:00 | Manikganj | 130 | 01:00 | 119 | 14:00
Aminbazar | 137 | 18:00 | 125 | 10:00 | Maniknagar | 130 | 08:00 | 117 | 13:00
Amnura | 136 | 05:00 | 128 | 09:00 | Matarbari | 128 | 08:00 | 115 | 20:00
Ashuganj | 137 | 05:00 | 130 | 12:00 | Matuail | 132 | 07:00 | 123 | 14:00
Bagerhat | 134 | 06:00 | 121 | 14:00 | Millgate | 132 | 04:00 | 119 | 12:00
Bajitpur | 131 | 00:00 | 123 | 14:00 | Mirpur | 135 | 06:00 | 124 | 14:00
Bakulia | 134 | 01:00 | 127 | 12:00 | Mirzapur | 131 | 18:30 | 123 | 14:00
Banani | 132 | 03:00 | 120 | 12:00 | Mithapukur | 133 | 06:00 | 122 | 09:00
Bangabhaban | 129 | 05:00 | 117 | 14:00 | MI_Cement | 133 | 04:00 | 123 | 13:00
Barapukuria | 138 | 01:00 | 130 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 06:00 | 132 | 12:00 | Mogbazar | 133 | 04:00 | 120 | 12:00
Barishal | 133 | 07:00 | 126 | 13:00 | Mongla | 135 | 04:00 | 122 | 14:00
Barishal-230 | 134 | 06:00 | 126 | 14:00 | Motijheel | 129 | 05:00 | 117 | 14:00
Baroaulia | 133 | 05:00 | 131 | 01:00 | Muktagacha | 134 | 00:00 | 125 | 17:00
Baroirhat | 128 | 06:00 | 116 | 14:00 | Munshiganj | 132 | 03:00 | 122 | 12:00
Bashundhara | 132 | 04:00 | 120 | 11:00 | Muradnagar | 130 | 07:00 | 118 | 14:00
BashundharaCement | 132 | 05:00 | 121 | 19:00 | Mymensingh | 135 | 00:00 | 112 | 14:00
Beanibazar | 132 | 04:00 | 127 | 15:00 | Naogaon | 132 | 05:00 | 119 | 12:00
Benapole | 135 | 06:00 | 122 | 13:00 | Narail | 138 | 05:00 | 122 | 14:00
Bhaluka | 128 | 01:00 | 116 | 14:00 | Narinda | 130 | 8:00 | 117 | 13:00
Bhandaria | 130 | 06:00 | 121 | 14:00 | Narshingdi | 132 | 18:00 | 116 | 14:00
Bhangura | 136 | 02:00 | 126 | 09:00 | Natore | 134 | 01:00 | 125 | 09:00
Bheramara | 137 | 00:00 | 129 | 09:00 | Nawabganj | 135 | 05:00 | 124 | 13:00
Bheramara(GK) | 137 | 00:00 | 129 | 08:00 | Netrakona | 124 | 03:00 | 109 | 17:00
Bhulta | 128 | 18:00 | 118 | 11:00 | New | 134 | 18:30 | 120 | 12:00
Bog-Sherpur | 133 | 05:00 | 123 | 13:00 | Niamatpur | 137 | 04:00 | 134 | 14:00
Bogura | 135 | 04:00 | 125 | 14:00 | Noapara | 135 | 06:00 | 123 | 14:00
Bogura-230 | 135 | 05:00 | 126 | 09:00 | Pabna | 137 | 01:00 | 128 | 11:00
Brahmanbaria | 130 | 05:00 | 120 | 14:00 | Palashbari | 131 | 06:00 | 119 | 13:00
Cantonment | 139 | 06:00 | 128 | 12:00 | Panchagarh | 136 | 02:00 | 119 | 09:00
Chandpur | 123 | 18:30 | 115 | 12:00 | Patuakhali | 136 | 03:00 | 131 | 13:00
Chandraghona | 136 | 07:00 | 128 | 14:00 | Payra | 138 | 06:00 | 133 | 14:00
Chapai | 135 | 05:00 | 128 | 00:00 | PHP | 126 | 06:00 | 115 | 13:00
Charsaidpur | 133 | 06:00 | 122 | 13:00 | Postogola | 135 | 03:00 | 125 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 129 | 06:00 | 115 | 14:00 | Purbachal | 132 | 02:00 | 119 | 12:00
Chhatak | 133 | 07:00 | 126 | 13:00 | Purbasadipur | 132 | 02:00 | 118 | 13:00
Chowmuhani | 120 | 00:00 | 112 | 14:00 | Rahanpur | 138 | 01:00 | 137 | 04:00
Chuadanga | 136 | 05:00 | 122 | 14:00 | Rahanpur-400 | 138 | 02:00 | 135 | 04:00
Coxsbazar | 130 | 07:00 | 116 | 20:00 | Rahim | 132 | 03:00 | 123 | 14:00
Cumilla(N) | 131 | 07:00 | 121 | 12:00 | Rajbari | 132 | 06:00 | 122 | 14:00
Cumilla(S) | 133 | 01:00 | 119 | 12:00 | Rajendrapur | 132 | 18:30 | 122 | 11:00
Daudkandi | 128 | 06:00 | 116 | 12:00 | Rajshahi | 136 | 06:00 | 126 | 12:00
Dhaka | 133 | 02:00 | 119 | 13:00 | Rajshahi-230 | 135 | 00:00 | 126 | 17:00
Dhamrai | 130 | 02:00 | 121 | 12:00 | Ramganj | 121 | 06:00 | 111 | 12:00
Dhanmondi | 133 | 04:00 | 123 | 14:00 | Rampur | 134 | 06:00 | 126 | 13:00
Dohazari | 131 | 03:00 | 124 | 12:00 | Rampura | 133 | 06:00 | 120 | 12:00
Faridpur | 132 | 06:00 | 125 | 13:00 | Rangamati | 135 | 06:00 | 127 | 13:00
Fatullah | 134 | 06:00 | 124 | 12:00 | Rangpur | 130 | 01:00 | 121 | 13:00
Fenchuganj | 137 | 06:00 | 129 | 14:00 | Ruppur | 139 | 06:00 | 130 | 13:00
Feni | 126 | 07:00 | 115 | 12:00 | Saidpur | 135 | 05:00 | 121 | 10:00
Ghatail | 130 | 00:00 | 122 | 16:00 | Satkhira | 135 | 06:00 | 122 | 19:00
Ghorashal | 137 | 05:00 | 129 | 13:00 | Satmasjid | 139 | 06:00 | 127 | 13:00
Goalpara | 138 | 06:00 | 126 | 14:00 | Savar | 136 | 18:00 | 122 | 12:00
Gollamari | 137 | 06:00 | 126 | 13:00 | SevenRings | 137 | 04:00 | 128 | 14:00
Gopalganj | 136 | 05:00 | 127 | 14:00 | ShahCement | 133 | 06:00 | 122 | 13:00
Gopalganj-400 | 138 | 06:00 | 130 | 13:00 | Shahjadpur | 140 | 03:00 | 130 | 15:00
Gulshan | 132 | 05:00 | 120 | 12:00 | Shahjibazar | 131 | 04:00 | 123 | 14:00
Halishahar | 134 | 05:00 | 125 | 14:00 | Shahmirpur | 135 | 03:00 | 127 | 14:00
Haripur | 133 | 04:00 | 124 | 12:00 | Shariatpur | 136 | 05:00 | 127 | 14:00
HaripurSBU | 133 | 04:00 | 124 | 12:00 | Sherpur | 137 | 19:30 | 126 | 10:00
Hasnabad | 135 | 06:00 | 125 | 13:00 | Shikalbaha | 125 | 06:00 | 118 | 13:00
Hathazari | 137 | 06:00 | 130 | 15:00 | Shikalbaha-230 | 137 | 07:00 | 129 | 13:00
Ishurdi | 139 | 00:00 | 130 | 09:00 | Shitalakhya | 133 | 04:00 | 123 | 14:00
Jaldhaka | 132 | 06:00 | 117 | 13:00 | Sholosohor | 136 | 07:00 | 128 | 12:00
Jamalpur | 140 | 19:00 | 128 | 10:00 | Shyampur | 138 | 07:00 | 124 | 12:00
Jashore | 136 | 06:00 | 122 | 14:00 | Shyampur-230 | 134 | 07:00 | 124 | 12:00
Jhenaidah | 137 | 03:00 | 132 | 13:00 | Siddhirganj | 132 | 04:00 | 123 | 14:00
Jhenaidah-230 | 138 | 05:00 | 126 | 13:00 | Sirajganj | 136 | 04:00 | 124 | 08:00
Joydebpur | 133 | 18:30 | 125 | 11:00 | Sonargaon | 130 | 02:00 | 121 | 12:00
Joypurhat | 130 | 01:00 | 117 | 09:00 | Sreemongol | 132 | 07:00 | 125 | 15:00
Juldah | 135 | 06:00 | 127 | 13:00 | Sreepur | 131 | 01:00 | 121 | 14:00
Kabirpur | 132 | 00:00 | 116 | 11:00 | Srinagar | 135 | 04:00 | 125 | 12:00
Kachua | 125 | 07:00 | 114 | 12:00 | SSM | 140 | 03:00 | 136 | 09:00
Kaliakoir | 136 | 04:00 | 123 | 12:00 | Sunamganj | 131 | 04:00 | 125 | 13:00
Kallyanpur | 136 | 06:00 | 125 | 13:00 | Sylhet | 132 | 01:00 | 127 | 13:00
Kalurghat | 136 | 07:00 | 128 | 13:00 | Sylhet-132 | 133 | 04:00 | 129 | 13:00
Kamrangirchar | 135 | 03:00 | 124 | 13:00 | Tangail | 129 | 04:00 | 122 | 14:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 134 | 02:00 | 117 | 09:00
Kazla | 128 | 05:00 | 117 | 13:00 | TK | 136 | 05:00 | 128 | 14:00
Keranigonj | 136 | 06:00 | 124 | 14:00 | Tongi | 134 | 04:00 | 122 | 10:00
Khagrachori | 135 | 06:00 | 126 | 13:00 | Ullahpara | 136 | 01:00 | 126 | 09:00
Khosba | 130 | 07:00 | 118 | 12:00 | Ullon | 133 | 02:00 | 119 | 13:00
Khulna | 136 | 06:00 | 124 | 14:00 | Uttara | 135 | 05:00 | 118 | 12:00
Khulna(S) | 138 | 06:00 | 126 | 14:00 | UttaraNew | 136 | 06:00 | 124 | 13:00
Khulshi | 134 | 06:00 | 124 | 13:00 | Zigatola | 136 | 06:00 | 125 | 12:00
Kishoreganj | 131 | 05:00 | 121 | 12:00
Kodda | 133 | 18:30 | 120 | 14:00
KSRM | 135 | 18:00 | 127 | 12:00
Kulaura | 134 | 03:00 | 129 | 14:00
Kurigram | 131 | 23:00 | 120 | 13:00
Kushtia | 137 | 05:00 | 127 | 13:00
Lalbag | 136 | 07:00 | 124 | 14:00
Lalmonirhat | 130 | 01:00 | 120 | 10:00
Madanganj | 132 | 05:00 | 122 | 14:00
Madaripur | 133 | 07:00 | 128 | 14:00
Madartek | 132 | 04:00 | 118 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division