## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-03-2025 | during | 12-03-2025 | during | 12-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 130 | 130 | 110 | 110 | 110 | 110 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 371 | 403 | 400.75 | 400.75 | 380 | 380 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 310 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 321 | 335 | 335 | 280 | 280 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 40 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 19 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 25 | 52.19 | 52.19 | 17 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 100 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 67 | 105 | 105 | 50 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 24 | 0 | 104 | 104 | 90 | 90 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 148 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 54 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2047 | 2242 | 5120.5 | 5184.5 | 3029.36 | 3121.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 202 | 201 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 81 | 81 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 20 | 2 | 30 | 2 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 32 | 32 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.37 | 0 | 4.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 51 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 35 | 35 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 0 | 3 | 6 | 3 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 352 | 351 | 350 | 350 | 350 | 350 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2026 | 2155 | 3171.09 | 3195.72 | 3031.09 | 3037.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 204 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 200 | 0 | 200 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 356.56 | 356.56 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 29 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 11 | 29 | 30 | 30 | 20 | 20 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 175 | 200 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 70 | 10 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 40 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 56 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 66 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 20.83 | 20.83 | 11 | 11 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 15 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 93 | 58 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1136 | 1118 | 2085.53 | 2235.53 | 1750.2 | 1929.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-03-2025 | during | 12-03-2025 | during | 12-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 30 | 30 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 155 | 200 | 200 | 134 | 134 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 88 | 88 | 115 | 115 | 98 | 98 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.77 | 0 | 40 | 0 | 40 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 281.77 | 255 | 643.7 | 601.5 | 380.7 | 338.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 41 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 28 | 32 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 164 | 162 | 162 | 162 | 162 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 22 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 340 | 335 | 350 | 350 | 350 | 350 | Due to air filter DP high FL is not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1533 | 1518 | 1600 | 1600 | 1552 | 1552
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 919 | 918 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 182 | 122 | 410 | 410 | 230 | 230 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 88 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 370 | 620 | 1234.2 | 1234.2 | 610 | 610 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1559 | 1660 | 3607.2 | 3512.2 | 2132.02 | 2037.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 8 | 10.12 | 10.12 | 7 | 7 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 135 | 135 | 123 | 123 | FGMO
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 1244 | 1244 | 1244 | 1244 | 1244 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 217 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1111.6 | 1942 | 2177.12 | 2176.12 | 2162 | 2161
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 158 | 128 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 141 | 125 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 330 | 375 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.62 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1214.36 | 1364 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.47 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 92 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1994.95 | 2063.5 | 3110.03 | 2943.53 | 2798.25 | 2631.75
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 60 | 62 | 62 | 62 | 62 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 171 | 165 | 150 | 150 | 175 | 175 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 155 | 0 | 184 | 0 | 184 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 411.6 | 330 | 694.6 | 474 | 685.62 | 465.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12100.92 | 13283.5 | 22209.77 | 21923.1 | 17521.24 | 17273.57
Forecast Scenario (12-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11750 |  | 0 |  | 11750
|  |  |  | 1:00 | 11200 |  | 0 |  | 11200
|  |  |  | 2:00 | 10750 |  | 0 |  | 10750
|  |  |  | 3:00 | 11000 |  | 0 |  | 11000
|  |  |  | 4:00 | 11450 |  | 0 |  | 11450
|  |  |  | 5:00 | 10400 |  | 0 |  | 10400
|  |  |  | 6:00 | 9600 |  | 0 |  | 9600
|  |  |  | 7:00 | 9900 |  | 0 |  | 9900
|  |  |  | 8:00 | 10460 |  | 0 |  | 10460
|  |  |  | 9:00 | 11200 |  | 0 |  | 11200
|  |  |  | 10:00 | 11600 |  | 0 |  | 11600
|  |  |  | 11:00 | 11950 |  | 0 |  | 11950
|  |  |  | 12:00 | 12380 |  | 0 |  | 12380
|  |  |  | 13:00 | 12750 |  | 0 |  | 12750
|  |  |  | 14:00 | 13050 |  | 0 |  | 13050
|  |  |  | 15:00 | 12910 |  | 0 |  | 12910
|  |  |  | 16:00 | 12700 |  | 0 |  | 12700
|  |  |  | 17:00 | 12880 |  | 0 |  | 12880
|  |  |  | 18:00 | 12580 |  | 0 |  | 12580
|  |  |  | 18:30 | 12800 |  | 0 |  | 12800
|  |  |  | 19:00 | 13100 |  | 0 |  | 13100
|  |  |  | 19:30 | 13230 |  | 0 |  | 13230
|  |  |  | 20:00 | 13080 |  | 0 |  | 13080
|  |  |  | 21:00 | 13100 |  | 0 |  | 13100
|  |  |  | 22:00 | 12830 |  | 0 |  | 12830
|  |  |  | 23:00 | 12370 |  | 0 |  | 12370
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 12380.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13230.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 284.99 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:00 hrs on 12-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-03-2025 | [28 empty] | Date: | 11-03-2025 | [28 empty] | Date: | 11-03-2025 | [28 empty] | Date: | 11-03-2025 | [28 empty] | Date: | 11-03-2025 | [18 empty] | Date: | 11-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 110 | 0 | 130 | 0 | 0 | 380 | 0 | 0 | 0 | 32 | 0 | 86 | 48 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 271 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 52 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 38 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1080 | 0 | 51 | 0 | 16 | 0 | 230 | 285 | 10 | 182 | 36 | 0 | 50 | 51 | 29 | 18 | 34 | 58 | 0 | 0 | 0 | 310 | 320 | 347 | 32 | 30 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 86 | 85 | 30 | 0 | 0 | 12 | 6495.5 | 924 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488 | 0 | 1152.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 153 | 0 | 360 | 0 | 0 | 2.5 | 174 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 130 | 220 | 0 | 0 | 1050 | 0 | 5364.88 | 11860.38 | 87.8
01:00 | 0 | 17 | 8 | 110 | 0 | 80 | 0 | 0 | 369 | 0 | 0 | 0 | 35 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 279 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 0 | 35 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 38 | 353 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 16 | 0 | 230 | 285 | 10 | 191 | 36 | 0 | 50 | 34 | 29 | 18 | 34 | 60 | 0 | 0 | 0 | 300 | 320 | 310 | 32 | 30 | 30 | 5 | 120 | 16 | 0 | 30 | 30 | 0 | 16 | 162 | 0 | 75 | 65 | 30 | 0 | 0 | 12 | 6122.5 | 924 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 0 | 1064.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 155 | 0 | 360 | 0 | 0 | 2.5 | 172 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 130 | 220 | 0 | 0 | 1050 | 0 | 5182.1 | 11304.6 | 87.8
02:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 35 | 0 | 43 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 400 | 309 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 0 | 35 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 38 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 16 | 0 | 230 | 285 | 10 | 196 | 33 | 0 | 50 | 34 | 29 | 11 | 34 | 56 | 0 | 0 | 0 | 320 | 320 | 313 | 32 | 30 | 30 | 5 | 120 | 16 | 0 | 30 | 30 | 0 | 16 | 162 | 0 | 55 | 55 | 30 | 0 | 0 | 12 | 5909.5 | 924 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 960.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 159 | 0 | 300 | 0 | 0 | 2.5 | 174 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 130 | 180 | 0 | 0 | 1050 | 0 | 4956.39 | 10865.89 | 87.8
03:00 | 0 | 50 | 8 | 110 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 35 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 30 | 0 | 360 | 315 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 0 | 48 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 38 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1035 | 0 | 51 | 0 | 16 | 0 | 180 | 260 | 10 | 216 | 33 | 0 | 50 | 34 | 29 | 11 | 34 | 60 | 0 | 0 | 0 | 325 | 320 | 345 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 10 | 30 | 0 | 16 | 162 | 0 | 59 | 78 | 30 | 0 | 0 | 12 | 6029.5 | 924 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 1074.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 163 | 0 | 260 | 0 | 0 | 2.5 | 177 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 0 | 1060 | 0 | 5042.47 | 11071.97 | 87.79
04:00 | 0 | 34 | 8 | 110 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 0 | 62 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 360 | 302 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 0 | 34 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1045 | 0 | 51 | 0 | 16 | 0 | 230 | 285 | 10 | 181 | 33 | 0 | 50 | 34 | 29 | 11 | 0 | 60 | 0 | 0 | 0 | 325 | 320 | 347 | 32 | 30 | 30 | 5 | 163 | 16 | 0 | 41 | 30 | 0 | 16 | 162 | 0 | 77 | 105 | 31 | 0 | 0 | 12 | 6096.5 | 924 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 1171.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 164 | 0 | 360 | 0 | 0 | 2.5 | 177 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 100 | 220 | 0 | 0 | 1050 | 0 | 5426.22 | 11522.72 | 87.79
05:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 400 | 277 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 0 | 8 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 353 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 954 | 0 | 51 | 0 | 16 | 0 | 230 | 285 | 10 | 160 | 33 | 0 | 50 | 0 | 9 | 11 | 0 | 56 | 0 | 0 | 0 | 310 | 320 | 347 | 32 | 30 | 30 | 5 | 120 | 16 | 0 | 41 | 30 | 0 | 16 | 163 | 0 | 79 | 65 | 31 | 0 | 0 | 12 | 5667.5 | 924 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 1115.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 161 | 0 | 330 | 0 | 0 | 2.5 | 176 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 0 | 950 | 0 | 4986.71 | 10654.21 | 87.78
06:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 292 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 0 | 0 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 353 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 830 | 0 | 10 | 0 | 16 | 0 | 230 | 285 | 10 | 152 | 36 | 0 | 50 | 0 | 0 | 11 | 0 | 48 | 0 | 0 | 0 | 290 | 320 | 305 | 5 | 30 | 30 | 5 | 120 | 16 | 0 | 11 | 30 | 0 | 16 | 162 | 0 | 55 | 55 | 31 | 0 | 0 | 12 | 5220.5 | 923 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 830.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 162 | 0 | 330 | 0 | 0 | 2.5 | 175 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 800 | 0 | 4498.33 | 9718.83 | 87.78
07:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 3 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 311 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 2 | 0 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 10 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 835 | 3 | 10 | 0 | 16 | 0 | 105 | 285 | 10 | 202 | 33 | 0 | 50 | 0 | 0 | 0 | 0 | 48 | 0 | 7 | 0 | 315 | 320 | 305 | 5 | 30 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 162 | 0 | 55 | 65 | 31 | 0 | 2.83 | 12 | 5259.33 | 924 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 411 | 0 | 832.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 2.51 | 161 | 0 | 0 | 0 | 162 | 0 | 400 | 0 | 0.21 | 2.5 | 172 | 62 | 0 | 2 | 0 | 0 | 0 | 0.4 | 3 | 0.05 | 0 | 220 | 5 | 100 | 220 | 0 | 0 | 800 | 0 | 4710.23 | 9969.56 | 87.77
08:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 17 | 0 | 64 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 350 | 312 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2 | 40 | 0 | 7 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1028 | 9 | 18 | 0 | 83 | 0 | 0 | 285 | 10 | 219 | 33 | 0 | 50 | 0 | 0 | 10 | 0 | 50 | 0 | 20 | 0 | 310 | 320 | 347 | 26 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 162 | 0 | 78 | 85 | 26 | 0 | 5.44 | 12 | 5705.44 | 924 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.81 | 377 | 0 | 958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 12.4 | 183 | 0 | 0 | 0 | 159 | 0 | 414 | 0 | 1.05 | 2.5 | 174 | 62 | 0 | 9 | 0 | 0 | 0 | 1.4 | 53 | 0.17 | 0 | 140 | 5 | 80 | 180 | 0 | 0 | 700 | 0 | 4712.83 | 10418.27 | 87.76
09:00 | 0 | 50 | 17 | 110 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 1 | 37 | 0 | 105 | 32 | 0 | 25 | 0 | 0 | 30 | 0 | 350 | 294 | 0 | 0 | 30 | 20 | 250 | 0 | 0 | 15 | 0 | 16.5 | 21 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 19.86 | 87 | 12 | 3 | 40 | 16 | 5 | 352 | 0 | 0 | 2 | 0 | 38 | 211 | 0 | 0 | 0 | 1224 | 14 | 51 | 12 | 158 | 0 | 0 | 285 | 10 | 182 | 33 | 31 | 40 | 61 | 6 | 11 | 0 | 52 | 0 | 35 | 0 | 300 | 320 | 347 | 30 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 79 | 89 | 24 | 1 | 18.34 | 12 | 6548.7 | 869 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 358 | 0 | 980.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 23.4 | 162 | 0 | 0 | 0 | 145 | 0 | 370 | 0 | 2.24 | 5.5 | 172 | 62 | 0 | 16 | 0 | 0 | 0 | 2.8 | 90 | 0.3 | 0 | 140 | 4 | 80 | 180 | 0 | 0 | 520 | 0 | 4495.22 | 11043.92 | 87.76
10:00 | 0 | 50 | 17 | 130 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 54 | 0 | 101 | 16 | 75 | 55 | 0 | 0 | 25 | 0 | 350 | 288 | 0 | 0 | 55 | 20 | 250 | 0 | 0 | 22 | 34 | 20 | 15 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 12 | 3 | 40 | 34 | 4 | 352 | 0 | 0 | 18 | 0 | 51 | 205 | 0 | 0 | 0 | 1184 | 18 | 51 | 75 | 177 | 0 | 0 | 285 | 10 | 183 | 33 | 95 | 40 | 51 | 9 | 17 | 0 | 52 | 0 | 46 | 0 | 290 | 320 | 347 | 28 | 30 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 88 | 110 | 11 | 1 | 16.15 | 12 | 6878.15 | 917 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 374 | 0 | 1120.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 39.78 | 171 | 0 | 0 | 0 | 143 | 0 | 330 | 0 | 3.65 | 5.5 | 171 | 62 | 0 | 16 | 0 | 0 | 0 | 4.7 | 110 | 0.46 | 0 | 140 | 4 | 80 | 180 | 0 | 0 | 520 | 0 | 4749.88 | 11628.03 | 87.75
11:00 | 8 | 50 | 17 | 130 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 54 | 0 | 115 | 16 | 75 | 55 | 10 | 60 | 30 | 16 | 350 | 302 | 0 | 0 | 55 | 16 | 250 | 0 | 0 | 26 | 54 | 20 | 20 | 0 | 0 | 35 | 15 | 0 | 0 | 9 | 0 | 0 | 0 | 50 | 12 | 4 | 40 | 34 | 4 | 352 | 0 | 0 | 18 | 0 | 51 | 201 | 0 | 0 | 0 | 1224 | 20 | 51 | 100 | 177 | 0 | 0 | 285 | 10 | 186 | 28 | 98 | 30 | 51 | 9 | 11 | 0 | 56 | 0 | 55 | 0 | 290 | 320 | 348 | 28 | 30 | 30 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 89 | 136 | 10 | 2 | 34.22 | 12 | 7111.22 | 918 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 373 | 0 | 1116.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 44.66 | 169 | 0 | 0 | 0 | 141 | 0 | 330 | 0 | 4.39 | 5.5 | 170 | 62 | 0 | 27 | 0 | 0 | 0 | 5.2 | 130 | 0.55 | 0 | 140 | 4 | 80 | 180 | 0 | 0 | 520 | 0 | 4787.26 | 11898.48 | 87.75
12:00 | 0 | 50 | 17 | 130 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 35 | 0 | 100 | 16 | 15 | 15 | 40 | 148 | 30 | 24 | 350 | 304 | 0 | 0 | 17 | 16 | 250 | 0 | 0 | 28 | 54 | 0 | 20 | 0 | 0 | 35 | 15 | 0 | 0 | 12 | 0 | 0 | 0 | 50 | 0 | 4 | 40 | 17 | 4 | 352 | 0 | 0 | 0 | 0 | 51 | 202 | 0 | 0 | 0 | 1224 | 20 | 51 | 70 | 175 | 0 | 0 | 285 | 11 | 199 | 29 | 93 | 30 | 56 | 15 | 11 | 0 | 54 | 0 | 57 | 0 | 310 | 320 | 340 | 28 | 30 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 164 | 0 | 88 | 135 | 5 | 2 | 39.77 | 12 | 7023.77 | 919 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 370 | 0 | 1214.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 49.47 | 158 | 0 | 0 | 0 | 141 | 0 | 330 | 0 | 4.62 | 5.5 | 171 | 62 | 0 | 18 | 0 | 0 | 0 | 5.6 | 155 | 0.6 | 0 | 217 | 4 | 130 | 220 | 0 | 0 | 540 | 0 | 5077.15 | 12100.92 | 87.74
13:00 | 0 | 50 | 17 | 130 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 35 | 0 | 97 | 16 | 15 | 0 | 55 | 148 | 30 | 0 | 350 | 287 | 0 | 0 | 17 | 16 | 280 | 0 | 0 | 29 | 62 | 15 | 19 | 0 | 0 | 35 | 15 | 1 | 0 | 17 | 0 | 0 | 0 | 50 | 0 | 4 | 40 | 17 | 12 | 352 | 0 | 0 | 0 | 0 | 51 | 201 | 0 | 0 | 0 | 1224 | 19 | 51 | 20 | 175 | 0 | 0 | 285 | 21 | 185 | 30 | 94 | 40 | 100 | 9 | 11 | 0 | 58 | 0 | 55 | 0 | 315 | 320 | 336 | 28 | 28 | 30 | 5 | 163 | 16 | 0 | 81 | 30 | 0 | 16 | 163 | 0 | 78 | 136 | 5 | 2 | 40.84 | 12 | 7032.84 | 918 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 477 | 0 | 1306.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 38.93 | 151 | 0 | 0 | 0 | 134 | 0 | 414 | 0 | 4.64 | 5.5 | 168 | 62 | 0 | 29 | 5 | 0 | 0 | 5.8 | 141 | 0.58 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 760 | 0 | 5623.99 | 12656.83 | 87.74
14:00 | 0 | 33 | 8 | 130 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 35 | 0 | 113 | 16 | 15 | 0 | 55 | 162 | 30 | 0 | 370 | 301 | 0 | 0 | 17 | 16 | 309 | 0 | 0 | 25 | 70 | 2 | 19 | 0 | 0 | 35 | 16 | 7 | 0 | 21 | 0 | 0 | 0 | 62 | 0 | 3 | 40 | 17 | 4 | 352 | 0 | 0 | 0 | 0 | 51 | 201 | 0 | 0 | 0 | 1224 | 17 | 51 | 20 | 175 | 0 | 0 | 285 | 29 | 211 | 30 | 95 | 40 | 100 | 9 | 11 | 0 | 68 | 0 | 47 | 0 | 310 | 320 | 337 | 28 | 28 | 30 | 0 | 163 | 16 | 0 | 80 | 30 | 0 | 16 | 165 | 0 | 79 | 135 | 5 | 2 | 34.21 | 12 | 7125.21 | 918 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 478 | 0 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 45.17 | 140 | 0 | 0 | 0 | 127 | 0 | 414 | 0 | 4.41 | 5.5 | 171 | 61 | 0 | 24 | 35 | 0 | 0 | 5.1 | 137 | 0.51 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 860 | 0 | 5815.69 | 12940.9 | 87.73
15:00 | 8 | 33 | 8 | 130 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 35 | 41 | 0 | 113 | 63 | 35 | 5 | 55 | 162 | 30 | 10 | 420 | 273 | 0 | 0 | 25 | 16 | 309 | 0 | 0 | 21 | 70 | 14 | 19 | 0 | 0 | 35 | 65 | 12 | 0 | 24 | 0 | 0 | 0 | 70 | 0 | 2 | 40 | 34 | 3 | 352 | 0 | 0 | 0 | 0 | 60 | 201 | 0 | 0 | 0 | 1224 | 14 | 51 | 30 | 187 | 0 | 0 | 285 | 29 | 183 | 33 | 71 | 40 | 126 | 9 | 6 | 0 | 66 | 0 | 36 | 0 | 305 | 320 | 337 | 28 | 5 | 30 | 5 | 163 | 16 | 0 | 80 | 30 | 0 | 16 | 164 | 0 | 79 | 135 | 5 | 1 | 21.97 | 12 | 7308.97 | 918 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 476 | 0 | 1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 36.26 | 131 | 0 | 0 | 0 | 125 | 0 | 414 | 0 | 3.35 | 4 | 171 | 61 | 0 | 11 | 49 | 0 | 0 | 3.9 | 102 | 0.39 | 0 | 291 | 6 | 130 | 220 | 0 | 0 | 860 | 0 | 5600.9 | 12909.87 | 87.73
16:00 | 16 | 33 | 8 | 130 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 54 | 0 | 128 | 63 | 70 | 15 | 55 | 162 | 30 | 17 | 420 | 302 | 0 | 0 | 35 | 16 | 309 | 0 | 0 | 11 | 70 | 14 | 19 | 0 | 0 | 35 | 50 | 12 | 0 | 16 | 0 | 0 | 0 | 24 | 0 | 1 | 40 | 34 | 7 | 352 | 0 | 0 | 0 | 0 | 34 | 201 | 0 | 0 | 0 | 1224 | 8 | 43 | 65 | 190 | 0 | 0 | 285 | 29 | 206 | 33 | 72 | 40 | 136 | 24 | 15 | 9 | 62 | 0 | 20 | 0 | 315 | 320 | 337 | 31 | 5 | 30 | 5 | 163 | 13 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 78 | 135 | 0 | 1 | 14.23 | 12 | 7430.23 | 918 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 477 | 0 | 1319 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19.06 | 127 | 0 | 0 | 0 | 128 | 0 | 382 | 0 | 1.86 | 4 | 168 | 60 | 0 | 8 | 49 | 0 | 0 | 2.3 | 60 | 0.24 | 0 | 250 | 5 | 130 | 220 | 0 | 0 | 800 | 0 | 5341.46 | 12771.69 | 87.72
17:00 | 24 | 33 | 11 | 130 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 49 | 54 | 0 | 131 | 115 | 95 | 15 | 55 | 162 | 30 | 16 | 320 | 290 | 0 | 0 | 35 | 16 | 314 | 0 | 0 | 4 | 70 | 17 | 19 | 0 | 0 | 35 | 50 | 13 | 0 | 14 | 0 | 0 | 0 | 70 | 12 | 0 | 80 | 34 | 17 | 350 | 0 | 0 | 7 | 0 | 34 | 201 | 0 | 0 | 0 | 1224 | 2 | 43 | 110 | 190 | 0 | 0 | 285 | 29 | 185 | 33 | 69 | 40 | 136 | 26 | 17 | 34 | 64 | 0 | 8 | 6 | 310 | 320 | 337 | 31 | 10 | 29 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 78 | 139 | 0 | 0 | 4.89 | 12 | 7577.89 | 919 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 476 | 0 | 1322 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 16 | 0 | 6.99 | 123 | 0 | 0 | 0 | 126 | 0 | 359 | 0 | 0.55 | 4 | 169 | 61 | 10 | 4 | 49 | 0 | 0 | 0.7 | 21 | 0.09 | 0 | 250 | 6 | 130 | 220 | 0 | 0 | 800 | 0 | 5271.33 | 12849.22 | 87.72
18:00 | 40 | 36 | 22 | 130 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 0 | 136 | 127 | 135 | 15 | 55 | 162 | 30 | 16 | 320 | 292 | 0 | 0 | 35 | 16 | 314 | 0 | 0 | 0 | 70 | 20 | 19 | 0 | 0 | 35 | 50 | 25 | 0 | 11 | 17 | 0 | 0 | 70 | 12 | 0 | 40 | 34 | 17 | 350 | 17 | 0 | 19 | 7 | 34 | 201 | 0 | 0 | 0 | 1141 | 0 | 43 | 120 | 117 | 0 | 0 | 275 | 26 | 192 | 5 | 77 | 40 | 136 | 31 | 17 | 34 | 68 | 0.1 | 0 | 32 | 310 | 320 | 306 | 5 | 10 | 30 | 5 | 163 | 22 | 0 | 41 | 30 | 0 | 16 | 164 | 0 | 88 | 154 | 0 | 0 | 0.08 | 12 | 7468.18 | 918 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 420 | 0 | 1268 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 4 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 121 | 0 | 340 | 0 | 0.02 | 4 | 174 | 60 | 35 | 0 | 49 | 0 | 0 | 0 | 1 | 0 | 0 | 208 | 7 | 130 | 220 | 0 | 0 | 860 | 2 | 5132.02 | 12600.2 | 87.71
19:00 | 0 | 65 | 25 | 130 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 17 | 0 | 149 | 127 | 145 | 0 | 55 | 162 | 30 | 16 | 400 | 277 | 0 | 0 | 35 | 16 | 315 | 0 | 0 | 0 | 70 | 18 | 21 | 0 | 0 | 35 | 50 | 42 | 0 | 0 | 17 | 0 | 0 | 87 | 50 | 0 | 40 | 34 | 13 | 350 | 17 | 0 | 19 | 25 | 37 | 200 | 0 | 0 | 0 | 1187 | 0 | 23 | 90 | 194 | 0 | 0 | 285 | 15 | 184 | 31 | 94 | 40 | 124 | 38 | 17 | 34 | 64 | 16 | 0 | 32 | 305 | 320 | 335 | 28 | 5 | 30 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 155 | 0 | 0 | 0 | 12 | 7776 | 871 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 1319 | 0 | 0 | 0 | 37 | 0 | 0 | 35 | 0 | 11 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 120 | 0 | 351 | 0 | 0 | 4 | 172 | 60 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 16 | 295 | 7 | 130 | 220 | 0 | 0 | 900 | 17 | 5440 | 13216 | 87.71
19:30 | 0 | 65 | 25 | 130 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 0 | 118 | 127 | 45 | 0 | 55 | 72 | 30 | 16 | 350 | 285 | 0 | 0 | 55 | 16 | 316 | 0 | 0 | 0 | 70 | 16 | 20 | 0 | 0 | 35 | 50 | 25 | 0 | 0 | 17 | 0 | 0 | 87 | 50 | 0 | 40 | 51 | 13 | 350 | 8 | 0 | 9 | 0 | 68 | 200 | 0 | 0 | 0 | 1224 | 0 | 43 | 60 | 194 | 0 | 0 | 285 | 29 | 182 | 34 | 68 | 40 | 100 | 38 | 17 | 34 | 64 | 0 | 0 | 33 | 280 | 320 | 335 | 31 | 10 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 155 | 0 | 0 | 0 | 12 | 7396 | 871 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 0 | 1360 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 123 | 0 | 355 | 0 | 0 | 4 | 171 | 60 | 35 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 8 | 130 | 220 | 0 | 0 | 1160 | 17 | 5849 | 13245
20:00 | 0 | 65 | 25 | 130 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 21 | 0 | 115 | 127 | 45 | 0 | 55 | 72 | 30 | 0 | 350 | 289 | 0 | 0 | 55 | 16 | 318 | 0 | 0 | 0 | 70 | 16 | 19 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 40 | 50 | 20 | 351 | 0 | 0 | 0 | 0 | 68 | 201 | 0 | 0 | 0 | 1224 | 0 | 43 | 40 | 200 | 0 | 0 | 285 | 29 | 183 | 34 | 68 | 40 | 100 | 39 | 17 | 34 | 68 | 0 | 0 | 0 | 290 | 320 | 335 | 32 | 40 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 155 | 0 | 0 | 0 | 12 | 7349 | 870 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 0 | 1365 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 123 | 0 | 367 | 0 | 0 | 5.5 | 167 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 8 | 130 | 220 | 0 | 0 | 1190 | 17 | 5880.5 | 13229.5 | 87.7
21:00 | 0 | 67 | 25 | 130 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 35 | 0 | 78 | 127 | 45 | 0 | 55 | 72 | 30 | 0 | 350 | 310 | 0 | 0 | 55 | 16 | 321 | 0 | 0 | 0 | 70 | 17 | 19 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 40 | 51 | 20 | 351 | 0 | 0 | 0 | 0 | 68 | 201 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 200 | 0 | 0 | 285 | 29 | 204 | 35 | 58 | 40 | 51 | 38 | 17 | 34 | 66 | 0 | 0 | 0 | 320 | 320 | 335 | 32 | 41 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 155 | 0 | 0 | 0 | 12 | 7288 | 918 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1364 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 125 | 0 | 375 | 0 | 0 | 5.5 | 165 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 8 | 130 | 220 | 0 | 0 | 1244 | 17 | 5995.5 | 13283.5 | 87.7
22:00 | 0 | 67 | 25 | 130 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 35 | 0 | 78 | 130 | 0 | 0 | 35 | 72 | 30 | 0 | 350 | 288 | 0 | 0 | 35 | 17 | 325 | 0 | 0 | 0 | 70 | 17 | 19 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 40 | 51 | 19 | 352 | 0 | 0 | 0 | 0 | 68 | 200 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 200 | 0 | 0 | 285 | 29 | 183 | 32 | 34 | 50 | 51 | 38 | 17 | 34 | 68 | 0 | 0 | 0 | 305 | 320 | 335 | 32 | 41 | 30 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 155 | 0 | 0 | 0 | 12 | 7163 | 917 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 629 | 0 | 1363 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 125 | 0 | 379 | 0 | 0 | 2.5 | 164 | 60 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 1244 | 0 | 5916.5 | 13079.5 | 87.69
23:00 | 0 | 67 | 25 | 130 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 54 | 0 | 78 | 130 | 0 | 0 | 0 | 72 | 30 | 0 | 350 | 285 | 0 | 0 | 0 | 17 | 327 | 0 | 0 | 0 | 70 | 18 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 24 | 0 | 40 | 0 | 21 | 351 | 0 | 0 | 0 | 0 | 68 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 199 | 0 | 0 | 285 | 29 | 182 | 34 | 31 | 50 | 51 | 39 | 14 | 34 | 66 | 0 | 0 | 0 | 300 | 320 | 335 | 32 | 41 | 30 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 88 | 146 | 0 | 0 | 0 | 12 | 6843 | 917 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 127 | 0 | 393 | 0 | 0 | 2.5 | 163 | 60 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 1244 | 0 | 5778.5 | 12621.5 | 87.69
Total KWH | 110160 | 980160 | 350880 | 2927400 | 0 | 108375 | 0 | 0 | 8938800 | 0 | 0 | 468360 | 886680 | 0 | 2162736 | 1350720 | 820723 | 257740 | 580819 | 1618560 | 745920 | 110400 | 8810500 | 7117789 | 0 | 0 | 538566 | 472600 | 6842085 | 0 | 0 | 188441 | 1147200 | 359400 | 457200 | 0 | 0 | 493036 | 431564 | 140160 | 0 | 266400 | 41840 | 0 | 70200 | 1097280 | 275520 | 26052 | 981000 | 531100 | 461760 | 8203636.36 | 30109 | 0 | 97920 | 41524.2 | 873999 | 4364479 | 0 | 0 | 0 | 26961816 | 143640 | 972724 | 838036 | 2960727 | 0 | 1598300 | 6874000 | 444480 | 4677000 | 763920 | 1120320 | 1038550 | 1661280 | 533400 | 287400 | 409260 | 1397760 | 17789 | 390791 | 78272 | 7465000 | 7682500 | 8407000 | 658512 | 844000 | 631680 | 114368 | 3481363.6 | 426984 | 0 | 1580160 | 718464 | 0 | 385000 | 3383440 | 0 | 1878000 | 2743200 | 291840 | 11050 | 239250 | 295200 | 161186270.16 | 22123636 | 4228416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602640 | 11258180 | 0 | 28025455 | 0 | 0 | 0 | 316032 | 0 | 0 | 118464 | 0 | 53256 | 651820 | 0 | 333752 | 3585909 | 0 | 0 | 0 | 3609227 | 0 | 8853745 | 0 | 30540 | 97434 | 4193000 | 1425163 | 170591 | 170118 | 620812 | 0 | 0 | 37739.28 | 996480 | 3930 | 55776 | 5695000 | 160077 | 2748000 | 5081660 | 0 | 0 | 22357818.18 | 72000 | 127676670.46 | 288862940.62

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12100.92 | MW | 12:00 Hr. | Energy Generated |  |  | 288.8629 |  | MKWHr.
| Day Peak Demand |  |  | 12143.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.367 |  | MKWHr.
| Evening Peak Generation |  |  | 13283.5 | MW | 21:00 Hr. | Energy Demand |  |  | 289.2299 |  | MKWHr.
| Evening Peak Demand |  |  | 13283.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 9718.83 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 937.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 13283.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.4001 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.7801 | 0 | 11.3837 | 0 | 0 | 0.18844 | 0 | 0 | 48.3522 | Gas | 125.6582 | Gas | 447756000.452
| Chattogram Zone |  |  | 4.8262 | 35.1655 | 4.1243 | 0 | 0.981 | 0.16969 | 0 | 0.2664 | 45.533 | Coal | 80.0946 | Coal | 573481154.6632
| Cumilla Zone |  |  | 19.6171 | 0 | 4.6584 | 0 | 0 | 0.39079 | 1.3978 | 0 | 26.064 | HFO | 26.4896 | HFO | 469613132.624
| Mymensingh Zone |  |  | 0.29184 | 0 | 4.9164 | 0 | 0 | 0.2503 | 0 | 0 | 5.4585 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7785 | Hydro | 0.981 | Hydro | 98100
| Khulna Zone |  |  | 4.2284 | 11.2582 | 0 | 0 | 0 | 0.60264 | 22.1236 | 0 | 38.2129 | Solar | 3.8262 | Solar | 61893937.7808
| Barishal Zone |  |  | 7.9897 | 28.0528 | 0.12778 | 0 | 0 | 0.00393 | 0 | 0 | 36.1743 | Import | 51.5469 | Import | 292020090.69
| Rajshahi Zone |  |  | 16.1463 | 0 | 0.48775 | 0 | 0 | 1.0161 | 28.0255 | 0 | 45.6756 | Wind | 0.2664 | Wind | 3900096
| Rangpur Zone |  |  | 0 | 5.6182 | 0.7914 | 0 | 0 | 1.2043 | 0 | 0 | 7.6139
| Total |  |  | 125.6582 | 80.0946 | 26.4896 | 0 | 0.981 | 3.8262 | 51.5469 | 0.2664 | 288.8629
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 447756000.452 |  | Hydro | 98100
|  |  |  | Coal | 573481154.6632 |  | Solar | 61893937.7808
|  |  |  | HFO | 469613132.624 |  | Import | 292020090.69
|  |  |  | HSD | 0 |  | Wind | 3900096
[5 empty] | Total: | 184,87,62,512 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1236 | Peak Hr Flow | 918.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6661091.008 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.0255 | Peak Hr Flow | 1364.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 572 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3978 | Peak Hr Flow | 66.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 926 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.5469 | Peak Hr Flow | 2348.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4879
|  |  |  | Chattogram |  | 0 |  | 1318
|  |  |  | Cumilla |  | 0 |  | 1200
|  |  |  | Mymensingh |  | 0 |  | 1044
|  |  |  | Sylhet |  | 0 |  | 446
|  |  |  | Khulna |  | 0 |  | 1467
|  |  |  | Barishal |  | 0 |  | 366
|  |  |  | Rajshahi |  | 0 |  | 1298
|  |  |  | Rangpur |  | 0 |  | 721
|  |  |  | Total |  | 0 |  | 12739
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1227.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 |  | Chandraghona 132/33kV S/S MAIN BUS-2 Scheduled S/D Due to Annual maintenance
| 08:49 | 13:28 | Jamalpur 132/33kV S/S T-3 LT Project Work S/D | [7 empty] | 14.0MW load
interrup.
| 08:49 | 13:28 | Jamalpur 132/33kV S/S T-3 HT Project Work S/D | [7 empty] | 14.0MW load
interrup.
| 08:54 | 09:26 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing Line Distance Relay (21L) relays.
| 09:29 | 12:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT Scheduled S/D Due to 33kV head sink
clean
| 09:30 | 12:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Scheduled S/D Due to 33kV head sink
clean
| 09:47 |  | Aminbazar- MPGL 132kV ckt-2 was switched ON.
| 10:50 | 11:58 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to Auxiliary Transformer-2 corrective | [7 empty] | 28.0MW load
|  |  | maintenance work. Shutdown taken by PBS. | [7 empty] | interrup.
| 10:50 | 11:58 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to Auxiliary Transformer-2 corrective | [7 empty] | 28.0MW load
|  |  | maintenance work. Shutdown taken by PBS. | [7 empty] | interrup.
| 11:08 |  | Aminbazar 400/230kV ATR-1 transformer was switched ON.
| 11:28 | 11:58 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Tripped showing O/C Protection P142 | [7 empty] | 34.0MW load
|  |  | relays Due to Nesco Hazipur 33kV Feeder Fault | [7 empty] | interrup.
| 11:28 | 11:57 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Tripped showing No Signal in 132 kV | [7 empty] | 34.0MW load
|  |  | Relay relays Due to Nesco Hazipur 33kV Feeder Fault | [7 empty] | interrup.
| 11:28 | 11:58 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Tripped showing O/C Protection P142 | [7 empty] | 34.0MW load
|  |  | relays Due to Nesco Hazipur 33kV Feeder Fault | [7 empty] | interrup.
| 11:31 |  | Aminbazar 400/230kV ATR-2 transformer was switched ON.
| 11:39 |  | Barishal-Barishal(N) 132 kV Ckt-2 Scheduled S/D from Barishal 132/33kV end Due to For
removal of faulty CB and Replace New CB.
| 12:00 |  | Day Peak Generation: 12097 MW.
| 12:05 |  | Barishal 132/33kV S/S Bus A Scheduled S/D Due to For Barisal North ckt -2 CB Change
Work.
| 12:08 | 13:36 | BIPTC S/S 20DF24 Forced S/D Due to Emergency due CB pole discrepancy & CB general fault.
|  | 12:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT is restored.
| 12:14 | 13:25 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to Transformer-1 corrective maintenance | [7 empty] | 27.0MW load
|  |  | purpose Shutdown taken. | [7 empty] | interrup.
| 12:14 | 13:25 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to Transformer-1 corrective maintenance | [7 empty] | 27.0MW load
|  |  | purpose Shutdown taken. | [7 empty] | interrup.
| 12:44 | 15:44 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast wall construction work | [7 empty] | 5.0MW load
interrup.
| 12:44 | 15:45 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast wall construction work | [7 empty] | 5.0MW load
interrup.
| 12:45 | 15:50 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Blast wall construction work | [7 empty] | 5.0MW load
interrup.
| 12:45 | 15:48 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Blast wall construction work | [7 empty] | 5.0MW load
interrup.
| 15:40 | 18:02 | The TK Chemical-Sikalbaha 132kV line tripped due to the tearing of a loop conductor in
the switchyard. Now, the Madunaghat-TK-Sikalbaha line has been fully shut down to perform
corrective work.
| 16:16 | 17:58 | Madunaghat-TKCL 132kV Ckt-1 Forced S/D from Madunaghat 132/33kV end.
| 19:55 |  | Fenchuganj CCPP-1 ST was sync.
| 21:00 |  | Evening Peak Gen. 13283 MW
| 05:45 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Forced S/D from Kalurghat 132/33kV end Due to
Maintenance
| 05:45 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Forced S/D from Kalurghat 132/33kV end Due to
Maintenance
| 07:50 |  | Jamalpur 132/33kV S/S Bus-A Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 108375 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 130 | 2927400 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 8938800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8810500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 310 | 7117789 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 257740 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 321 | 6842085 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 110160 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 468360 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 1350720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 580819 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 538566 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 359400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 457200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 745920 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16 | 472600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 350880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 820723 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 2162736 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 67 | 980160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 110400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1618560 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 188441 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 886680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1147200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2242 | 48352214
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 41524.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 143640 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 97920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 981000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 201 | 4364479 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 873999 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 41840 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1097280 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 461760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 140160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26052 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 431564 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 70200 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 531100 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 275520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 493036 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 30109 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26961816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 266400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 351 | 8203636.36 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2155 | 45533035.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 204 | 4677000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 1598300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6874000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 763920 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 444480 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 200 | 2960727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 972724 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 838036 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 78272 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1038550 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 1661280 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1397760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 17789 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 287400 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 409260 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 533400 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 58 | 1120320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 390791 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1118 | 26064009
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 291840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2743200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1878000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 239250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 295200 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 255 | 5458540
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 844000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 631680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3481363.6 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 658512 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 114368 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718464 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1580160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 3383440 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 385000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 426984 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7465000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8407000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7682500 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1518 | 35778471.6
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 918 | 22123636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 122 | 4228416 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 602640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 620 | 11258180 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1660 | 38212872
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 55776 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 160077 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2748000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 22357818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5081660 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 72000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5695000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3930 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1942 | 36174261.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 128 | 3585909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 125 | 3609227 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 375 | 8853745 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 97434 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 16 | 53256 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 316032 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 118464 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1364 | 28025455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 333752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 651820 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2063.5 | 45675634
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 1425163 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 4193000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 620812 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37739.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 170591 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170118 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 996480 | -
Rangpur Area Total |  |  |  |  | 950 | 330 | 7613903.28
Eastern Grid Total |  |  |  |  | 16921.242 | 7288 | 161186270.16
Western Grid Total |  |  |  |  | 11614.5 | 5995.5 | 127676670.46
National Grid Total |  |  |  |  | 28535.742 | 13283.5 | 288862940.62
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8887.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3852.2 | MW
i) Dhaka area |  |  | 4879.42 |  | MW | i) Khulna area |  |  |  | 1467 | MW
ii) Chattogram area |  |  | 1318 |  | MW | ii) Barishal area |  |  |  | 366 | MW
iii) Cumilla area |  |  | 1200 |  | MW | iii) Rajshahi area |  |  |  | 1298.2 | MW
iv) Mymensingh area |  |  | 1044 |  | MW | iv) Rangpur area |  |  |  | 721 | MW
v) Sylhet area |  |  | 446 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12739.62 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 66 | 18:00 | 133 | Payra | 26 | 21:00
2 | AKSML | 16 | 07:00 | 68 | Jamalpur | 112 | 18:00 | 134 | Postogola | 49 | 17:00
3 | Aftabnagar | 32 | 13:00 | 69 | Jashore | 128 | 19:00 | 135 | Purbachal | 16 | 18:00
4 | Agargaon | 97 | 13:00 | 70 | Jhenaidah | 112 | 19:00 | 136 | Purbasadipur | 120 | 17:00
5 | Agrabad | 88 | 19:00 | 71 | Joydebpur | 144 | 12:00 | 137 | Rahanpur | 24 | 04:00
6 | Amnura | 38 | 09:00 | 72 | Joypurhat | 59 | 09:00 | 138 | Rahim | 44 | 16:00
7 | Ashuganj | 84 | 15:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 63 | 19:00
8 | BSRM | 201 | 13:00 | 74 | KSRM | 28 | 15:00 | 140 | Rajendrapur | 112 | 15:00
9 | Bagerhat | 71 | 19:00 | 75 | Kabirpur | 254 | 17:00 | 141 | Rajshahi | 91 | 19:30
10 | Bajitpur | 42 | 18:00 | 76 | Kachua | 71 | 19:00 | 142 | Rajshahi-230 | 70 | 04:00
11 | Bakulia | 88 | 19:00 | 77 | Kallyanpur | 99 | 18:30 | 143 | Ramganj | 102 | 19:00
12 | Banani | 28 | 13:00 | 78 | Kalurghat | 40 | 09:00 | 144 | Rampur | 37 | 19:00
13 | Bangabhaban | 13 | 10:00 | 79 | Kamrangirchar | 66 | 12:00 | 145 | Rangamati | 15 | 18:30
14 | Barapukuria | 56 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 126 | 17:00
15 | Barguna | 18 | 20:00 | 81 | Kazla | 100 | 19:30 | 147 | Ruppur | 6.8 | 16:00
16 | Barishal | 93 | 19:00 | 82 | Keranigonj | 73 | 19:00 | 148 | SSM | 10 | 00:00
17 | Barishal-230 | 76 | 18:30 | 83 | Khagrachori | 28 | 19:00 | 149 | Saidpur | 109 | 17:00
18 | Baroaulia | 57 | 10:00 | 84 | Khosba | 30 | 19:00 | 150 | Satkhira | 118 | 19:00
19 | Baroirhat | 48 | 19:00 | 85 | Khulna | 77 | 19:00 | 151 | Satmasjid | 88 | 14:00
20 | Bashundhara | 164 | 14:00 | 86 | Khulshi | 159 | 16:00 | 152 | Savar | 213 | 15:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 122 | 18:00 | 153 | SevenRings | 17.3 | 12:00
22 | Beanibazar | 48 | 18:30 | 88 | Kodda | 294 | 21:00 | 154 | ShahCement | 39 | 23:00
23 | Benapole | 58 | 19:00 | 89 | Kulaura | 32 | 18:30 | 155 | Shahjadpur | 77 | 16:00
24 | Bhaluka | 136 | 15:00 | 90 | Kurigram | 61 | 17:00 | 156 | Shahjibazar | 107 | 22:00
25 | Bhandaria | 42 | 21:00 | 91 | Kushtia | 119 | 19:00 | 157 | Shahmirpur | 49.5 | 19:00
26 | Bhangura | 38 | 13:00 | 92 | Lalbag | 72 | 16:00 | 158 | Shariatpur | 63 | 19:00
27 | Bheramara(GK) | 47 | 19:00 | 93 | Lalmonirhat | 50 | 18:00 | 159 | Sherpur | 150 | 17:00
28 | Bhulta | 269 | 16:00 | 94 | MI_Cement | 16.8 | 13:00 | 160 | Shikalbaha | 26 | 00:00
29 | Bog-Sherpur | 72 | 17:00 | 95 | Madanganj | 38 | 19:30 | 161 | Shitalakhya | 78.3 | 16:00
30 | Bogura | 135 | 13:00 | 96 | Madaripur | 81 | 17:00 | 162 | Sholosohor | 39 | 15:00
31 | Borhanuddin | 63 | 21:00 | 97 | Madartek | 77.27 | 22:00 | 163 | Shyampur | 178 | 09:00
32 | Brahmanbaria | 111 | 22:00 | 98 | Madunaghat | 44 | 19:00 | 164 | Siddhirganj | 125 | 10:00
33 | Cantonment | 118 | 14:00 | 99 | Magura | 56 | 19:00 | 165 | Sirajganj | 102 | 19:30
34 | Chandpur | 58 | 18:00 | 100 | Mahasthangarh | 62 | 19:30 | 166 | Sonargaon | 93 | 15:00
35 | Chandraghona | 28 | 18:30 | 101 | Manikganj | 124 | 19:00 | 167 | Sreemongol | 55 | 22:00
36 | Chapai | 60 | 01:00 | 102 | Maniknagar | 64 | 13:00 | 168 | Sreepur | 88 | 10:00
37 | Charsaidpur | 32 | 16:00 | 103 | Matarbari | 42 | 21:00 | 169 | Srinagar | 36.6 | 20:00
38 | Chauddagram | 64 | 14:00 | 104 | Matuail | 63 | 12:00 | 170 | Sunamganj | 42 | 20:00
39 | Chhatak | 28 | 20:00 | 105 | Millgate | 84 | 10:00 | 171 | Sylhet | 30 | 21:00
40 | Chowmuhani | 175 | 21:00 | 106 | Mirpur | 123.5 | 20:00 | 172 | Sylhet-132 | 91 | 14:00
41 | Chuadanga | 88 | 19:00 | 107 | Mirsorai | 10 | 12:00 | 173 | TK | 32 | 19:00
42 | Coxsbazar | 116 | 19:30 | 108 | Mirzapur | 47 | 19:00 | 174 | Tangail | 170 | 03:00
43 | Cumilla(N) | 147 | 22:00 | 109 | Mithapukur | 54 | 17:00 | 175 | Thakurgaon | 83 | 18:00
44 | Cumilla(S) | 154 | 14:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 118 | 12:00
45 | Daudkandi | 136 | 19:00 | 111 | Mogbazar | 134.7 | 14:00 | 177 | Ullahpara | 30 | 04:00
46 | Dhaka | 48 | 13:00 | 112 | Mongla | 43 | 15:00 | 178 | Ullon | 43 | 21:00
47 | Dhamrai | 122 | 09:00 | 113 | Motijheel | 35 | 15:00 | 179 | Uttara | 79 | 13:00
48 | Dhanmondi | 130 | 14:00 | 114 | Muktagacha | 30 | 15:00 | 180 | UttaraNew | 43 | 20:00
49 | Dohazari | 88 | 21:00 | 115 | Munshiganj | 87 | 21:00 | 181 | Zigatola | 68 | 14:00
50 | Faridpur | 130 | 19:00 | 116 | Muradnagar | 23 | 18:30
51 | Fatullah | 95 | 15:00 | 117 | Mymensingh | 187 | 18:00
52 | Fenchuganj | 25 | 19:00 | 118 | Naogaon | 112 | 10:00
53 | Feni | 95 | 18:30 | 119 | Narail | 47 | 18:30
54 | GPH | 93 | 03:00 | 120 | Narinda | 68 | 13:00
55 | Ghatail | 82 | 17:00 | 121 | Narshingdi | 159 | 21:00
56 | Ghorashal | 12 | 00:00 | 122 | Natore | 135 | 04:00
57 | Ghorashal-230 | 80 | 19:30 | 123 | Nawabganj | 45.4 | 20:00
58 | Goalpara | 28 | 19:00 | 124 | Netrakona | 140 | 17:00
59 | Gollamari | 62 | 19:00 | 125 | New | 80.9 | 14:00
60 | Gopalganj | 88 | 19:00 | 126 | Niamatpur | 93 | 09:00
61 | Gulshan | 102 | 13:00 | 127 | Noapara | 40 | 19:00
62 | Halishahar | 76 | 15:00 | 128 | PHP | 8 | 02:00
63 | HaripurSBU | 183 | 00:00 | 129 | Pabna | 95 | 18:00
64 | Hasnabad | 83 | 19:30 | 130 | Palashbari | 100 | 17:00
65 | Hathazari | 67 | 19:00 | 131 | Panchagarh | 48 | 18:00
66 | Ishurdi | 64 | 19:00 | 132 | Patuakhali | 59 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11860.38 | 0 |  | 11860.38
1:00 | 11304.6 | 0 |  | 11304.6
2:00 | 10865.89 | 0 |  | 10865.89
3:00 | 11071.97 | 0 |  | 11071.97
4:00 | 11522.72 | 0 |  | 11522.72
5:00 | 10654.21 | 0 |  | 10654.21
6:00 | 9718.83 | 0 |  | 9718.83
7:00 | 9969.56 | 0 |  | 9969.56
8:00 | 10418.27 | 0 |  | 10418.27
9:00 | 11043.92 | 0 |  | 11043.92
10:00 | 11628.03 | 53 |  | 11683.03
11:00 | 11898.48 | 48 |  | 11948.48
12:00 | 12100.92 | 41 |  | 12143.77
13:00 | 12656.83 | 46 |  | 12704.83
14:00 | 12940.9 | 20 |  | 12961.9
15:00 | 12909.87 | 60 |  | 12972.57
16:00 | 12771.69 | 57 |  | 12831.69
17:00 | 12849.22 | 42 |  | 12893.22
18:00 | 12600.2 | 0 |  | 12600.2
19:00 | 13216 | 0 |  | 13216
19:30 | 13245 | 0 |  | 13245
20:00 | 13229.5 | 0 |  | 13229.5
21:00 | 13283.5 | 0 |  | 13283.5
22:00 | 13079.5 | 0 |  | 13079.5
23:00 | 12621.5 | 0 |  | 12621.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6495.5 | 5364.88 | 11860.38 | DAILY GENERATION CURVE
00:30 | 6309 | 5273.49 | 11582.49
01:00 | 6122.5 | 5182.1 | 11304.6 | 11-03-2025
01:30 | 6016 | 5069.245 | 11085.245
02:00 | 5909.5 | 4956.39 | 10865.89
02:30 | 5969.5 | 4999.43 | 10968.93
03:00 | 6029.5 | 5042.47 | 11071.97
03:30 | 6063 | 5234.345 | 11297.345
04:00 | 6096.5 | 5426.22 | 11522.72
04:30 | 5882 | 5206.465 | 11088.465
05:00 | 5667.5 | 4986.71 | 10654.21
05:30 | 5444 | 4742.52 | 10186.52
06:00 | 5220.5 | 4498.33 | 9718.83
06:30 | 5239.915 | 4604.28 | 9844.195
07:00 | 5259.33 | 4710.23 | 9969.56
07:30 | 5482.385 | 4711.53 | 10193.915
08:00 | 5705.44 | 4712.83 | 10418.27
08:30 | 6127.07 | 4604.025 | 10731.095
09:00 | 6548.7 | 4495.22 | 11043.92
09:30 | 6713.425 | 4622.55 | 11335.975
10:00 | 6878.15 | 4749.88 | 11628.03
10:30 | 6994.685 | 4768.57 | 11763.255
11:00 | 7111.22 | 4787.26 | 11898.48
11:30 | 7067.495 | 4932.205 | 11999.7
12:00 | 7023.77 | 5077.15 | 12100.92
12:30 | 7028.305 | 5350.57 | 12378.875
13:00 | 7032.84 | 5623.99 | 12656.83
13:30 | 7079.025 | 5719.84 | 12798.865
14:00 | 7125.21 | 5815.69 | 12940.9
14:30 | 7217.09 | 5708.295 | 12925.385
15:00 | 7308.97 | 5600.9 | 12909.87
15:30 | 7369.6 | 5471.18 | 12840.78
16:00 | 7430.23 | 5341.46 | 12771.69
16:30 | 7504.06 | 5306.395 | 12810.455
17:00 | 7577.89 | 5271.33 | 12849.22
17:30 | 7523.035 | 5201.675 | 12724.71
18:00 | 7468.18 | 5132.02 | 12600.2
18:30 | 7622.09 | 5286.01 | 12908.1
19:00 | 7776 | 5440 | 13216
19:30 | 7396 | 5849 | 13245
20:00 | 7349 | 5880.5 | 13229.5
20:30 | 7318.5 | 5938 | 13256.5 |  | Executive Engineer
21:00 | 7288 | 5995.5 | 13283.5 |  | Network Operation Division
21:30 | 7225.5 | 5956 | 13181.5
22:00 | 7163 | 5916.5 | 13079.5
22:30 | 7003 | 5847.5 | 12850.5
23:00 | 6843 | 5778.5 | 12621.5

## En-Curve
QF-LDC-12
Date | 11-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3844 | 1746 | 924 | 0 | 58 | 1152.38 | 40 | 3456 | 0 | 142 | 475 | 0 | 0 | 23 | 0 | DAILY ENERGY CURVE
00:30 | 3779.5 | 1718 | 924 | 0 | 59 | 1108.49 | 40 | 3388.5 | 0 | 117 | 417.5 | 0 | 0 | 30.5 | 0 | 11-03-2025
01:00 | 3715 | 1690 | 924 | 0 | 60 | 1064.6 | 40 | 3321 | 0 | 92 | 360 | 0 | 0 | 38 | 0
01:30 | 3639 | 1666 | 924 | 0 | 58 | 1012.745 | 40 | 3284 | 0 | 84 | 334.5 | 0 | 0 | 43 | 0 | Energy Generated | 288.8629 |  | MKWHr
02:00 | 3563 | 1642 | 924 | 0 | 56 | 960.89 | 40 | 3247 | 0 | 76 | 309 | 0 | 0 | 48 | 0 | Energy not Served | 0.367 |  | MKWHr
02:30 | 3506.5 | 1639 | 924 | 0 | 58 | 1017.93 | 40 | 3305.5 | 0 | 111 | 331 | 0 | 0 | 36 | 0 | Total Energy Requirement | 289.2299 |  | MKWHr
03:00 | 3450 | 1636 | 924 | 0 | 60 | 1074.97 | 40 | 3364 | 0 | 146 | 353 | 0 | 0 | 24 | 0
03:30 | 3561 | 1665.5 | 924 | 0 | 60 | 1123.345 | 40 | 3417.5 | 0 | 143 | 344.5 | 0 | 0 | 18.5 | 0
04:00 | 3672 | 1695 | 924 | 0 | 60 | 1171.72 | 40 | 3471 | 0 | 140 | 336 | 0 | 0 | 13 | 0
04:30 | 3602.5 | 1653 | 924 | 0 | 58 | 1143.465 | 40 | 3291.5 | 0 | 94.5 | 274.5 | 0 | 0 | 7 | 0
05:00 | 3533 | 1611 | 924 | 0 | 56 | 1115.21 | 40 | 3112 | 0 | 49 | 213 | 0 | 0 | 1 | 0
05:30 | 3503.5 | 1525 | 923.5 | 0 | 52 | 973.02 | 40 | 2947.5 | 0 | 37 | 184.5 | 0 | 0 | 0.5 | 0
06:00 | 3474 | 1439 | 923 | 0 | 48 | 830.83 | 40 | 2783 | 0 | 25 | 156 | 0 | 0 | 0 | 0
06:30 | 3477 | 1500 | 923.5 | 0 | 48 | 831.745 | 40 | 2817.5 | 18.45 | 25 | 162.5 | 0 | 0 | 0.5 | 0
07:00 | 3480 | 1561 | 924 | 0 | 48 | 832.66 | 40 | 2852 | 36.9 | 25 | 169 | 0 | 0 | 1 | 0
07:30 | 3473 | 1606.25 | 924 | 0 | 49 | 895.58 | 40 | 2842.5 | 106.085 | 41 | 216 | 0 | 0 | 0.5 | 0
08:00 | 3466 | 1651.5 | 924 | 0 | 50 | 958.5 | 40 | 2833 | 175.27 | 57 | 263 | 0 | 0 | 0 | 0
08:30 | 3437 | 1701.25 | 896.5 | 0 | 51 | 969.74 | 40 | 2830.5 | 249.175 | 78 | 477.93 | 0 | 0 | 0 | 0
09:00 | 3408 | 1751 | 869 | 0 | 52 | 980.98 | 40 | 2828 | 323.08 | 99 | 692.86 | 0 | 0 | 0 | 0
09:30 | 3392.5 | 1728.75 | 893 | 0 | 52 | 1050.885 | 40 | 2815.5 | 375.91 | 108 | 879.43 | 0 | 0 | 0 | 26.5
10:00 | 3377 | 1706.5 | 917 | 0 | 52 | 1120.79 | 40 | 2803 | 428.74 | 117 | 1066 | 0 | 0 | 0 | 53
10:30 | 3359 | 1713.5 | 917.5 | 0 | 54 | 1118.875 | 40 | 2822 | 477.38 | 127 | 1129.5 | 0 | 0 | 4.5 | 50.5
11:00 | 3341 | 1720.5 | 918 | 0 | 56 | 1116.96 | 40 | 2841 | 526.02 | 137 | 1193 | 0 | 0 | 9 | 48
11:30 | 3356.5 | 1762.5 | 918.5 | 0 | 55 | 1165.66 | 40 | 2888.5 | 545.04 | 137 | 1120.5 | 0 | 0 | 10.5 | 44.5
12:00 | 3372 | 1804.5 | 919 | 0 | 54 | 1214.36 | 40 | 2936 | 564.06 | 137 | 1048 | 0 | 0 | 12 | 41
12:30 | 3408.5 | 1815.5 | 918.5 | 0 | 56 | 1260.45 | 40 | 3143 | 553.925 | 141 | 1027.5 | 0 | 0 | 14.5 | 43.5
13:00 | 3445 | 1826.5 | 918 | 0 | 58 | 1306.54 | 40 | 3350 | 543.79 | 145 | 1007 | 0 | 0 | 17 | 46
13:30 | 3458.5 | 1831 | 918 | 0 | 63 | 1361.27 | 40 | 3401.5 | 523.595 | 136 | 1047 | 0 | 0 | 19 | 33
14:00 | 3472 | 1835.5 | 918 | 0 | 68 | 1416 | 40 | 3453 | 503.4 | 127 | 1087 | 0 | 0 | 21 | 20
14:30 | 3439.5 | 1855.25 | 918 | 0 | 67 | 1370.5 | 40 | 3444 | 436.635 | 150.5 | 1181.5 | 0 | 0 | 22.5 | 40
15:00 | 3407 | 1875 | 918 | 0 | 66 | 1325 | 40 | 3435 | 369.87 | 174 | 1276 | 0 | 0 | 24 | 60
15:30 | 3406 | 1899.5 | 918 | 0 | 64 | 1322 | 40 | 3383 | 296.78 | 174 | 1317.5 | 0 | 0 | 20 | 58.5
16:00 | 3405 | 1924 | 918 | 0 | 62 | 1319 | 40 | 3331 | 223.69 | 174 | 1359 | 0 | 0 | 16 | 57
16:30 | 3380.5 | 1878 | 918.5 | 0 | 63 | 1320.5 | 60 | 3330.5 | 153.455 | 204.5 | 1486.5 | 0 | 0 | 15 | 49.5
17:00 | 3356 | 1832 | 919 | 0 | 64 | 1322 | 80 | 3330 | 83.22 | 235 | 1614 | 0 | 0 | 14 | 42
17:30 | 3310.5 | 1763 | 918.5 | 0 | 66 | 1295 | 60 | 3271.5 | 42.66 | 269.5 | 1715.55 | 0 | 0 | 12.5 | 21
18:00 | 3265 | 1694 | 918 | 0 | 68 | 1268 | 40 | 3213 | 2.1 | 304 | 1817.1 | 0 | 0 | 11 | 0
18:30 | 3295 | 1777.5 | 894.5 | 0 | 66 | 1293.5 | 40 | 3341 | 1.05 | 320 | 1874.05 | 0 | 0 | 5.5 | 0
19:00 | 3325 | 1861 | 871 | 0 | 64 | 1319 | 40 | 3469 | 0 | 336 | 1931 | 0 | 0 | 0 | 0
19:30 | 3342 | 1786 | 871 | 0 | 64 | 1360 | 40 | 3853 | 0 | 337 | 1592 | 0 | 0 | 0 | 0
20:00 | 3392 | 1814.5 | 870 | 0 | 68 | 1365 | 40 | 3920 | 0 | 287 | 1473 | 0 | 0 | 0 | 0
20:30 | 3413.5 | 1844.5 | 894 | 0 | 67 | 1364.5 | 40 | 3945.5 | 0 | 288 | 1399.5 | 0 | 0 | 0 | 0
21:00 | 3435 | 1874.5 | 918 | 0 | 66 | 1364 | 40 | 3971 | 0 | 289 | 1326 | 0 | 0 | 0 | 0
21:30 | 3422 | 1876 | 917.5 | 0 | 67 | 1363.5 | 40 | 3975.5 | 0 | 290.5 | 1229.5 | 0 | 0 | 0 | 0
22:00 | 3409 | 1877.5 | 917 | 0 | 68 | 1363 | 40 | 3980 | 0 | 292 | 1133 | 0 | 0 | 0 | 0
22:30 | 3394.5 | 1873 | 917 | 0 | 67 | 1329 | 40 | 3974.5 | 0 | 292 | 963.5 | 0 | 0 | 0 | 0
23:00 | 3380 | 1868.5 | 917 | 0 | 66 | 1295 | 40 | 3969 | 0 | 292 | 794 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 06:00 | 376 | 14:00 | Payra | 421 | 08:00 | 410 | 14:00
Ashuganj | 406 | 18:00 | 372 | 13:00 | Rahanpur | 412 | 06:00 | 47 | 00:00
Bhulta | 403 | 06:00 | 373 | 14:00 | Rampal | 410 | 08:00 | 390 | 14:00
Bibiana | 397 | 18:00 | 383 | 14:00
BIPTC | 399 | 16:00 | 388 | 11:00
Bogura | 404 | 06:00 | 384 | 13:00
Gopalganj | 411 | 09:00 | 388 | 14:00
Kaliakoir | 376 | 18:00 | 350 | 14:00
Madunaghat | 403 | 09:00 | 392 | 14:00
Meghnaghat | 398 | 09:00 | 377 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 06:00 | 214 | 11:00 | Keranigonj | 230 | 06:00 | 213 | 14:00
AKSML | 233 | 19:00 | 225 | 23:00 | Khulna(S) | 236 | 06:00 | 221 | 14:00
Aminbazar | 232 | 06:00 | 216 | 14:00 | Madunaghat | 236 | 09:00 | 228 | 14:00
Ashuganj | 233 | 05:00 | 223 | 13:00 | Madunaghat-400 | 237 | 09:00 | 229 | 14:00
Ashuganj-400 | 233 | 04:00 | 218 | 13:00 | Maniknagar | 225 | 05:00 | 210 | 14:00
Baghabari | 236 | 02:00 | 225 | 13:00 | Meghnaghat | 233 | 05:00 | 220 | 14:00
Barapukuria | 225 | 06:00 | 215 | 17:00 | Meghnaghat-400 | 230 | 06:00 | 216 | 14:00
Barapukuria-230 | 225 | 06:00 | 215 | 17:00 | Mirsorai | 231 | 18:30 | 219 | 14:00
Barishal | 240 | 09:00 | 229 | 14:00 | Rajshahi | 234 | 01:00 | 220 | 14:00
Bheramara | 234 | 01:00 | 222 | 12:00 | Rampal | 235 | 09:00 | 221 | 14:00
Bhulta | 227 | 06:00 | 211 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 18:00 | 220 | 14:00 | Rampura | 227 | 06:00 | 208 | 14:00
BIPTC | 237 | 01:00 | 222 | 14:00 | Shikalbaha | 233 | 19:00 | 226 | 14:00
Bogura | 235 | 06:00 | 223 | 13:00 | Shyampur | 228 | 06:00 | 213 | 14:00
Bogura-400 | 244 | 15:00 | 223 | 13:00 | Siddhirganj | 229 | 18:00 | 213 | 14:00
Borhanuddin | 243 | 09:00 | 237 | 14:00 | Sirajgonj | 240 | 05:00 | 232 | 14:00
BSRM | 230 | 18:30 | 219 | 14:00 | Sreepur | 232 | 06:00 | 220 | 14:00
Cumilla(N) | 226 | 18:30 | 213 | 14:00 | Tongi | 222 | 04:00 | 208 | 15:00
Faridpur | 239 | 09:00 | 225 | 14:00
Fenchuganj | 232 | 05:00 | 226 | 14:00
Ghorashal | 230 | 00:00 | 220 | 15:00
Ghorashal-230 | 227 | 18:30 | 211 | 14:00
Gopalganj | 236 | 08:00 | 224 | 14:00
GPH | 233 | 09:00 | 223 | 14:00
Haripur | 228 | 06:00 | 212 | 14:00
Hasnabad | 228 | 03:00 | 16 | 15:00
Hathazari | 237 | 09:00 | 228 | 14:00
Ishurdi | 237 | 01:00 | 224 | 14:00
Jhenaidah | 233 | 06:00 | 218 | 14:00
Kaliakoir | 235 | 18:00 | 217 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 121 | 14:00 | Madunaghat | 136 | 09:00 | 130 | 14:00
Agargaon | 139 | 06:00 | 127 | 11:00 | Magura | 135 | 06:00 | 125 | 14:00
Agrabad | 135 | 08:00 | 129 | 07:00 | Mahasthangarh | 132 | 06:00 | 123 | 17:00
AKS | 132 | 09:00 | 127 | 14:00 | Manikganj | 132 | 18:00 | 119 | 14:00
Aminbazar | 135 | 04:00 | 125 | 14:00 | Maniknagar | 132 | 18:30 | 118 | 14:00
Amnura | 136 | 02:00 | 127 | 14:00 | Matarbari | 126 | 08:00 | 115 | 21:00
Ashuganj | 136 | 06:00 | 131 | 14:00 | Matuail | 132 | 05:00 | 123 | 14:00
Bagerhat | 133 | 06:00 | 120 | 14:00 | Millgate | 134 | 04:00 | 124 | 14:00
Bajitpur | 133 | 02:00 | 125 | 13:00 | Mirpur | 136 | 06:00 | 123 | 11:00
Bakulia | 137 | 09:00 | 131 | 14:00 | Mirzapur | 130 | 05:00 | 120 | 14:00
Banani | 134 | 05:00 | 120 | 14:00 | Mithapukur | 133 | 06:00 | 121 | 17:00
Bangabhaban | 129 | 19:00 | 117 | 14:00 | MI_Cement | 134 | 18:30 | 122.5 | 14:00
Barapukuria | 139 | 02:00 | 131 | 09:00 | Modern | 0 | 0 | 0 | 0
Barguna | 138 | 09:00 | 133 | 14:00 | Mogbazar | 135 | 05:00 | 122 | 14:00
Barishal | 134 | 06:00 | 127 | 12:00 | Mongla | 133 | 09:00 | 122 | 06:00
Barishal-230 | 135 | 08:00 | 126 | 14:00 | Motijheel | 129 | 19:00 | 117 | 14:00
Baroaulia | 134 | 19:00 | 129 | 15:00 | Muktagacha | 134 | 08:00 | 121 | 17:00
Baroirhat | 127 | 08:00 | 118 | 14:00 | Munshiganj | 133 | 18:00 | 121 | 14:00
Bashundhara | 134 | 04:00 | 120 | 14:00 | Muradnagar | 129 | 06:00 | 118 | 14:00
BashundharaCement | 132 | 18:30 | 123 | 15:00 | Mymensingh | 135 | 05:00 | 114 | 16:00
Beanibazar | 131 | 05:00 | 127 | 14:00 | Naogaon | 130 | 05:00 | 120 | 10:00
Benapole | 134 | 06:00 | 121 | 14:00 | Narail | 134 | 05:00 | 124 | 12:00
Bhaluka | 130 | 18:30 | 118 | 13:00 | Narinda | 132 | 18:30 | 118 | 14:00
Bhandaria | 132 | 08:00 | 122 | 18:00 | Narshingdi | 125 | 02:00 | 118 | 21:00
Bhangura | 134 | 02:00 | 126 | 14:00 | Natore | 134 | 05:00 | 125 | 12:00
Bheramara | 136 | 01:00 | 129 | 14:00 | Nawabganj | 136 | 06:00 | 123 | 14:00
Bheramara(GK) | 136 | 01:00 | 129 | 14:00 | Netrakona | 124 | 01:00 | 112 | 13:00
Bhulta | 128 | 18:00 | 116 | 14:00 | New | 135 | 05:00 | 122 | 14:00
Bog-Sherpur | 132 | 05:00 | 125 | 10:00 | Niamatpur | 140 | 05:00 | 133 | 13:00
Bogura | 133 | 05:00 | 126 | 14:00 | Noapara | 136 | 06:00 | 124 | 14:00
Bogura-230 | 133 | 02:00 | 126 | 13:00 | Pabna | 135 | 00:00 | 128 | 14:00
Brahmanbaria | 127 | 07:00 | 1 | 11:00 | Palashbari | 131 | 06:00 | 118 | 17:00
Cantonment | 139 | 06:00 | 126 | 11:00 | Panchagarh | 137 | 05:00 | 120 | 16:00
Chandpur | 130 | 19:00 | 118 | 22:00 | Patuakhali | 136 | 07:00 | 132 | 14:00
Chandraghona | 136 | 09:00 | 131 | 13:00 | Payra | 138 | 06:00 | 134 | 14:00
Chapai | 138 | 06:00 | 131 | 13:00 | PHP | 127 | 18:30 | 115 | 14:00
Charsaidpur | 135 | 18:00 | 122 | 14:00 | Postogola | 136 | 18:00 | 125 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 08:00 | 116 | 14:00 | Purbachal | 133 | 01:00 | 120 | 14:00
Chhatak | 132 | 09:00 | 127 | 14:00 | Purbasadipur | 133 | 05:00 | 119 | 10:00
Chowmuhani | 124 | 09:00 | 113 | 14:00 | Rahanpur | 141 | 05:00 | 135 | 13:00
Chuadanga | 134 | 05:00 | 121 | 14:00 | Rahanpur-400 | 141 | 02:00 | 135 | 13:00
Coxsbazar | 124 | 05:00 | 116 | 22:00 | Rahim | 131 | 07:00 | 123 | 15:00
Cumilla(N) | 130 | 18:30 | 121 | 14:00 | Rajbari | 132 | 09:00 | 124 | 14:00
Cumilla(S) | 133 | 06:00 | 119 | 14:00 | Rajendrapur | 137 | 18:30 | 121 | 15:00
Daudkandi | 127 | 05:00 | 115 | 14:00 | Rajshahi | 136 | 06:00 | 126 | 14:00
Dhaka | 134 | 02:00 | 122 | 14:00 | Rajshahi-230 | 135 | 02:00 | 125 | 13:00
Dhamrai | 133 | 06:00 | 121 | 14:00 | Ramganj | 124 | 08:00 | 114 | 21:00
Dhanmondi | 134.5 | 05:00 | 123 | 14:00 | Rampur | 135 | 09:00 | 128 | 13:00
Dohazari | 132 | 08:00 | 125 | 13:00 | Rampura | 135 | 06:00 | 121 | 14:00
Faridpur | 133 | 06:00 | 126 | 14:00 | Rangamati | 135 | 09:00 | 129 | 14:00
Fatullah | 134 | 06:00 | 124 | 14:00 | Rangpur | 133 | 06:00 | 120 | 17:00
Fenchuganj | 133 | 07:00 | 131 | 14:00 | Ruppur | 137 | 05:00 | 131 | 13:00
Feni | 125 | 18:30 | 113 | 14:00 | Saidpur | 135 | 05:00 | 120 | 17:00
Ghatail | 130 | 04:00 | 118 | 14:00 | Satkhira | 134 | 06:00 | 123 | 12:00
Ghorashal | 136 | 18:00 | 130 | 15:00 | Satmasjid | 139 | 06:00 | 127 | 13:00
Goalpara | 136 | 06:00 | 126 | 14:00 | Savar | 135 | 06:00 | 124 | 10:00
Gollamari | 137 | 05:00 | 126 | 14:00 | SevenRings | 138 | 18:30 | 128 | 14:00
Gopalganj | 137 | 06:00 | 128 | 14:00 | ShahCement | 135 | 18:00 | 122 | 14:00
Gopalganj-400 | 139 | 09:00 | 131 | 14:00 | Shahjadpur | 136 | 02:00 | 130 | 12:00
Gulshan | 135 | 06:00 | 121 | 14:00 | Shahjibazar | 131 | 08:00 | 125 | 15:00
Halishahar | 132 | 10:00 | 128 | 14:00 | Shahmirpur | 137 | 09:00 | 130 | 14:00
Haripur | 132 | 05:00 | 123 | 14:00 | Shariatpur | 137 | 09:00 | 127 | 14:00
HaripurSBU | 133 | 06:00 | 124 | 14:00 | Sherpur | 137 | 09:00 | 123 | 16:00
Hasnabad | 134 | 05:00 | 125 | 13:00 | Shikalbaha | 126 | 18:00 | 120 | 00:00
Hathazari | 137 | 09:00 | 130 | 14:00 | Shikalbaha-230 | 137 | 19:00 | 131 | 14:00
Ishurdi | 137 | 01:00 | 131 | 14:00 | Shitalakhya | 134 | 18:30 | 122.5 | 14:00
Jaldhaka | 133 | 05:00 | 119 | 10:00 | Sholosohor | 135 | 09:00 | 130 | 14:00
Jamalpur | 139 | 13:00 | 127 | 16:00 | Shyampur | 133 | 18:30 | 125 | 09:00
Jashore | 135 | 06:00 | 122 | 14:00 | Shyampur-230 | 134 | 06:00 | 122 | 14:00
Jhenaidah | 136 | 04:00 | 126 | 13:00 | Siddhirganj | 134 | 18:00 | 123 | 14:00
Jhenaidah-230 | 136 | 05:00 | 126 | 14:00 | Sirajganj | 133 | 00:00 | 124 | 16:00
Joydebpur | 135 | 18:00 | 124 | 14:00 | Sonargaon | 130 | 05:00 | 119 | 14:00
Joypurhat | 129 | 05:00 | 117 | 10:00 | Sreemongol | 131 | 07:00 | 126 | 14:00
Juldah | 135 | 09:00 | 130 | 11:00 | Sreepur | 130 | 01:00 | 122 | 08:00
Kabirpur | 132 | 18:30 | 121 | 14:00 | Srinagar | 135 | 05:00 | 124 | 13:00
Kachua | 128 | 09:00 | 118 | 21:00 | SSM | 136 | 00:00 | 134 | 01:00
Kaliakoir | 135 | 18:00 | 124 | 14:00 | Sunamganj | 130 | 06:00 | 126 | 13:00
Kallyanpur | 135 | 06:00 | 124 | 11:00 | Sylhet | 131 | 06:00 | 128 | 13:00
Kalurghat | 135 | 09:00 | 130 | 15:00 | Sylhet-132 | 132 | 03:00 | 129 | 15:00
Kamrangirchar | 135 | 05:00 | 123 | 14:00 | Tangail | 128 | 02:00 | 118 | 17:00
Kaptai | 135 | 6:00 | 127 | 12:00 | Thakurgaon | 135 | 05:00 | 118 | 10:00
Kazla | 132 | 19:00 | 117 | 15:00 | TK | 136 | 10:00 | 131 | 13:00
Keranigonj | 136 | 06:00 | 124 | 14:00 | Tongi | 135 | 04:00 | 124 | 15:00
Khagrachori | 134 | 06:00 | 128 | 14:00 | Ullahpara | 135 | 05:00 | 127 | 11:00
Khosba | 129 | 18:30 | 117 | 14:00 | Ullon | 133 | 01:00 | 113 | 06:00
Khulna | 134 | 05:00 | 124 | 14:00 | Uttara | 135 | 06:00 | 120 | 14:00
Khulna(S) | 137 | 06:00 | 126 | 14:00 | UttaraNew | 136 | 05:00 | 124 | 14:00
Khulshi | 134 | 08:00 | 127 | 14:00 | Zigatola | 136 | 05:00 | 124 | 11:00
Kishoreganj | 130 | 05:00 | 121 | 13:00
Kodda | 134 | 18:30 | 118 | 14:00
KSRM | 137 | 07:00 | 129 | 13:00
Kulaura | 133 | 07:00 | 130 | 14:00
Kurigram | 135 | 06:00 | 116 | 17:00
Kushtia | 136 | 05:00 | 127 | 14:00
Lalbag | 135 | 06:00 | 123 | 11:00
Lalmonirhat | 130 | 02:00 | 120 | 09:00
Madanganj | 132 | 18:30 | 123 | 15:00
Madaripur | 137 | 09:00 | 130 | 14:00
Madartek | 135 | 06:00 | 121 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division