## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-03-2025 | during | 13-03-2025 | during | 13-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 251 | 230 | 130 | 130 | 130 | 130 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 360 | 401 | 400.75 | 400.75 | 385 | 385 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 275 | 280 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 63 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 22 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 8 | 30 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 25 | 52.19 | 52.19 | 8 | 8 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 114 | 140 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 33 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1961.5 | 2264 | 5140.5 | 5204.5 | 3169.36 | 3233.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 224 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 64 | 82 | 64 | 82 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 36 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 27 | 2 | 30 | 2 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 44 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.95 | 0 | 3.95 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 51 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1026 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 8 | 8 | 8 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 342 | 340 | 350 | 350 | 350 | 350 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1674 | 2197 | 3175.67 | 3197.72 | 3175.67 | 3197.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 200 | 200 | 200 | 200 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 300 | 300 | 285 | 285 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 30 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 200 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 15 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 9 | 100 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 72 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 17 | 20.83 | 20.83 | 18 | 18 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 14 | 37 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 7 | 93 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1032 | 1248 | 2238.97 | 2178.97 | 2082.2 | 2022.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-03-2025 | during | 13-03-2025 | during | 13-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 17 | 23 | 210 | 210 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 166 | 200 | 200 | 135 | 135 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 88 | 115 | 115 | 78 | 78 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.91 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 245.91 | 289 | 653.7 | 601.5 | 351.7 | 299.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 42 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 28 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 35 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 164 | 162 | 162 | 162 | 162 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 16 | 16 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 332 | 387 | 350 | 350 | 350 | 350 | Due to Air Filter DP High FGMO not available.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1541 | 1575 | 1613 | 1613 | 1570 | 1570
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 919 | 870 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 184 | 172 | 410 | 410 | 230 | 230 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94.1 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 618 | 625 | 1234.2 | 1234.2 | 610 | 610 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1815.1 | 1667 | 3604.2 | 3514.2 | 2234.02 | 2144.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 9 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 135 | 135 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1110 | 1240 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1772.66 | 1906 | 2177.12 | 2176.12 | 2137.12 | 2136.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 155 | 214 | 214 | 165 | 165 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 148 | 148 | 220 | 220 | 160 | 160 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 4 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 90 | 90 | 90 | 90 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.74 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1265.69 | 1381 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.59 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 98 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2152.02 | 2180.5 | 3110.13 | 2943.53 | 2739.35 | 2572.75
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 57 | 62 | 62 | 62 | 62 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 175 | 176 | 160 | 160 | 175 | 175 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.2 | 0 | 6.1 | 0 | 6.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 139 | 0 | 165 | 0 | 165 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 388.2 | 302 | 685.1 | 484 | 666.12 | 465.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12582.39 | 13628.5 | 22398.39 | 21913.54 | 18125.54 | 17640.69
Forecast Scenario (13-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11860 |  | 0 |  | 11860
|  |  |  | 1:00 | 11300 |  | 0 |  | 11300
|  |  |  | 2:00 | 10860 |  | 0 |  | 10860
|  |  |  | 3:00 | 11070 |  | 0 |  | 11070
|  |  |  | 4:00 | 11520 |  | 0 |  | 11520
|  |  |  | 5:00 | 10650 |  | 0 |  | 10650
|  |  |  | 6:00 | 9710 |  | 0 |  | 9710
|  |  |  | 7:00 | 9970 |  | 0 |  | 9970
|  |  |  | 8:00 | 10410 |  | 0 |  | 10410
|  |  |  | 9:00 | 11040 |  | 0 |  | 11040
|  |  |  | 10:00 | 11680 |  | 0 |  | 11680
|  |  |  | 11:00 | 12440 |  | 0 |  | 12440
|  |  |  | 12:00 | 12640 |  | 0 |  | 12640
|  |  |  | 13:00 | 13200 |  | 0 |  | 13200
|  |  |  | 14:00 | 13460 |  | 0 |  | 13460
|  |  |  | 15:00 | 13470 |  | 0 |  | 13470
|  |  |  | 16:00 | 13330 |  | 0 |  | 13330
|  |  |  | 17:00 | 13390 |  | 0 |  | 13390
|  |  |  | 18:00 | 13100 |  | 0 |  | 13100
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 13510 |  | 0 |  | 13510
|  |  |  | 19:30 | 13540 |  | 0 |  | 13540
|  |  |  | 20:00 | 13530 |  | 0 |  | 13530
|  |  |  | 21:00 | 13480 |  | 0 |  | 13480
|  |  |  | 22:00 | 13280 |  | 0 |  | 13280
|  |  |  | 23:00 | 12800 |  | 0 |  | 12800
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 12640.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13540.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13540.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 286.52 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:11 hrs on 13-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12582.39 | MW | 12:00 Hr. | Energy Generated |  |  | 295.363 |  | MKWHr.
| Day Peak Demand |  |  | 12613.39 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.467 |  | MKWHr.
| Evening Peak Generation |  |  | 13628.5 | MW | 21:00 Hr. | Energy Demand |  |  | 295.83 |  | MKWHr.
| Evening Peak Demand |  |  | 13628.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 9836.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 974.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 13628.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.3466 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.9753 | 0 | 11.727 | 0 | 0 | 0.2028 | 0 | 0 | 48.9051 | Gas | 128.9403 | Gas | 461169430.6
| Chattogram Zone |  |  | 4.9944 | 33.5273 | 3.0558 | 0 | 0.97518 | 0.15691 | 0 | 0.04032 | 42.7498 | Coal | 84.233 | Coal | 603207499.3236
| Cumilla Zone |  |  | 19.8008 | 0 | 4.4332 | 0 | 0 | 0.47108 | 1.4131 | 0 | 26.1182 | HFO | 25.9045 | HFO | 456014582.89
| Mymensingh Zone |  |  | 0.2352 | 0 | 4.9922 | 0 | 0 | 0.28218 | 0 | 0 | 5.5096 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 37.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.338 | Hydro | 0.97518 | Hydro | 97518
| Khulna Zone |  |  | 4.0775 | 13.1782 | 0 | 0 | 0 | 0.6624 | 21.9535 | 0 | 39.8715 | Solar | 3.8395 | Solar | 61462655.4982
| Barishal Zone |  |  | 8.3968 | 31.9126 | 0.10502 | 0 | 0 | 0.0045345 | 0 | 0 | 40.419 | Import | 51.4302 | Import | 291994991.6
| Rajshahi Zone |  |  | 17.1224 | 0 | 0.69622 | 0 | 0 | 1.0208 | 28.0636 | 0 | 46.903 | Wind | 0.04032 | Wind | 590284.8
| Rangpur Zone |  |  | 0 | 5.6149 | 0.8951 | 0 | 0 | 1.0388 | 0 | 0 | 7.5488
| Total |  |  | 128.9403 | 84.233 | 25.9045 | 0 | 0.97518 | 3.8395 | 51.4302 | 0.04032 | 295.363
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 461169430.6 |  | Hydro | 97518
|  |  |  | Coal | 603207499.3236 |  | Solar | 61462655.4982
|  |  |  | HFO | 456014582.89 |  | Import | 291994991.6
|  |  |  | HSD | 0 |  | Wind | 590284.8
[5 empty] | Total: | 187,45,36,962 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9535 | Peak Hr Flow | 870.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 12246927.371 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.0636 | Peak Hr Flow | 1381.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 712 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4131 | Peak Hr Flow | 72.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 980 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.4302 | Peak Hr Flow | 2323.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4939
|  |  |  | Chattogram |  | 0 |  | 1295
|  |  |  | Cumilla |  | 0 |  | 1288
|  |  |  | Mymensingh |  | 0 |  | 1058
|  |  |  | Sylhet |  | 0 |  | 466
|  |  |  | Khulna |  | 0 |  | 1535
|  |  |  | Barishal |  | 0 |  | 398
|  |  |  | Rajshahi |  | 0 |  | 1319
|  |  |  | Rangpur |  | 0 |  | 697
|  |  |  | Total |  | 0 |  | 12995
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1227.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 13:11 | Gopalganj 132/33kV S/S T1 LT Project Work S/D Due to Scaffolding work for blast wall.
| 08:21 | 13:10 | Gopalganj 132/33kV S/S T1 HT Project Work S/D Due to Scaffolding work for blast wall.
| 08:22 |  | Hathazari 230/132/33kV S/S MT-02 LT Scheduled S/D
| 08:22 |  | Hathazari 230/132/33kV S/S MT-02 HT Scheduled S/D
| 08:30 | 12:03 | Chandpur 132/33kV S/S 412T HT Scheduled S/D Due to High temperature remove work | [7 empty] | 4.0MW load
interrup.
|  | 09:44 | Jamalpur 132/33kV S/S Bus-A is restored.
| 09:55 | 13:50 | Jamalpur 132/33kV S/S Bus-B Project Work S/D
| 09:58 | 14:10 | Jamalpur-Mymensingh 132kV Ckt-1 Project Work S/D from Jamalpur 132/33kV end.
| 10:37 | 16:33 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Scheduled S/D Due to Clamp replacing on jack
bus.
| 10:52 | 16:35 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-1 Scheduled S/D Due to Clamp replacing on
jackbus for 132kv Ullon line.
| 11:58 | 17:10 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to project work
| 11:59 | 17:10 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to project work
| 12:00 |  | Day peak Generation is 12578 MW
| 12:00 | 15:42 | Rampura 230/132kV S/S Auto Transformer - 02 LT Tripped showing Differential relay trip
relays Due to Lockout relay operated
|  | 12:07 | Chandpur 132/33kV S/S 412T LT is restored.
| 12:08 |  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to Checking
|  | 14:28 | Jamalpur 132/33kV S/S T-4 HT is restored.
|  | 14:28 | Jamalpur 132/33kV S/S T-4 LT is restored.
|  | 19:52 | Ashuganj-Shahjibazar 132kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation: 13628 MW.
| 22:51 | 00:08 | Ashuganj 230/132/33kV S/S T-3 Kalabagan HT Forced S/D Due to conductor demaged | [7 empty] | 20.0MW load
interrup.
| 00:12 |  | Meghnaghat CCPP 450 MW ST tripped.
| 03:59 |  | Meghnaghat CCPP 450 MW ST sync.
| 03:59 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
| 04:57 | 06:58 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Red
hot maintenance
| 05:17 | 05:55 | BSRM-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Distance
Relay Auto reclose Relay relays.
| 05:17 | 05:40 | BSRM-Cumilla(N) 230 kV Ckt-2 Tripped from BSRM Mirsorai ss end showing earth fault.
| 05:43 | 06:21 | Ishwardi-Natore 132kV Ckt-2 Tripped from Ishurdi 132/33kV end showing BBC LZ 32 relays.
| 05:57 | 07:07 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to
Maintenance work of Hathazari ss
| 06:00 |  | Min. Gen. 10221 MW
| 06:47 | 06:55 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance Relay | [7 empty] | 25.0MW load
|  |  | -Y Phase, Zone -1 relays Due to Unknown | [7 empty] | interrup. Barishal
132/33kV end
| 07:08 |  | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Auxiliary-1 Loop Tightening | [7 empty] | 2.5MW load
|  |  | for High Temperature. | [7 empty] | interrup.
| 07:09 |  | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Auxiliary-1 Loop Tightening | [7 empty] | 2.5MW load
|  |  | for High Temperature. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 230 | 4598100 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 8665200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8063500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 6931782 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 244855 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 6618985 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 251856 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 2211360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 511495 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 294456 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 470400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 504000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 565560 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 557800 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 343680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 461171 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 140 | 2413008 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 33 | 828480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 65280 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1424160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 202795 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 781200 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1572000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2264 | 48905123
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 28719 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133110 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 11040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 975180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 4558995 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 519382 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 95664 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 36 | 229562 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 1008000 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 435360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 241920 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23805 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 293564 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 38410 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 332873 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 119040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 109145 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 28436 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25483634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 40320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 340 | 8043636.36 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2197 | 42749795.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4584000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6854000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 767592 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 659040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4416000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1017124 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 15 | 172290 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 179008 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1200360 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1373760 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1413120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 88973 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 302700 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1069320 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 568680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 981120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 471082 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1248 | 26118169
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 23 | 235200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 166 | 2779200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1840800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 270280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293760 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 78480 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 289 | 5509620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 965000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 711840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3460664 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 35 | 772848 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 110640 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 652800 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1788480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 4401610 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 383000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 522786 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7242000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8699000 | Due to air filter DP high FL is not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7627300 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1575 | 37337968
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 870 | 21953454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 172 | 4077504 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 662400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 625 | 13178180 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1667 | 39871538
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 45024 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 9 | 170438 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2997000 | FGMO
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1240 | 25323636.36 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5229360 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 60000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6589000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4534.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1906 | 40418992.86
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 75566 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 10462 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 45986 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 155 | 3721818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 148 | 3776073 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9517818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 44947 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 106668 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 68736 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 202752 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 180480 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 67296 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1381 | 28063636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 331496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 661880 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2180.5 | 46903034
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1354909 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 176 | 4260000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 633379 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 22650.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 261724 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 122612 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 893520 | -
Rangpur Area Total |  |  |  |  | 950 | 302 | 7548794.12
Eastern Grid Total |  |  |  |  | 16921.242 | 7573 | 160620675.36
Western Grid Total |  |  |  |  | 11614.5 | 6055.5 | 134742358.98
National Grid Total |  |  |  |  | 28535.742 | 13628.5 | 295363034.34
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9045.54 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3949.2 | MW
i) Dhaka area |  |  | 4938.54 |  | MW | i) Khulna area |  |  |  | 1535 | MW
ii) Chattogram area |  |  | 1295 |  | MW | ii) Barishal area |  |  |  | 398 | MW
iii) Cumilla area |  |  | 1288 |  | MW | iii) Rajshahi area |  |  |  | 1319.2 | MW
iv) Mymensingh area |  |  | 1058 |  | MW | iv) Rangpur area |  |  |  | 697 | MW
v) Sylhet area |  |  | 466 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12994.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 66 | 18:00 | 133 | Payra | 26 | 19:00
2 | AKSML | 13 | 17:00 | 68 | Jamalpur | 114 | 18:00 | 134 | Postogola | 47 | 15:00
3 | Aftabnagar | 32 | 14:00 | 69 | Jashore | 131 | 19:30 | 135 | Purbachal | 17 | 18:00
4 | Agargaon | 98 | 15:00 | 70 | Jhenaidah | 118 | 19:00 | 136 | Purbasadipur | 118 | 17:00
5 | Agrabad | 88 | 19:30 | 71 | Joydebpur | 141 | 20:00 | 137 | Rahanpur | 24 | 18:30
6 | Amnura | 39 | 18:00 | 72 | Joypurhat | 58 | 10:00 | 138 | Rahim | 35 | 05:00
7 | Ashuganj | 85 | 14:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 63 | 19:00
8 | BSRM | 196 | 06:00 | 74 | KSRM | 39 | 18:00 | 140 | Rajendrapur | 116 | 13:00
9 | Bagerhat | 77 | 19:00 | 75 | Kabirpur | 266 | 09:00 | 141 | Rajshahi | 92 | 19:30
10 | Bajitpur | 44 | 18:00 | 76 | Kachua | 74 | 18:00 | 142 | Rajshahi-230 | 74 | 18:00
11 | Bakulia | 91 | 19:30 | 77 | Kallyanpur | 99 | 18:30 | 143 | Ramganj | 110 | 21:00
12 | Banani | 26.8 | 13:00 | 78 | Kalurghat | 42 | 12:00 | 144 | Rampur | 38 | 18:30
13 | Bangabhaban | 13 | 10:00 | 79 | Kamrangirchar | 56 | 01:00 | 145 | Rangamati | 15 | 18:30
14 | Barapukuria | 57 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 130 | 17:00
15 | Barguna | 18 | 21:00 | 81 | Kazla | 100 | 17:00 | 147 | Ruppur | 6.6 | 15:00
16 | Barishal | 98 | 19:00 | 82 | Keranigonj | 75 | 19:30 | 148 | SSM | 12 | 02:00
17 | Barishal-230 | 80 | 19:00 | 83 | Khagrachori | 28 | 18:00 | 149 | Saidpur | 108 | 17:00
18 | Baroaulia | 60 | 13:00 | 84 | Khosba | 32 | 21:00 | 150 | Satkhira | 122 | 19:00
19 | Baroirhat | 51 | 19:00 | 85 | Khulna | 80 | 19:30 | 151 | Satmasjid | 90 | 19:00
20 | Bashundhara | 160 | 20:00 | 86 | Khulshi | 157 | 00:00 | 152 | Savar | 221 | 14:00
21 | BashundharaCement | 7 | 02:00 | 87 | Kishoreganj | 125 | 18:00 | 153 | SevenRings | 7.37 | 00:00
22 | Beanibazar | 50 | 18:30 | 88 | Kodda | 299 | 08:00 | 154 | ShahCement | 38 | 20:00
23 | Benapole | 60 | 19:00 | 89 | Kulaura | 33 | 18:00 | 155 | Shahjadpur | 78 | 12:00
24 | Bhaluka | 146 | 16:00 | 90 | Kurigram | 59 | 17:00 | 156 | Shahjibazar | 107 | 22:00
25 | Bhandaria | 45 | 21:00 | 91 | Kushtia | 108 | 00:00 | 157 | Shahmirpur | 52 | 00:00
26 | Bhangura | 37 | 13:00 | 92 | Lalbag | 70 | 11:00 | 158 | Shariatpur | 69 | 21:00
27 | Bheramara(GK) | 49 | 18:00 | 93 | Lalmonirhat | 54 | 17:00 | 159 | Sherpur | 142 | 18:00
28 | Bhulta | 263 | 23:00 | 94 | MI_Cement | 16.7 | 15:00 | 160 | Shikalbaha | 26 | 21:00
29 | Bog-Sherpur | 74 | 13:00 | 95 | Madanganj | 39 | 21:00 | 161 | Shitalakhya | 74 | 16:00
30 | Bogura | 137 | 21:00 | 96 | Madaripur | 88 | 19:00 | 162 | Sholosohor | 39 | 15:00
31 | Borhanuddin | 69 | 22:00 | 97 | Madartek | 79.03 | 22:00 | 163 | Shyampur | 176 | 16:00
32 | Brahmanbaria | 115 | 21:00 | 98 | Madunaghat | 45 | 20:00 | 164 | Siddhirganj | 132 | 14:00
33 | Cantonment | 120 | 14:00 | 99 | Magura | 57 | 19:00 | 165 | Sirajganj | 104 | 19:30
34 | Chandpur | 60 | 21:00 | 100 | Mahasthangarh | 60 | 04:00 | 166 | Sonargaon | 96 | 22:00
35 | Chandraghona | 29 | 19:30 | 101 | Manikganj | 124 | 19:00 | 167 | Sreemongol | 61 | 18:00
36 | Chapai | 60 | 19:00 | 102 | Maniknagar | 66 | 13:00 | 168 | Sreepur | 86 | 09:00
37 | Charsaidpur | 32 | 15:00 | 103 | Matarbari | 43 | 19:00 | 169 | Srinagar | 39.2 | 21:00
38 | Chauddagram | 68 | 22:00 | 104 | Matuail | 62 | 14:00 | 170 | Sunamganj | 43 | 20:00
39 | Chhatak | 26 | 20:00 | 105 | Millgate | 80 | 14:00 | 171 | Sylhet | 31 | 19:00
40 | Chowmuhani | 193 | 19:30 | 106 | Mirpur | 127 | 20:00 | 172 | Sylhet-132 | 95 | 22:00
41 | Chuadanga | 91 | 19:00 | 107 | Mirsorai | 12 | 12:00 | 173 | TK | 27 | 20:00
42 | Coxsbazar | 121 | 21:00 | 108 | Mirzapur | 44 | 14:00 | 174 | Tangail | 172 | 18:00
43 | Cumilla(N) | 161 | 19:30 | 109 | Mithapukur | 54 | 17:00 | 175 | Thakurgaon | 82 | 17:00
44 | Cumilla(S) | 159 | 14:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 115 | 15:00
45 | Daudkandi | 141 | 21:00 | 111 | Mogbazar | 132.3 | 14:00 | 177 | Ullahpara | 32 | 03:00
46 | Dhaka | 48 | 12:00 | 112 | Mongla | 46 | 19:00 | 178 | Ullon | 44 | 20:00
47 | Dhamrai | 120 | 17:00 | 113 | Motijheel | 34 | 12:00 | 179 | Uttara | 85 | 13:00
48 | Dhanmondi | 129 | 13:00 | 114 | Muktagacha | 33 | 18:00 | 180 | UttaraNew | 51 | 15:00
49 | Dohazari | 91 | 19:00 | 115 | Munshiganj | 94 | 23:00 | 181 | Zigatola | 69 | 21:00
50 | Faridpur | 134 | 18:30 | 116 | Muradnagar | 24 | 18:30
51 | Fatullah | 93 | 15:00 | 117 | Mymensingh | 192 | 18:00
52 | Fenchuganj | 27 | 21:00 | 118 | Naogaon | 112 | 08:00
53 | Feni | 104 | 21:00 | 119 | Narail | 50 | 18:30
54 | GPH | 31 | 13:00 | 120 | Narinda | 78 | 13:00
55 | Ghatail | 74 | 17:00 | 121 | Narshingdi | 155 | 19:00
56 | Ghorashal | 13 | 12:00 | 122 | Natore | 132 | 18:00
57 | Ghorashal-230 | 78 | 00:00 | 123 | Nawabganj | 46.6 | 21:00
58 | Goalpara | 30 | 21:00 | 124 | Netrakona | 135 | 18:00
59 | Gollamari | 64 | 19:00 | 125 | New | 85 | 15:00
60 | Gopalganj | 91.4 | 19:00 | 126 | Niamatpur | 97 | 17:00
61 | Gulshan | 104 | 13:00 | 127 | Noapara | 42 | 19:00
62 | Halishahar | 67 | 15:00 | 128 | PHP | 8 | 05:00
63 | HaripurSBU | 185 | 13:00 | 129 | Pabna | 98 | 18:00
64 | Hasnabad | 89 | 21:00 | 130 | Palashbari | 102 | 18:00
65 | Hathazari | 71 | 19:00 | 131 | Panchagarh | 46 | 17:00
66 | Ishurdi | 63 | 13:00 | 132 | Patuakhali | 65 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12030.5 | 67 |  | 12100.52
1:00 | 11590.5 | 57 |  | 11650.5
2:00 | 11291.5 | 0 |  | 11291.5
3:00 | 11348.5 | 0 |  | 11348.5
4:00 | 11747.5 | 0 |  | 11747.5
5:00 | 10711.9 | 0 |  | 10711.9
6:00 | 9836.5 | 0 |  | 9836.5
7:00 | 9865.92 | 0 |  | 9865.92
8:00 | 10592.46 | 0 |  | 10592.46
9:00 | 11353.52 | 20 |  | 11374.52
10:00 | 11946.24 | 20 |  | 11967.24
11:00 | 12092.44 | 15 |  | 12108.44
12:00 | 12582.39 | 30 |  | 12613.39
13:00 | 12928.99 | 23 |  | 12952.99
14:00 | 13073.6 | 62 |  | 13138.6
15:00 | 13027.01 | 63 |  | 13093.01
16:00 | 12956.46 | 65 |  | 13024.39
17:00 | 12975.28 | 45 |  | 13022.28
18:00 | 13065.04 | 0 |  | 13065.04
19:00 | 13507.67 | 0 |  | 13507.67
19:30 | 13595.24 | 0 |  | 13595.24
20:00 | 13440.83 | 0 |  | 13440.83
21:00 | 13628.5 | 0 |  | 13628.5
22:00 | 13401.5 | 0 |  | 13401.5
23:00 | 12833 | 0 |  | 12833
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6615 | 5415.5 | 12030.5 | DAILY GENERATION CURVE
00:30 | 6547 | 5263.5 | 11810.5
01:00 | 6479 | 5111.5 | 11590.5 | 12-03-2025
01:30 | 6392.5 | 5048.5 | 11441
02:00 | 6306 | 4985.5 | 11291.5
02:30 | 6335 | 4985 | 11320
03:00 | 6364 | 4984.5 | 11348.5
03:30 | 6410.5 | 5137.5 | 11548
04:00 | 6457 | 5290.5 | 11747.5
04:30 | 6208.2 | 5021.5 | 11229.7
05:00 | 5959.4 | 4752.5 | 10711.9
05:30 | 5666.7 | 4607.5 | 10274.2
06:00 | 5374 | 4462.5 | 9836.5
06:30 | 5382.325 | 4468.885 | 9851.21
07:00 | 5390.65 | 4475.27 | 9865.92
07:30 | 5603.48 | 4625.71 | 10229.19
08:00 | 5816.31 | 4776.15 | 10592.46
08:30 | 5958.315 | 5014.675 | 10972.99
09:00 | 6100.32 | 5253.2 | 11353.52
09:30 | 6147.8 | 5502.08 | 11649.88
10:00 | 6195.28 | 5750.96 | 11946.24
10:30 | 6226.745 | 5792.595 | 12019.34
11:00 | 6258.21 | 5834.23 | 12092.44
11:30 | 6356.31 | 5981.105 | 12337.415
12:00 | 6454.41 | 6127.98 | 12582.39
12:30 | 6581.025 | 6174.665 | 12755.69
13:00 | 6707.64 | 6221.35 | 12928.99
13:30 | 6813.355 | 6187.94 | 13001.295
14:00 | 6919.07 | 6154.53 | 13073.6
14:30 | 6940.045 | 6110.26 | 13050.305
15:00 | 6961.02 | 6065.99 | 13027.01
15:30 | 6980.095 | 6011.64 | 12991.735
16:00 | 6999.17 | 5957.29 | 12956.46
16:30 | 7076.035 | 5889.835 | 12965.87
17:00 | 7152.9 | 5822.38 | 12975.28
17:30 | 7275.495 | 5744.665 | 13020.16
18:00 | 7398.09 | 5666.95 | 13065.04
18:30 | 7569.045 | 5717.31 | 13286.355
19:00 | 7740 | 5767.67 | 13507.67
19:30 | 7613 | 5982.24 | 13595.24
20:00 | 7551 | 5889.83 | 13440.83
20:30 | 7562 | 5972.665 | 13534.665 |  | Executive Engineer
21:00 | 7573 | 6055.5 | 13628.5 |  | Network Operation Division
21:30 | 7437.5 | 6077.5 | 13515
22:00 | 7302 | 6099.5 | 13401.5
22:30 | 7097 | 6020.25 | 13117.25
23:00 | 6892 | 5941 | 12833

## En-Curve
QF-LDC-12
Date | 12-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3397 | 1845.5 | 917 | 0 | 62 | 1262 | 40 | 3585 | 0 | 242 | 680 | 0 | 0 | 0 | 67 | DAILY ENERGY CURVE
00:30 | 3340 | 1812 | 917.5 | 0 | 59 | 1209.5 | 40 | 3476.5 | 0 | 224 | 732 | 0 | 0 | 0 | 62 | 12-03-2025
01:00 | 3283 | 1778.5 | 918 | 0 | 56 | 1157 | 40 | 3368 | 0 | 206 | 784 | 0 | 0 | 0 | 57
01:30 | 3193.5 | 1762 | 918 | 0 | 54 | 1129.5 | 40 | 3329.5 | 0 | 206 | 807.5 | 0 | 0 | 1 | 28.5 | Energy Generated | 295.363 |  | MKWHr
02:00 | 3104 | 1745.5 | 918 | 0 | 52 | 1102 | 40 | 3291 | 0 | 206 | 831 | 0 | 0 | 2 | 0 | Energy not Served | 0.467 |  | MKWHr
02:30 | 3089.5 | 1744 | 918 | 0 | 52 | 1106 | 40 | 3318 | 0 | 214.5 | 835 | 0 | 0 | 3 | 0 | Total Energy Requirement | 295.83 |  | MKWHr
03:00 | 3075 | 1742.5 | 918 | 0 | 52 | 1110 | 40 | 3345 | 0 | 223 | 839 | 0 | 0 | 4 | 0
03:30 | 3231.5 | 1845.5 | 917.5 | 0 | 52 | 1112.5 | 40 | 3398 | 0 | 220.5 | 727.5 | 0 | 0 | 3 | 0
04:00 | 3388 | 1948.5 | 917 | 0 | 52 | 1115 | 40 | 3451 | 0 | 218 | 616 | 0 | 0 | 2 | 0
04:30 | 3374 | 1889.2 | 917.5 | 0 | 51 | 1017.5 | 40 | 3241 | 0 | 171 | 527.5 | 0 | 0 | 1 | 0
05:00 | 3360 | 1829.9 | 918 | 0 | 50 | 920 | 40 | 3031 | 0 | 124 | 439 | 0 | 0 | 0 | 0
05:30 | 3310.5 | 1727.7 | 918 | 0 | 49 | 867.5 | 40 | 2895 | 0 | 106.5 | 360 | 0 | 0 | 0 | 0
06:00 | 3261 | 1625.5 | 918 | 0 | 48 | 815 | 40 | 2759 | 0 | 89 | 281 | 0 | 0 | 0 | 0
06:30 | 3299 | 1617.5 | 918 | 0 | 49 | 815.5 | 40 | 2734 | 22.21 | 89 | 267 | 0 | 0 | 0 | 0
07:00 | 3337 | 1609.5 | 918 | 0 | 50 | 816 | 40 | 2709 | 44.42 | 89 | 253 | 0 | 0 | 0 | 0
07:30 | 3429 | 1720.5 | 894 | 0 | 51 | 815.13 | 40 | 2782 | 110.56 | 106 | 281 | 0 | 0 | 0 | 0
08:00 | 3521 | 1831.5 | 870 | 0 | 52 | 814.26 | 40 | 2855 | 176.7 | 123 | 309 | 0 | 0 | 0 | 0
08:30 | 3531 | 1871 | 870.5 | 0 | 54 | 865.085 | 40 | 3016.5 | 250.905 | 144 | 330 | 0 | 0 | 0 | 10
09:00 | 3541 | 1910.5 | 871 | 0 | 56 | 915.91 | 40 | 3178 | 325.11 | 165 | 351 | 0 | 0 | 0 | 20
09:30 | 3546 | 1849.5 | 893.5 | 0 | 52 | 1017.345 | 40 | 3321 | 391.035 | 181.5 | 358 | 0 | 0 | 0 | 20
10:00 | 3551 | 1788.5 | 916 | 0 | 48 | 1118.78 | 40 | 3464 | 456.96 | 198 | 365 | 0 | 0 | 0 | 20
10:30 | 3585.5 | 1782.25 | 917 | 0 | 48 | 1119.065 | 40 | 3465 | 490.025 | 195.5 | 377 | 0 | 0 | 0 | 17.5
11:00 | 3620 | 1776 | 918 | 0 | 48 | 1119.35 | 40 | 3466 | 523.09 | 193 | 389 | 0 | 0 | 0 | 15
11:30 | 3618 | 1777.75 | 918.5 | 0 | 55 | 1192.52 | 40 | 3552.5 | 544.145 | 196.5 | 441.5 | 0 | 0 | 1 | 22.5
12:00 | 3616 | 1779.5 | 919 | 0 | 62 | 1265.69 | 40 | 3639 | 565.2 | 200 | 494 | 0 | 0 | 2 | 30
12:30 | 3611 | 1759.75 | 918.5 | 0 | 63 | 1313.55 | 40 | 3710.5 | 563.39 | 208.5 | 562.5 | 0 | 0 | 5 | 26.5
13:00 | 3606 | 1740 | 918 | 0 | 64 | 1361.41 | 40 | 3782 | 561.58 | 217 | 631 | 0 | 0 | 8 | 23
13:30 | 3623 | 1761.75 | 918 | 0 | 68 | 1364.18 | 40 | 3775.5 | 519.865 | 226 | 696.5 | 0 | 0 | 8.5 | 42.5
14:00 | 3640 | 1783.5 | 918 | 0 | 72 | 1366.95 | 40 | 3769 | 478.15 | 235 | 762 | 0 | 0 | 9 | 62
14:30 | 3643 | 1767.5 | 918 | 0 | 70 | 1366.41 | 40 | 3775 | 424.895 | 238.5 | 797.5 | 0 | 0 | 9.5 | 62.5
15:00 | 3646 | 1751.5 | 918 | 0 | 68 | 1365.87 | 40 | 3781 | 371.64 | 242 | 833 | 0 | 0 | 10 | 63
15:30 | 3633.5 | 1769.5 | 918 | 0 | 66 | 1363.105 | 40 | 3795.5 | 298.63 | 242 | 858.5 | 0 | 0 | 7 | 64
16:00 | 3621 | 1787.5 | 918 | 0 | 64 | 1360.34 | 40 | 3810 | 225.62 | 242 | 884 | 0 | 0 | 4 | 65
16:30 | 3557 | 1763 | 917.5 | 0 | 64 | 1361.35 | 40 | 3830.5 | 153.52 | 242.5 | 1033.5 | 0 | 0 | 3 | 55
17:00 | 3493 | 1738.5 | 917 | 0 | 64 | 1362.36 | 40 | 3851 | 81.42 | 243 | 1183 | 0 | 0 | 2 | 45
17:30 | 3449.5 | 1724 | 917.5 | 0 | 66 | 1315.355 | 40 | 3629 | 41.805 | 357.5 | 1478.5 | 0 | 0 | 1 | 22.5
18:00 | 3406 | 1709.5 | 918 | 0 | 68 | 1268.35 | 40 | 3407 | 2.19 | 472 | 1774 | 0 | 0 | 0 | 0
18:30 | 3508 | 1759 | 894.5 | 0 | 69 | 1208.76 | 40 | 3434 | 1.095 | 523.5 | 1848.5 | 0 | 0 | 0 | 0
19:00 | 3610 | 1808.5 | 871 | 0 | 70 | 1149.17 | 40 | 3461 | 0 | 575 | 1923 | 0 | 0 | 0 | 0
19:30 | 3624 | 1796.5 | 870 | 0 | 70 | 1199.74 | 40 | 3790 | 0 | 561 | 1644 | 0 | 0 | 0 | 0
20:00 | 3697 | 1850.5 | 871 | 0 | 62 | 1263.33 | 40 | 3914 | 0 | 401 | 1342 | 0 | 0 | 0 | 0
20:30 | 3727.5 | 1897 | 870.5 | 0 | 67 | 1322.165 | 40 | 3941.5 | 0 | 385 | 1284 | 0 | 0 | 0 | 0
21:00 | 3758 | 1943.5 | 870 | 0 | 72 | 1381 | 40 | 3969 | 0 | 369 | 1226 | 0 | 0 | 0 | 0
21:30 | 3689.5 | 1926.5 | 893.5 | 0 | 71 | 1371.5 | 40 | 3967.5 | 0 | 370.5 | 1185 | 0 | 0 | 0 | 0
22:00 | 3621 | 1909.5 | 917 | 0 | 70 | 1362 | 40 | 3966 | 0 | 372 | 1144 | 0 | 0 | 0 | 0
22:30 | 3599.5 | 1910.25 | 917.5 | 0 | 67 | 1360.5 | 40 | 3940.5 | 0 | 284.5 | 997.5 | 0 | 0 | 0 | 0
23:00 | 3578 | 1911 | 918 | 0 | 64 | 1359 | 40 | 3915 | 0 | 197 | 851 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 05:00 | 373 | 15:00 | Payra | 419 | 06:00 | 408 | 14:00
Ashuganj | 403 | 18:00 | 371 | 16:00 | Rahanpur | 414 | 05:00 | 393 | 16:00
Bhulta | 403 | 18:00 | 371 | 15:00 | Rampal | 410 | 06:00 | 389 | 15:00
Bibiana | 396 | 05:00 | 382 | 13:00
BIPTC | 397 | 01:00 | 387 | 15:00
Bogura | 405 | 06:00 | 379 | 16:00
Gopalganj | 408 | 06:00 | 385 | 14:00
Kaliakoir | 377 | 18:00 | 273 | 04:00
Madunaghat | 403 | 19:00 | 390 | 13:00
Meghnaghat | 397 | 06:00 | 373 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 05:00 | 215 | 15:00 | Keranigonj | 230 | 05:00 | 213 | 15:00
AKSML | 233 | 18:30 | 225 | 15:00 | Khulna(S) | 239 | 06:00 | 220 | 21:00
Aminbazar | 233 | 05:00 | 217 | 11:00 | Madunaghat | 236 | 19:00 | 226 | 14:00
Ashuganj | 234 | 05:00 | 218 | 13:00 | Madunaghat-400 | 237 | 19:00 | 226 | 13:00
Ashuganj-400 | 234 | 05:00 | 218 | 13:00 | Maniknagar | 227 | 04:00 | 211 | 15:00
Baghabari | 236 | 03:00 | 222 | 15:00 | Meghnaghat | 235 | 05:00 | 220 | 15:00
Barapukuria | 225 | 18:30 | 213 | 16:00 | Meghnaghat-400 | 230 | 06:00 | 215 | 15:00
Barapukuria-230 | 225 | 18:30 | 213 | 16:00 | Mirsorai | 231 | 18:00 | 218 | 15:00
Barishal | 239 | 06:00 | 228 | 15:00 | Rajshahi | 236 | 02:00 | 222 | 16:00
Bheramara | 236 | 01:00 | 222 | 12:00 | Rampal | 237 | 06:00 | 221 | 14:00
Bhulta | 229 | 18:00 | 211 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 05:00 | 220 | 12:00 | Rampura | 226 | 05:00 | 209 | 15:00
BIPTC | 237 | 01:00 | 221 | 21:00 | Shikalbaha | 235 | 18:30 | 223 | 12:00
Bogura | 235 | 06:00 | 219 | 16:00 | Shyampur | 229 | 05:00 | 213 | 15:00
Bogura-400 | 234 | 06:00 | 220 | 14:00 | Siddhirganj | 228 | 18:00 | 213 | 12:00
Borhanuddin | 243 | 06:00 | 235 | 14:00 | Sirajgonj | 240 | 01:00 | 230 | 16:00
BSRM | 230 | 18:00 | 218 | 15:00 | Sreepur | 233 | 02:00 | 220 | 14:00
Cumilla(N) | 226 | 02:00 | 213 | 13:00 | Tongi | 226 | 04:00 | 208 | 15:00
Faridpur | 236 | 05:00 | 223 | 14:00
Fenchuganj | 234 | 05:00 | 225 | 15:00
Ghorashal | 230 | 00:00 | 220 | 12:00
Ghorashal-230 | 228 | 05:00 | 211 | 15:00
Gopalganj | 235 | 06:00 | 223 | 12:00
GPH | 233 | 18:30 | 222 | 15:00
Haripur | 227 | 02:00 | 214 | 12:00
Hasnabad | 229 | 05:00 | 213 | 15:00
Hathazari | 239 | 18:30 | 226 | 12:00
Ishurdi | 237 | 01:00 | 224 | 12:00
Jhenaidah | 235 | 02:00 | 217 | 21:00
Kaliakoir | 235 | 18:00 | 216 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 122 | 15:00 | Madunaghat | 134 | 06:00 | 129 | 11:00
Agargaon | 139 | 05:00 | 127 | 15:00 | Magura | 138 | 05:00 | 125 | 21:00
Agrabad | 137 | 18:00 | 123 | 17:00 | Mahasthangarh | 132 | 05:00 | 121 | 16:00
AKS | 130 | 00:00 | 125 | 10:00 | Manikganj | 130 | 04:00 | 119 | 11:00
Aminbazar | 137 | 05:00 | 125 | 12:00 | Maniknagar | 133 | 04:00 | 122 | 14:00
Amnura | 138 | 06:00 | 128 | 12:00 | Matarbari | 124 | 06:00 | 115 | 23:00
Ashuganj | 136 | 05:00 | 130 | 13:00 | Matuail | 133 | 18:00 | 123 | 15:00
Bagerhat | 136 | 06:00 | 118 | 20:00 | Millgate | 134 | 01:00 | 122 | 15:00
Bajitpur | 131 | 04:00 | 122 | 15:00 | Mirpur | 136 | 05:00 | 124 | 15:00
Bakulia | 138 | 18:00 | 128 | 15:00 | Mirzapur | 131 | 05:00 | 121 | 17:00
Banani | 135 | 05:00 | 121 | 15:00 | Mithapukur | 133 | 18:30 | 120 | 16:00
Bangabhaban | 134 | 04:00 | 122 | 15:00 | MI_Cement | 133 | 01:00 | 122 | 16:00
Barapukuria | 140 | 09:00 | 129 | 16:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 05:00 | 131 | 23:00 | Mogbazar | 135 | 05:00 | 122 | 15:00
Barishal | 134 | 05:00 | 125 | 14:00 | Mongla | 136 | 06:00 | 119 | 21:00
Barishal-230 | 134 | 05:00 | 126 | 15:00 | Motijheel | 134 | 04:00 | 122 | 15:00
Baroaulia | 136 | 18:00 | 127 | 11:00 | Muktagacha | 135 | 06:00 | 120 | 00:00
Baroirhat | 129 | 18:00 | 118 | 12:00 | Munshiganj | 132 | 05:00 | 121 | 16:00
Bashundhara | 135 | 05:00 | 121 | 15:00 | Muradnagar | 128 | 06:00 | 118 | 15:00
BashundharaCement | 132 | 01:00 | 122 | 15:00 | Mymensingh | 135 | 05:00 | 113 | 12:00
Beanibazar | 132 | 05:00 | 127 | 14:00 | Naogaon | 130 | 06:00 | 118 | 16:00
Benapole | 136 | 04:00 | 120 | 21:00 | Narail | 138 | 03:00 | 124 | 21:00
Bhaluka | 129 | 08:00 | 118 | 12:00 | Narinda | 133 | 04:00 | 122 | 14:00
Bhandaria | 131 | 06:00 | 118 | 21:00 | Narshingdi | 132 | 18:00 | 110 | 13:00
Bhangura | 134 | 03:00 | 124 | 18:00 | Natore | 134 | 06:00 | 125 | 13:00
Bheramara | 136 | 01:00 | 130 | 12:00 | Nawabganj | 135 | 05:00 | 123 | 15:00
Bheramara(GK) | 138 | 03:00 | 130 | 12:00 | Netrakona | 126 | 06:00 | 109 | 16:00
Bhulta | 130 | 18:00 | 119 | 16:00 | New | 136 | 05:00 | 123 | 15:00
Bog-Sherpur | 132 | 06:00 | 122 | 16:00 | Niamatpur | 140 | 02:00 | 132 | 13:00
Bogura | 134 | 05:00 | 123 | 16:00 | Noapara | 138 | 06:00 | 124 | 14:00
Bogura-230 | 133 | 03:00 | 124 | 14:00 | Pabna | 135 | 01:00 | 127 | 15:00
Brahmanbaria | 129 | 08:00 | 118 | 15:00 | Palashbari | 131 | 18:30 | 117 | 16:00
Cantonment | 139 | 05:00 | 127 | 15:00 | Panchagarh | 140 | 18:00 | 122 | 09:00
Chandpur | 130 | 18:30 | 114 | 11:00 | Patuakhali | 135 | 04:00 | 131 | 19:00
Chandraghona | 134 | 02:00 | 128 | 11:00 | Payra | 138 | 06:00 | 134 | 12:00
Chapai | 138 | 05:00 | 129 | 13:00 | PHP | 126 | 19:00 | 116 | 11:00
Charsaidpur | 134 | 03:00 | 122 | 23:00 | Postogola | 137 | 18:30 | 124 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 128 | 18:00 | 116 | 11:00 | Purbachal | 135 | 04:00 | 121 | 14:00
Chhatak | 132 | 05:00 | 127 | 14:00 | Purbasadipur | 136 | 18:00 | 118 | 16:00
Chowmuhani | 125 | 18:00 | 115 | 12:00 | Rahanpur | 141 | 02:00 | 134 | 14:00
Chuadanga | 137 | 05:00 | 122 | 22:00 | Rahanpur-400 | 142 | 05:00 | 134 | 16:00
Coxsbazar | 123 | 08:00 | 117 | 00:00 | Rahim | 132 | 02:00 | 123 | 15:00
Cumilla(N) | 129 | 02:00 | 122 | 11:00 | Rajbari | 132 | 06:00 | 123 | 16:00
Cumilla(S) | 130 | 00:00 | 120 | 11:00 | Rajendrapur | 135 | 18:30 | 117 | 15:00
Daudkandi | 127 | 06:00 | 116 | 15:00 | Rajshahi | 135 | 05:00 | 126 | 15:00
Dhaka | 136 | 05:00 | 122 | 15:00 | Rajshahi-230 | 137 | 06:00 | 124 | 13:00
Dhamrai | 132 | 01:00 | 121 | 15:00 | Ramganj | 128 | 18:00 | 110 | 11:00
Dhanmondi | 135 | 05:00 | 121 | 15:00 | Rampur | 135 | 18:00 | 126 | 12:00
Dohazari | 132 | 06:00 | 125 | 00:00 | Rampura | 135 | 05:00 | 122 | 14:00
Faridpur | 136 | 16:00 | 126 | 12:00 | Rangamati | 134 | 18:30 | 128 | 10:00
Fatullah | 134 | 03:00 | 123 | 16:00 | Rangpur | 135 | 18:30 | 119 | 16:00
Fenchuganj | 136 | 19:00 | 130 | 14:00 | Ruppur | 138 | 09:00 | 131 | 14:00
Feni | 129 | 18:00 | 117 | 11:00 | Saidpur | 134 | 05:00 | 119 | 17:00
Ghatail | 132 | 05:00 | 117 | 13:00 | Satkhira | 135 | 05:00 | 120 | 21:00
Ghorashal | 137 | 18:00 | 128 | 13:00 | Satmasjid | 139 | 05:00 | 127 | 15:00
Goalpara | 138 | 02:00 | 124 | 10:00 | Savar | 136 | 04:00 | 123 | 15:00
Gollamari | 138 | 05:00 | 126 | 21:00 | SevenRings | 140 | 18:30 | 127 | 15:00
Gopalganj | 138 | 06:00 | 126 | 21:00 | ShahCement | 134 | 03:00 | 122 | 16:00
Gopalganj-400 | 139 | 06:00 | 130 | 12:00 | Shahjadpur | 138 | 06:00 | 130 | 12:00
Gulshan | 135 | 05:00 | 122 | 19:00 | Shahjibazar | 132 | 02:00 | 122 | 15:00
Halishahar | 133 | 19:30 | 127 | 11:00 | Shahmirpur | 136 | 19:00 | 129 | 11:00
Haripur | 133 | 18:30 | 125 | 11:00 | Shariatpur | 137 | 07:00 | 127 | 13:00
HaripurSBU | 133 | 18:30 | 125 | 11:00 | Sherpur | 137 | 05:00 | 120 | 00:00
Hasnabad | 135 | 04:00 | 125 | 16:00 | Shikalbaha | 125 | 18:30 | 118 | 11:00
Hathazari | 137 | 18:30 | 129 | 11:00 | Shikalbaha-230 | 137 | 18:30 | 129 | 14:00
Ishurdi | 138 | 01:00 | 131 | 15:00 | Shitalakhya | 133 | 01:00 | 122 | 16:00
Jaldhaka | 131 | 06:00 | 119 | 09:00 | Sholosohor | 135 | 18:00 | 128 | 12:00
Jamalpur | 140 | 05:00 | 118 | 03:00 | Shyampur | 133 | 18:00 | 122 | 16:00
Jashore | 137 | 06:00 | 123 | 14:00 | Shyampur-230 | 133 | 03:00 | 123 | 15:00
Jhenaidah | 138 | 06:00 | 125 | 21:00 | Siddhirganj | 132 | 05:00 | 123 | 15:00
Jhenaidah-230 | 138 | 05:00 | 125 | 21:00 | Sirajganj | 133 | 01:00 | 124 | 13:00
Joydebpur | 136 | 18:00 | 124 | 14:00 | Sonargaon | 130 | 18:00 | 121 | 11:00
Joypurhat | 128 | 02:00 | 115 | 16:00 | Sreemongol | 131 | 08:00 | 124 | 16:00
Juldah | 137 | 18:30 | 128 | 11:00 | Sreepur | 131 | 02:00 | 122 | 11:00
Kabirpur | 134 | 18:30 | 120 | 11:00 | Srinagar | 135 | 04:00 | 123 | 15:00
Kachua | 128 | 18:00 | 115 | 11:00 | SSM | 138 | 19:30 | 130 | 11:00
Kaliakoir | 135 | 02:00 | 124 | 12:00 | Sunamganj | 130 | 03:00 | 126 | 01:00
Kallyanpur | 136 | 03:00 | 125 | 15:00 | Sylhet | 131 | 02:00 | 127 | 13:00
Kalurghat | 136 | 18:00 | 128 | 13:00 | Sylhet-132 | 132 | 03:00 | 129 | 15:00
Kamrangirchar | 136 | 06:00 | 123 | 15:00 | Tangail | 128 | 05:00 | 117 | 17:00
Kaptai | 135 | 6:00 | 126 | 12:00 | Thakurgaon | 139 | 18:00 | 119 | 09:00
Kazla | 134 | 05:00 | 122 | 13:00 | TK | 137 | 18:30 | 129 | 13:00
Keranigonj | 136 | 06:00 | 124 | 16:00 | Tongi | 138 | 19:00 | 124 | 15:00
Khagrachori | 134 | 18:00 | 127 | 11:00 | Ullahpara | 134 | 05:00 | 125 | 15:00
Khosba | 128 | 06:00 | 118 | 14:00 | Ullon | 134 | 02:00 | 122 | 15:00
Khulna | 137 | 05:00 | 123 | 21:00 | Uttara | 134 | 06:00 | 121 | 12:00
Khulna(S) | 140 | 06:00 | 126 | 20:00 | UttaraNew | 135 | 06:00 | 124 | 15:00
Khulshi | 134 | 18:30 | 126 | 11:00 | Zigatola | 135 | 06:00 | 123 | 16:00
Kishoreganj | 131 | 03:00 | 119 | 15:00
Kodda | 135 | 18:30 | 120 | 14:00
KSRM | 136 | 18:00 | 127 | 11:00
Kulaura | 134 | 05:00 | 129 | 15:00
Kurigram | 131 | 18:00 | 117 | 16:00
Kushtia | 137 | 05:00 | 127 | 21:00
Lalbag | 134 | 18:00 | 123 | 15:00
Lalmonirhat | 132 | 18:00 | 120 | 10:00
Madanganj | 132 | 01:00 | 122 | 15:00
Madaripur | 136 | 06:00 | 128 | 16:00
Madartek | 135 | 05:00 | 122 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-03-2025 | [28 empty] | Date: | 12-03-2025 | [28 empty] | Date: | 12-03-2025 | [28 empty] | Date: | 12-03-2025 | [28 empty] | Date: | 12-03-2025 | [18 empty] | Date: | 12-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 40 | 34 | 8 | 130 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 54 | 0 | 78 | 130 | 45 | 15 | 0 | 72 | 30 | 0 | 350 | 278 | 0 | 0 | 0 | 18 | 326 | 0 | 0 | 0 | 70 | 18 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 24 | 0 | 40 | 0 | 16 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1190 | 0 | 51 | 0 | 199 | 0 | 0 | 285 | 29 | 182 | 33 | 17 | 50 | 51 | 38 | 12 | 34 | 62 | 0 | 0 | 0 | 290 | 320 | 335 | 32 | 41 | 30 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 162 | 0 | 49 | 58 | 0 | 0 | 0 | 8 | 6615 | 917 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 128 | 0 | 414 | 0 | 0 | 2.5 | 164 | 60 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 130 | 220 | 0 | 0 | 1000 | 0 | 5415.5 | 12030.5 | 87.68
01:00 | 48 | 17 | 8 | 130 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 54 | 54 | 0 | 78 | 130 | 45 | 55 | 0 | 72 | 25 | 0 | 350 | 268 | 0 | 0 | 17 | 18 | 305 | 0 | 0 | 0 | 51 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 24 | 0 | 40 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 199 | 0 | 0 | 285 | 29 | 182 | 35 | 19 | 50 | 51 | 32 | 12 | 34 | 56 | 0 | 0 | 0 | 275 | 300 | 320 | 32 | 41 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 49 | 58 | 0 | 0 | 0 | 12 | 6479 | 918 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 131 | 0 | 360 | 0 | 0 | 2.5 | 171 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 122 | 220 | 0 | 0 | 930 | 0 | 5111.5 | 11590.5 | 87.68
02:00 | 64 | 17 | 8 | 130 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 54 | 54 | 0 | 78 | 130 | 45 | 55 | 0 | 72 | 25 | 0 | 300 | 270 | 0 | 0 | 35 | 19 | 260 | 0 | 0 | 0 | 51 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 48 | 24 | 0 | 40 | 0 | 23 | 346 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 200 | 0 | 0 | 260 | 29 | 182 | 35 | 34 | 50 | 51 | 30 | 12 | 34 | 52 | 0 | 0 | 0 | 285 | 300 | 312 | 32 | 41 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 49 | 58 | 0 | 0 | 0 | 12 | 6306 | 918 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 0 | 1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 136 | 0 | 300 | 0 | 0 | 2.5 | 172 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 130 | 220 | 0 | 0 | 900 | 0 | 4985.5 | 11291.5 | 87.67
03:00 | 73 | 34 | 8 | 130 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 37 | 54 | 0 | 78 | 130 | 45 | 55 | 0 | 72 | 25 | 0 | 300 | 310 | 0 | 0 | 35 | 20 | 260 | 0 | 0 | 0 | 51 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 48 | 24 | 0 | 40 | 0 | 23 | 347 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 200 | 0 | 0 | 240 | 29 | 198 | 35 | 34 | 50 | 51 | 28 | 12 | 34 | 52 | 0 | 0 | 0 | 280 | 300 | 312 | 32 | 41 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 49 | 76 | 0 | 0 | 0 | 12 | 6364 | 918 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 0 | 1110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 143 | 0 | 300 | 0 | 0 | 2.5 | 175 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 100 | 180 | 0 | 0 | 900 | 0 | 4984.5 | 11348.5 | 87.67
04:00 | 0 | 34 | 8 | 130 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 17 | 0 | 71 | 130 | 0 | 0 | 35 | 72 | 25 | 0 | 420 | 286 | 0 | 0 | 0 | 20 | 335 | 0 | 0 | 0 | 46 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 29 | 345 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 200 | 0 | 0 | 280 | 29 | 182 | 35 | 41 | 50 | 34 | 29 | 12 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 312 | 32 | 41 | 30 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 78 | 134 | 0 | 0 | 0 | 12 | 6457 | 917 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 147 | 0 | 414 | 0 | 0 | 2.5 | 179 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 960 | 0 | 5290.5 | 11747.5 | 87.66
05:00 | 0 | 17 | 8 | 130 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 0 | 60 | 64 | 0 | 0 | 35 | 72 | 25 | 0 | 350 | 289 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 35 | 20.4 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 356 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 885 | 0 | 51 | 0 | 199 | 0 | 0 | 285 | 29 | 182 | 35 | 0 | 50 | 0 | 29 | 12 | 0 | 50 | 0 | 0 | 0 | 290 | 320 | 312 | 29 | 41 | 30 | 5 | 120 | 22 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 79 | 135 | 0 | 0 | 0 | 12 | 5959.4 | 918 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 149 | 0 | 350 | 0 | 0 | 2.5 | 175 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 7 | 130 | 220 | 0 | 0 | 940 | 0 | 4752.5 | 10711.9 | 87.66
06:00 | 0 | 17 | 8 | 130 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 0 | 52 | 64 | 0 | 0 | 17 | 0 | 25 | 0 | 350 | 306 | 0 | 0 | 0 | 22 | 270 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 355 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 805 | 0 | 10 | 0 | 108 | 0 | 0 | 285 | 29 | 182 | 35 | 0 | 50 | 0 | 9 | 12 | 0 | 48 | 0 | 0 | 0 | 290 | 320 | 312 | 32 | 41 | 30 | 5 | 120 | 22 | 0 | 11 | 30 | 0 | 16 | 163 | 0 | 79 | 95 | 0 | 0 | 0 | 12 | 5374 | 918 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 148 | 0 | 320 | 0 | 0 | 2.5 | 179 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 6 | 130 | 220 | 0 | 0 | 750 | 0 | 4462.5 | 9836.5 | 87.65
07:00 | 0 | 17 | 8 | 130 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 304 | 0 | 0 | 0 | 23 | 270 | 0 | 0 | 2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 356 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 805 | 2 | 10 | 0 | 108 | 0 | 0 | 285 | 29 | 218 | 35 | 0 | 50 | 0 | 0 | 12 | 0 | 50 | 0 | 8 | 0 | 305 | 320 | 312 | 32 | 41 | 30 | 5 | 163 | 21 | 0 | 11 | 30 | 0 | 16 | 163 | 0 | 79 | 95 | 19 | 0 | 2.65 | 12 | 5390.65 | 918 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.85 | 411 | 0 | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.48 | 159 | 0 | 0 | 0 | 154 | 0 | 320 | 0 | 0.29 | 2.5 | 175 | 62 | 0 | 1 | 0 | 0 | 0 | 0.1 | 11 | 0.05 | 0 | 150 | 5 | 130 | 220 | 0 | 0 | 750 | 0 | 4475.27 | 9865.92 | 87.65
08:00 | 0 | 17 | 8 | 130 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 76 | 98 | 0 | 0 | 0 | 40 | 25 | 0 | 350 | 288 | 0 | 0 | 0 | 23 | 331 | 0 | 0 | 9 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 6 | 352 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 805 | 7 | 18 | 0 | 195 | 0 | 0 | 285 | 29 | 183 | 35 | 0 | 50 | 0 | 0 | 12 | 0 | 52 | 0 | 26 | 0 | 315 | 320 | 312 | 32 | 41 | 30 | 5 | 163 | 21 | 0 | 83 | 30 | 0 | 16 | 163 | 0 | 69 | 95 | 19 | 0 | 11.31 | 12 | 5816.31 | 870 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.01 | 410 | 0 | 814.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 13.69 | 165 | 0 | 0 | 0 | 156 | 0 | 414 | 0 | 1.2 | 2.5 | 177 | 61 | 0 | 7 | 0 | 0 | 0 | 0.3 | 41 | 0.19 | 0 | 250 | 4 | 130 | 220 | 0 | 0 | 800 | 0 | 4776.15 | 10592.46 | 87.64
09:00 | 0 | 50 | 17 | 130 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 17 | 0 | 104 | 98 | 0 | 0 | 0 | 54 | 25 | 0 | 420 | 275 | 0 | 0 | 0 | 20 | 280 | 0 | 0 | 16 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 5 | 343 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 875 | 12 | 51 | 0 | 197 | 0 | 0 | 285 | 29 | 184 | 35 | 0 | 50 | 0 | 0 | 12 | 0 | 56 | 0 | 43 | 0 | 300 | 320 | 312 | 32 | 41 | 30 | 5 | 163 | 21 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 69 | 95 | 19 | 1 | 22.32 | 12 | 6100.32 | 871 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.95 | 478 | 0 | 915.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 28.46 | 166 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 2.41 | 5.5 | 174 | 61 | 0 | 12 | 0 | 0 | 0 | 0.6 | 76 | 0.37 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 940 | 0 | 5253.2 | 11353.52 | 87.64
10:00 | 0 | 50 | 17 | 171 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 17 | 0 | 107 | 97 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 263 | 0 | 0 | 0 | 15 | 250 | 0 | 0 | 24 | 34 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 4 | 343 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1009 | 15 | 51 | 0 | 199 | 0 | 0 | 285 | 29 | 182 | 34 | 0 | 50 | 0 | 2 | 11 | 0 | 48 | 0 | 56 | 0 | 315 | 320 | 312 | 32 | 41 | 30 | 5 | 163 | 21 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 78 | 95 | 17 | 2 | 33.28 | 12 | 6195.28 | 916 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.64 | 520 | 0 | 1118.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 38.63 | 166 | 0 | 0 | 0 | 152 | 0 | 414 | 0 | 3.48 | 5.5 | 174 | 61 | 0 | 17 | 0 | 0 | 0 | 2.4 | 112 | 0.53 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 1050 | 0 | 5750.96 | 11946.24 | 87.64
11:00 | 0 | 50 | 17 | 251 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 17 | 0 | 114 | 64 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 285 | 0 | 0 | 0 | 15 | 250 | 0 | 0 | 28 | 62 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 4 | 341 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 972 | 18 | 43 | 0 | 200 | 0 | 0 | 285 | 29 | 189 | 33 | 0 | 50 | 0 | 9 | 11 | 0 | 48 | 0 | 65 | 0 | 295 | 320 | 312 | 29 | 40 | 30 | 5 | 163 | 21 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 95 | 17 | 2 | 40.21 | 12 | 6258.21 | 918 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.25 | 518 | 0 | 1119.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 48.01 | 166 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 4.39 | 4 | 175 | 63 | 0 | 5 | 0 | 0 | 0 | 1.6 | 127 | 0.63 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 1090 | 0 | 5834.23 | 12092.44 | 87.63
12:00 | 0 | 50 | 17 | 251 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 114 | 63 | 0 | 0 | 0 | 90 | 8 | 0 | 300 | 275 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 29 | 70 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 24 | 0 | 4 | 40 | 0 | 4 | 342 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 1026 | 19 | 43 | 0 | 200 | 0 | 0 | 285 | 29 | 183 | 33 | 7 | 51 | 9 | 14 | 15 | 34 | 62 | 0 | 67 | 0 | 305 | 320 | 332 | 32 | 40 | 30 | 5 | 163 | 21 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 78 | 95 | 17 | 2 | 41.91 | 12 | 6454.41 | 919 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1 | 618 | 0 | 1265.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 52.59 | 165 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 4.74 | 4 | 175 | 61 | 0 | 10 | 0 | 0 | 0 | 3.2 | 139 | 0.66 | 0 | 307 | 5 | 130 | 220 | 0 | 0 | 1110 | 0 | 6127.98 | 12582.39 | 87.62
13:00 | 0 | 50 | 17 | 251 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 115 | 63 | 0 | 0 | 30 | 90 | 8 | 0 | 300 | 274 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 28 | 87 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 48 | 0 | 4 | 40 | 0 | 10 | 340 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 1172 | 19 | 51 | 0 | 199 | 0 | 0 | 285 | 23 | 184 | 33 | 22 | 51 | 22 | 13 | 12 | 84 | 64 | 0 | 65 | 0 | 305 | 320 | 330 | 32 | 40 | 30 | 5 | 120 | 21 | 0 | 83 | 30 | 0 | 16 | 165 | 0 | 87 | 95 | 11 | 2 | 39.64 | 8 | 6707.64 | 918 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.08 | 618 | 0 | 1361.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 50.15 | 164 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 4.67 | 4 | 174 | 61 | 0 | 24 | 0 | 0 | 0 | 4.4 | 136 | 0.64 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1110 | 0 | 6221.35 | 12928.99 | 87.62
14:00 | 0 | 35 | 8 | 241 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 21 | 0 | 124 | 94 | 0 | 0 | 55 | 90 | 8 | 0 | 300 | 287 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 26 | 98 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 5 | 340 | 0 | 0 | 0 | 0 | 1 | 214 | 0 | 0 | 0 | 1172 | 17 | 51 | 0 | 199 | 0 | 0 | 285 | 20 | 186 | 30 | 51 | 51 | 51 | 9 | 12 | 98 | 72 | 16 | 57 | 0 | 300 | 320 | 387 | 31 | 38 | 30 | 5 | 163 | 22 | 0 | 82 | 20 | 0 | 16 | 165 | 0 | 89 | 98 | 10 | 2 | 34.07 | 11 | 6919.07 | 918 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 619 | 0 | 1366.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 44.99 | 164 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 4.12 | 5.5 | 173 | 58 | 0 | 11 | 0 | 0 | 0 | 4.4 | 109 | 0.57 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1100 | 0 | 6154.53 | 13073.6 | 87.61
15:00 | 0 | 33 | 8 | 250 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 54 | 0 | 96 | 93 | 0 | 0 | 55 | 35 | 18 | 0 | 300 | 292 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 21 | 108 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 70 | 0 | 2 | 40 | 15 | 3 | 342 | 0 | 0 | 0 | 0 | 15 | 214 | 0 | 0 | 0 | 1172 | 13 | 51 | 0 | 192 | 0 | 0 | 285 | 20 | 195 | 30 | 54 | 51 | 83 | 8 | 6 | 98 | 68 | 16 | 44 | 0 | 310 | 320 | 389 | 31 | 40 | 30 | 5 | 120 | 22 | 0 | 82 | 20 | 0 | 16 | 163 | 0 | 89 | 133 | 10 | 1 | 26.02 | 12 | 6961.02 | 918 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.15 | 622 | 0 | 1365.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 29.09 | 162 | 0 | 0 | 0 | 145 | 0 | 414 | 0 | 2.72 | 5.5 | 171 | 57 | 0 | 11 | 0 | 0 | 0 | 3.2 | 86 | 0.46 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1110 | 0 | 6065.99 | 13027.01 | 87.61
16:00 | 0 | 33 | 8 | 240 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 0 | 117 | 93 | 0 | 0 | 55 | 35 | 18 | 0 | 300 | 295 | 0 | 0 | 0 | 14 | 250 | 0 | 0 | 13 | 108 | 21 | 14 | 0 | 0 | 0 | 5 | 0 | 0 | 4 | 0 | 0 | 0 | 70 | 0 | 1 | 40 | 17 | 9 | 343 | 0 | 0 | 0 | 0 | 17 | 215 | 0 | 0 | 0 | 1192 | 8 | 51 | 0 | 189 | 0 | 0 | 285 | 24 | 204 | 27 | 68 | 50 | 85 | 33 | 11 | 114 | 64 | 16 | 27 | 0 | 305 | 320 | 389 | 31 | 40 | 28 | 5 | 163 | 22 | 0 | 83 | 20 | 0 | 16 | 163 | 0 | 80 | 143 | 0 | 1 | 15.17 | 12 | 6999.17 | 918 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.96 | 621 | 0 | 1360.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 18.46 | 160 | 0 | 0 | 0 | 143 | 0 | 414 | 0 | 1.74 | 5.5 | 171 | 56 | 0 | 7 | 0 | 0 | 0 | 1.8 | 49 | 0.49 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1120 | 0 | 5957.29 | 12956.46 | 87.6
17:00 | 8 | 34 | 8 | 241 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 11 | 17 | 0 | 105 | 93 | 45 | 4 | 55 | 35 | 24 | 5 | 300 | 258 | 0 | 0 | 17 | 14 | 250 | 0 | 0 | 5 | 108 | 21 | 21 | 0 | 0 | 8 | 45 | 1 | 0 | 2 | 0 | 0 | 12 | 70 | 12 | 0 | 40 | 17 | 17 | 342 | 17 | 0 | 0 | 5 | 17 | 214 | 0 | 0 | 0 | 1224 | 3 | 51 | 8 | 192 | 0 | 0 | 285 | 29 | 183 | 28 | 68 | 50 | 85 | 36 | 11 | 114 | 64 | 16 | 9 | 0 | 300 | 320 | 388 | 34 | 40 | 28 | 5 | 163 | 22 | 0 | 85 | 20 | 0 | 16 | 163 | 2 | 88 | 145 | 0 | 0 | 4.9 | 12 | 7152.9 | 917 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.63 | 620 | 0 | 1362.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 5.92 | 155 | 0 | 0 | 0 | 139 | 0 | 350 | 0 | 0.56 | 5.5 | 172 | 56 | 7 | 3 | 55 | 0 | 0 | 0.3 | 17 | 0.11 | 16 | 307 | 6 | 100 | 180 | 0 | 0 | 1130 | 17 | 5822.38 | 12975.28 | 87.6
18:00 | 32 | 50 | 18 | 241 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 34 | 0 | 125 | 124 | 145 | 25 | 55 | 72 | 33 | 16 | 300 | 242 | 0 | 0 | 35 | 25 | 250 | 0 | 0 | 0 | 125 | 21 | 21 | 0 | 0 | 17 | 95 | 12 | 0 | 0 | 34 | 10 | 17 | 85 | 12 | 0 | 40 | 18 | 25 | 340 | 17 | 0 | 0 | 8 | 22 | 216 | 0 | 0 | 0 | 1027 | 0 | 51 | 30 | 143 | 0 | 0 | 285 | 29 | 162 | 29 | 79 | 50 | 100 | 36 | 17 | 114 | 68 | 16 | 0 | 2 | 300 | 320 | 370 | 34 | 41 | 28 | 5 | 163 | 22 | 0 | 86 | 20 | 0 | 15 | 163 | 18 | 88 | 164 | 0 | 0 | 0.09 | 12 | 7398.09 | 918 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 504 | 0 | 1268.35 | 0 | 41 | 0 | 11 | 5 | 32 | 15 | 21 | 16 | 0 | 10 | 0 | 153 | 0 | 0 | 0 | 139 | 0 | 350 | 0 | 0.01 | 5.5 | 175 | 56 | 70 | 0 | 113 | 0 | 0 | 0 | 1 | 0 | 16 | 265 | 7 | 80 | 180 | 0 | 0 | 1040 | 17 | 5666.95 | 13065.04 | 87.59
19:00 | 0 | 50 | 25 | 241 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 54 | 0 | 143 | 108 | 95 | 0 | 55 | 72 | 30 | 29 | 320 | 287 | 0 | 0 | 55 | 25 | 270 | 0 | 0 | 0 | 125 | 23 | 21 | 0 | 0 | 17 | 95 | 34 | 0 | 0 | 51 | 24 | 0 | 100 | 12 | 0 | 40 | 50 | 24 | 341 | 0 | 0 | 8 | 8 | 74 | 222 | 0 | 0 | 0 | 1058 | 0 | 27 | 60 | 189 | 0 | 0 | 285 | 21 | 183 | 26 | 96 | 50 | 155 | 38 | 17 | 52 | 70 | 0 | 0 | 39 | 280 | 320 | 386 | 34 | 41 | 28 | 5 | 163 | 22 | 0 | 86 | 20 | 0 | 15 | 163 | 17 | 88 | 165 | 0 | 0 | 0 | 12 | 7740 | 871 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 1149.17 | 0 | 41 | 0 | 35 | 5 | 49 | 35 | 28 | 16 | 0 | 30 | 0 | 153 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 5.5 | 179 | 57 | 72 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 295 | 9 | 130 | 220 | 0 | 0 | 970 | 17 | 5767.67 | 13507.67 | 87.59
19:30 | 0 | 50 | 25 | 241 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 35 | 35 | 0 | 149 | 95 | 45 | 0 | 55 | 72 | 30 | 16 | 320 | 264 | 0 | 0 | 55 | 25 | 250 | 0 | 0 | 0 | 125 | 23 | 21 | 0 | 0 | 17 | 45 | 42 | 0 | 0 | 51 | 24 | 0 | 100 | 0 | 0 | 40 | 51 | 24 | 340 | 0 | 0 | 0 | 8 | 85 | 224 | 0 | 0 | 0 | 1140 | 0 | 51 | 20 | 189 | 0 | 0 | 285 | 29 | 182 | 26 | 96 | 50 | 155 | 38 | 11 | 52 | 70 | 0 | 0 | 39 | 265 | 320 | 385 | 34 | 41 | 28 | 5 | 163 | 22 | 0 | 86 | 30 | 0 | 15 | 163 | 0 | 88 | 165 | 23 | 0 | 0 | 12 | 7613 | 870 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 0 | 1199.74 | 0 | 41 | 0 | 35 | 5 | 42 | 35 | 34 | 16 | 0 | 30 | 0 | 155 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 0 | 5.5 | 175 | 57 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 0 | 1150 | 17 | 5982.24 | 13595.24 | 87.59
20:00 | 0 | 50 | 25 | 240 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 35 | 0 | 149 | 80 | 15 | 0 | 35 | 72 | 30 | 0 | 320 | 294 | 0 | 0 | 17 | 25 | 320 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 17 | 15 | 44 | 0 | 0 | 51 | 24 | 0 | 100 | 0 | 0 | 40 | 51 | 31 | 340 | 0 | 0 | 0 | 0 | 85 | 225 | 0 | 0 | 0 | 1224 | 0 | 51 | 20 | 195 | 0 | 0 | 285 | 29 | 183 | 27 | 96 | 50 | 100 | 37 | 11 | 52 | 62 | 0 | 0 | 39 | 275 | 320 | 386 | 35 | 41 | 28 | 5 | 163 | 22 | 0 | 86 | 30 | 0 | 15 | 163 | 0 | 88 | 165 | 22 | 0 | 0 | 12 | 7551 | 871 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 1263.33 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 16 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 145 | 0 | 414 | 0 | 0 | 5.5 | 174 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 0 | 1190 | 0 | 5889.83 | 13440.83 | 87.58
21:00 | 0 | 33 | 25 | 230 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 0 | 140 | 80 | 15 | 0 | 17 | 54 | 30 | 0 | 420 | 280 | 0 | 0 | 17 | 28 | 326 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 17 | 15 | 44 | 0 | 0 | 36 | 24 | 0 | 70 | 0 | 0 | 40 | 51 | 27 | 340 | 0 | 0 | 0 | 0 | 85 | 224 | 0 | 0 | 0 | 1224 | 0 | 51 | 15 | 195 | 0 | 0 | 285 | 29 | 183 | 30 | 93 | 50 | 100 | 37 | 17 | 52 | 72 | 0 | 0 | 39 | 280 | 320 | 387 | 35 | 42 | 28 | 5 | 163 | 22 | 0 | 83 | 30 | 0 | 16 | 164 | 0 | 88 | 166 | 23 | 0 | 0 | 12 | 7573 | 870 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 0 | 1381 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 0 | 5.5 | 176 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 0 | 1240 | 0 | 6055.5 | 13628.5 | 87.58
22:00 | 0 | 33 | 25 | 230 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 26 | 0 | 102 | 80 | 15 | 0 | 17 | 54 | 30 | 0 | 350 | 292 | 0 | 0 | 17 | 26 | 250 | 0 | 0 | 0 | 90 | 22 | 22 | 0 | 0 | 17 | 15 | 40 | 0 | 0 | 39 | 24 | 0 | 70 | 0 | 0 | 40 | 51 | 29 | 331 | 0 | 0 | 0 | 0 | 85 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 285 | 28 | 182 | 29 | 75 | 50 | 100 | 38 | 17 | 52 | 70 | 0 | 0 | 39 | 305 | 320 | 391 | 35 | 42 | 28 | 5 | 163 | 22 | 0 | 83 | 28 | 0 | 17 | 163 | 0 | 88 | 166 | 23 | 0 | 0 | 12 | 7302 | 917 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623 | 0 | 1362 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 5.5 | 180 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 0 | 1244 | 0 | 6099.5 | 13401.5 | 87.57
23:00 | 0 | 33 | 25 | 230 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 35 | 0 | 93 | 64 | 0 | 0 | 0 | 54 | 30 | 0 | 350 | 305 | 0 | 0 | 0 | 27 | 250 | 0 | 0 | 0 | 58 | 22 | 22 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 17 | 0 | 0 | 24 | 0 | 0 | 40 | 17 | 32 | 332 | 0 | 0 | 0 | 0 | 34 | 165 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 285 | 29 | 195 | 29 | 73 | 50 | 100 | 37 | 17 | 52 | 64 | 0 | 0 | 0 | 290 | 320 | 391 | 35 | 43 | 30 | 5 | 163 | 22 | 0 | 83 | 28 | 0 | 17 | 163 | 15 | 88 | 145 | 21 | 0 | 0 | 12 | 6892 | 918 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569 | 0 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 159 | 0 | 414 | 0 | 0 | 4 | 182 | 57 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 0 | 1244 | 0 | 5941 | 12833 | 87.57
Total KWH | 251856 | 828480 | 343680 | 4598100 | 0 | 0 | 0 | 0 | 8665200 | 0 | 0 | 324000 | 781200 | 0 | 2413008 | 2211360 | 461171 | 244855 | 511495 | 1424160 | 565560 | 65280 | 8063500 | 6931782 | 0 | 0 | 294456 | 557800 | 6618985 | 0 | 0 | 202795 | 1572000 | 470400 | 504000 | 0 | 0 | 109145 | 293564 | 241920 | 0 | 40320 | 229562 | 95664 | 38410 | 1008000 | 119040 | 23805 | 975180 | 332873 | 435360 | 8043636.36 | 28436 | 0 | 11040 | 28719 | 519382 | 4558995 | 0 | 0 | 0 | 25483634 | 133110 | 1017124 | 172290 | 4416000 | 0 | 0 | 6854000 | 659040 | 4584000 | 767592 | 981120 | 1200360 | 1373760 | 568680 | 302700 | 1069320 | 1413120 | 88973 | 471082 | 179008 | 7242000 | 7627300 | 8699000 | 772848 | 965000 | 711840 | 110640 | 3460664 | 522786 | 0 | 1788480 | 652800 | 0 | 383000 | 4401610 | 78480 | 1840800 | 2779200 | 235200 | 11900 | 270280 | 293760 | 160620675.36 | 21953454 | 4077504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 662400 | 13178180 | 0 | 28063636 | 0 | 75566 | 0 | 180480 | 10462 | 202752 | 67296 | 45986 | 68736 | 661880 | 44947 | 331496 | 3721818 | 0 | 0 | 0 | 3776073 | 0 | 9517818 | 0 | 27420 | 106668 | 4260000 | 1354909 | 261724 | 122612 | 633379 | 0 | 0 | 22650.12 | 893520 | 4534.5 | 45024 | 6589000 | 170438 | 2997000 | 5229360 | 0 | 0 | 25323636.36 | 60000 | 134742358.98 | 295363034.34