## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-03-2025 | [28 empty] | Date: | 14-03-2025 | [28 empty] | Date: | 14-03-2025 | [28 empty] | Date: | 14-03-2025 | [28 empty] | Date: | 14-03-2025 | [18 empty] | Date: | 14-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 130 | 0 | 0 | 373 | 0 | 0 | 0 | 54 | 0 | 132 | 115 | 0 | 0 | 55 | 54 | 20 | 25 | 450 | 250 | 0 | 0 | 17 | 27 | 330 | 0 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 26 | 30 | 13 | 0 | 20 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 74 | 29 | 320 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 60 | 16 | 0 | 180 | 285 | 29 | 186 | 34 | 41 | 50 | 200 | 31 | 11 | 114 | 70 | 0 | 0 | 39 | 300 | 320 | 287 | 34 | 43 | 30 | 5 | 0 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 78 | 155 | 20 | 0 | 0 | 8 | 7342 | 922 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 35 | 1367.72 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 157 | 0 | 350 | 0 | 0 | 5.5 | 178 | 57 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 10 | 100 | 220 | 0 | 0 | 1244 | 35 | 6054.22 | 13396.22 | 87.44
01:00 | 0 | 17 | 8 | 0 | 0 | 130 | 0 | 0 | 371 | 0 | 0 | 12 | 54 | 0 | 132 | 115 | 0 | 0 | 55 | 54 | 17 | 20 | 450 | 277 | 0 | 0 | 17 | 24 | 280 | 0 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 35 | 30 | 0 | 0 | 9 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 74 | 33 | 324 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1150 | 0 | 51 | 70 | 8 | 0 | 254 | 285 | 29 | 165 | 34 | 31 | 50 | 200 | 30 | 11 | 114 | 62 | 0 | 0 | 39 | 280 | 320 | 290 | 34 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 65 | 20 | 0 | 0 | 12 | 7142 | 924 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 35 | 1363.78 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 165 | 0 | 300 | 0 | 0 | 2.5 | 173 | 57 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 10 | 100 | 180 | 0 | 0 | 1120 | 35 | 5682.28 | 12824.28 | 87.44
02:00 | 0 | 17 | 8 | 0 | 0 | 130 | 0 | 0 | 367 | 0 | 0 | 17 | 54 | 0 | 132 | 110 | 0 | 0 | 55 | 54 | 17 | 16 | 300 | 276 | 0 | 0 | 17 | 24 | 250 | 0 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 35 | 30 | 0 | 0 | 34 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 76 | 34 | 322 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1150 | 0 | 51 | 70 | 8 | 0 | 253 | 285 | 29 | 141 | 34 | 17 | 50 | 200 | 28 | 11 | 114 | 68 | 0 | 0 | 39 | 275 | 320 | 290 | 34 | 42 | 30 | 5 | 0 | 6 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 68 | 57 | 21 | 0 | 0 | 12 | 6922 | 924 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 35 | 1361.68 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 167 | 0 | 300 | 0 | 0 | 2.5 | 177 | 59 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 10 | 100 | 180 | 0 | 0 | 1000 | 35 | 5580.18 | 12502.18 | 87.43
03:00 | 0 | 34 | 8 | 0 | 0 | 110 | 0 | 0 | 333 | 0 | 0 | 17 | 54 | 0 | 132 | 110 | 0 | 0 | 55 | 54 | 17 | 16 | 350 | 262 | 0 | 0 | 17 | 26 | 310 | 0 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 35 | 30 | 0 | 0 | 33 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 74 | 14 | 323 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 58 | 0 | 260 | 285 | 30 | 0 | 34 | 17 | 50 | 200 | 28 | 11 | 106 | 64 | 0 | 0 | 32 | 290 | 320 | 313 | 34 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 68 | 85 | 22 | 0 | 0 | 12 | 7009 | 924 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 35 | 1362.49 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 160 | 0 | 320 | 0 | 0 | 2.5 | 175 | 56 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 9 | 130 | 220 | 0 | 0 | 1000 | 35 | 5671.99 | 12680.99 | 87.43
04:00 | 0 | 34 | 8 | 0 | 0 | 110 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 0 | 132 | 110 | 0 | 0 | 0 | 54 | 17 | 0 | 420 | 260 | 0 | 0 | 0 | 26 | 330 | 0 | 0 | 0 | 108 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 35 | 20 | 322 | 0 | 0 | 0 | 8 | 51 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 157 | 0 | 220 | 285 | 30 | 0 | 34 | 42 | 50 | 200 | 29 | 11 | 37 | 60 | 0 | 0 | 0 | 280 | 320 | 350 | 35 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 135 | 22 | 0 | 0 | 12 | 6871 | 923 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 1362.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 2.5 | 175 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 130 | 220 | 0 | 0 | 1160 | 0 | 5734.62 | 12605.62 | 87.42
05:00 | 0 | 17 | 8 | 80 | 0 | 0 | 0 | c | 370 | 0 | 0 | 0 | 54 | 0 | 132 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 303 | 0 | 0 | 0 | 26 | 325 | 0 | 0 | 0 | 90 | 20 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 23 | 323 | 0 | 0 | 0 | 8 | 17 | 161 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 157 | 0 | 140 | 285 | 30 | 0 | 34 | 51 | 50 | 155 | 28 | 11 | 8 | 58 | 0 | 0 | 0 | 275 | 320 | 380 | 35 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 133 | 22 | 0 | 0 | 12 | 6353 | 923 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 1255.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 380 | 0 | 0 | 2.5 | 175 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 130 | 220 | 0 | 0 | 1120 | 0 | 5357.49 | 11710.49 | 87.42
06:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 255 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 90 | 20 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 23 | 323 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 972 | 0 | 51 | 0 | 157 | 0 | 260 | 285 | 30 | 0 | 31 | 34 | 50 | 120 | 28 | 11 | 0 | 56 | 0 | 0 | 0 | 280 | 320 | 350 | 35 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 65 | 22 | 0 | 0 | 12 | 5996 | 924 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1159.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 2.5 | 177 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 130 | 220 | 0 | 0 | 1050 | 0 | 5071.07 | 11067.07 | 87.41
07:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 298 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 1 | 52 | 26 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 26 | 323 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 905 | 2 | 51 | 0 | 175 | 0 | 70 | 285 | 31 | 0 | 31 | 17 | 50 | 68 | 21 | 11 | 0 | 62 | 0 | 6 | 0 | 300 | 320 | 350 | 35 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 163 | 0 | 78 | 69 | 23 | 0 | 2.45 | 12 | 5682.45 | 924 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 385 | 0 | 1062.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2.93 | 142 | 0 | 0 | 0 | 133 | 0 | 350 | 0 | 0.16 | 2.5 | 176 | 57 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 0.05 | 0 | 164 | 6 | 130 | 220 | 0 | 0 | 980 | 0 | 4991.46 | 10673.91 | 87.41
08:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 54 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 314 | 0 | 0 | 0 | 30 | 325 | 0 | 0 | 5 | 52 | 26 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 320 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 952 | 8 | 51 | 0 | 182 | 0 | 0 | 285 | 31 | 0 | 30 | 17 | 50 | 68 | 9 | 11 | 0 | 56 | 0 | 16 | 0 | 310 | 320 | 365 | 35 | 42 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 105 | 23 | 0 | 12.57 | 12 | 5813.57 | 869 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 386 | 0 | 1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 6.48 | 185 | 0 | 0 | 0 | 136 | 0 | 350 | 0 | 0.83 | 2.5 | 175 | 58 | 0 | 8 | 0 | 0 | 0 | 1.5 | 8 | 0.14 | 0 | 180 | 6 | 130 | 220 | 0 | 0 | 1000 | 0 | 5064.45 | 10878.02 | 87.4
09:00 | 0 | 50 | 17 | 110 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 17 | 0 | 79 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 305 | 0 | 0 | 0 | 30 | 323 | 0 | 0 | 8 | 35 | 22 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 27 | 323 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 967 | 13 | 51 | 0 | 182 | 0 | 0 | 285 | 32 | 0 | 30 | 17 | 50 | 34 | 9 | 11 | 0 | 46 | 0 | 29 | 0 | 315 | 320 | 387 | 35 | 43 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 105 | 16 | 1 | 22.45 | 12 | 5860.45 | 869 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.64 | 384 | 0 | 1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 20.61 | 201 | 0 | 0 | 0 | 173 | 0 | 350 | 0 | 3.07 | 2.5 | 177 | 57 | 0 | 12 | 0 | 0 | 0 | 3.6 | 45 | 0.23 | 0 | 243 | 6 | 130 | 220 | 0 | 0 | 1000 | 0 | 5294.65 | 11155.1 | 87.4
10:00 | 0 | 50 | 17 | 110 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 360 | 277 | 0 | 0 | 0 | 30 | 325 | 0 | 0 | 18 | 35 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 20 | 323 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 1100 | 17 | 51 | 0 | 182 | 0 | 0 | 285 | 33 | 0 | 32 | 17 | 50 | 34 | 9 | 11 | 0 | 50 | 0 | 45 | 0 | 300 | 320 | 344 | 32 | 43 | 30 | 5 | 0 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 0 | 78 | 105 | 32 | 2 | 25.94 | 12 | 5849.94 | 916 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.54 | 384 | 0 | 993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 38.64 | 205 | 0 | 0 | 0 | 189 | 0 | 350 | 0 | 4.09 | 5.5 | 177 | 58 | 0 | 21 | 0 | 0 | 0 | 4.9 | 32 | 0.47 | 0 | 250 | 6 | 130 | 180 | 0 | 0 | 1030 | 0 | 5372.14 | 11222.08 | 87.39
11:00 | 0 | 50 | 17 | 110 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 360 | 303 | 0 | 0 | 0 | 30 | 270 | 0 | 0 | 28 | 52 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 15 | 321 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 1100 | 19 | 51 | 0 | 187 | 0 | 0 | 285 | 38 | 0 | 32 | 50 | 50 | 34 | 14 | 11 | 0 | 62 | 0 | 52 | 0 | 310 | 320 | 384 | 35 | 40 | 30 | 5 | 0 | 22 | 0 | 85 | 20 | 0 | 17 | 164 | 0 | 78 | 105 | 32 | 2 | 42.46 | 12 | 5917.46 | 916 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.66 | 383 | 0 | 971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 44.77 | 170 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 5.02 | 5.5 | 173 | 58 | 0 | 26 | 0 | 0 | 0 | 6 | 57 | 0.55 | 0 | 250 | 6 | 130 | 220 | 0 | 0 | 1200 | 0 | 5614.5 | 11531.96 | 87.38
12:00 | 0 | 50 | 17 | 120 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 17 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 17 | 0 | 360 | 267 | 0 | 0 | 0 | 30 | 320 | 0 | 0 | 31 | 70 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 0 | 4 | 40 | 9 | 19 | 322 | 0 | 0 | 0 | 0 | 21 | 211 | 0 | 0 | 0 | 1204 | 19 | 51 | 10 | 187 | 0 | 40 | 285 | 39 | 0 | 28 | 51 | 50 | 57 | 9 | 11 | 34 | 68 | 0 | 54 | 0 | 290 | 320 | 350 | 32 | 41 | 30 | 5 | 0 | 22 | 0 | 85 | 25 | 0 | 17 | 165 | 0 | 78 | 116 | 48 | 2 | 24.26 | 12 | 6291.26 | 916 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.23 | 384 | 0 | 1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 54.16 | 170 | 0 | 0 | 0 | 201 | 0 | 414 | 0 | 5.19 | 5.5 | 172 | 58 | 0 | 31 | 0 | 0 | 0 | 6.4 | 117 | 0.59 | 0 | 250 | 6 | 130 | 220 | 0 | 0 | 1244 | 0 | 5886.07 | 12177.33 | 87.37
13:00 | 0 | 45 | 17 | 120 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 17 | 0 | 14 | 16 | 0 | 0 | 0 | 17 | 17 | 0 | 420 | 255 | 0 | 0 | 0 | 30 | 317 | 0 | 0 | 29 | 108 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 40 | 0 | 4 | 40 | 20 | 33 | 320 | 0 | 0 | 0 | 0 | 34 | 210 | 0 | 0 | 0 | 1178 | 18 | 51 | 20 | 185 | 0 | 90 | 285 | 38 | 138 | 31 | 50 | 50 | 68 | 8 | 11 | 34 | 72 | 0 | 62 | 0 | 290 | 320 | 350 | 32 | 40 | 30 | 5 | 0 | 22 | 0 | 85 | 28 | 0 | 17 | 165 | 0 | 85 | 143 | 44 | 2 | 36.82 | 12 | 6686.82 | 916 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.98 | 383 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 54.74 | 191 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 4.98 | 5.5 | 173 | 57 | 0 | 28 | 0 | 0 | 0 | 6 | 152 | 0.58 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1244 | 0 | 6087.78 | 12774.6 | 87.36
14:00 | 0 | 34 | 17 | 230 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 305 | 0 | 0 | 0 | 29 | 250 | 0 | 0 | 25 | 108 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 33 | 324 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 1092 | 17 | 51 | 20 | 185 | 0 | 0 | 285 | 38 | 43 | 31 | 64 | 50 | 68 | 9 | 11 | 34 | 60 | 0 | 48 | 0 | 295 | 320 | 393 | 32 | 41 | 30 | 5 | 0 | 22 | 0 | 85 | 30 | 0 | 17 | 164 | 0 | 88 | 143 | 46 | 2 | 23.33 | 12 | 6371.33 | 916 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.75 | 385 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 43.82 | 169 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 4.34 | 5.5 | 170 | 56 | 0 | 19 | 0 | 0 | 0 | 5.4 | 135 | 0.5 | 0 | 211 | 6 | 126 | 180 | 0 | 0 | 1120 | 0 | 5729.31 | 12100.64 | 87.35
15:00 | 0 | 17 | 8 | 256 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 89 | 32 | 0 | 0 | 0 | 20 | 17 | 0 | 350 | 302 | 0 | 0 | 0 | 23 | 280 | 0 | 0 | 20 | 108 | 16.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 48 | 0 | 2 | 40 | 0 | 2 | 323 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 1093 | 13 | 51 | 20 | 173 | 0 | 0 | 285 | 38 | 32 | 32 | 64 | 50 | 71 | 8 | 11 | 52 | 66 | 0 | 23 | 0 | 320 | 320 | 377 | 32 | 40 | 29 | 5 | 0 | 22 | 0 | 84 | 28 | 0 | 17 | 164 | 0 | 88 | 145 | 47 | 2 | 30.49 | 12 | 6442.99 | 916 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.94 | 380 | 0 | 1064.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 36.67 | 201 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 3.86 | 5.5 | 169 | 57 | 0 | 19 | 0 | 0 | 0 | 4.3 | 103 | 0.38 | 0 | 307 | 7 | 128 | 220 | 0 | 0 | 1180 | 0 | 5789.99 | 12232.98 | 87.34
16:00 | 0 | 17 | 8 | 260 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 16 | 17 | 0 | 115 | 55 | 0 | 0 | 13 | 35 | 17 | 0 | 350 | 307 | 0 | 0 | 17 | 23 | 280 | 0 | 0 | 13 | 108 | 22.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 48 | 0 | 1 | 40 | 17 | 24 | 323 | 0 | 0 | 0 | 0 | 32 | 210 | 0 | 0 | 0 | 1167 | 8 | 51 | 20 | 184 | 0 | 0 | 285 | 39 | 38 | 32 | 51 | 50 | 100 | 17 | 11 | 52 | 66 | 0 | 24 | 0 | 310 | 320 | 357 | 32 | 40 | 29 | 5 | 0 | 22 | 0 | 84 | 28 | 0 | 17 | 164 | 0 | 77 | 144 | 45 | 1 | 18.76 | 12 | 6694.26 | 916 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.69 | 380 | 0 | 1200.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 23.78 | 205 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 2.42 | 5.5 | 162 | 56 | 0 | 12 | 0 | 0 | 0 | 2.8 | 62 | 0.24 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1200 | 0 | 5834.05 | 12528.31 | 87.33
17:00 | 0 | 17 | 8 | 260 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 17 | 0 | 120 | 80 | 0 | 0 | 17 | 35 | 17 | 3 | 320 | 280 | 0 | 0 | 17 | 30 | 280 | 0 | 0 | 4 | 108 | 22 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 16 | 0 | 48 | 10 | 0 | 40 | 17 | 34 | 323 | 0 | 0 | 0 | 0 | 34 | 215 | 0 | 0 | 0 | 1209 | 2 | 51 | 20 | 184 | 0 | 0 | 285 | 40 | 61 | 32 | 51 | 50 | 100 | 36 | 11 | 52 | 66 | 0 | 5 | 0 | 305 | 320 | 350 | 32 | 40 | 30 | 5 | 0 | 22 | 0 | 84 | 28 | 0 | 17 | 164 | 17 | 93 | 155 | 42 | 0 | 5.95 | 12 | 6772.95 | 916 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.77 | 380 | 0 | 1266.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8.87 | 205 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 0.86 | 5.5 | 163 | 56 | 21 | 4 | 35 | 0 | 0 | 0.9 | 21 | 0.1 | 16 | 307 | 6 | 130 | 220 | 0 | 0 | 1200 | 7 | 5859.19 | 12632.14 | 87.32
18:00 | 0 | 20 | 8 | 260 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 17 | 0 | 120 | 80 | 15 | 0 | 17 | 35 | 17 | 16 | 320 | 308 | 0 | 0 | 17 | 24 | 280 | 0 | 0 | 0 | 108 | 22 | 14 | 0 | 0 | 0 | 15 | 12 | 0 | 4 | 17 | 16 | 0 | 72 | 35 | 0 | 40 | 17 | 35 | 324 | 0 | 0 | 0 | 0 | 35 | 216 | 0 | 0 | 0 | 1162 | 0 | 51 | 26 | 145 | 0 | 0 | 285 | 40 | 114 | 33 | 67 | 50 | 100 | 35 | 11 | 52 | 64 | 0 | 0 | 0 | 295 | 320 | 390 | 32 | 40 | 30 | 5 | 0 | 22 | 0 | 51 | 28 | 0 | 17 | 164 | 17 | 88 | 164 | 42 | 0 | 0.18 | 12 | 6875.18 | 916 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 381 | 0 | 1355.39 | 0 | 0 | 0 | 6 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 180 | 0 | 414 | 0 | 0.04 | 5.5 | 165 | 56 | 35 | 0 | 38 | 0 | 0 | 0 | 1 | 0 | 16 | 278 | 8 | 130 | 190 | 0 | 0 | 1200 | 17 | 5856.1 | 12731.28 | 87.31
19:00 | 0 | 40 | 17 | 260 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 28 | 0 | 120 | 112 | 30 | 0 | 34 | 108 | 17 | 40 | 320 | 273 | 0 | 0 | 17 | 30 | 250 | 0 | 0 | 0 | 108 | 20.8 | 14 | 0 | 0 | 2 | 65 | 12 | 0 | 11 | 34 | 18 | 0 | 88 | 70 | 0 | 40 | 20 | 34 | 321 | 0 | 0 | 0 | 0 | 61 | 215 | 0 | 0 | 0 | 1216 | 0 | 51 | 43 | 182 | 0 | 0 | 285 | 41 | 218 | 33 | 69 | 50 | 120 | 36 | 11 | 88 | 62 | 0 | 0 | 42 | 300 | 320 | 350 | 32 | 43 | 30 | 5 | 0 | 22 | 0 | 85 | 28 | 0 | 17 | 164 | 17 | 87 | 165 | 47 | 0 | 0 | 12 | 7549.8 | 878 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 9 | 1357.36 | 0 | 0 | 0 | 54 | 0 | 80 | 7 | 13 | 0 | 0 | 30 | 0 | 179 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 0 | 5.5 | 167 | 56 | 70 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 220 | 0 | 0 | 1180 | 54 | 6093.86 | 13643.66 | 87.3
19:30 | 0 | 51 | 17 | 260 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 54 | 35 | 0 | 88 | 95 | 0 | 0 | 35 | 72 | 17 | 32 | 320 | 276 | 0 | 0 | 35 | 30 | 250 | 0 | 0 | 0 | 100 | 22.5 | 14 | 0 | 0 | 35 | 30 | 12 | 0 | 15 | 45 | 48 | 0 | 72 | 30 | 0 | 40 | 51 | 34 | 323 | 0 | 0 | 0 | 0 | 68 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 75 | 182 | 0 | 0 | 285 | 42 | 183 | 33 | 69 | 50 | 155 | 36 | 18 | 88 | 66 | 0 | 0 | 39 | 295 | 320 | 350 | 32 | 43 | 30 | 5 | 0 | 22 | 0 | 85 | 28 | 0 | 17 | 164 | 17 | 65 | 165 | 52 | 0 | 0 | 12 | 7532.5 | 868 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 17 | 1359.96 | 0 | 16 | 0 | 35 | 0 | 80 | 0 | 13 | 0 | 0 | 30 | 0 | 204 | 0 | 0 | 0 | 198 | 0 | 414 | 0 | 0 | 5.5 | 169 | 56 | 35 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 220 | 0 | 0 | 1244 | 54 | 6127.46 | 13659.96
20:00 | 0 | 51 | 17 | 260 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 45 | 35 | 0 | 91 | 95 | 0 | 0 | 35 | 72 | 17 | 32 | 320 | 305 | 0 | 0 | 35 | 30 | 280 | 0 | 0 | 0 | 90 | 18 | 14 | 0 | 0 | 35 | 30 | 12 | 0 | 16 | 51 | 48 | 0 | 72 | 24 | 0 | 40 | 51 | 35 | 323 | 0 | 0 | 0 | 0 | 68 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 72 | 184 | 0 | 0 | 285 | 42 | 187 | 34 | 63 | 50 | 155 | 36 | 11 | 88 | 72 | 0 | 0 | 39 | 290 | 320 | 350 | 32 | 43 | 30 | 5 | 0 | 24 | 0 | 85 | 26 | 0 | 17 | 164 | 17 | 65 | 165 | 67 | 0 | 0 | 12 | 7577 | 868 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 27 | 1362.72 | 0 | 20 | 0 | 35 | 4 | 80 | 0 | 13 | 0 | 0 | 30 | 0 | 206 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 5.5 | 166 | 56 | 35 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 220 | 0 | 0 | 1244 | 17 | 6163.22 | 13740.22 | 87.29
21:00 | 0 | 51 | 17 | 260 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 35 | 0 | 88 | 95 | 0 | 0 | 35 | 72 | 17 | 32 | 320 | 310 | 0 | 0 | 35 | 30 | 280 | 0 | 0 | 0 | 90 | 19 | 14 | 0 | 0 | 35 | 30 | 12 | 0 | 17 | 51 | 48 | 0 | 72 | 24 | 0 | 40 | 51 | 35 | 323 | 0 | 0 | 0 | 3 | 68 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 185 | 0 | 0 | 285 | 43 | 201 | 34 | 36 | 50 | 155 | 37 | 11 | 88 | 72 | 0 | 0 | 39 | 310 | 320 | 381 | 32 | 43 | 30 | 5 | 0 | 24 | 0 | 85 | 28 | 0 | 17 | 164 | 17 | 65 | 165 | 82 | 0 | 0 | 12 | 7633 | 916 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 34 | 1368.31 | 0 | 21 | 0 | 35 | 4 | 80 | 0 | 28 | 0 | 0 | 30 | 0 | 206 | 0 | 0 | 0 | 198 | 0 | 414 | 0 | 0 | 5.5 | 165 | 56 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 220 | 0 | 0 | 1244 | 17 | 6269.81 | 13902.81 | 87.28
22:00 | 0 | 51 | 17 | 260 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 35 | 0 | 88 | 95 | 0 | 0 | 35 | 72 | 17 | 32 | 320 | 304 | 0 | 0 | 35 | 30 | 280 | 0 | 0 | 0 | 90 | 19 | 14 | 0 | 0 | 35 | 30 | 12 | 0 | 20 | 51 | 48 | 0 | 72 | 24 | 0 | 40 | 51 | 41 | 324 | 0 | 0 | 0 | 8 | 68 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 187 | 0 | 0 | 285 | 44 | 194 | 35 | 34 | 50 | 155 | 37 | 11 | 88 | 72 | 0 | 0 | 40 | 310 | 320 | 370 | 32 | 43 | 30 | 5 | 0 | 24 | 0 | 86 | 28 | 0 | 17 | 164 | 17 | 65 | 165 | 71 | 0 | 0 | 12 | 7617 | 915 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 35 | 1367.84 | 0 | 13 | 0 | 35 | 13 | 81 | 0 | 28 | 0 | 0 | 30 | 0 | 205 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 5.5 | 170 | 56 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 220 | 0 | 0 | 1244 | 17 | 6281.34 | 13898.34 | 87.27
23:00 | 0 | 51 | 17 | 140 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 35 | 0 | 88 | 95 | 0 | 0 | 35 | 72 | 17 | 32 | 320 | 308 | 0 | 0 | 17 | 31 | 280 | 0 | 0 | 0 | 90 | 19 | 15 | 0 | 0 | 35 | 30 | 7 | 0 | 10 | 51 | 48 | 0 | 72 | 24 | 0 | 40 | 51 | 41 | 318 | 0 | 0 | 0 | 8 | 68 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 187 | 0 | 0 | 285 | 44 | 196 | 35 | 34 | 50 | 155 | 37 | 11 | 88 | 72 | 0 | 0 | 40 | 300 | 320 | 357 | 32 | 43 | 30 | 5 | 0 | 24 | 0 | 86 | 0 | 0 | 17 | 164 | 17 | 65 | 165 | 74 | 0 | 0 | 12 | 7360 | 916 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 35 | 1356.75 | 0 | 17 | 0 | 35 | 23 | 81 | 0 | 28 | 0 | 0 | 18 | 0 | 205 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 0 | 5.5 | 169 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 220 | 0 | 0 | 1244 | 17 | 6274.25 | 13634.25 | 87.26
Total KWH | 0 | 808320 | 294720 | 3512500 | 0 | 582469 | 0 | 0 | 9270000 | 0 | 0 | 324000 | 839880 | 0 | 2127168 | 1433760 | 43909 | 0 | 502586 | 832320 | 380520 | 253440 | 8824500 | 6975942 | 0 | 0 | 277645 | 689400 | 7059539 | 0 | 0 | 180851 | 2138400 | 498000 | 290880 | 0 | 0 | 319909 | 348764 | 76800 | 0 | 281280 | 274488 | 263700 | 0 | 1251840 | 205440 | 20961 | 960060 | 729309 | 647520 | 7563636.36 | 0 | 0 | 0 | 73060.2 | 1003636 | 4490208 | 0 | 0 | 0 | 27245452 | 134730 | 1093312 | 945090 | 3680000 | 0 | 1738300 | 6926000 | 875040 | 1864000 | 788760 | 978240 | 1183190 | 2867040 | 576240 | 273310 | 1241460 | 1517760 | 0 | 359009 | 355792 | 7247000 | 7680900 | 8806000 | 796104 | 988000 | 681480 | 116400 | 0 | 435456 | 0 | 2012160 | 540192 | 0 | 408000 | 4395820 | 139680 | 1843200 | 3009600 | 879360 | 13150 | 251000 | 298320 | 161835907.56 | 22059636 | 6100704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495360 | 9309091 | 256800 | 29417854.45 | 0 | 69471 | 0 | 446880 | 45017 | 472032 | 9504 | 92597 | 43397 | 688850 | 143305 | 346496 | 4524727 | 0 | 0 | 0 | 4387636 | 0 | 9189963.6 | 0 | 32520 | 107352 | 4194000 | 1344872 | 271548 | 178771 | 767491 | 0 | 0 | 41288.52 | 745920 | 3834 | 213216 | 6546000 | 192977 | 2990000 | 5181360 | 0 | 0 | 27970909.09 | 279600 | 139160979.66 | 300996887.22

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-03-2025 | during | 15-03-2025 | during | 15-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 260 | 110 | 110 | 140.01 | 140.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 392 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 320 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 267 | 310 | 335 | 335 | 300 | 300 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 95 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 19 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 17 | 52.19 | 52.19 | 17 | 17 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 88 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 51 | 105 | 105 | 50 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 32 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1775 | 2238 | 5120.5 | 5184.5 | 3228.12 | 3292.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 3 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 215 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 21 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 48 | 64 | 74 | 64 | 74 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 72 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 19 | 35 | 2 | 30 | 2 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.91 | 0 | 3.91 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 9 | 51 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1204 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 17 | 3 | 3 | 3 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 322 | 323 | 320 | 320 | 330 | 330 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1880 | 2248 | 3139.63 | 3154.72 | 3149.63 | 3164.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 40 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 28 | 34 | 46.94 | 46.94 | 34 | 34 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 39 | 43 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 80 | 150 | 150 | 80 | 80 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 57 | 155 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 72 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 20.83 | 20.83 | 12 | 12 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 88 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 37 | 113 | 113 | 36 | 36 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 36 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 54 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 974 | 1367 | 2053.97 | 1988.97 | 1756.2 | 1691.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-03-2025 | during | 15-03-2025 | during | 15-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 48 | 82 | 210 | 210 | 48 | 48 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 165 | 200 | 200 | 165 | 165 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 65 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 24.26 | 0 | 45.5 | 0 | 45.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 280.26 | 341 | 649.2 | 601.5 | 452.2 | 404.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 41 | 43 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 32 | 32 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 25 | 28 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 164 | 162 | 162 | 162 | 162 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 381 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1382 | 1439 | 1481 | 1481 | 1412 | 1412
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 916 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 256 | 280 | 410 | 410 | 260 | 260 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73.23 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 384 | 380 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1629.23 | 1610 | 3604.2 | 3514.2 | 2167.02 | 2077.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 135 | 135 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1850.59 | 1944 | 2176.12 | 2176.12 | 2176.12 | 2176.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 21 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 4 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 28 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 206 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 201 | 198 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 90 | 90 | 90 | 90 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.19 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1069 | 1368.31 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.16 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2021.85 | 2389.81 | 3105.15 | 2938.53 | 2843.78 | 2677.16
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 56 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 172 | 165 | 170 | 170 | 170 | 170 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 80 | 80 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.1 | 0 | 6.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 117 | 0 | 151 | 0 | 151 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 384.4 | 326 | 674.1 | 492 | 607.12 | 425.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12177.33 | 13902.81 | 22003.87 | 21531.54 | 17792.19 | 17319.86
Forecast Scenario (15-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11990 |  | 0 |  | 11990
|  |  |  | 1:00 | 11420 |  | 0 |  | 11420
|  |  |  | 2:00 | 11080 |  | 0 |  | 11080
|  |  |  | 3:00 | 11390 |  | 0 |  | 11390
|  |  |  | 4:00 | 12080 |  | 0 |  | 12080
|  |  |  | 5:00 | 11080 |  | 0 |  | 11080
|  |  |  | 6:00 | 10360 |  | 0 |  | 10360
|  |  |  | 7:00 | 10540 |  | 0 |  | 10540
|  |  |  | 8:00 | 11240 |  | 0 |  | 11240
|  |  |  | 9:00 | 11960 |  | 0 |  | 11960
|  |  |  | 10:00 | 12260 |  | 0 |  | 12260
|  |  |  | 11:00 | 12740 |  | 0 |  | 12740
|  |  |  | 12:00 | 13070 |  | 0 |  | 13070
|  |  |  | 13:00 | 13480 |  | 0 |  | 13480
|  |  |  | 14:00 | 13730 |  | 0 |  | 13730
|  |  |  | 15:00 | 13680 |  | 0 |  | 13680
|  |  |  | 16:00 | 13540 |  | 0 |  | 13540
|  |  |  | 17:00 | 13880 |  | 0 |  | 13880
|  |  |  | 18:00 | 13850 |  | 0 |  | 13850
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14290 |  | 0 |  | 14290
|  |  |  | 19:30 | 14260 |  | 0 |  | 14260
|  |  |  | 20:00 | 14280 |  | 0 |  | 14280
|  |  |  | 21:00 | 14270 |  | 0 |  | 14270
|  |  |  | 22:00 | 13730 |  | 0 |  | 13730
|  |  |  | 23:00 | 13460 |  | 0 |  | 13460
Probable Maximum Temperature: |  |  | 34.60°C
Probable Maximum Demand at Day Peak: |  |  | 13070.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14290.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14290.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 303.40 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:45 hrs on 15-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12177.33 | MW | 12:00 Hr. | Energy Generated |  |  | 300.9969 |  | MKWHr.
| Day Peak Demand |  |  | 12272.33 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.263 |  | MKWHr.
| Evening Peak Generation |  |  | 13902.81 | MW | 21:00 Hr. | Energy Demand |  |  | 301.2599 |  | MKWHr.
| Evening Peak Demand |  |  | 13902.81 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 10673.91 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 973.8 |  | MMCFD
| Maximum Generation of the Day |  |  | 13902.81 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.2047 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.0838 | 0 | 9.8761 | 0 | 0 | 0.18085 | 0 | 0 | 48.1407 | Gas | 129.305 | Gas | 413870332.86
| Chattogram Zone |  |  | 5.1377 | 34.8091 | 4.5469 | 0 | 0.96006 | 0.15569 | 0 | 0.28128 | 45.8908 | Coal | 84.174 | Coal | 597390822.9455
| Cumilla Zone |  |  | 18.4219 | 0 | 6.9639 | 0 | 0 | 0.35901 | 1.5178 | 0 | 27.2625 | HFO | 29.7886 | HFO | 513078788.194
| Mymensingh Zone |  |  | 0.87936 | 0 | 5.2908 | 0 | 0 | 0.26415 | 0 | 0 | 6.4343 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.1075 | Hydro | 0.96006 | Hydro | 96006
| Khulna Zone |  |  | 6.1007 | 9.3091 | 0.2568 | 0 | 0 | 0.49536 | 22.0596 | 0 | 38.2216 | Solar | 3.4927 | Solar | 56051555.3572
| Barishal Zone |  |  | 8.3643 | 34.5169 | 0.49282 | 0 | 0 | 0.003834 | 0 | 0 | 43.3779 | Import | 52.9953 | Import | 283000470.75
| Rajshahi Zone |  |  | 18.2097 | 0 | 1.3222 | 0 | 0 | 1.0679 | 29.4179 | 0 | 50.0176 | Wind | 0.28128 | Wind | 4117939.2
| Rangpur Zone |  |  | 0 | 5.5389 | 1.039 | 0 | 0 | 0.96598 | 0 | 0 | 7.5439
| Total |  |  | 129.305 | 84.174 | 29.7886 | 0 | 0.96006 | 3.4927 | 52.9953 | 0.28128 | 300.9969
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 413870332.86 |  | Hydro | 96006
|  |  |  | Coal | 597390822.9455 |  | Solar | 56051555.3572
|  |  |  | HFO | 513078788.194 |  | Import | 283000470.75
|  |  |  | HSD | 0 |  | Wind | 4117939.2
[5 empty] | Total: | 186,76,05,915 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0596 | Peak Hr Flow | 916.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 13714745 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.4179 | Peak Hr Flow | 1368.31 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 824 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5178 | Peak Hr Flow | 72.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1014 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.9953 | Peak Hr Flow | 2356.31 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4825
|  |  |  | Chattogram |  | 0 |  | 1317
|  |  |  | Cumilla |  | 0 |  | 1348
|  |  |  | Mymensingh |  | 0 |  | 1154
|  |  |  | Sylhet |  | 0 |  | 495
|  |  |  | Khulna |  | 0 |  | 1729
|  |  |  | Barishal |  | 0 |  | 420
|  |  |  | Rajshahi |  | 0 |  | 1361
|  |  |  | Rangpur |  | 0 |  | 704
|  |  |  | Total |  | 0 |  | 13353
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) GT |  |  | 109
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 598.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1390.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:22 |  | Rampura 230/132kV S/S Auto Transformer - 02 LT Project Work S/D Due to To install interim
tx-2 on to proper pad permanently
|  | 08:22 | Bogura 132/33kV S/S Transformer-4 LT is restored.
|  | 08:22 | Bogura 132/33kV S/S Transformer-4 HT is restored.
| 09:00 |  | Chauddagram-Feni 132 kV Ckt-1 Project Work S/D from Chauddagram 132/33kV end Due to
Project work for feni grid
| 09:15 | 14:50 | Ishurdi 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to lup & clamp connector change & T03
connector join .
| 09:50 |  | Baghabari-Shahjadpur 132 kV Ckt-2 Scheduled S/D from Shahjadpur 132/33kV end Due to
Re-conducting
| 09:57 |  | Magura 33KV Bus Section-2 S/D.
|  | 10:42 | Bheramara(GK) 132/33kV S/S TR-2 HT is restored.
|  | 10:46 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT is restored.
| 10:48 | 11:43 | Bheramara(GK) 132/33kV S/S TR-2 LT Forced S/D Due to Replacement H-T lead of Aux.-1
(WZPDCL)
|  | 10:48 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT is restored.
| 10:49 | 11:42 | Bheramara(GK) 132/33kV S/S TR-2 HT Forced S/D Due to Replacement H-T lead of Aux.-1
(WZPDCL)
| 11:00 |  | Magura 33KV Bus Section-2 S/D Withdraw.
| 12:35 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 17:36 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 03:57 |  | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Tripped showing Distance Relay relays Due
to 21 Trip ZCOM Trip OC/EF START/TRIP Pole Discrepancy
| 05:40 | 06:36 | Rangpur-Saidpur 132kV Ckt-2 Tripped from Rangpur 132/33kV end showing no relays relays
Due to forced trip
| 05:40 | 06:36 | Rangpur-Saidpur 132kV Ckt-1 Tripped from Rangpur 132/33kV end showing no relays relays
Due to Froce trip ordered by ALDC
| 06:00 |  | Minimum Generation is 11195 MW
| 07:20 |  | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Project Work S/D from BIPTC end Due to Cradle
fixing... and from Jhenaidah 230/132kVend.
| 07:23 |  | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Project Work S/D from BIPTC end Due to Cradle
fixing. and from Jhenaidah 230/132kVend.
| 07:27 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 LT Forced S/D Due to Red hot remove
| 07:27 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT Forced S/D Due to Red hot remove
| 07:37 |  | Chandraghona-Kaptai 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual Maintenance
| 07:47 |  | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D Due to BY NLDC MANTAINENCE WORK
| 07:48 |  | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Scheduled S/D Due to Conductor armoring
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 582469 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 3512500 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9270000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8824500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 310 | 6975942 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7059539 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 95 | 1433760 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 502586 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 277645 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 498000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 290880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 380520 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 689400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 294720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 43909 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 2127168 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 808320 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 32 | 253440 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 832320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 180851 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 839880 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 2138400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2238 | 48140749
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 3 | 73060.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134730 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960060 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 4490208 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1003636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 48 | 263700 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 274488 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 72 | 1251840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 647520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 76800 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 348764 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 729309 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 205440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 319909 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27245452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 17 | 281280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 323 | 7563636.36 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2248 | 45890793.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 1864000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 1738300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6926000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 788760 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 43 | 875040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 3680000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1093312 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 945090 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 355792 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1183190 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 2867040 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1517760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 273310 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1241460 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 576240 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 978240 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 359009 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1367 | 27262543
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 82 | 879360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 165 | 3009600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 65 | 1843200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298320 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 139680 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 341 | 6434310
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 43 | 988000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 681480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 32 | 796104 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116400 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 28 | 540192 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2012160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 4395820 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 408000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 435456 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7247000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 8806000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7680900 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2368.568 | 1439 | 34107512
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 916 | 22059636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 280 | 6100704 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 256800 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 495360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 380 | 9309091 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1610 | 38221591
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 213216 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 192977 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 2990000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27970909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5181360 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 279600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6546000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3834 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1944 | 43377896.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 21 | 69471 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 4 | 45017 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 28 | 92597 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 206 | 4524727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 198 | 4387636 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9189963.6 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 143305 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 107352 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 43397 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 472032 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 446880 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 9504 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1368.31 | 29417854.45 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 346496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 688850 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2389.81 | 50017602.05
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1344872 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 4194000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 767491 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41288.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 271548 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 178771 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 745920 | -
Rangpur Area Total |  |  |  |  | 950 | 326 | 7543890.52
Eastern Grid Total |  |  |  |  | 16921.242 | 7633 | 161835907.56
Western Grid Total |  |  |  |  | 11614.5 | 6269.81 | 139160979.66
National Grid Total |  |  |  |  | 28535.742 | 13902.81 | 300996887.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9139.06 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4213.2 | MW
i) Dhaka area |  |  | 4824.66 |  | MW | i) Khulna area |  |  |  | 1728.6 | MW
ii) Chattogram area |  |  | 1317.4 |  | MW | ii) Barishal area |  |  |  | 420 | MW
iii) Cumilla area |  |  | 1348 |  | MW | iii) Rajshahi area |  |  |  | 1360.6 | MW
iv) Mymensingh area |  |  | 1154 |  | MW | iv) Rangpur area |  |  |  | 704 | MW
v) Sylhet area |  |  | 495 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13352.26 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 68 | 10:00 | 133 | Payra | 28 | 21:00
2 | AKSML | 14.2 | 17:00 | 68 | Jamalpur | 114 | 17:00 | 134 | Postogola | 47 | 00:00
3 | Aftabnagar | 34 | 18:30 | 69 | Jashore | 143 | 21:00 | 135 | Purbachal | 18 | 00:00
4 | Agargaon | 98 | 19:00 | 70 | Jhenaidah | 132 | 21:00 | 136 | Purbasadipur | 119 | 12:00
5 | Agrabad | 84 | 19:30 | 71 | Joydebpur | 127 | 00:00 | 137 | Rahanpur | 26 | 04:00
6 | Amnura | 40 | 19:30 | 72 | Joypurhat | 57 | 08:00 | 138 | Rahim | 26 | 16:00
7 | Ashuganj | 87 | 00:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 72 | 21:00
8 | BSRM | 200 | 00:00 | 74 | KSRM | 29 | 23:00 | 140 | Rajendrapur | 118 | 00:00
9 | Bagerhat | 83 | 21:00 | 75 | Kabirpur | 216 | 00:00 | 141 | Rajshahi | 104 | 04:00
10 | Bajitpur | 53 | 20:00 | 76 | Kachua | 81 | 19:00 | 142 | Rajshahi-230 | 76 | 21:00
11 | Bakulia | 86 | 00:00 | 77 | Kallyanpur | 102 | 18:30 | 143 | Ramganj | 120 | 18:30
12 | Banani | 22.6 | 19:30 | 78 | Kalurghat | 30 | 00:00 | 144 | Rampur | 39 | 00:00
13 | Bangabhaban | 4 | 10:00 | 79 | Kamrangirchar | 55.2 | 00:00 | 145 | Rangamati | 15 | 19:00
14 | Barapukuria | 55 | 10:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 120 | 18:00
15 | Barguna | 20 | 21:00 | 81 | Kazla | 92 | 19:30 | 147 | Ruppur | 7 | 10:00
16 | Barishal | 100 | 21:00 | 82 | Keranigonj | 74 | 00:00 | 148 | SSM | 13 | 04:00
17 | Barishal-230 | 90 | 19:00 | 83 | Khagrachori | 30 | 19:00 | 149 | Saidpur | 94 | 18:00
18 | Baroaulia | 58 | 08:00 | 84 | Khosba | 35 | 21:00 | 150 | Satkhira | 132 | 19:00
19 | Baroirhat | 53 | 21:00 | 85 | Khulna | 84 | 18:30 | 151 | Satmasjid | 93 | 20:00
20 | Bashundhara | 163 | 21:00 | 86 | Khulshi | 152 | 00:00 | 152 | Savar | 173 | 00:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 140 | 21:00 | 153 | SevenRings | 19.61 | 04:00
22 | Beanibazar | 54 | 21:00 | 88 | Kodda | 273 | 01:00 | 154 | ShahCement | 38 | 03:00
23 | Benapole | 66 | 22:00 | 89 | Kulaura | 38 | 18:30 | 155 | Shahjadpur | 76 | 20:00
24 | Bhaluka | 132 | 18:00 | 90 | Kurigram | 62 | 17:00 | 156 | Shahjibazar | 116 | 21:00
25 | Bhandaria | 50 | 21:00 | 91 | Kushtia | 134 | 21:00 | 157 | Shahmirpur | 51 | 00:00
26 | Bhangura | 38 | 03:00 | 92 | Lalbag | 63 | 12:00 | 158 | Shariatpur | 80 | 21:00
27 | Bheramara(GK) | 56 | 21:00 | 93 | Lalmonirhat | 48 | 18:00 | 159 | Sherpur | 148 | 13:00
28 | Bhulta | 259 | 00:00 | 94 | MI_Cement | 16.7 | 17:00 | 160 | Shikalbaha | 27 | 00:00
29 | Bog-Sherpur | 76 | 03:00 | 95 | Madanganj | 40 | 23:00 | 161 | Shitalakhya | 62.6 | 00:00
30 | Bogura | 147 | 04:00 | 96 | Madaripur | 105 | 21:00 | 162 | Sholosohor | 37 | 00:00
31 | Borhanuddin | 76 | 22:00 | 97 | Madartek | 81.82 | 22:00 | 163 | Shyampur | 162 | 00:00
32 | Brahmanbaria | 125 | 20:00 | 98 | Madunaghat | 49 | 21:00 | 164 | Siddhirganj | 110 | 00:00
33 | Cantonment | 114 | 19:00 | 99 | Magura | 63 | 19:00 | 165 | Sirajganj | 90 | 19:00
34 | Chandpur | 66 | 21:00 | 100 | Mahasthangarh | 62 | 20:00 | 166 | Sonargaon | 100 | 00:00
35 | Chandraghona | 30 | 19:00 | 101 | Manikganj | 136 | 21:00 | 167 | Sreemongol | 66 | 19:00
36 | Chapai | 67 | 03:00 | 102 | Maniknagar | 60 | 00:00 | 168 | Sreepur | 92 | 00:00
37 | Charsaidpur | 46 | 03:00 | 103 | Matarbari | 46 | 22:00 | 169 | Srinagar | 45 | 21:00
38 | Chauddagram | 70 | 21:00 | 104 | Matuail | 54 | 00:00 | 170 | Sunamganj | 48 | 21:00
39 | Chhatak | 28 | 22:00 | 105 | Millgate | 76 | 00:00 | 171 | Sylhet | 28 | 00:00
40 | Chowmuhani | 217 | 18:00 | 106 | Mirpur | 128 | 19:00 | 172 | Sylhet-132 | 103 | 21:00
41 | Chuadanga | 109 | 21:00 | 107 | Mirsorai | 10 | 00:00 | 173 | TK | 29 | 19:00
42 | Coxsbazar | 119 | 18:30 | 108 | Mirzapur | 45 | 19:00 | 174 | Tangail | 190 | 21:00
43 | Cumilla(N) | 166 | 19:30 | 109 | Mithapukur | 51 | 18:00 | 175 | Thakurgaon | 82 | 13:00
44 | Cumilla(S) | 158 | 00:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 121 | 10:00
45 | Daudkandi | 127 | 21:00 | 111 | Mogbazar | 117.7 | 19:30 | 177 | Ullahpara | 32 | 07:00
46 | Dhaka | 30 | 19:00 | 112 | Mongla | 32 | 19:00 | 178 | Ullon | 44 | 18:30
47 | Dhamrai | 110 | 00:00 | 113 | Motijheel | 32 | 20:00 | 179 | Uttara | 84 | 19:00
48 | Dhanmondi | 112 | 20:00 | 114 | Muktagacha | 36 | 18:00 | 180 | UttaraNew | 54 | 22:00
49 | Dohazari | 94 | 19:00 | 115 | Munshiganj | 103 | 21:00 | 181 | Zigatola | 70 | 19:00
50 | Faridpur | 150 | 21:00 | 116 | Muradnagar | 28 | 19:00
51 | Fatullah | 80 | 10:00 | 117 | Mymensingh | 197 | 19:00
52 | Fenchuganj | 30 | 18:30 | 118 | Naogaon | 115 | 04:00
53 | Feni | 107 | 21:00 | 119 | Narail | 56 | 19:00
54 | GPH | 21 | 21:00 | 120 | Narinda | 63.5 | 20:00
55 | Ghatail | 80 | 18:00 | 121 | Narshingdi | 166 | 00:00
56 | Ghorashal | 12 | 00:00 | 122 | Natore | 141 | 21:00
57 | Ghorashal-230 | 78 | 00:00 | 123 | Nawabganj | 56.6 | 21:00
58 | Goalpara | 32 | 00:00 | 124 | Netrakona | 131 | 16:00
59 | Gollamari | 60 | 20:00 | 125 | New | 72.4 | 00:00
60 | Gopalganj | 102.6 | 21:00 | 126 | Niamatpur | 93 | 15:00
61 | Gulshan | 84 | 19:00 | 127 | Noapara | 39.5 | 22:00
62 | Halishahar | 43 | 20:00 | 128 | PHP | 5 | 01:00
63 | HaripurSBU | 174 | 01:00 | 129 | Pabna | 103 | 19:00
64 | Hasnabad | 90 | 00:00 | 130 | Palashbari | 96 | 17:00
65 | Hathazari | 72 | 19:00 | 131 | Panchagarh | 45 | 17:00
66 | Ishurdi | 68 | 19:00 | 132 | Patuakhali | 70 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13396.22 | 0 |  | 13396.22
1:00 | 12824.28 | 0 |  | 12824.28
2:00 | 12502.18 | 0 |  | 12502.18
3:00 | 12680.99 | 0 |  | 12680.99
4:00 | 12605.62 | 0 |  | 12605.62
5:00 | 11710.49 | 0 |  | 11710.49
6:00 | 11067.07 | 0 |  | 11067.07
7:00 | 10673.91 | 0 |  | 10673.91
8:00 | 10878.02 | 0 |  | 10878.02
9:00 | 11155.1 | 55 |  | 11212.1
10:00 | 11222.08 | 64 |  | 11289.08
11:00 | 11531.96 | 53 |  | 11586.96
12:00 | 12177.33 | 91 |  | 12272.33
13:00 | 12774.6 | 0 |  | 12774.6
14:00 | 12100.64 | 0 |  | 12100.64
15:00 | 12232.98 | 0 |  | 12232.98
16:00 | 12528.31 | 0 |  | 12528.31
17:00 | 12632.14 | 0 |  | 12632.14
18:00 | 12731.28 | 0 |  | 12731.28
19:00 | 13643.66 | 0 |  | 13643.66
19:30 | 13659.96 | 0 |  | 13659.96
20:00 | 13740.22 | 0 |  | 13740.22
21:00 | 13902.81 | 0 |  | 13902.81
22:00 | 13898.34 | 0 |  | 13898.34
23:00 | 13634.25 | 0 |  | 13634.25
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7342 | 6054.22 | 13396.22 | DAILY GENERATION CURVE
00:30 | 7242 | 5868.25 | 13110.25
01:00 | 7142 | 5682.28 | 12824.28 | 14-03-2025
01:30 | 7032 | 5631.23 | 12663.23
02:00 | 6922 | 5580.18 | 12502.18
02:30 | 6965.5 | 5626.085 | 12591.585
03:00 | 7009 | 5671.99 | 12680.99
03:30 | 6940 | 5703.305 | 12643.305
04:00 | 6871 | 5734.62 | 12605.62
04:30 | 6612 | 5546.055 | 12158.055
05:00 | 6353 | 5357.49 | 11710.49
05:30 | 6174.5 | 5214.28 | 11388.78
06:00 | 5996 | 5071.07 | 11067.07
06:30 | 5839.225 | 5031.265 | 10870.49
07:00 | 5682.45 | 4991.46 | 10673.91
07:30 | 5748.01 | 5027.955 | 10775.965
08:00 | 5813.57 | 5064.45 | 10878.02
08:30 | 5837.01 | 5179.55 | 11016.56
09:00 | 5860.45 | 5294.65 | 11155.1
09:30 | 5855.195 | 5333.395 | 11188.59
10:00 | 5849.94 | 5372.14 | 11222.08
10:30 | 5883.7 | 5493.32 | 11377.02
11:00 | 5917.46 | 5614.5 | 11531.96
11:30 | 6104.36 | 5750.285 | 11854.645
12:00 | 6291.26 | 5886.07 | 12177.33
12:30 | 6489.04 | 5986.925 | 12475.965
13:00 | 6686.82 | 6087.78 | 12774.6
13:30 | 6529.075 | 5908.545 | 12437.62
14:00 | 6371.33 | 5729.31 | 12100.64
14:30 | 6407.16 | 5759.65 | 12166.81
15:00 | 6442.99 | 5789.99 | 12232.98
15:30 | 6568.625 | 5812.02 | 12380.645
16:00 | 6694.26 | 5834.05 | 12528.31
16:30 | 6733.605 | 5846.62 | 12580.225
17:00 | 6772.95 | 5859.19 | 12632.14
17:30 | 6824.065 | 5857.645 | 12681.71
18:00 | 6875.18 | 5856.1 | 12731.28
18:30 | 7212.49 | 5974.98 | 13187.47
19:00 | 7549.8 | 6093.86 | 13643.66
19:30 | 7532.5 | 6127.46 | 13659.96
20:00 | 7577 | 6163.22 | 13740.22
20:30 | 7605 | 6216.515 | 13821.515 |  | Executive Engineer
21:00 | 7633 | 6269.81 | 13902.81 |  | Network Operation Division
21:30 | 7625 | 6275.575 | 13900.575
22:00 | 7617 | 6281.34 | 13898.34
22:30 | 7488.5 | 6277.795 | 13766.295
23:00 | 7360 | 6274.25 | 13634.25

## En-Curve
QF-LDC-12
Date | 14-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3627 | 1596.5 | 922 | 0 | 70 | 1367.72 | 40 | 3715 | 0 | 304 | 1734 | 0 | 0 | 20 | 0 | DAILY ENERGY CURVE
00:30 | 3604 | 1573.5 | 923 | 0 | 66 | 1365.75 | 40 | 3614.5 | 0 | 295.5 | 1613.5 | 0 | 0 | 14.5 | 0 | 14-03-2025
01:00 | 3581 | 1550.5 | 924 | 0 | 62 | 1363.78 | 40 | 3514 | 0 | 287 | 1493 | 0 | 0 | 9 | 0
01:30 | 3563 | 1468 | 924 | 0 | 65 | 1362.73 | 40 | 3457 | 0 | 284.5 | 1477.5 | 0 | 0 | 21.5 | 0 | Energy Generated | 300.9969 |  | MKWHr
02:00 | 3545 | 1385.5 | 924 | 0 | 68 | 1361.68 | 40 | 3400 | 0 | 282 | 1462 | 0 | 0 | 34 | 0 | Energy not Served | 0.263 |  | MKWHr
02:30 | 3521 | 1452 | 924 | 0 | 66 | 1362.085 | 40 | 3435 | 0 | 287 | 1471 | 0 | 0 | 33.5 | 0 | Total Energy Requirement | 301.2599 |  | MKWHr
03:00 | 3497 | 1518.5 | 924 | 0 | 64 | 1362.49 | 40 | 3470 | 0 | 292 | 1480 | 0 | 0 | 33 | 0
03:30 | 3561 | 1594 | 923.5 | 0 | 62 | 1362.305 | 40 | 3550 | 0 | 276 | 1245.5 | 0 | 0 | 29 | 0
04:00 | 3625 | 1669.5 | 923 | 0 | 60 | 1362.12 | 40 | 3630 | 0 | 260 | 1011 | 0 | 0 | 25 | 0
04:30 | 3538.5 | 1691 | 923 | 0 | 59 | 1309.055 | 40 | 3497 | 0 | 203.5 | 867.5 | 0 | 0 | 29.5 | 0
05:00 | 3452 | 1712.5 | 923 | 0 | 58 | 1255.99 | 40 | 3364 | 0 | 147 | 724 | 0 | 0 | 34 | 0
05:30 | 3453.5 | 1690 | 923.5 | 0 | 57 | 1207.78 | 40 | 3237.5 | 0 | 131 | 624 | 0 | 0 | 24.5 | 0
06:00 | 3455 | 1667.5 | 924 | 0 | 56 | 1159.57 | 40 | 3111 | 0 | 115 | 524 | 0 | 0 | 15 | 0
06:30 | 3388 | 1714.5 | 924 | 0 | 59 | 1111.095 | 40 | 3050.5 | 13.895 | 96 | 458.5 | 0 | 0 | 15 | 0
07:00 | 3321 | 1761.5 | 924 | 0 | 62 | 1062.62 | 40 | 2990 | 27.79 | 77 | 393 | 0 | 0 | 15 | 0
07:30 | 3344.5 | 1778.5 | 896.5 | 0 | 59 | 1060.31 | 40 | 3030.5 | 62.655 | 85 | 408 | 0 | 0 | 11 | 0
08:00 | 3368 | 1795.5 | 869 | 0 | 56 | 1058 | 40 | 3071 | 97.52 | 93 | 423 | 0 | 0 | 7 | 0
08:30 | 3427 | 1792 | 869 | 0 | 51 | 1060 | 40 | 3111 | 169.56 | 105.5 | 387 | 0 | 0 | 4.5 | 27.5
09:00 | 3486 | 1788.5 | 869 | 0 | 46 | 1062 | 40 | 3151 | 241.6 | 118 | 351 | 0 | 0 | 2 | 55
09:30 | 3496.5 | 1716.5 | 892.5 | 0 | 48 | 1027.5 | 40 | 3236.5 | 298.09 | 118 | 311.5 | 0 | 0 | 3.5 | 59.5
10:00 | 3507 | 1644.5 | 916 | 0 | 50 | 993 | 40 | 3322 | 354.58 | 118 | 272 | 0 | 0 | 5 | 64
10:30 | 3477.5 | 1679.5 | 916 | 0 | 56 | 982 | 40 | 3403.5 | 402.52 | 126.5 | 291 | 0 | 0 | 2.5 | 58.5
11:00 | 3448 | 1714.5 | 916 | 0 | 62 | 971 | 40 | 3485 | 450.46 | 135 | 310 | 0 | 0 | 0 | 53
11:30 | 3530.5 | 1697.5 | 916 | 0 | 65 | 1020 | 40 | 3559.5 | 487.645 | 144 | 391 | 0 | 0 | 3.5 | 72
12:00 | 3613 | 1680.5 | 916 | 0 | 68 | 1069 | 40 | 3634 | 524.83 | 153 | 472 | 0 | 0 | 7 | 91
12:30 | 3721 | 1711 | 916 | 0 | 70 | 1115.5 | 40 | 3648 | 551.465 | 169.5 | 525.5 | 0 | 0 | 8 | 45.5
13:00 | 3829 | 1741.5 | 916 | 0 | 72 | 1162 | 40 | 3662 | 578.1 | 186 | 579 | 0 | 0 | 9 | 0
13:30 | 3762.5 | 1698.5 | 916 | 0 | 66 | 1162 | 40 | 3510 | 528.62 | 180.5 | 568 | 0 | 0 | 5.5 | 0
14:00 | 3696 | 1655.5 | 916 | 0 | 60 | 1162 | 40 | 3358 | 479.14 | 175 | 557 | 0 | 0 | 2 | 0
14:30 | 3726 | 1674.25 | 916 | 0 | 63 | 1113.17 | 40 | 3433.5 | 433.39 | 170 | 595.5 | 0 | 0 | 2 | 0
15:00 | 3756 | 1693 | 916 | 0 | 66 | 1064.34 | 40 | 3509 | 387.64 | 165 | 634 | 0 | 0 | 2 | 0
15:30 | 3754 | 1710 | 916 | 0 | 66 | 1132.48 | 40 | 3552 | 320.165 | 176.5 | 708.5 | 0 | 0 | 5 | 0
16:00 | 3752 | 1727 | 916 | 0 | 66 | 1200.62 | 40 | 3595 | 252.69 | 188 | 783 | 0 | 0 | 8 | 0
16:30 | 3748 | 1704.75 | 916 | 0 | 66 | 1233.405 | 40 | 3616.5 | 168.57 | 208.5 | 874 | 0 | 0 | 4.5 | 0
17:00 | 3744 | 1682.5 | 916 | 0 | 66 | 1266.19 | 40 | 3638 | 84.45 | 229 | 965 | 0 | 0 | 1 | 0
17:30 | 3768.5 | 1639 | 916 | 0 | 65 | 1310.79 | 40 | 3602 | 43.42 | 255.5 | 1039 | 0 | 0 | 2.5 | 0
18:00 | 3793 | 1595.5 | 916 | 0 | 64 | 1355.39 | 40 | 3566 | 2.39 | 282 | 1113 | 0 | 0 | 4 | 0
18:30 | 3818.5 | 1634.4 | 897 | 0 | 63 | 1356.375 | 40 | 3596.5 | 1.195 | 388 | 1385 | 0 | 0 | 7.5 | 0
19:00 | 3844 | 1673.3 | 878 | 0 | 62 | 1357.36 | 40 | 3627 | 0 | 494 | 1657 | 0 | 0 | 11 | 0
19:30 | 3839 | 1681 | 868 | 0 | 66 | 1359.96 | 40 | 3704 | 0 | 534 | 1553 | 0 | 0 | 15 | 0
20:00 | 3937 | 1698.5 | 868 | 0 | 72 | 1362.72 | 40 | 3700 | 0 | 538 | 1508 | 0 | 0 | 16 | 0
20:30 | 3979 | 1712.5 | 892 | 0 | 72 | 1365.515 | 40 | 3699.5 | 0 | 546 | 1498.5 | 0 | 0 | 16.5 | 0
21:00 | 4021 | 1726.5 | 916 | 0 | 72 | 1368.31 | 40 | 3699 | 0 | 554 | 1489 | 0 | 0 | 17 | 0
21:30 | 4009 | 1728.5 | 915.5 | 0 | 72 | 1368.075 | 40 | 3702.5 | 0 | 555.5 | 1491 | 0 | 0 | 18.5 | 0
22:00 | 3997 | 1730.5 | 915 | 0 | 72 | 1367.84 | 40 | 3706 | 0 | 557 | 1493 | 0 | 0 | 20 | 0
22:30 | 3909.5 | 1728.5 | 915.5 | 0 | 72 | 1362.295 | 40 | 3701.5 | 0 | 558 | 1464 | 0 | 0 | 15 | 0
23:00 | 3822 | 1726.5 | 916 | 0 | 72 | 1356.75 | 40 | 3697 | 0 | 559 | 1435 | 0 | 0 | 10 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 393 | 06:00 | 378 | 00:00 | Payra | 416 | 02:00 | 409 | 15:00
Ashuganj | 395 | 13:00 | 379 | 14:00 | Rahanpur | 411 | 06:00 | 400 | 18:00
Bhulta | 399 | 06:00 | 381 | 15:00 | Rampal | 406 | 06:00 | 388 | 21:00
Bibiana | 392 | 02:00 | 384 | 21:00
BIPTC | 398 | 09:00 | 391 | 00:00
Bogura | 401 | 06:00 | 387 | 18:00
Gopalganj | 402 | 06:00 | 388 | 22:00
Kaliakoir | 365 | 02:00 | 356 | 12:00
Madunaghat | 400 | 02:00 | 393 | 13:00
Meghnaghat | 392 | 06:00 | 380 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 220 | 15:00 | Keranigonj | 227 | 06:00 | 218 | 15:00
AKSML | 233 | 02:00 | 224 | 11:00 | Khulna(S) | 235 | 06:00 | 220 | 18:30
Aminbazar | 228 | 04:00 | 221 | 00:00 | Madunaghat | 233 | 01:00 | 227 | 14:00
Ashuganj | 230 | 05:00 | 223 | 11:00 | Madunaghat-400 | 234 | 02:00 | 228 | 00:00
Ashuganj-400 | 230 | 05:00 | 223 | 11:00 | Maniknagar | 223 | 04:00 | 216 | 15:00
Baghabari | 233 | 01:00 | 224 | 17:00 | Meghnaghat | 232 | 06:00 | 225 | 23:00
Barapukuria | 223 | 00:00 | 217 | 09:00 | Meghnaghat-400 | 227 | 06:00 | 220 | 15:00
Barapukuria-230 | 223 | 00:00 | 217 | 09:00 | Mirsorai | 229 | 03:00 | 221 | 11:00
Barishal | 236 | 02:00 | 229 | 20:00 | Rajshahi | 235 | 02:00 | 222 | 16:00
Bheramara | 235 | 02:00 | 223 | 16:00 | Rampal | 233 | 06:00 | 220 | 19:30
Bhulta | 225 | 06:00 | 216 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 03:00 | 220 | 13:00 | Rampura | 225 | 06:00 | 215 | 15:00
BIPTC | 236 | 02:00 | 222 | 18:00 | Shikalbaha | 233 | 03:00 | 224 | 11:00
Bogura | 232 | 06:00 | 224 | 18:00 | Shyampur | 226 | 06:00 | 218 | 15:00
Bogura-400 | 232 | 06:00 | 224 | 18:00 | Siddhirganj | 226 | 06:00 | 219 | 15:00
Borhanuddin | 242 | 07:00 | 233 | 11:00 | Sirajgonj | 239 | 06:00 | 233 | 12:00
BSRM | 231 | 02:00 | 221 | 11:00 | Sreepur | 232 | 06:00 | 223 | 18:00
Cumilla(N) | 223 | 04:00 | 218 | 11:00 | Tongi | 222 | 04:00 | 214 | 12:00
Faridpur | 232 | 06:00 | 224 | 19:30
Fenchuganj | 232 | 05:00 | 224 | 15:00
Ghorashal | 230 | 01:00 | 220 | 00:00
Ghorashal-230 | 226 | 06:00 | 216 | 15:00
Gopalganj | 232 | 06:00 | 224 | 19:30
GPH | 232 | 03:00 | 226 | 11:00
Haripur | 224 | 02:00 | 218 | 15:00
Hasnabad | 225 | 04:00 | 218 | 15:00
Hathazari | 232 | 01:00 | 226 | 14:00
Ishurdi | 236 | 02:00 | 224 | 19:30
Jhenaidah | 233 | 06:00 | 215 | 19:30
Kaliakoir | 227 | 02:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 126 | 14:00 | Madunaghat | 133 | 00:00 | 130 | 12:00
Agargaon | 137 | 06:00 | 130 | 15:00 | Magura | 133 | 07:00 | 122 | 19:00
Agrabad | 133 | 19:00 | 128 | 14:00 | Mahasthangarh | 131 | 00:00 | 125 | 16:00
AKS | 131 | 03:00 | 126 | 15:00 | Manikganj | 128 | 04:00 | 122 | 07:00
Aminbazar | 132 | 01:00 | 128 | 11:00 | Maniknagar | 132 | 06:00 | 127 | 00:00
Amnura | 136 | 05:00 | 128 | 17:00 | Matarbari | 122 | 06:00 | 116 | 17:00
Ashuganj | 134 | 01:00 | 130 | 11:00 | Matuail | 130 | 02:00 | 126.5 | 15:00
Bagerhat | 132 | 06:00 | 116 | 19:00 | Millgate | 133 | 02:00 | 127 | 11:00
Bajitpur | 130 | 04:00 | 122 | 12:00 | Mirpur | 132 | 02:00 | 127 | 11:00
Bakulia | 134 | 01:00 | 129 | 11:00 | Mirzapur | 128 | 00:00 | 122 | 18:00
Banani | 132 | 04:00 | 125 | 15:00 | Mithapukur | 133 | 00:00 | 123 | 09:00
Bangabhaban | 132 | 06:00 | 126 | 15:00 | MI_Cement | 130 | 02:00 | 126 | 00:00
Barapukuria | 138 | 06:00 | 130 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 06:00 | 132 | 13:00 | Mogbazar | 133 | 02:00 | 127 | 13:00
Barishal | 131 | 01:00 | 125 | 21:00 | Mongla | 133 | 06:00 | 120 | 19:00
Barishal-230 | 132 | 02:00 | 126 | 21:00 | Motijheel | 132 | 06:00 | 126 | 15:00
Baroaulia | 133 | 19:00 | 128 | 11:00 | Muktagacha | 133 | 04:00 | 125 | 09:00
Baroirhat | 125 | 01:00 | 118 | 13:00 | Munshiganj | 129 | 03:00 | 125 | 15:00
Bashundhara | 134 | 04:00 | 125 | 12:00 | Muradnagar | 126 | 02:00 | 121 | 14:00
BashundharaCement | 130 | 06:00 | 125 | 15:00 | Mymensingh | 134 | 21:00 | 114 | 11:00
Beanibazar | 131 | 01:00 | 127 | 18:30 | Naogaon | 129 | 06:00 | 123 | 09:00
Benapole | 130 | 05:00 | 118 | 19:00 | Narail | 134 | 06:00 | 121 | 20:00
Bhaluka | 127 | 05:00 | 119 | 11:00 | Narinda | 132 | 6:00 | 127 | 12:00
Bhandaria | 127 | 06:00 | 118 | 21:00 | Narshingdi | 128 | 05:00 | 114 | 00:00
Bhangura | 133 | 01:00 | 127 | 16:00 | Natore | 133 | 00:00 | 126 | 17:00
Bheramara | 136 | 02:00 | 129 | 19:30 | Nawabganj | 134 | 06:00 | 128 | 15:00
Bheramara(GK) | 137 | 06:00 | 128 | 19:30 | Netrakona | 124 | 01:00 | 110 | 18:00
Bhulta | 126 | 18:00 | 121 | 00:00 | New | 138 | 21:00 | 128 | 11:00
Bog-Sherpur | 131 | 06:00 | 124 | 18:00 | Niamatpur | 139 | 06:00 | 134 | 18:00
Bogura | 133 | 01:00 | 127 | 17:00 | Noapara | 132 | 01:00 | 122 | 19:00
Bogura-230 | 132 | 00:00 | 127 | 17:00 | Pabna | 138 | 03:00 | 127 | 19:30
Brahmanbaria | 126 | 07:00 | 121 | 00:00 | Palashbari | 129 | 06:00 | 121 | 09:00
Cantonment | 137 | 06:00 | 130 | 15:00 | Panchagarh | 139 | 19:00 | 116 | 09:00
Chandpur | 127 | 03:00 | 118 | 13:00 | Patuakhali | 135 | 18:30 | 132 | 07:00
Chandraghona | 134 | 02:00 | 130 | 11:00 | Payra | 137 | 02:00 | 134 | 13:00
Chapai | 137 | 06:00 | 132 | 00:00 | PHP | 125 | 02:00 | 115 | 13:00
Charsaidpur | 131 | 06:00 | 126 | 00:00 | Postogola | 132 | 02:00 | 128 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 125 | 01:00 | 119 | 15:00 | Purbachal | 133 | 06:00 | 125 | 15:00
Chhatak | 132 | 06:00 | 126 | 22:00 | Purbasadipur | 134 | 18:30 | 117 | 09:00
Chowmuhani | 118 | 01:00 | 113 | 21:00 | Rahanpur | 140 | 06:00 | 137 | 03:00
Chuadanga | 133 | 06:00 | 118 | 21:00 | Rahanpur-400 | 140 | 05:00 | 136 | 18:00
Coxsbazar | 121 | 05:00 | 117 | 00:00 | Rahim | 130 | 02:00 | 126 | 00:00
Cumilla(N) | 128 | 04:00 | 123 | 13:00 | Rajbari | 130 | 06:00 | 123 | 19:30
Cumilla(S) | 131 | 06:00 | 120 | 13:00 | Rajendrapur | 131 | 05:00 | 122 | 13:00
Daudkandi | 124 | 01:00 | 119 | 15:00 | Rajshahi | 134 | 05:00 | 127 | 17:00
Dhaka | 133 | 02:00 | 126 | 15:00 | Rajshahi-230 | 135 | 02:00 | 126 | 18:00
Dhamrai | 129 | 03:00 | 124 | 11:00 | Ramganj | 121 | 04:00 | 111 | 13:00
Dhanmondi | 134.5 | 06:00 | 120 | 22:00 | Rampur | 134 | 03:00 | 127 | 11:00
Dohazari | 129 | 03:00 | 125 | 11:00 | Rampura | 134 | 06:00 | 126 | 15:00
Faridpur | 130 | 06:00 | 125 | 21:00 | Rangamati | 133 | 02:00 | 128 | 11:00
Fatullah | 132 | 06:00 | 127 | 15:00 | Rangpur | 131 | 06:00 | 121 | 17:00
Fenchuganj | 133 | 03:00 | 130 | 19:30 | Ruppur | 138 | 05:00 | 130 | 19:30
Feni | 124 | 01:00 | 115 | 14:00 | Saidpur | 133 | 18:30 | 121 | 09:00
Ghatail | 129 | 00:00 | 121 | 18:00 | Satkhira | 133 | 06:00 | 117 | 19:00
Ghorashal | 135 | 01:00 | 130 | 12:00 | Satmasjid | 136 | 03:00 | 130 | 13:00
Goalpara | 135 | 06:00 | 122 | 19:00 | Savar | 133 | 02:00 | 125 | 11:00
Gollamari | 136 | 06:00 | 126 | 19:00 | SevenRings | 136 | 06:00 | 130 | 11:00
Gopalganj | 135 | 06:00 | 126 | 19:00 | ShahCement | 131 | 06:00 | 126 | 00:00
Gopalganj-400 | 137 | 06:00 | 131 | 19:30 | Shahjadpur | 136 | 04:00 | 131 | 17:00
Gulshan | 133 | 06:00 | 125 | 15:00 | Shahjibazar | 129 | 07:00 | 123 | 22:00
Halishahar | 134 | 19:00 | 128 | 11:00 | Shahmirpur | 135 | 18:00 | 131 | 10:00
Haripur | 130 | 02:00 | 126 | 15:00 | Shariatpur | 136 | 06:00 | 127 | 21:00
HaripurSBU | 130 | 02:00 | 126 | 00:00 | Sherpur | 136 | 00:00 | 125 | 10:00
Hasnabad | 132 | 03:00 | 128 | 15:00 | Shikalbaha | 125 | 03:00 | 119 | 11:00
Hathazari | 135 | 01:00 | 130 | 13:00 | Shikalbaha-230 | 137 | 19:00 | 130 | 12:00
Ishurdi | 138 | 02:00 | 131 | 18:00 | Shitalakhya | 130 | 02:00 | 126 | 15:00
Jaldhaka | 131 | 19:00 | 118 | 09:00 | Sholosohor | 134 | 02:00 | 129 | 11:00
Jamalpur | 139 | 00:00 | 128 | 03:00 | Shyampur | 132 | 18:00 | 125 | 00:00
Jashore | 132 | 06:00 | 119 | 18:30 | Shyampur-230 | 132 | 06:00 | 127 | 00:00
Jhenaidah | 135 | 04:00 | 123 | 18:30 | Siddhirganj | 130 | 03:00 | 126 | 15:00
Jhenaidah-230 | 135 | 06:00 | 123 | 19:30 | Sirajganj | 132 | 02:00 | 126 | 17:00
Joydebpur | 139 | 06:00 | 122 | 11:00 | Sonargaon | 129 | 06:00 | 124 | 15:00
Joypurhat | 127 | 06:00 | 120 | 09:00 | Sreemongol | 130 | 08:00 | 125 | 20:00
Juldah | 136 | 19:00 | 129 | 11:00 | Sreepur | 131 | 06:00 | 124 | 11:00
Kabirpur | 131 | 06:00 | 123 | 12:00 | Srinagar | 134 | 04:00 | 128 | 15:00
Kachua | 126 | 04:00 | 117 | 13:00 | SSM | 138 | 06:00 | 132 | 10:00
Kaliakoir | 132 | 04:00 | 126 | 12:00 | Sunamganj | 130 | 05:00 | 125 | 18:30
Kallyanpur | 132 | 01:00 | 127 | 14:00 | Sylhet | 132 | 05:00 | 127 | 18:00
Kalurghat | 135 | 02:00 | 129 | 13:00 | Sylhet-132 | 131 | 00:00 | 129 | 14:00
Kamrangirchar | 134 | 06:00 | 128 | 00:00 | Tangail | 126 | 00:00 | 120 | 18:00
Kaptai | 136 | 3:00 | 132 | 1:00 | Thakurgaon | 138 | 19:00 | 115 | 09:00
Kazla | 131 | 05:00 | 126 | 13:00 | TK | 135 | 02:00 | 131 | 11:00
Keranigonj | 135 | 06:00 | 129 | 15:00 | Tongi | 135 | 04:00 | 129 | 12:00
Khagrachori | 132 | 02:00 | 127 | 13:00 | Ullahpara | 133 | 03:00 | 127 | 18:00
Khosba | 125 | 02:00 | 121 | 13:00 | Ullon | 133 | 06:00 | 126 | 15:00
Khulna | 132 | 05:00 | 122 | 19:00 | Uttara | 132 | 06:00 | 125 | 15:00
Khulna(S) | 136 | 06:00 | 125 | 18:30 | UttaraNew | 133 | 02:00 | 126 | 15:00
Khulshi | 132 | 19:00 | 127 | 11:00 | Zigatola | 135 | 06:00 | 128 | 14:00
Kishoreganj | 127 | 05:00 | 120 | 11:00
Kodda | 131 | 05:00 | 123 | 12:00
KSRM | 134 | 19:00 | 129 | 11:00
Kulaura | 133 | 03:00 | 129 | 18:30
Kurigram | 132 | 18:30 | 119 | 09:00
Kushtia | 135 | 03:00 | 125 | 20:00
Lalbag | 135 | 06:00 | 129 | 00:00
Lalmonirhat | 130 | 00:00 | 122 | 17:00
Madanganj | 130 | 06:00 | 125 | 15:00
Madaripur | 135 | 06:00 | 129 | 18:30
Madartek | 133 | 06:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division