## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-03-2025 | during | 16-03-2025 | during | 16-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 140 | 160 | 260 | 260 | 140 | 140 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 405 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 290 | 275 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 325 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 25 | 8 | 0 | 8 | 0 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24.6 | 25 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 14 | 30 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 9 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 133 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 50 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 68 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 40 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 5 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2139.6 | 2742 | 5262.5 | 5240.5 | 3231.8 | 3209.8
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 13 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 214 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 10 | 87 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 63 | 64 | 74 | 64 | 74 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 48 | 98 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 15 | 2 | 32 | 2 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 27 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.92 | 0 | 3.92 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 190 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 9 | 70 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 61 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1173 | 1076 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 2 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 312 | 290 | 575 | 575 | 575 | 575 | U2 may be started
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1834 | 2407 | 3391.64 | 3410.72 | 3391.64 | 3410.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 184 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 103 | 200 | 200 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 35 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 36 | 44 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 23 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 23 | 132 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 39 | 38 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 155 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 50 | 70 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 16 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 70 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 37 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 63 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 50 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1185 | 1569 | 2238.97 | 2188.97 | 1898.03 | 1848.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-03-2025 | during | 16-03-2025 | during | 16-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 69 | 60 | 210 | 210 | 90 | 90 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 164 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 86 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.87 | 0 | 30 | 0 | 30 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 262.87 | 376.5 | 633.7 | 601.5 | 513.7 | 481.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 42 | 40 | 43 | 43 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 15 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 29 | 34 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 164 | 162 | 162 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 333 | 385 | 360 | 360 | 360 | 360 | cooling water temperature High due to IDCT Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1345 | 1448 | 1623 | 1623 | 1587 | 1587
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 918 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 25 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 40 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 361 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95.43 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 380 | 380 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1760.43 | 1664 | 3584.2 | 3512.2 | 2402.02 | 2330.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 67 | 396 | 495 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 64 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 124 | 130.1 | 130.1 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1220 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 90 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.67 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1883.67 | 2126 | 2568.22 | 2666.22 | 2177.12 | 2176.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 41 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 21 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 210 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 210 | 195 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 378 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 28 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.1 | 0 | 5.52 | 0 | 5.52 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1018.18 | 1356.92 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.41 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1958.19 | 2580.42 | 3105.05 | 2938.53 | 2843.68 | 2677.16
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 54 | 55 | 55 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 163 | 170 | 170 | 170 | 170 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 6.1 | 0 | 6.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 94 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 27 | 0 | 27 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 114 | 0 | 126 | 0 | 126 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 373 | 424 | 646.1 | 487 | 617.12 | 458.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12741.76 | 15336.92 | 23053.38 | 22668.64 | 18662.11 | 18178.37
Forecast Scenario (16-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13390 |  | 0 |  | 13390
|  |  |  | 1:00 | 12960 |  | 0 |  | 12960
|  |  |  | 2:00 | 12630 |  | 0 |  | 12630
|  |  |  | 3:00 | 12810 |  | 0 |  | 12810
|  |  |  | 4:00 | 13030 |  | 0 |  | 13030
|  |  |  | 5:00 | 12130 |  | 0 |  | 12130
|  |  |  | 6:00 | 11220 |  | 0 |  | 11220
|  |  |  | 7:00 | 11500 |  | 0 |  | 11500
|  |  |  | 8:00 | 12050 |  | 0 |  | 12050
|  |  |  | 9:00 | 12660 |  | 0 |  | 12660
|  |  |  | 10:00 | 13190 |  | 0 |  | 13190
|  |  |  | 11:00 | 13440 |  | 0 |  | 13440
|  |  |  | 12:00 | 13930 |  | 0 |  | 13930
|  |  |  | 13:00 | 14420 |  | 0 |  | 14420
|  |  |  | 14:00 | 14480 |  | 0 |  | 14480
|  |  |  | 15:00 | 14630 |  | 0 |  | 14630
|  |  |  | 16:00 | 14570 |  | 0 |  | 14570
|  |  |  | 17:00 | 14650 |  | 0 |  | 14650
|  |  |  | 18:00 | 14660 |  | 0 |  | 14660
|  |  |  | 18:30 | 14700 |  | 0 |  | 14700
|  |  |  | 19:00 | 14840 |  | 0 |  | 14840
|  |  |  | 19:30 | 15150 |  | 0 |  | 15150
|  |  |  | 20:00 | 15330 |  | 0 |  | 15330
|  |  |  | 21:00 | 15420 |  | 0 |  | 15420
|  |  |  | 22:00 | 15020 |  | 0 |  | 15020
|  |  |  | 23:00 | 14680 |  | 0 |  | 14680
Probable Maximum Temperature: |  |  | 35.60°C
Probable Maximum Demand at Day Peak: |  |  | 13930.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15420.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15420.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 327.64 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:27 hrs on 16-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12741.76 | MW | 12:00 Hr. | Energy Generated |  |  | 318.5733 |  | MKWHr.
| Day Peak Demand |  |  | 12741.76 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.46 |  | MKWHr.
| Evening Peak Generation |  |  | 15336.92 | MW | 21:00 Hr. | Energy Demand |  |  | 319.0333 |  | MKWHr.
| Evening Peak Demand |  |  | 15376.92 | MW | 21:00 Hr. | Maximum Temperature |  |  | 37.9 |  | °C
| Minimum Generation of the Day |  |  | 11195.75 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1008.4 |  | MMCFD
| Maximum Generation of the Day |  |  | 15336.92 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.665 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.4967 | 0 | 15.1942 | 0 | 0 | 0.2085 | 0 | 0 | 54.8994 | Gas | 133.6063 | Gas | 430660270.83
| Chattogram Zone |  |  | 5.122 | 34.3618 | 7.1222 | 0 | 0.96138 | 0.15438 | 0 | 0.08832 | 47.81 | Coal | 85.1097 | Coal | 601179938.2879
| Cumilla Zone |  |  | 20.603 | 0 | 9.0864 | 0 | 0 | 0.3404 | 1.4899 | 0 | 31.5197 | HFO | 41.8317 | HFO | 747562955.306
| Mymensingh Zone |  |  | 1.5408 | 0 | 5.1173 | 0 | 0 | 0.25015 | 0 | 0 | 6.9082 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.0106 | Hydro | 0.96138 | Hydro | 96138
| Khulna Zone |  |  | 7.5413 | 9.2945 | 0.78406 | 0 | 0 | 0.48816 | 22.082 | 0 | 40.1901 | Solar | 3.4737 | Solar | 55708957.7044
| Barishal Zone |  |  | 8.3739 | 35.9477 | 0.75835 | 0 | 0 | 0.002863 | 0 | 0 | 45.0828 | Import | 53.5023 | Import | 286779835.84
| Rajshahi Zone |  |  | 17.9181 | 0 | 2.3528 | 0 | 0 | 1.0802 | 29.9303 | 0 | 51.2814 | Wind | 0.08832 | Wind | 1293004.8
| Rangpur Zone |  |  | 0 | 5.5057 | 1.4164 | 0 | 0 | 0.94899 | 0 | 0 | 7.871
| Total |  |  | 133.6063 | 85.1097 | 41.8317 | 0 | 0.96138 | 3.4737 | 53.5023 | 0.08832 | 318.5733
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 430660270.83 |  | Hydro | 96138
|  |  |  | Coal | 601179938.2879 |  | Solar | 55708957.7044
|  |  |  | HFO | 747562955.306 |  | Import | 286779835.84
|  |  |  | HSD | 0 |  | Wind | 1293004.8
[5 empty] | Total: | 212,32,81,100 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.082 | Peak Hr Flow | 918.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 14210672.843 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.9303 | Peak Hr Flow | 1356.92 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 804 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4899 | Peak Hr Flow | 70.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1042 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.5023 | Peak Hr Flow | 2344.92 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 14 |  | 5384
|  |  |  | Chattogram |  | 0 |  | 1432
|  |  |  | Cumilla |  | 10 |  | 1430
|  |  |  | Mymensingh |  | 14 |  | 1247
|  |  |  | Sylhet |  | 0 |  | 549
|  |  |  | Khulna |  | 0 |  | 1829
|  |  |  | Barishal |  | 0 |  | 460
|  |  |  | Rajshahi |  | 0 |  | 1535
|  |  |  | Rangpur |  | 0 |  | 792
|  |  |  | Total |  | 38 |  | 14658
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1227.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:29 | 16:41 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D
| 08:30 | 16:40 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D
| 08:33 | 11:38 | Chandpur 132/33kV S/S 33 kV T-5 section Scheduled S/D Due to Maintenance | [7 empty] | 17.0MW load
interrup.
| 08:41 | 12:44 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to Maintenance
| 08:43 | 17:58 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D
| 08:44 | 17:58 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D
|  | 08:53 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 is restored.
|  | 09:54 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) is restored.
| 09:57 | 14:33 | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to Conductor
armoring
|  | 11:15 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT is restored.
|  | 11:18 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 LT is restored.
| 11:25 | 12:24 | Bheramara(GK) 132/33kV S/S TR-3 LT Forced S/D Due to 33kV Pbs feeder heatsink Problem | [7 empty] | 3.0MW load
interrup.
| 11:26 | 12:23 | Bheramara(GK) 132/33kV S/S TR-3 HT Forced S/D Due to 33kV Pbs feeder heatsink Problem | [7 empty] | 3.0MW load
interrup.
| 11:43 |  | Sirajganj Unit-1 ST tripped.
| 12:00 |  | Day Peak Gen. 12741 MW
| 12:05 | 12:30 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Oil sample collection | [7 empty] | 10.0MW load
interrup.
| 12:05 | 12:30 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Oil sample collection | [7 empty] | 10.0MW load
interrup.
| 12:05 | 12:30 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Oil sample collection | [7 empty] | 10.0MW load
interrup.
|  | 14:52 | Chandraghona-Kaptai 132 kV Ckt-1 is restored.
|  | 15:55 | Chauddagram-Feni 132 kV Ckt-2 is restored.
|  | 16:00 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 is restored.
|  | 16:01 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 is restored.
| 16:04 | 17:08 | Bheramara(GK) 132/33kV S/S TR-3 LT Forced S/D Due to 33kV Mirpur Feeder Heatsink Problem | [7 empty] | 3.0MW load
interrup.
| 16:05 | 17:07 | Bheramara(GK) 132/33kV S/S TR-3 HT Forced S/D Due to 33kV Mirpur Feeder Heatsink Problem | [7 empty] | 3.0MW load
interrup.
| 16:44 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
|  | 21:57 | Chandpur 132/33kV S/S 422T LT is restored.
| 21:58 |  | Chandpur 132/33kV S/S 412T LT Scheduled S/D Due to Heating Problem
| 00:40 | 00:51 | Sylhet 132/33kV S/S Sylhet-90MW P/S Tripped showing Distance Protection. relays Due to
Distance Protection.
| 01:25 | 01:34 | BSRM-Cumilla(N) 230 kV Ckt-1 Tripped from BSRM 230/33kV end showing distance relays Due
to trip
| 02:56 | 03:03 | Sylhet 132/33kV S/S T1 LT Tripped showing O/C and E/F. relays Due to O/C and E/F. | [7 empty] | 10.0MW load
interrup.
| 07:04 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U2
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 160 | 3405700 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9414000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10021000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 7056233 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 526175 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 331000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7737622 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 167904 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 1941600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 597130 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 303848 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 555600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 300600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 383.6 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 674600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 336960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 2851331 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3015216 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 836160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 531840 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1200960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208500 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 707040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1854000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2742 | 54899402.6
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 13 | 107344.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 129465 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 961380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 4620833 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1109854 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 63 | 353616 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 372626 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 98 | 1514880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 501120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 27 | 172800 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24918 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 190 | 1254545 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 10793 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1078073 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 813120 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 61 | 301091 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 33455 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1076 | 27212725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 88320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 290 | 7149090.91 | U2 S/D 8/Mar/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2407 | 47810049.71
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4593000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 103 | 596000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6930000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 822240 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1006560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4349091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 817696 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 1456945 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 723440 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1190280 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 2956800 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 70 | 1489920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52 | 674098 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 298090 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 1725960 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 579600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 63 | 969600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 340400 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1569 | 31519720
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 60 | 1540800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2913600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 86 | 1591200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 237000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293520 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 318960 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 376.5 | 6908230
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 962000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 674040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 15 | 111027 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 34 | 765360 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116544 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 275712 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1991040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 3400570 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 408000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 374784 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7238000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 8995000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7698500 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2368.568 | 1448 | 33010577
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 918 | 22082036 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 25 | 144480 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 40 | 283904 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 7541280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 355680 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 488160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 380 | 9294545 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1664 | 40190085
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 67 | 312000 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 291552 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 195797 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 124 | 3028000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 28632727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5150060 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 466800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7003000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2863 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2126 | 45082799.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 41 | 227372 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 21 | 89598 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 132325 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 210 | 4052182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 195 | 4623524 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9129745.5 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 28 | 151050 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 112662 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 6778 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 654224 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 98 | 743808 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 347616 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1356.92 | 29930299 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 363752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 682430 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2580.42 | 51281385.5
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1284654 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 4221000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 793478 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36755.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 622903 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 168478 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 743760 | -
Rangpur Area Total |  |  |  |  | 950 | 424 | 7871028.04
Eastern Grid Total |  |  |  |  | 16921.242 | 8542.5 | 174147979.31
Western Grid Total |  |  |  |  | 11614.5 | 6794.42 | 144425297.81
National Grid Total |  |  |  |  | 28535.742 | 15336.92 | 318573277.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10003.24 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4617.1 | MW
i) Dhaka area |  |  | 5369.74 |  | MW | i) Khulna area |  |  |  | 1829.2 | MW
ii) Chattogram area |  |  | 1432 |  | MW | ii) Barishal area |  |  |  | 460.5 | MW
iii) Cumilla area |  |  | 1419.5 |  | MW | iii) Rajshahi area |  |  |  | 1535.4 | MW
iv) Mymensingh area |  |  | 1233 |  | MW | iv) Rangpur area |  |  |  | 792 | MW
v) Sylhet area |  |  | 549 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14620.34 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 71 | 18:00 | 133 | Payra | 28 | 20:00
2 | AKSML | 16 | 14:00 | 68 | Jamalpur | 132 | 19:00 | 134 | Postogola | 53 | 19:30
3 | Aftabnagar | 36 | 19:00 | 69 | Jashore | 153 | 21:00 | 135 | Purbachal | 19 | 18:30
4 | Agargaon | 106 | 14:00 | 70 | Jhenaidah | 137 | 19:00 | 136 | Purbasadipur | 117 | 13:00
5 | Agrabad | 90 | 18:30 | 71 | Joydebpur | 146 | 16:00 | 137 | Rahanpur | 32 | 19:00
6 | Amnura | 42 | 22:00 | 72 | Joypurhat | 65 | 21:00 | 138 | Rahim | 24 | 16:00
7 | Ashuganj | 93.5 | 23:00 | 73 | Juldah | 14 | 00:00 | 139 | Rajbari | 80 | 21:00
8 | BSRM | 193 | 23:00 | 74 | KSRM | 24 | 14:00 | 140 | Rajendrapur | 130 | 16:00
9 | Bagerhat | 87 | 19:00 | 75 | Kabirpur | 254 | 18:00 | 141 | Rajshahi | 110 | 21:00
10 | Bajitpur | 48 | 01:00 | 76 | Kachua | 84 | 18:30 | 142 | Rajshahi-230 | 83 | 22:00
11 | Bakulia | 94 | 19:00 | 77 | Kallyanpur | 111 | 13:00 | 143 | Ramganj | 116 | 21:00
12 | Banani | 25.6 | 14:00 | 78 | Kalurghat | 40 | 11:00 | 144 | Rampur | 40 | 19:00
13 | Bangabhaban | 6 | 10:00 | 79 | Kamrangirchar | 55 | 19:00 | 145 | Rangamati | 17 | 19:00
14 | Barapukuria | 57 | 21:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 142 | 18:00
15 | Barguna | 20 | 21:00 | 81 | Kazla | 104 | 18:30 | 147 | Ruppur | 5 | 12:00
16 | Barishal | 111 | 19:00 | 82 | Keranigonj | 81 | 19:30 | 148 | SSM | 3 | 23:00
17 | Barishal-230 | 96 | 21:00 | 83 | Khagrachori | 34 | 18:30 | 149 | Saidpur | 113 | 17:00
18 | Baroaulia | 66 | 11:00 | 84 | Khosba | 37 | 21:00 | 150 | Satkhira | 137 | 19:00
19 | Baroirhat | 59 | 19:00 | 85 | Khulna | 89 | 18:30 | 151 | Satmasjid | 103 | 19:30
20 | Bashundhara | 177 | 21:00 | 86 | Khulshi | 167 | 19:30 | 152 | Savar | 233 | 15:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 136 | 14:00 | 153 | SevenRings | 18.87 | 17:00
22 | Beanibazar | 60 | 19:00 | 88 | Kodda | 298 | 19:00 | 154 | ShahCement | 39 | 19:30
23 | Benapole | 72 | 21:00 | 89 | Kulaura | 43 | 18:30 | 155 | Shahjadpur | 95 | 21:00
24 | Bhaluka | 156 | 16:00 | 90 | Kurigram | 62 | 17:00 | 156 | Shahjibazar | 126 | 21:00
25 | Bhandaria | 52 | 21:00 | 91 | Kushtia | 146 | 21:00 | 157 | Shahmirpur | 47 | 00:00
26 | Bhangura | 42 | 21:00 | 92 | Lalbag | 65 | 09:00 | 158 | Shariatpur | 80 | 19:00
27 | Bheramara(GK) | 61 | 22:00 | 93 | Lalmonirhat | 52 | 18:00 | 159 | Sherpur | 158 | 18:30
28 | Bhulta | 243 | 22:00 | 94 | MI_Cement | 17.6 | 13:00 | 160 | Shikalbaha | 21 | 19:00
29 | Bog-Sherpur | 80 | 21:00 | 95 | Madanganj | 41 | 16:00 | 161 | Shitalakhya | 81.8 | 16:00
30 | Bogura | 151 | 22:00 | 96 | Madaripur | 110 | 22:00 | 162 | Sholosohor | 43 | 15:00
31 | Borhanuddin | 80 | 21:00 | 97 | Madartek | 87.02 | 23:00 | 163 | Shyampur | 172 | 12:00
32 | Brahmanbaria | 128 | 18:00 | 98 | Madunaghat | 51 | 19:00 | 164 | Siddhirganj | 118 | 14:00
33 | Cantonment | 122 | 13:00 | 99 | Magura | 68 | 19:00 | 165 | Sirajganj | 114 | 19:30
34 | Chandpur | 68 | 21:00 | 100 | Mahasthangarh | 72 | 21:00 | 166 | Sonargaon | 102 | 20:00
35 | Chandraghona | 33 | 18:30 | 101 | Manikganj | 142 | 21:00 | 167 | Sreemongol | 74 | 18:30
36 | Chapai | 67 | 04:00 | 102 | Maniknagar | 66 | 14:00 | 168 | Sreepur | 105 | 12:00
37 | Charsaidpur | 42 | 01:00 | 103 | Matarbari | 48 | 21:00 | 169 | Srinagar | 46 | 20:00
38 | Chauddagram | 73 | 18:30 | 104 | Matuail | 70 | 15:00 | 170 | Sunamganj | 51 | 21:00
39 | Chhatak | 29 | 20:00 | 105 | Millgate | 86 | 14:00 | 171 | Sylhet | 29 | 21:00
40 | Chowmuhani | 219 | 22:00 | 106 | Mirpur | 140 | 12:00 | 172 | Sylhet-132 | 109 | 21:00
41 | Chuadanga | 116 | 22:00 | 107 | Mirsorai | 11 | 15:00 | 173 | TK | 31 | 21:00
42 | Coxsbazar | 129 | 19:00 | 108 | Mirzapur | 47 | 19:30 | 174 | Tangail | 198 | 18:00
43 | Cumilla(N) | 171 | 19:30 | 109 | Mithapukur | 58 | 17:00 | 175 | Thakurgaon | 91 | 19:00
44 | Cumilla(S) | 169 | 19:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 124 | 09:00
45 | Daudkandi | 152 | 20:00 | 111 | Mogbazar | 134.5 | 14:00 | 177 | Ullahpara | 33 | 19:00
46 | Dhaka | 46 | 12:00 | 112 | Mongla | 33 | 19:00 | 178 | Ullon | 47 | 20:00
47 | Dhamrai | 120 | 19:00 | 113 | Motijheel | 36 | 16:00 | 179 | Uttara | 89 | 19:00
48 | Dhanmondi | 129 | 13:00 | 114 | Muktagacha | 38 | 18:00 | 180 | UttaraNew | 57 | 21:00
49 | Dohazari | 104 | 21:00 | 115 | Munshiganj | 110 | 23:00 | 181 | Zigatola | 77 | 20:00
50 | Faridpur | 166 | 21:00 | 116 | Muradnagar | 29 | 21:00
51 | Fatullah | 95 | 09:00 | 117 | Mymensingh | 213 | 20:00
52 | Fenchuganj | 42 | 18:00 | 118 | Naogaon | 130 | 22:00
53 | Feni | 113 | 21:00 | 119 | Narail | 59 | 22:00
54 | GPH | 92 | 18:00 | 120 | Narinda | 84 | 13:00
55 | Ghatail | 88 | 20:00 | 121 | Narshingdi | 188 | 19:00
56 | Ghorashal | 14 | 09:00 | 122 | Natore | 157 | 21:00
57 | Ghorashal-230 | 88 | 23:00 | 123 | Nawabganj | 59.4 | 21:00
58 | Goalpara | 32 | 00:00 | 124 | Netrakona | 140 | 21:00
59 | Gollamari | 84 | 21:00 | 125 | New | 87.8 | 14:00
60 | Gopalganj | 108.2 | 21:00 | 126 | Niamatpur | 99 | 21:00
61 | Gulshan | 98 | 13:00 | 127 | Noapara | 48 | 19:00
62 | Halishahar | 71 | 15:00 | 128 | PHP | 5 | 01:00
63 | HaripurSBU | 173 | 15:00 | 129 | Pabna | 120 | 20:00
64 | Hasnabad | 95 | 16:00 | 130 | Palashbari | 108 | 19:00
65 | Hathazari | 74 | 19:00 | 131 | Panchagarh | 50 | 18:00
66 | Ishurdi | 77 | 21:00 | 132 | Patuakhali | 74.5 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13178.77 | 0 |  | 13178.77
1:00 | 12505.59 | 0 |  | 12505.59
2:00 | 12372.78 | 0 |  | 12372.78
3:00 | 12433.71 | 0 |  | 12433.71
4:00 | 12795.02 | 0 |  | 12795.02
5:00 | 11873.91 | 0 |  | 11873.91
6:00 | 11195.75 | 0 |  | 11195.75
7:00 | 11226.9 | 0 |  | 11226.9
8:00 | 11668.32 | 0 |  | 11668.32
9:00 | 11780.66 | 0 |  | 11780.66
10:00 | 11975.84 | 0 |  | 11975.84
11:00 | 12246.89 | 0 |  | 12246.89
12:00 | 12741.76 | 0 |  | 12741.76
13:00 | 13300.32 | 0 |  | 13300.32
14:00 | 13820.11 | 52 |  | 13874.11
15:00 | 13839.78 | 70 |  | 13912.78
16:00 | 13798.99 | 71 |  | 13872.99
17:00 | 13880.48 | 32 |  | 13913.48
18:00 | 14048.17 | 32 |  | 14081.17
19:00 | 15045 | 73 |  | 15121
19:30 | 14955.5 | 25 |  | 14981.5
20:00 | 15024.5 | 0 |  | 15024.5
21:00 | 15336.92 | 38 |  | 15376.92
22:00 | 15156.67 | 53 |  | 15211.67
23:00 | 14795.97 | 39 |  | 14836.97
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7073 | 6105.77 | 13178.77 | DAILY GENERATION CURVE
00:30 | 6932 | 5910.18 | 12842.18
01:00 | 6791 | 5714.59 | 12505.59 | 15-03-2025
01:30 | 6719.5 | 5719.685 | 12439.185
02:00 | 6648 | 5724.78 | 12372.78
02:30 | 6682.5 | 5720.745 | 12403.245
03:00 | 6717 | 5716.71 | 12433.71
03:30 | 6793 | 5821.365 | 12614.365
04:00 | 6869 | 5926.02 | 12795.02
04:30 | 6545.5 | 5788.965 | 12334.465
05:00 | 6222 | 5651.91 | 11873.91
05:30 | 6093 | 5441.83 | 11534.83
06:00 | 5964 | 5231.75 | 11195.75
06:30 | 5971.395 | 5239.93 | 11211.325
07:00 | 5978.79 | 5248.11 | 11226.9
07:30 | 6090.765 | 5356.845 | 11447.61
08:00 | 6202.74 | 5465.58 | 11668.32
08:30 | 6259.49 | 5465 | 11724.49
09:00 | 6316.24 | 5464.42 | 11780.66
09:30 | 6375.415 | 5502.835 | 11878.25
10:00 | 6434.59 | 5541.25 | 11975.84
10:30 | 6486.74 | 5624.625 | 12111.365
11:00 | 6538.89 | 5708 | 12246.89
11:30 | 6652.68 | 5841.645 | 12494.325
12:00 | 6766.47 | 5975.29 | 12741.76
12:30 | 7048.935 | 5972.105 | 13021.04
13:00 | 7331.4 | 5968.92 | 13300.32
13:30 | 7529.45 | 6030.765 | 13560.215
14:00 | 7727.5 | 6092.61 | 13820.11
14:30 | 7775.94 | 6054.005 | 13829.945
15:00 | 7824.38 | 6015.4 | 13839.78
15:30 | 7883.19 | 5936.195 | 13819.385
16:00 | 7942 | 5856.99 | 13798.99
16:30 | 7942.365 | 5897.37 | 13839.735
17:00 | 7942.73 | 5937.75 | 13880.48
17:30 | 7996.99 | 5967.335 | 13964.325
18:00 | 8051.25 | 5996.92 | 14048.17
18:30 | 8305.375 | 6241.21 | 14546.585
19:00 | 8559.5 | 6485.5 | 15045
19:30 | 8521 | 6434.5 | 14955.5
20:00 | 8534 | 6490.5 | 15024.5
20:30 | 8538.25 | 6642.46 | 15180.71 |  | Executive Engineer
21:00 | 8542.5 | 6794.42 | 15336.92 |  | Network Operation Division
21:30 | 8548 | 6698.795 | 15246.795
22:00 | 8553.5 | 6603.17 | 15156.67
22:30 | 8430 | 6546.32 | 14976.32
23:00 | 8306.5 | 6489.47 | 14795.97

## En-Curve
QF-LDC-12
Date | 15-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3783 | 1799 | 915 | 0 | 66 | 1352.77 | 40 | 3705 | 0 | 455 | 1058 | 0 | 0 | 5 | 0 | DAILY ENERGY CURVE
00:30 | 3791.5 | 1785.75 | 915.5 | 0 | 64 | 1360.93 | 40 | 3547 | 0 | 388.5 | 942.5 | 0 | 0 | 6.5 | 0 | 15-03-2025
01:00 | 3800 | 1772.5 | 916 | 0 | 62 | 1369.09 | 40 | 3389 | 0 | 322 | 827 | 0 | 0 | 8 | 0
01:30 | 3783.5 | 1726.5 | 915.5 | 0 | 64 | 1366.185 | 40 | 3386.5 | 0 | 322 | 827.5 | 0 | 0 | 7.5 | 0 | Energy Generated | 318.5733 |  | MKWHr
02:00 | 3767 | 1680.5 | 915 | 0 | 66 | 1363.28 | 40 | 3384 | 0 | 322 | 828 | 0 | 0 | 7 | 0 | Energy not Served | 0.46 |  | MKWHr
02:30 | 3712 | 1681.5 | 915.5 | 0 | 66 | 1363.245 | 40 | 3457.5 | 0 | 331.5 | 831.5 | 0 | 0 | 4.5 | 0 | Total Energy Requirement | 319.0333 |  | MKWHr
03:00 | 3657 | 1682.5 | 916 | 0 | 66 | 1363.21 | 40 | 3531 | 0 | 341 | 835 | 0 | 0 | 2 | 0
03:30 | 3772.5 | 1721 | 916 | 0 | 64 | 1364.865 | 40 | 3611 | 0 | 287.5 | 835.5 | 0 | 0 | 2 | 0
04:00 | 3888 | 1759.5 | 916 | 0 | 62 | 1366.52 | 40 | 3691 | 0 | 234 | 836 | 0 | 0 | 2 | 0
04:30 | 3806.5 | 1765 | 917 | 0 | 60 | 1314.465 | 40 | 3570 | 0 | 196.5 | 664 | 0 | 0 | 1 | 0
05:00 | 3725 | 1770.5 | 918 | 0 | 58 | 1262.41 | 40 | 3449 | 0 | 159 | 492 | 0 | 0 | 0 | 0
05:30 | 3652.5 | 1779 | 918 | 0 | 56 | 1191.33 | 40 | 3323.5 | 0 | 126 | 448.5 | 0 | 0 | 0 | 0
06:00 | 3580 | 1787.5 | 918 | 0 | 54 | 1120.25 | 40 | 3198 | 0 | 93 | 405 | 0 | 0 | 0 | 0
06:30 | 3611 | 1780.5 | 920 | 0 | 54 | 1119.98 | 40 | 3184.5 | 19.845 | 84 | 397 | 0 | 0 | 0.5 | 0
07:00 | 3642 | 1773.5 | 922 | 0 | 54 | 1119.71 | 40 | 3171 | 39.69 | 75 | 389 | 0 | 0 | 1 | 0
07:30 | 3725 | 1758.25 | 900 | 0 | 55 | 1116.745 | 40 | 3203.5 | 81.615 | 74.5 | 492.5 | 0 | 0 | 0.5 | 0
08:00 | 3808 | 1743 | 878 | 0 | 56 | 1113.78 | 40 | 3236 | 123.54 | 74 | 596 | 0 | 0 | 0 | 0
08:30 | 3841.5 | 1741.75 | 877.5 | 0 | 55 | 1069.7 | 40 | 3225 | 184.54 | 99.5 | 590 | 0 | 0 | 0 | 0
09:00 | 3875 | 1740.5 | 877 | 0 | 54 | 1025.62 | 40 | 3214 | 245.54 | 125 | 584 | 0 | 0 | 0 | 0
09:30 | 3936 | 1739 | 900 | 0 | 50 | 1021.865 | 40 | 3201.5 | 271.385 | 136.5 | 582 | 0 | 0 | 0 | 0
10:00 | 3997 | 1737.5 | 923 | 0 | 46 | 1018.11 | 40 | 3189 | 297.23 | 148 | 580 | 0 | 0 | 0 | 0
10:30 | 3943.5 | 1743 | 923.5 | 0 | 46 | 1016.775 | 40 | 3313.5 | 331.09 | 152 | 602 | 0 | 0 | 0 | 0
11:00 | 3890 | 1748.5 | 924 | 0 | 46 | 1015.44 | 40 | 3438 | 364.95 | 156 | 624 | 0 | 0 | 0 | 0
11:30 | 3879.5 | 1735.8 | 924 | 0 | 48 | 1016.81 | 40 | 3533 | 454.715 | 164 | 698.5 | 0 | 0 | 0 | 0
12:00 | 3869 | 1723.1 | 924 | 0 | 50 | 1018.18 | 40 | 3628 | 544.48 | 172 | 773 | 0 | 0 | 0 | 0
12:30 | 3832.5 | 1759.1 | 923.5 | 0 | 48 | 1053.715 | 40 | 3632.5 | 553.225 | 184.5 | 990 | 0 | 0 | 4 | 0
13:00 | 3796 | 1795.1 | 923 | 0 | 46 | 1089.25 | 40 | 3637 | 561.97 | 197 | 1207 | 0 | 0 | 8 | 0
13:30 | 3790.5 | 1785.05 | 923.5 | 0 | 58 | 1152.625 | 40 | 3646.5 | 546.04 | 194 | 1417 | 0 | 0 | 7 | 26
14:00 | 3785 | 1775 | 924 | 0 | 70 | 1216 | 40 | 3656 | 530.11 | 191 | 1627 | 0 | 0 | 6 | 52
14:30 | 3725.5 | 1777.25 | 924 | 0 | 68 | 1262.5 | 40 | 3682 | 469.195 | 211 | 1665 | 0 | 0 | 5.5 | 61
15:00 | 3666 | 1779.5 | 924 | 0 | 66 | 1309 | 40 | 3708 | 408.28 | 231 | 1703 | 0 | 0 | 5 | 70
15:30 | 3640 | 1781 | 924 | 0 | 66 | 1310 | 40 | 3689.5 | 337.885 | 256 | 1769 | 0 | 0 | 6 | 70.5
16:00 | 3614 | 1782.5 | 924 | 0 | 66 | 1311 | 40 | 3671 | 267.49 | 281 | 1835 | 0 | 0 | 7 | 71
16:30 | 3640 | 1786.5 | 924 | 0 | 65 | 1334.5 | 40 | 3659 | 182.735 | 301.5 | 1898.5 | 0 | 0 | 8 | 51.5
17:00 | 3666 | 1790.5 | 924 | 0 | 64 | 1358 | 40 | 3647 | 97.98 | 322 | 1962 | 0 | 0 | 9 | 32
17:30 | 3679 | 1718 | 924 | 0 | 64 | 1353 | 40 | 3567 | 50.325 | 394 | 2168.5 | 0 | 0 | 6.5 | 32
18:00 | 3692 | 1645.5 | 924 | 0 | 64 | 1348 | 40 | 3487 | 2.67 | 466 | 2375 | 0 | 0 | 4 | 32
18:30 | 3779.5 | 1698.75 | 898 | 0 | 69 | 1352.5 | 40 | 3555.5 | 1.335 | 579.5 | 2565.5 | 0 | 0 | 7 | 52.5
19:00 | 3867 | 1752 | 872 | 0 | 74 | 1357 | 40 | 3624 | 0 | 693 | 2756 | 0 | 0 | 10 | 73
19:30 | 3836 | 1804 | 872 | 0 | 72 | 1354 | 40 | 3661 | 0 | 712 | 2595.5 | 0 | 0 | 9 | 25
20:00 | 3903 | 1813 | 873 | 0 | 70 | 1358 | 40 | 3683 | 0 | 738 | 2537.5 | 0 | 0 | 9 | 0
20:30 | 3949.5 | 1816.75 | 895.5 | 0 | 70 | 1357.46 | 40 | 3632 | 0 | 746 | 2668 | 0 | 0 | 5.5 | 19
21:00 | 3996 | 1820.5 | 918 | 0 | 70 | 1356.92 | 40 | 3581 | 0 | 754 | 2798.5 | 0 | 0 | 2 | 38
21:30 | 3992 | 1806 | 919 | 0 | 71 | 1356.795 | 40 | 3607 | 0 | 752.5 | 2701.5 | 0 | 0 | 1 | 45.5
22:00 | 3988 | 1791.5 | 920 | 0 | 72 | 1356.67 | 40 | 3633 | 0 | 751 | 2604.5 | 0 | 0 | 0 | 53
22:30 | 4001.5 | 1785.5 | 920 | 0 | 74 | 1357.82 | 40 | 3677.5 | 0 | 744.5 | 2375.5 | 0 | 0 | 0 | 46
23:00 | 4015 | 1779.5 | 920 | 0 | 76 | 1358.97 | 40 | 3722 | 0 | 738 | 2146.5 | 0 | 0 | 0 | 39
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 06:00 | 374 | 11:00 | Payra | 415 | 07:00 | 407 | 13:00
Ashuganj | 395 | 13:00 | 380 | 14:00 | Rahanpur | 410 | 06:00 | 386 | 16:00
Bhulta | 395 | 18:00 | 377 | 14:00 | Rampal | 404 | 06:00 | 382 | 15:00
Bibiana | 391 | 04:00 | 384 | 16:00
BIPTC | 397 | 03:00 | 389 | 13:00
Bogura | 400 | 06:00 | 368 | 17:00
Gopalganj | 400 | 06:00 | 384 | 15:00
Kaliakoir | 366 | 03:00 | 355 | 12:00
Madunaghat | 400 | 19:00 | 392 | 12:00
Meghnaghat | 389 | 03:00 | 376 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 06:00 | 217 | 12:00 | Keranigonj | 225 | 03:00 | 216 | 15:00
AKSML | 233 | 03:00 | 225 | 12:00 | Khulna(S) | 232 | 06:00 | 211 | 16:00
Aminbazar | 226 | 05:00 | 219 | 11:00 | Madunaghat | 235 | 19:00 | 228 | 11:00
Ashuganj | 229 | 06:00 | 222 | 13:00 | Madunaghat-400 | 236 | 19:00 | 229 | 12:00
Ashuganj-400 | 229 | 06:00 | 222 | 13:00 | Maniknagar | 222 | 02:00 | 213 | 15:00
Baghabari | 233 | 05:00 | 224 | 15:00 | Meghnaghat | 230 | 06:00 | 222 | 16:00
Barapukuria | 224 | 21:00 | 217 | 08:00 | Meghnaghat-400 | 226 | 03:00 | 217 | 14:00
Barapukuria-230 | 224 | 21:00 | 217 | 08:00 | Mirsorai | 230 | 19:00 | 223 | 01:00
Barishal | 235 | 06:00 | 227 | 15:00 | Rajshahi | 234 | 03:00 | 221 | 15:00
Bheramara | 235 | 03:00 | 223 | 15:00 | Rampal | 232 | 06:00 | 213 | 15:00
Bhulta | 223 | 03:00 | 214 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 03:00 | 219 | 15:00 | Rampura | 222 | 03:00 | 213 | 12:00
BIPTC | 237 | 06:00 | 224 | 15:00 | Shikalbaha | 234 | 19:00 | 226 | 10:00
Bogura | 232 | 06:00 | 225 | 16:00 | Shyampur | 224 | 03:00 | 216 | 15:00
Bogura-400 | 232 | 06:00 | 225 | 17:00 | Siddhirganj | 224 | 18:30 | 216 | 12:00
Borhanuddin | 241 | 08:00 | 235 | 13:00 | Sirajgonj | 253 | 13:00 | 233 | 14:00
BSRM | 230 | 19:00 | 223 | 01:00 | Sreepur | 229 | 06:00 | 222 | 01:00
Cumilla(N) | 223 | 07:00 | 216 | 15:00 | Tongi | 222 | 04:00 | 212 | 11:00
Faridpur | 232 | 06:00 | 222 | 14:00
Fenchuganj | 228 | 04:00 | 222 | 21:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 224 | 03:00 | 216 | 12:00
Gopalganj | 231 | 06:00 | 221 | 15:00
GPH | 233 | 19:00 | 225 | 11:00
Haripur | 223 | 03:00 | 216 | 12:00
Hasnabad | 224 | 07:00 | 217 | 18:30
Hathazari | 236 | 22:00 | 218 | 14:00
Ishurdi | 236 | 03:00 | 225 | 15:00
Jhenaidah | 231 | 06:00 | 200 | 14:00
Kaliakoir | 228 | 03:00 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 02:00 | 123 | 12:00 | Madunaghat | 135 | 19:00 | 130 | 14:00
Agargaon | 136 | 03:00 | 129 | 12:00 | Magura | 133 | 06:00 | 110 | 15:00
Agrabad | 134 | 19:00 | 127 | 11:00 | Mahasthangarh | 131 | 06:00 | 124 | 17:00
AKS | 133 | 18:00 | 126 | 12:00 | Manikganj | 128 | 04:00 | 122 | 21:00
Aminbazar | 136 | 03:00 | 126 | 15:00 | Maniknagar | 131 | 06:00 | 124 | 15:00
Amnura | 136 | 00:00 | 125 | 16:00 | Matarbari | 123 | 07:00 | 116 | 00:00
Ashuganj | 135 | 18:30 | 130 | 13:00 | Matuail | 129 | 05:00 | 125 | 12:00
Bagerhat | 130 | 06:00 | 113 | 15:00 | Millgate | 133 | 02:00 | 126 | 11:00
Bajitpur | 131 | 04:00 | 122 | 13:00 | Mirpur | 131 | 02:00 | 125 | 15:00
Bakulia | 136 | 19:00 | 130 | 11:00 | Mirzapur | 128 | 06:00 | 121 | 18:00
Banani | 132 | 03:00 | 122 | 14:00 | Mithapukur | 132 | 21:00 | 123 | 10:00
Bangabhaban | 131 | 06:00 | 124 | 15:00 | MI_Cement | 130 | 03:00 | 124 | 11:00
Barapukuria | 139 | 21:00 | 131 | 11:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 22:00 | 131 | 15:00 | Mogbazar | 132 | 02:00 | 125 | 11:00
Barishal | 130 | 07:00 | 124 | 14:00 | Mongla | 129 | 06:00 | 115 | 15:00
Barishal-230 | 131 | 06:00 | 125 | 14:00 | Motijheel | 131 | 06:00 | 124 | 15:00
Baroaulia | 134 | 21:00 | 130 | 05:00 | Muktagacha | 135 | 06:00 | 123 | 18:00
Baroirhat | 125 | 08:00 | 117 | 15:00 | Munshiganj | 131 | 18:00 | 124 | 11:00
Bashundhara | 133 | 06:00 | 123 | 12:00 | Muradnagar | 125 | 03:00 | 120 | 14:00
BashundharaCement | 129 | 18:00 | 124 | 12:00 | Mymensingh | 134 | 14:00 | 112 | 22:00
Beanibazar | 130 | 03:00 | 126 | 14:00 | Naogaon | 128 | 05:00 | 120 | 16:00
Benapole | 128 | 06:00 | 110 | 15:00 | Narail | 133 | 06:00 | 112 | 15:00
Bhaluka | 123 | 00:00 | 118 | 13:00 | Narinda | 131 | 06:00 | 124 | 15:00
Bhandaria | 127 | 06:00 | 118 | 14:00 | Narshingdi | 129 | 18:00 | 115 | 00:00
Bhangura | 133 | 01:00 | 126 | 15:00 | Natore | 132 | 03:00 | 124 | 17:00
Bheramara | 137 | 05:00 | 128 | 15:00 | Nawabganj | 133 | 06:00 | 125 | 15:00
Bheramara(GK) | 137 | 06:00 | 128 | 15:00 | Netrakona | 120 | 06:00 | 109 | 22:00
Bhulta | 126 | 18:30 | 121 | 11:00 | New | 134 | 18:00 | 126 | 12:00
Bog-Sherpur | 130 | 06:00 | 124 | 15:00 | Niamatpur | 138 | 02:00 | 129 | 16:00
Bogura | 132 | 18:30 | 127 | 10:00 | Noapara | 130 | 05:00 | 115 | 14:00
Bogura-230 | 132 | 06:00 | 127 | 10:00 | Pabna | 135 | 06:00 | 127 | 15:00
Brahmanbaria | 127 | 08:00 | 121 | 14:00 | Palashbari | 129 | 21:00 | 118 | 17:00
Cantonment | 136 | 03:00 | 129 | 14:00 | Panchagarh | 140 | 21:00 | 120 | 10:00
Chandpur | 125 | 08:00 | 110 | 15:00 | Patuakhali | 137 | 18:00 | 131 | 08:00
Chandraghona | 135 | 19:00 | 129 | 12:00 | Payra | 136 | 06:00 | 133 | 14:00
Chapai | 136 | 02:00 | 126 | 18:30 | PHP | 125 | 09:00 | 116 | 15:00
Charsaidpur | 129 | 02:00 | 125 | 11:00 | Postogola | 134 | 18:00 | 127 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 125 | 08:00 | 118 | 14:00 | Purbachal | 131 | 02:00 | 122 | 13:00
Chhatak | 130 | 02:00 | 126 | 15:00 | Purbasadipur | 135 | 21:00 | 118 | 08:00
Chowmuhani | 120 | 10:00 | 111 | 15:00 | Rahanpur | 140 | 06:00 | 131 | 16:00
Chuadanga | 131 | 05:00 | 108 | 15:00 | Rahanpur-400 | 140 | 06:00 | 132 | 15:00
Coxsbazar | 122 | 07:00 | 118 | 00:00 | Rahim | 130 | 03:00 | 125 | 11:00
Cumilla(N) | 127 | 06:00 | 122 | 15:00 | Rajbari | 128 | 06:00 | 122 | 14:00
Cumilla(S) | 131 | 01:00 | 121 | 14:00 | Rajendrapur | 129 | 18:30 | 120 | 15:00
Daudkandi | 123 | 02:00 | 118 | 14:00 | Rajshahi | 135 | 06:00 | 126 | 16:00
Dhaka | 132 | 02:00 | 124 | 13:00 | Rajshahi-230 | 135 | 03:00 | 120 | 23:00
Dhamrai | 129 | 02:00 | 123 | 12:00 | Ramganj | 121 | 07:00 | 110 | 15:00
Dhanmondi | 132 | 06:00 | 124.4 | 14:00 | Rampur | 134 | 19:00 | 127 | 12:00
Dohazari | 131 | 19:00 | 125 | 12:00 | Rampura | 132 | 03:00 | 124 | 12:00
Faridpur | 130 | 06:00 | 125 | 01:00 | Rangamati | 133 | 19:00 | 129 | 11:00
Fatullah | 131 | 03:00 | 126 | 11:00 | Rangpur | 133 | 21:00 | 123 | 09:00
Fenchuganj | 132 | 04:00 | 129 | 16:00 | Ruppur | 137 | 05:00 | 130 | 15:00
Feni | 122 | 07:00 | 115 | 12:00 | Saidpur | 135 | 21:00 | 122 | 08:00
Ghatail | 129 | 05:00 | 117 | 18:00 | Satkhira | 128 | 03:00 | 114 | 14:00
Ghorashal | 133 | 01:00 | 130 | 11:00 | Satmasjid | 136 | 06:00 | 128 | 15:00
Goalpara | 133 | 06:00 | 119 | 14:00 | Savar | 131 | 03:00 | 124 | 15:00
Gollamari | 135 | 06:00 | 120 | 15:00 | SevenRings | 135 | 03:00 | 129 | 16:00
Gopalganj | 134 | 06:00 | 124 | 15:00 | ShahCement | 129 | 02:00 | 125 | 11:00
Gopalganj-400 | 136 | 06:00 | 129 | 15:00 | Shahjadpur | 142 | 10:00 | 130 | 14:00
Gulshan | 132 | 06:00 | 124 | 12:00 | Shahjibazar | 129 | 09:00 | 123 | 18:00
Halishahar | 135 | 19:00 | 128 | 11:00 | Shahmirpur | 137 | 19:00 | 129 | 11:00
Haripur | 130 | 03:00 | 126 | 11:00 | Shariatpur | 134 | 06:00 | 127 | 14:00
HaripurSBU | 130 | 03:00 | 126 | 11:00 | Sherpur | 135 | 04:00 | 126 | 18:30
Hasnabad | 130 | 01:00 | 127 | 15:00 | Shikalbaha | 125 | 18:00 | 119 | 11:00
Hathazari | 136 | 19:00 | 130 | 11:00 | Shikalbaha-230 | 137 | 19:00 | 131 | 11:00
Ishurdi | 138 | 03:00 | 130 | 15:00 | Shitalakhya | 130 | 03:00 | 124 | 11:00
Jaldhaka | 133 | 21:00 | 119 | 08:00 | Sholosohor | 135 | 19:00 | 130 | 11:00
Jamalpur | 136 | 04:00 | 127 | 18:00 | Shyampur | 131 | 02:00 | 126 | 14:00
Jashore | 131 | 06:00 | 111 | 15:00 | Shyampur-230 | 130 | 02:00 | 123 | 15:00
Jhenaidah | 134 | 06:00 | 113 | 15:00 | Siddhirganj | 130 | 03:00 | 125 | 12:00
Jhenaidah-230 | 134 | 06:00 | 113 | 15:00 | Sirajganj | 130 | 05:00 | 122 | 17:00
Joydebpur | 129 | 18:30 | 124 | 00:00 | Sonargaon | 128 | 07:00 | 123 | 17:00
Joypurhat | 127 | 05:00 | 118 | 10:00 | Sreemongol | 130 | 09:00 | 124 | 22:00
Juldah | 136 | 22:00 | 129 | 10:00 | Sreepur | 128 | 02:00 | 121 | 14:00
Kabirpur | 131 | 06:00 | 122 | 12:00 | Srinagar | 133 | 03:00 | 126 | 14:00
Kachua | 126 | 08:00 | 117 | 15:00 | SSM | 139 | 21:00 | 131 | 00:00
Kaliakoir | 133 | 02:00 | 126 | 11:00 | Sunamganj | 130 | 03:00 | 124 | 21:00
Kallyanpur | 133 | 02:00 | 126 | 15:00 | Sylhet | 130 | 04:00 | 127 | 14:00
Kalurghat | 136 | 19:30 | 130 | 11:00 | Sylhet-132 | 131 | 03:00 | 128 | 21:00
Kamrangirchar | 134 | 06:00 | 126 | 20:00 | Tangail | 128 | 05:00 | 118 | 18:00
Kaptai | 135 | 6:00 | 124 | 12:00 | Thakurgaon | 139 | 21:00 | 118 | 10:00
Kazla | 130 | 04:00 | 123 | 13:00 | TK | 136 | 19:00 | 130 | 11:00
Keranigonj | 134 | 06:00 | 126 | 16:00 | Tongi | 135 | 04:00 | 127 | 11:00
Khagrachori | 131 | 08:00 | 127 | 12:00 | Ullahpara | 131 | 05:00 | 124 | 17:00
Khosba | 124 | 02:00 | 120 | 14:00 | Ullon | 132 | 06:00 | 124 | 12:00
Khulna | 133 | 06:00 | 117 | 15:00 | Uttara | 132 | 03:00 | 125 | 11:00
Khulna(S) | 135 | 06:00 | 120 | 16:00 | UttaraNew | 132 | 02:00 | 125 | 15:00
Khulshi | 133 | 19:00 | 127 | 11:00 | Zigatola | 133 | 03:00 | 126 | 13:00
Kishoreganj | 126 | 09:00 | 120 | 13:00
Kodda | 129 | 01:00 | 122 | 15:00
KSRM | 135 | 18:00 | 129 | 11:00
Kulaura | 131 | 03:00 | 128 | 15:00
Kurigram | 132 | 21:00 | 118 | 13:00
Kushtia | 135 | 05:00 | 121 | 15:00
Lalbag | 134 | 06:00 | 121 | 21:00
Lalmonirhat | 130 | 22:00 | 120 | 08:00
Madanganj | 129 | 18:00 | 124 | 12:00
Madaripur | 134 | 06:00 | 128 | 15:00
Madartek | 132 | 03:00 | 123 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-03-2025 | [28 empty] | Date: | 15-03-2025 | [28 empty] | Date: | 15-03-2025 | [28 empty] | Date: | 15-03-2025 | [28 empty] | Date: | 15-03-2025 | [18 empty] | Date: | 15-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 140 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 35 | 0 | 88 | 110 | 0 | 0 | 17 | 54 | 17 | 16 | 420 | 282 | 0 | 0 | 35 | 31 | 330 | 0 | 0 | 0 | 90 | 20 | 15 | 0 | 0 | 17 | 15 | 3 | 0 | 5 | 20 | 48 | 0 | 72 | 12 | 0 | 40 | 51 | 40 | 320 | 0 | 0 | 0 | 8 | 17 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 187 | 0 | 0 | 285 | 44 | 184 | 35 | 23 | 50 | 155 | 28 | 11 | 88 | 66 | 0 | 0 | 40 | 300 | 320 | 349 | 32 | 41 | 30 | 5 | 0 | 24 | 0 | 86 | 0 | 0 | 17 | 164 | 0 | 65 | 58 | 73 | 0 | 0 | 12 | 7073 | 915 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 17 | 1352.77 | 0 | 0 | 0 | 35 | 5 | 80 | 0 | 0 | 0 | 0 | 20 | 0 | 206 | 0 | 0 | 0 | 186 | 0 | 414 | 0 | 0 | 4 | 171 | 57 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 130 | 220 | 0 | 0 | 1244 | 17 | 6105.77 | 13178.77 | 87.25
01:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 0 | 88 | 110 | 0 | 0 | 17 | 54 | 17 | 0 | 420 | 312 | 0 | 0 | 17 | 31 | 323 | 101 | 0 | 0 | 90 | 22 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 8 | 17 | 0 | 0 | 72 | 12 | 0 | 40 | 17 | 41 | 311 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1100 | 0 | 51 | 10 | 187 | 0 | 0 | 285 | 44 | 204 | 35 | 16 | 50 | 155 | 28 | 11 | 88 | 62 | 0 | 0 | 40 | 285 | 320 | 349 | 32 | 41 | 30 | 5 | 0 | 24 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 65 | 58 | 73 | 0 | 0 | 12 | 6791 | 916 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1369.09 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 167 | 0 | 350 | 0 | 0 | 2.5 | 170 | 56 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 130 | 180 | 0 | 0 | 1120 | 0 | 5714.59 | 12505.59 | 87.24
02:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 17 | 0 | 88 | 110 | 0 | 0 | 17 | 54 | 17 | 0 | 350 | 285 | 0 | 0 | 17 | 31 | 328 | 41 | 0 | 0 | 90 | 23 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 7 | 17 | 0 | 0 | 72 | 12 | 0 | 40 | 17 | 41 | 311 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1100 | 0 | 51 | 10 | 187 | 0 | 0 | 285 | 44 | 183 | 35 | 17 | 50 | 155 | 28 | 11 | 88 | 66 | 0 | 0 | 40 | 290 | 320 | 349 | 32 | 41 | 30 | 5 | 0 | 24 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 65 | 58 | 73 | 0 | 0 | 12 | 6648 | 915 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 1363.28 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 179 | 0 | 350 | 0 | 0 | 2.5 | 176 | 56 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 130 | 180 | 0 | 0 | 1110 | 0 | 5724.78 | 12372.78 | 87.23
03:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 91 | 129 | 0 | 0 | 17 | 54 | 17 | 0 | 350 | 282 | 0 | 0 | 17 | 31 | 300 | 40 | 0 | 0 | 90 | 23 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 17 | 0 | 0 | 72 | 12 | 0 | 40 | 17 | 41 | 312 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1178 | 0 | 51 | 10 | 187 | 0 | 0 | 285 | 45 | 184 | 35 | 17 | 50 | 155 | 28 | 11 | 88 | 66 | 0 | 0 | 40 | 295 | 320 | 349 | 32 | 41 | 30 | 5 | 0 | 24 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 65 | 62 | 84 | 0 | 0 | 12 | 6717 | 916 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 1363.21 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 154 | 0 | 320 | 0 | 0 | 2.5 | 177 | 56 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 130 | 180 | 0 | 0 | 1120 | 0 | 5716.71 | 12433.71 | 87.22
04:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 17 | 0 | 107 | 129 | 0 | 0 | 17 | 54 | 17 | 0 | 420 | 270 | 0 | 0 | 0 | 31 | 327 | 101 | 0 | 0 | 80 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 72 | 0 | 0 | 40 | 17 | 41 | 314 | 0 | 0 | 0 | 0 | 17 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 187 | 0 | 0 | 285 | 44 | 184 | 35 | 44 | 50 | 155 | 28 | 11 | 52 | 62 | 0 | 0 | 0 | 290 | 320 | 350 | 32 | 41 | 30 | 5 | 0 | 8 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 65 | 135 | 85 | 0 | 0 | 12 | 6869 | 916 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1366.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 0 | 2.5 | 176 | 56 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 0 | 1232 | 0 | 5926.02 | 12795.02 | 87.21
05:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 68 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 288 | 0 | 0 | 0 | 31 | 328 | 0 | 0 | 0 | 52 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 40 | 312 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 187 | 0 | 0 | 285 | 41 | 183 | 35 | 50 | 50 | 85 | 27 | 11 | 52 | 58 | 0 | 0 | 0 | 295 | 320 | 300 | 32 | 41 | 30 | 5 | 0 | 0 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 45 | 105 | 92 | 0 | 0 | 12 | 6222 | 918 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1262.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 2.5 | 178 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 9 | 100 | 220 | 0 | 0 | 1160 | 0 | 5651.91 | 11873.91 | 87.2
06:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 62 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 302 | 0 | 0 | 0 | 31 | 328 | 0 | 0 | 0 | 52 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 306 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 187 | 0 | 0 | 285 | 42 | 183 | 35 | 34 | 50 | 85 | 28 | 11 | 34 | 54 | 0 | 0 | 0 | 295 | 320 | 290 | 32 | 41 | 30 | 5 | 0 | 0 | 0 | 86 | 0 | 0 | 17 | 164 | 0 | 45 | 105 | 95 | 0 | 0 | 12 | 5964 | 918 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1120.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 133 | 0 | 314 | 0 | 0 | 2.5 | 176 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 100 | 220 | 0 | 0 | 1030 | 0 | 5231.75 | 11195.75 | 87.19
07:00 | 0 | 17 | 8 | 140 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 17 | 2 | 420 | 306 | 0 | 0 | 0 | 31 | 328 | 0 | 0 | 2 | 34 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 18 | 308 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 1 | 51 | 0 | 187 | 0 | 0 | 285 | 42 | 197 | 35 | 17 | 50 | 87 | 15 | 11 | 34 | 54 | 0 | 6 | 0 | 300 | 320 | 319 | 32 | 41 | 30 | 5 | 0 | 0 | 0 | 86 | 0 | 0 | 17 | 164 | 0 | 45 | 105 | 100 | 0 | 3.79 | 12 | 5978.79 | 922 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.83 | 381 | 0 | 1119.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3.61 | 170 | 0 | 0 | 0 | 133 | 0 | 331 | 0 | 0.24 | 2.5 | 178 | 54 | 0 | 2 | 0 | 0 | 0 | 0.2 | 6 | 0.02 | 0 | 250 | 7 | 100 | 220 | 0 | 0 | 1000 | 0 | 5248.11 | 11226.9 | 87.18
08:00 | 0 | 16 | 8 | 140 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 109 | 16 | 0 | 0 | 0 | 0 | 17 | 21 | 450 | 290 | 0 | 0 | 0 | 10 | 328 | 0 | 0 | 10 | 34 | 25.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 5 | 308 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1005 | 4 | 51 | 0 | 185 | 0 | 0 | 285 | 42 | 184 | 35 | 13 | 50 | 153 | 8 | 11 | 70 | 56 | 16 | 17 | 0 | 290 | 320 | 350 | 29 | 43 | 30 | 5 | 0 | 0 | 0 | 86 | 0 | 0 | 17 | 164 | 0 | 45 | 132 | 93 | 1 | 9.24 | 12 | 6202.74 | 878 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.62 | 382 | 0 | 1113.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 11.4 | 170 | 0 | 0 | 0 | 173 | 0 | 383 | 0 | 1.45 | 5.5 | 178 | 56 | 0 | 8 | 0 | 0 | 0 | 1.7 | 18 | 0.13 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1000 | 0 | 5465.58 | 11668.32 | 87.17
09:00 | 0 | 33 | 10 | 140 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 120 | 16 | 0 | 0 | 0 | 25 | 17 | 26 | 450 | 292 | 0 | 0 | 0 | 10 | 324 | 0 | 0 | 14 | 35 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 4 | 312 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 1000 | 12 | 51 | 0 | 185 | 0 | 0 | 285 | 42 | 185 | 35 | 12 | 50 | 136 | 9 | 11 | 70 | 54 | 34 | 34 | 31 | 290 | 320 | 350 | 26 | 42 | 30 | 5 | 0 | 0 | 0 | 86 | 0 | 0 | 17 | 164 | 0 | 45 | 95 | 80 | 1 | 19.24 | 12 | 6316.24 | 877 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.48 | 382 | 0 | 1025.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 31.9 | 170 | 0 | 0 | 0 | 202 | 0 | 381 | 0 | 3.63 | 5.5 | 173 | 56 | 0 | 17 | 0 | 0 | 0 | 3.1 | 20 | 0.19 | 0 | 291 | 6 | 130 | 220 | 0 | 0 | 1000 | 0 | 5464.42 | 11780.66 | 87.16
10:00 | 8 | 50 | 16 | 140 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 7 | 0 | 0 | 132 | 16 | 0 | 0 | 0 | 35 | 17 | 16 | 450 | 309 | 0 | 0 | 0 | 23 | 322 | 0 | 0 | 22 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 313 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1013 | 16 | 23 | 0 | 185 | 0 | 0 | 285 | 42 | 204 | 35 | 17 | 50 | 100 | 9 | 11 | 70 | 46 | 34 | 42 | 31 | 310 | 320 | 383 | 29 | 41 | 30 | 5 | 0 | 0 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 45 | 95 | 80 | 1 | 14.59 | 12 | 6434.59 | 923 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.82 | 381 | 0 | 1018.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 22.98 | 170 | 0 | 0 | 0 | 213 | 0 | 414 | 0 | 4.17 | 5.5 | 174 | 58 | 0 | 11 | 0 | 0 | 0 | 4.4 | 27 | 0.27 | 0 | 250 | 6 | 130 | 220 | 0 | 0 | 1000 | 0 | 5541.25 | 11975.84 | 87.16
11:00 | 8 | 50 | 16 | 140 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 0 | 0 | 133 | 16 | 0 | 0 | 12 | 35 | 17 | 16 | 450 | 300 | 0 | 0 | 0 | 24 | 322 | 0 | 0 | 29 | 35 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 3 | 313 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1113 | 18 | 23 | 1 | 185 | 0 | 0 | 285 | 42 | 186 | 36 | 37 | 50 | 100 | 9 | 11 | 70 | 46 | 34 | 33 | 39 | 315 | 320 | 330 | 29 | 42 | 30 | 5 | 0 | 0 | 0 | 83 | 0 | 0 | 17 | 164 | 0 | 45 | 95 | 69 | 2 | 24.89 | 12 | 6538.89 | 924 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.46 | 380 | 0 | 1015.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 44.28 | 181 | 0 | 0 | 0 | 211 | 0 | 384 | 0 | 5.12 | 5.5 | 178 | 57 | 0 | 16 | 0 | 0 | 0 | 4.7 | 49 | 0.5 | 0 | 307 | 4 | 130 | 220 | 0 | 0 | 1090 | 0 | 5708 | 12246.89 | 87.15
12:00 | 25 | 50 | 16 | 140 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 5 | 0 | 133 | 32 | 9 | 0 | 55 | 40 | 17 | 16 | 450 | 290 | 0 | 0 | 17 | 14 | 318 | 0 | 0 | 31 | 35 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 9 | 4 | 40 | 0 | 3 | 312 | 0 | 0 | 0 | 0 | 10 | 216 | 0 | 0 | 0 | 1173 | 19 | 23 | 23 | 185 | 0 | 0 | 285 | 36 | 184 | 35 | 51 | 50 | 100 | 13 | 11 | 34 | 50 | 16 | 50 | 39 | 300 | 320 | 333 | 29 | 42 | 30 | 5 | 0 | 22 | 0 | 82 | 0 | 0 | 17 | 165 | 0 | 45 | 95 | 69 | 2 | 39.87 | 12 | 6766.47 | 924 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.43 | 380 | 0 | 1018.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 57.41 | 181 | 0 | 0 | 0 | 210 | 0 | 378 | 0 | 5.1 | 5.5 | 180 | 56 | 0 | 17 | 0 | 0 | 0 | 6 | 114 | 0.67 | 0 | 307 | 6 | 130 | 220 | 0 | 0 | 1220 | 0 | 5975.29 | 12741.76 | 87.15
13:00 | 28 | 50 | 16 | 140 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 21 | 0 | 149 | 32 | 115 | 0 | 55 | 108 | 17 | 16 | 450 | 300 | 0 | 0 | 17 | 29 | 320 | 0 | 0 | 31 | 60 | 24.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 87 | 60 | 4 | 40 | 11 | 12 | 313 | 0 | 0 | 0 | 0 | 51 | 216 | 0 | 0 | 0 | 1158 | 18 | 23 | 43 | 185 | 0 | 0 | 285 | 39 | 185 | 35 | 50 | 50 | 104 | 8 | 11 | 70 | 46 | 34 | 60 | 39 | 320 | 320 | 375 | 34 | 39 | 30 | 5 | 0 | 24 | 0 | 82 | 0 | 0 | 17 | 164 | 0 | 45 | 106 | 65 | 2 | 42.8 | 12 | 7331.4 | 923 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.8 | 380 | 0 | 1089.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 55.86 | 84 | 0 | 0 | 0 | 206 | 0 | 378 | 0 | 5.22 | 5.5 | 178 | 57 | 0 | 31 | 0 | 0 | 0 | 6.6 | 158 | 0.69 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1244 | 0 | 5968.92 | 13300.32 | 87.14
14:00 | 8 | 34 | 16 | 140 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 46 | 0 | 149 | 32 | 278 | 30 | 55 | 108 | 17 | 16 | 450 | 300 | 0 | 0 | 17 | 29 | 318 | 0 | 0 | 28 | 70 | 24.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 88 | 100 | 3 | 40 | 30 | 4 | 311 | 0 | 0 | 0 | 0 | 87 | 216 | 0 | 0 | 0 | 1184 | 16 | 23 | 68 | 185 | 0 | 0 | 285 | 40 | 191 | 32 | 50 | 50 | 104 | 8 | 11 | 70 | 70 | 43 | 53 | 39 | 300 | 320 | 386 | 33 | 39 | 29 | 5 | 0 | 24 | 0 | 82 | 0 | 0 | 17 | 165 | 0 | 68 | 140 | 65 | 2 | 34 | 12 | 7727.5 | 924 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.87 | 378 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 48.67 | 57 | 0 | 0 | 0 | 206 | 0 | 382 | 0 | 4.86 | 5.5 | 176 | 56 | 35 | 28 | 0 | 0 | 0 | 2.3 | 140 | 0.41 | 0 | 307 | 8 | 130 | 220 | 0 | 0 | 1244 | 0 | 6092.61 | 13820.11 | 87.14
15:00 | 8 | 34 | 16 | 141 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 149 | 52 | 278 | 55 | 35 | 72 | 17 | 16 | 450 | 300 | 0 | 0 | 17 | 28 | 316 | 0 | 0 | 22 | 90 | 24 | 14 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 0 | 88 | 100 | 2 | 40 | 39 | 4 | 314 | 0 | 0 | 0 | 0 | 87 | 214 | 0 | 0 | 0 | 1224 | 12 | 23 | 87 | 185 | 0 | 0 | 285 | 40 | 183 | 32 | 51 | 50 | 102 | 8 | 11 | 70 | 66 | 52 | 28 | 39 | 305 | 320 | 386 | 33 | 39 | 29 | 5 | 0 | 24 | 0 | 84 | 28 | 0 | 17 | 163 | 0 | 76 | 140 | 58 | 1 | 27.38 | 12 | 7824.38 | 924 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.36 | 387 | 0 | 1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 39.69 | 65 | 0 | 0 | 0 | 203 | 0 | 366 | 0 | 3.75 | 5.5 | 178 | 54 | 35 | 19 | 25 | 0 | 0 | 3.1 | 111 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1244 | 0 | 6015.4 | 13839.78 | 87.13
16:00 | 8 | 34 | 16 | 140 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 0 | 149 | 93 | 300 | 55 | 35 | 72 | 17 | 16 | 450 | 302 | 0 | 0 | 17 | 28 | 317 | 0 | 0 | 13 | 100 | 24 | 14 | 0 | 0 | 0 | 45 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 100 | 1 | 40 | 76 | 9 | 313 | 0 | 0 | 0 | 3 | 87 | 214 | 0 | 0 | 0 | 1224 | 8 | 23 | 113 | 185 | 0 | 0 | 285 | 41 | 187 | 32 | 51 | 50 | 51 | 30 | 11 | 88 | 66 | 52 | 25 | 38 | 300 | 320 | 388 | 33 | 40 | 29 | 5 | 0 | 24 | 0 | 84 | 30 | 0 | 17 | 163 | 0 | 76 | 142 | 32 | 1 | 17 | 12 | 7942 | 924 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.67 | 382 | 7 | 1311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 24.42 | 68 | 0 | 0 | 0 | 197 | 0 | 337 | 0 | 2.6 | 5.5 | 171 | 54 | 35 | 12 | 44 | 0 | 0 | 2.8 | 70 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1220 | 0 | 5856.99 | 13798.99 | 87.13
17:00 | 8 | 34 | 16 | 140 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 33 | 0 | 149 | 93 | 300 | 55 | 35 | 72 | 17 | 24 | 450 | 300 | 0 | 0 | 17 | 28 | 317 | 0 | 0 | 4 | 108 | 24 | 14 | 0 | 0 | 0 | 80 | 3 | 0 | 9 | 0 | 8 | 0 | 100 | 90 | 0 | 40 | 93 | 9 | 312 | 0 | 0 | 0 | 8 | 87 | 214 | 0 | 0 | 0 | 1224 | 3 | 23 | 120 | 185 | 0 | 0 | 285 | 41 | 186 | 32 | 51 | 50 | 51 | 35 | 11 | 88 | 64 | 43 | 11 | 38 | 310 | 320 | 367 | 33 | 40 | 28 | 5 | 0 | 24 | 0 | 85 | 30 | 0 | 17 | 163 | 0 | 76 | 143 | 32 | 0 | 6.73 | 12 | 7942.73 | 924 | 234 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 17.88 | 383 | 17 | 1358 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8.58 | 79 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0.89 | 5.5 | 168 | 53 | 65 | 5 | 52 | 0 | 0 | 0.9 | 23 | 0 | 16 | 307 | 6 | 124 | 220 | 0 | 0 | 1200 | 17 | 5937.75 | 13880.48 | 87.12
18:00 | 8 | 35 | 16 | 140 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 54 | 0 | 149 | 141 | 300 | 55 | 35 | 72 | 17 | 31 | 370 | 305 | 0 | 0 | 17 | 23 | 320 | 0 | 0 | 0 | 108 | 21 | 14 | 0 | 0 | 0 | 115 | 12 | 0 | 4 | 17 | 15 | 0 | 100 | 60 | 0 | 40 | 110 | 19 | 311 | 17 | 0 | 0 | 8 | 87 | 214 | 0 | 0 | 0 | 1155 | 0 | 23 | 125 | 185 | 0 | 0 | 285 | 41 | 193 | 32 | 64 | 50 | 105 | 36 | 15 | 88 | 64 | 52 | 0 | 38 | 285 | 320 | 388 | 34 | 40 | 28 | 5 | 0 | 24 | 0 | 61 | 28 | 0 | 17 | 162 | 16 | 85 | 163 | 32 | 0 | 0.25 | 12 | 8051.25 | 924 | 239 | 0 | 18 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 386 | 22 | 1348 | 0 | 0 | 0 | 67 | 4 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 150 | 0 | 350 | 0 | 0.04 | 5.5 | 166 | 54 | 73 | 0 | 65 | 0 | 0 | 0.1 | 1 | 0 | 48 | 265 | 8 | 126 | 190 | 0 | 0 | 1150 | 54 | 5996.92 | 14048.17 | 87.11
19:00 | 8 | 50 | 16 | 150 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 0 | 149 | 141 | 300 | 55 | 35 | 72 | 17 | 34 | 450 | 273 | 0 | 0 | 17 | 30 | 320 | 0 | 0 | 0 | 108 | 24.5 | 14 | 0 | 0 | 5 | 190 | 14 | 0 | 10 | 51 | 53 | 2 | 100 | 88 | 0 | 40 | 110 | 13 | 312 | 34 | 0 | 0 | 8 | 87 | 214 | 0 | 0 | 0 | 1224 | 0 | 15 | 127 | 185 | 0 | 0 | 285 | 41 | 183 | 33 | 70 | 50 | 155 | 36 | 16 | 88 | 74 | 52 | 0 | 38 | 290 | 320 | 385 | 34 | 41 | 30 | 5 | 0 | 24 | 0 | 85 | 30 | 0 | 17 | 163 | 27 | 85 | 163 | 62 | 0 | 0 | 12 | 8559.5 | 872 | 248 | 0 | 29 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 35 | 1357 | 0 | 39 | 0 | 86 | 5 | 84 | 60 | 10 | 7 | 0 | 20 | 0 | 192 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 0 | 5.5 | 165 | 54 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 58 | 307 | 10 | 124 | 220 | 0 | 0 | 1180 | 72 | 6485.5 | 15045 | 87.11
19:30 | 8 | 50 | 25 | 160 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 54 | 0 | 149 | 141 | 260 | 55 | 35 | 54 | 17 | 51 | 450 | 294 | 0 | 0 | 17 | 30 | 320 | 0 | 0 | 0 | 108 | 24.5 | 14 | 0 | 0 | 53 | 135 | 25 | 0 | 9 | 51 | 55 | 0 | 100 | 48 | 0 | 40 | 110 | 17 | 300 | 18 | 0 | 0 | 8 | 87 | 214 | 0 | 0 | 0 | 1224 | 0 | 15 | 130 | 185 | 0 | 0 | 285 | 43 | 183 | 31 | 69 | 50 | 155 | 36 | 16 | 70 | 72 | 52 | 0 | 38 | 300 | 320 | 385 | 34 | 41 | 28 | 5 | 15 | 24 | 0 | 85 | 30 | 0 | 17 | 163 | 54.5 | 85 | 163 | 63 | 0 | 0 | 12 | 8521 | 872 | 248 | 0 | 34 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 40 | 1354 | 0 | 41 | 0 | 70 | 5 | 85 | 35 | 15 | 8 | 0 | 20 | 0 | 210 | 0 | 0 | 0 | 196 | 0 | 360 | 0 | 0 | 5.5 | 161 | 55 | 73 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 10 | 130 | 220 | 0 | 0 | 1232 | 72 | 6434.5 | 14955.5
20:00 | 8 | 50 | 25 | 160 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 54 | 0 | 149 | 142 | 260 | 55 | 35 | 54 | 17 | 57 | 450 | 306 | 0 | 0 | 17 | 30 | 320 | 0 | 0 | 0 | 108 | 24.5 | 14 | 0 | 0 | 53 | 135 | 28 | 0 | 9 | 51 | 63 | 0 | 100 | 48 | 0 | 40 | 110 | 18 | 290 | 0 | 0 | 0 | 8 | 87 | 214 | 0 | 0 | 0 | 1224 | 0 | 15 | 130 | 185 | 0 | 0 | 285 | 44 | 196 | 34 | 69 | 50 | 155 | 36 | 16 | 70 | 70 | 52 | 0 | 38 | 295 | 320 | 387 | 34 | 40 | 28 | 5 | 15 | 24 | 0 | 85 | 30 | 0 | 17 | 162 | 54.5 | 85 | 164 | 62 | 0 | 0 | 12 | 8534 | 873 | 246 | 0 | 25 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 51 | 1358 | 0 | 41 | 0 | 70 | 15 | 86 | 35 | 35 | 0 | 0 | 20 | 0 | 210 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 0 | 5.5 | 163 | 55 | 73 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 10 | 130 | 220 | 0 | 18 | 1244 | 35 | 6490.5 | 15024.5 | 87.11
21:00 | 8 | 50 | 25 | 160 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 0 | 149 | 143 | 260 | 55 | 35 | 54 | 17 | 68 | 450 | 275 | 0 | 0 | 17 | 30 | 325 | 0 | 0 | 0 | 108 | 25 | 14 | 0 | 0 | 61 | 190 | 27 | 0 | 2 | 51 | 63 | 0 | 98 | 70 | 0 | 40 | 110 | 15 | 290 | 0 | 0 | 0 | 13 | 87 | 214 | 0 | 0 | 0 | 1076 | 0 | 51 | 132 | 185 | 0 | 103 | 285 | 44 | 183 | 35 | 63 | 50 | 155 | 37 | 16 | 70 | 70 | 52 | 0 | 38 | 300 | 320 | 385 | 34 | 40 | 29 | 5 | 15 | 24 | 0 | 85 | 30 | 0 | 17 | 164 | 54.5 | 86 | 164 | 60 | 0 | 0 | 12 | 8542.5 | 918 | 250 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 51 | 1356.92 | 0 | 41 | 0 | 98 | 21 | 86 | 90 | 35 | 0 | 0 | 28 | 0 | 210 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 0 | 5.5 | 163 | 54 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 10 | 124 | 220 | 0 | 67 | 1244 | 90 | 6794.42 | 15336.92 | 87.1
22:00 | 8 | 50 | 25 | 160 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 54 | 0 | 149 | 143 | 225 | 55 | 35 | 54 | 17 | 67 | 450 | 282 | 0 | 0 | 17 | 30 | 325 | 0 | 0 | 0 | 108 | 25 | 15 | 0 | 0 | 72 | 190 | 27 | 0 | 0 | 51 | 63 | 0 | 100 | 40 | 0 | 40 | 110 | 19 | 273 | 0 | 0 | 0 | 17 | 87 | 214 | 0 | 0 | 0 | 1138 | 0 | 51 | 132 | 185 | 0 | 143 | 285 | 46 | 183 | 35 | 51 | 50 | 155 | 37 | 17 | 70 | 72 | 52 | 0 | 38 | 285 | 320 | 383 | 35 | 40 | 30 | 5 | 15 | 24 | 0 | 85 | 28 | 0 | 17 | 164 | 54.5 | 86 | 155 | 59 | 0 | 0 | 12 | 8553.5 | 920 | 250 | 0 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 68 | 1356.67 | 0 | 41 | 0 | 113 | 21 | 86 | 50 | 30 | 0 | 0 | 28 | 0 | 214 | 0 | 0 | 0 | 200 | 0 | 360 | 0 | 0 | 5.5 | 164 | 54 | 53 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 10 | 126 | 190 | 0 | 69 | 1244 | 90 | 6603.17 | 15156.67 | 87.1
23:00 | 8 | 50 | 17 | 160 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 54 | 0 | 149 | 143 | 175 | 15 | 35 | 54 | 17 | 49 | 450 | 306 | 0 | 0 | 17 | 30 | 325 | 0 | 0 | 0 | 108 | 25 | 15 | 0 | 0 | 35 | 150 | 28 | 0 | 0 | 51 | 63 | 0 | 88 | 12 | 0 | 40 | 85 | 24 | 273 | 0 | 0 | 0 | 17 | 87 | 161 | 0 | 0 | 0 | 1172 | 0 | 51 | 130 | 143 | 0 | 240 | 285 | 47 | 160 | 35 | 42 | 50 | 155 | 38 | 17 | 70 | 76 | 52 | 0 | 31 | 280 | 320 | 385 | 35 | 41 | 30 | 5 | 21 | 23 | 0 | 85 | 28 | 0 | 17 | 164 | 54.5 | 87 | 155 | 59 | 0 | 0 | 12 | 8306.5 | 920 | 254 | 0 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 68 | 1358.97 | 0 | 41 | 0 | 50 | 23 | 86 | 35 | 30 | 0 | 0 | 28 | 0 | 214 | 0 | 0 | 0 | 202 | 0 | 360 | 0 | 0 | 5.5 | 163 | 56 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 130 | 190 | 0 | 127 | 1244 | 54 | 6489.47 | 14795.97 | 87.09
Total KWH | 167904 | 836160 | 336960 | 3405700 | 0 | 0 | 0 | 0 | 9414000 | 0 | 0 | 324000 | 707040 | 0 | 3015216 | 1941600 | 2851331 | 526175 | 597130 | 1200960 | 383.6 | 531840 | 10021000 | 7056233 | 0 | 0 | 303848 | 674600 | 7737622 | 331000 | 0 | 208500 | 1854000 | 555600 | 300600 | 0 | 0 | 301091 | 1254545 | 172800 | 0 | 88320 | 372626 | 353616 | 10793 | 1514880 | 813120 | 24918 | 961380 | 1078073 | 501120 | 7149090.91 | 33455 | 0 | 0 | 107344.8 | 1109854 | 4620833 | 0 | 0 | 0 | 27212725 | 129465 | 817696 | 1456945 | 4349091 | 0 | 596000 | 6930000 | 1006560 | 4593000 | 822240 | 969600 | 1190280 | 2956800 | 579600 | 298090 | 1725960 | 1489920 | 674098 | 340400 | 723440 | 7238000 | 7698500 | 8995000 | 765360 | 962000 | 674040 | 116544 | 111027 | 374784 | 0 | 1991040 | 275712 | 0 | 408000 | 3400570 | 318960 | 1591200 | 2913600 | 1540800 | 13150 | 237000 | 293520 | 174147979.31 | 22082036 | 7541280 | 0 | 144480 | 283904 | 0 | 0 | 0 | 0 | 0 | 0 | 488160 | 9294545 | 355680 | 29930299 | 0 | 227372 | 0 | 743808 | 89598 | 654224 | 347616 | 132325 | 6778 | 682430 | 151050 | 363752 | 4052182 | 0 | 0 | 0 | 4623524 | 0 | 9129745.5 | 0 | 34020 | 112662 | 4221000 | 1284654 | 622903 | 168478 | 793478 | 0 | 0 | 36755.04 | 743760 | 2863 | 291552 | 7003000 | 195797 | 3028000 | 5150060 | 0 | 312000 | 28632727.27 | 466800 | 144425297.81 | 318573277.12