## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-03-2025 | during | 17-03-2025 | during | 17-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 120 | 260 | 260 | 160 | 160 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 402 | 320 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 285 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 32 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 316 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 107 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 24 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 21 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 29 | 28 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 51 | 104 | 104 | 70 | 70 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 62 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 0 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2293 | 2558 | 5272.5 | 5240.5 | 3227.3 | 3195.3
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 4 | 13 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 38 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 162 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 52 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 16 | 48 | 48 | 64 | 48 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 67 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 90 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 15 | 2 | 32 | 2 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.86 | 0 | 3.86 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 100 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 6 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 96 | 40 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 31 | 45 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 72 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 943 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 7 | 2 | 3 | 2 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 592 | 585 | 575 | 575 | 575 | 575 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2144 | 2753 | 3492.58 | 3516.72 | 3377.58 | 3401.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 190 | 215 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 230 | 236 | 230 | 230 | 230 | 230 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 240 | 285 | 285 | 285 | 285 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 33 | 46.94 | 46.94 | 35 | 35 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55 | 31 | 31 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 23 | 27 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 48 | 127 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 24 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 156 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 80 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 16 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 72 | 113 | 113 | 36 | 36 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 55 | 69 | 115 | 115 | 95 | 95 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 56 | 0 | 56 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1344 | 1536 | 2274.97 | 2218.97 | 1998.03 | 1942.03
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-03-2025 | during | 17-03-2025 | during | 17-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 34 | 210 | 210 | 65 | 65 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 134 | 153 | 200 | 200 | 150 | 150 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 87 | 115 | 115 | 90 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45 | 0 | 39.87 | 0 | 39.87 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 320 | 303 | 643.57 | 601.5 | 423.57 | 381.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 39 | 43 | 43 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 0 | 20 | 20 | 20 | 20 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 34 | 34 | 40 | 40 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 28 | 25 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 162 | 162 | 162 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 385 | 380 | 380 | 380 | 380 | FGMO not available due to Air Compressor problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1195 | 1541 | 1633 | 1633 | 1597 | 1597
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 869 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 246 | 228 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 66 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 539 | 0 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1792 | 1163 | 3597.2 | 3512.2 | 2180.02 | 2095.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 364 | 363 | 483 | 594 | 420 | 420 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 10 | 10.12 | 10.12 | 6 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 130.1 | 130.1 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 20 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1652 | 2218 | 2655.22 | 2765.22 | 2576 | 2579
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 46 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 3 | 21 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 30 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 196 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 203 | 150 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 353 | 321 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 6 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 17 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 46 | 86 | 90 | 90 | 90 | 90 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 33 | 85 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 15 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 6 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1364 | 1367 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2354 | 2424.5 | 3099.15 | 2938.53 | 2837.78 | 2677.16
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 56 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 163 | 172 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 41 | 103 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 172 | 0 | 170 | 0 | 170 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 502 | 421 | 688.4 | 487 | 654.42 | 453.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 13596 | 14917.5 | 23356.59 | 22913.64 | 18871.7 | 18321.75
Forecast Scenario (17-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14400 |  | 0 |  | 14400
|  |  |  | 1:00 | 13670 |  | 0 |  | 13670
|  |  |  | 2:00 | 13240 |  | 0 |  | 13240
|  |  |  | 3:00 | 13270 |  | 0 |  | 13270
|  |  |  | 4:00 | 13480 |  | 0 |  | 13480
|  |  |  | 5:00 | 12460 |  | 0 |  | 12460
|  |  |  | 6:00 | 11900 |  | 0 |  | 11900
|  |  |  | 7:00 | 11820 |  | 0 |  | 11820
|  |  |  | 8:00 | 12270 |  | 0 |  | 12270
|  |  |  | 9:00 | 12840 |  | 0 |  | 12840
|  |  |  | 10:00 | 13270 |  | 0 |  | 13270
|  |  |  | 11:00 | 13400 |  | 0 |  | 13400
|  |  |  | 12:00 | 13590 |  | 0 |  | 13590
|  |  |  | 13:00 | 14300 |  | 0 |  | 14300
|  |  |  | 14:00 | 14300 |  | 0 |  | 14300
|  |  |  | 15:00 | 14400 |  | 0 |  | 14400
|  |  |  | 16:00 | 14300 |  | 0 |  | 14300
|  |  |  | 17:00 | 14400 |  | 0 |  | 14400
|  |  |  | 18:00 | 14400 |  | 0 |  | 14400
|  |  |  | 18:30 | 14850 |  | 0 |  | 14850
|  |  |  | 19:00 | 15300 |  | 0 |  | 15300
|  |  |  | 19:30 | 15200 |  | 0 |  | 15200
|  |  |  | 20:00 | 15300 |  | 0 |  | 15300
|  |  |  | 21:00 | 15500 |  | 0 |  | 15500
|  |  |  | 22:00 | 15400 |  | 0 |  | 15400
|  |  |  | 23:00 | 15000 |  | 0 |  | 15000
Probable Maximum Temperature: |  |  | 35.20°C
Probable Maximum Demand at Day Peak: |  |  | 13590.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 332.21 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:20 hrs on 17-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-03-2025 | [28 empty] | Date: | 16-03-2025 | [28 empty] | Date: | 16-03-2025 | [28 empty] | Date: | 16-03-2025 | [28 empty] | Date: | 16-03-2025 | [18 empty] | Date: | 16-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 34 | 8 | 160 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 54 | 0 | 149 | 143 | 145 | 15 | 17 | 54 | 17 | 49 | 450 | 263 | 0 | 0 | 17 | 31 | 320 | 0 | 0 | 0 | 108 | 25 | 0 | 0 | 0 | 35 | 100 | 28 | 0 | 0 | 51 | 63 | 0 | 76 | 12 | 0 | 40 | 51 | 22 | 281 | 0 | 0 | 0 | 17 | 87 | 161 | 0 | 0 | 0 | 1207 | 0 | 51 | 133 | 55 | 0 | 250 | 285 | 37 | 148 | 35 | 20 | 50 | 99 | 29 | 17 | 114 | 76 | 52 | 0 | 31 | 290 | 320 | 384 | 35 | 41 | 30 | 5 | 48 | 22 | 0 | 85 | 28 | 0 | 17 | 164 | 55 | 87 | 135 | 60 | 0 | 0 | 7 | 7970 | 920 | 254 | 0 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 68 | 1364 | 0 | 40 | 0 | 50 | 23 | 86 | 35 | 30 | 0 | 0 | 28 | 0 | 214 | 0 | 0 | 0 | 201 | 0 | 360 | 0 | 0 | 6 | 164 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 124 | 190 | 0 | 142 | 1150 | 54 | 6410 | 14380 | 87.09
01:00 | 8 | 17 | 8 | 160 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 54 | 0 | 149 | 143 | 145 | 15 | 0 | 54 | 17 | 49 | 370 | 297 | 0 | 0 | 17 | 30 | 270 | 0 | 0 | 0 | 108 | 25 | 15 | 0 | 0 | 35 | 100 | 29 | 0 | 1 | 51 | 55 | 0 | 76 | 12 | 0 | 40 | 51 | 27 | 283 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1121 | 0 | 51 | 132 | 8 | 0 | 245 | 285 | 25 | 156 | 35 | 17 | 50 | 51 | 28 | 17 | 114 | 74 | 52 | 0 | 32 | 290 | 320 | 324 | 0 | 41 | 30 | 5 | 86 | 0 | 0 | 85 | 28 | 0 | 17 | 164 | 55 | 48 | 58 | 60 | 0 | 0 | 12 | 7457 | 919 | 255 | 0 | 20 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 68 | 1272 | 0 | 40 | 0 | 50 | 22 | 86 | 35 | 30 | 0 | 0 | 28 | 0 | 180 | 0 | 0 | 0 | 150 | 0 | 360 | 0 | 0 | 6 | 159 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 10 | 130 | 190 | 0 | 177 | 1060 | 54 | 6085 | 13542 | 87.08
02:00 | 8 | 17 | 8 | 160 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 54 | 0 | 149 | 143 | 145 | 15 | 0 | 54 | 17 | 20 | 320 | 275 | 0 | 0 | 17 | 30 | 240 | 0 | 0 | 0 | 108 | 26 | 15 | 0 | 0 | 35 | 100 | 26 | 0 | 0 | 51 | 55 | 0 | 76 | 12 | 0 | 40 | 51 | 30 | 282 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1103 | 0 | 51 | 127 | 8 | 0 | 50 | 285 | 30 | 182 | 35 | 17 | 50 | 51 | 28 | 17 | 114 | 66 | 52 | 0 | 32 | 300 | 320 | 322 | 5 | 40 | 30 | 5 | 141 | 0 | 0 | 85 | 28 | 0 | 17 | 164 | 55 | 48 | 58 | 64 | 0 | 0 | 12 | 7163 | 919 | 259 | 0 | 20 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 68 | 1268 | 0 | 40 | 0 | 50 | 12 | 86 | 35 | 30 | 0 | 0 | 28 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 6 | 167 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 10 | 100 | 190 | 0 | 197 | 1050 | 54 | 5971 | 13134 | 87.08
03:00 | 8 | 17 | 8 | 160 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 54 | 0 | 149 | 143 | 15 | 15 | 17 | 54 | 17 | 16 | 320 | 250 | 0 | 0 | 17 | 30 | 240 | 0 | 0 | 0 | 108 | 26 | 15 | 0 | 0 | 0 | 50 | 16 | 0 | 8 | 51 | 55 | 0 | 76 | 12 | 0 | 40 | 51 | 30 | 282 | 0 | 0 | 0 | 8 | 87 | 161 | 0 | 0 | 0 | 1188 | 0 | 51 | 128 | 45 | 0 | 100 | 285 | 44 | 182 | 35 | 40 | 50 | 51 | 29 | 17 | 114 | 68 | 52 | 0 | 32 | 285 | 320 | 368 | 32 | 40 | 30 | 5 | 163 | 16 | 0 | 85 | 29 | 0 | 17 | 164 | 55 | 49 | 65 | 64 | 0 | 0 | 12 | 7236 | 919 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 17 | 1361 | 0 | 40 | 0 | 35 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 6 | 171 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 220 | 0 | 222 | 1080 | 17 | 5939 | 13175 | 87.07
04:00 | 0 | 34 | 8 | 160 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 54 | 0 | 149 | 127 | 0 | 0 | 17 | 54 | 17 | 16 | 370 | 250 | 0 | 0 | 17 | 30 | 320 | 0 | 0 | 0 | 108 | 26 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 8 | 8 | 55 | 0 | 76 | 0 | 0 | 40 | 34 | 33 | 282 | 0 | 0 | 0 | 8 | 51 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 45 | 0 | 245 | 285 | 46 | 183 | 35 | 51 | 50 | 51 | 28 | 17 | 114 | 70 | 52 | 0 | 32 | 285 | 320 | 383 | 5 | 39 | 30 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 55 | 78 | 134 | 64 | 0 | 0 | 12 | 7340 | 919 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 170 | 0 | 360 | 0 | 0 | 6 | 170 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 271 | 1232 | 0 | 6102 | 13442 | 87.07
05:00 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 0 | 110 | 95 | 0 | 0 | 17 | 17 | 17 | 0 | 370 | 301 | 0 | 0 | 0 | 30 | 320 | 0 | 0 | 0 | 64 | 20 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 9 | 0 | 0 | 0 | 76 | 0 | 0 | 40 | 0 | 35 | 284 | 0 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 1046 | 0 | 51 | 10 | 45 | 0 | 240 | 285 | 45 | 201 | 32 | 27 | 50 | 51 | 28 | 12 | 88 | 70 | 24 | 0 | 0 | 290 | 320 | 383 | 5 | 39 | 30 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 0 | 79 | 135 | 64 | 0 | 0 | 12 | 6679 | 920 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 180 | 0 | 360 | 0 | 0 | 6 | 168 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 7 | 130 | 220 | 0 | 296 | 1100 | 0 | 5790 | 12469 | 87.06
06:00 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 17 | 0 | 105 | 96 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 270 | 0 | 0 | 0 | 30 | 320 | 0 | 0 | 0 | 52 | 20 | 5 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 30 | 324 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 45 | 0 | 245 | 285 | 30 | 182 | 32 | 16 | 50 | 51 | 28 | 11 | 88 | 64 | 0 | 0 | 0 | 295 | 320 | 382 | 5 | 39 | 30 | 5 | 120 | 16 | 0 | 86 | 30 | 0 | 17 | 164 | 0 | 55 | 135 | 64 | 0 | 0 | 12 | 6393 | 919 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 188 | 0 | 360 | 0 | 0 | 6 | 172 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 130 | 180 | 0 | 311 | 1000 | 0 | 5516 | 11909 | 87.06
07:00 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 17 | 0 | 105 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 291 | 0 | 0 | 0 | 32 | 320 | 0 | 0 | 3 | 35 | 23 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 40 | 0 | 7 | 300 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 3 | 51 | 0 | 8 | 0 | 245 | 285 | 30 | 201 | 32 | 17 | 50 | 51 | 17 | 11 | 52 | 58 | 0 | 7 | 0 | 295 | 320 | 383 | 5 | 39 | 30 | 5 | 120 | 16 | 0 | 83 | 30 | 0 | 17 | 164 | 0 | 55 | 115 | 64 | 0 | 2 | 12 | 6273 | 920 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 413 | 0 | 1134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3 | 214 | 0 | 0 | 0 | 187 | 0 | 320 | 0 | 1 | 6 | 172 | 56 | 0 | 2 | 0 | 0 | 0 | 1 | 5 | 1 | 0 | 200 | 7 | 130 | 180 | 0 | 310 | 1000 | 0 | 5553 | 11826 | 87.05
08:00 | 0 | 16 | 8 | 160 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 17 | 0 | 116 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 270 | 0 | 0 | 0 | 32 | 320 | 0 | 0 | 10 | 35 | 27 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 48 | 0 | 2 | 40 | 0 | 3 | 346 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1003 | 4 | 51 | 0 | 8 | 0 | 245 | 285 | 30 | 195 | 32 | 16 | 50 | 51 | 10 | 11 | 52 | 62 | 0 | 27 | 0 | 310 | 320 | 384 | 5 | 39 | 30 | 5 | 120 | 16 | 0 | 83 | 30 | 0 | 17 | 164 | 0 | 77 | 134 | 61 | 1 | 9 | 12 | 6452 | 868 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 616 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 214 | 0 | 0 | 0 | 191 | 0 | 370 | 0 | 2 | 6 | 169 | 58 | 0 | 5 | 0 | 0 | 0 | 2 | 12 | 1 | 0 | 250 | 6 | 130 | 180 | 0 | 315 | 1000 | 0 | 5831 | 12283 | 87.05
09:00 | 0 | 34 | 11 | 160 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 24 | 0 | 142 | 61 | 0 | 0 | 0 | 15 | 17 | 0 | 420 | 265 | 0 | 0 | 0 | 31 | 310 | 0 | 0 | 16 | 35 | 21 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 2 | 40 | 0 | 6 | 430 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1001 | 14 | 51 | 0 | 8 | 0 | 245 | 285 | 30 | 186 | 32 | 17 | 50 | 51 | 10 | 11 | 52 | 56 | 0 | 42 | 0 | 300 | 320 | 384 | 20 | 39 | 30 | 5 | 163 | 16 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 78 | 134 | 61 | 1 | 28 | 12 | 6716 | 868 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 619 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 12 | 214 | 0 | 0 | 0 | 193 | 0 | 350 | 0 | 2 | 6 | 168 | 58 | 0 | 9 | 0 | 0 | 0 | 4 | 40 | 1 | 0 | 232 | 5 | 124 | 220 | 0 | 362 | 1000 | 0 | 6086 | 12802 | 87.04
10:00 | 0 | 50 | 17 | 160 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 4 | 35 | 0 | 141 | 48 | 30 | 0 | 32 | 54 | 17 | 3 | 420 | 283 | 0 | 0 | 10 | 23 | 300 | 0 | 0 | 26 | 74 | 21 | 15 | 0 | 0 | 5 | 45 | 0 | 0 | 0 | 7 | 0 | 0 | 62 | 24 | 4 | 40 | 5 | 2 | 450 | 0 | 0 | 0 | 0 | 13 | 162 | 0 | 0 | 0 | 1000 | 17 | 23 | 6 | 8 | 0 | 235 | 285 | 30 | 186 | 33 | 17 | 50 | 51 | 8 | 11 | 88 | 62 | 16 | 56 | 0 | 295 | 320 | 384 | 32 | 40 | 30 | 5 | 120 | 16 | 0 | 83 | 30 | 0 | 18 | 165 | 1 | 77 | 134 | 30 | 2 | 25 | 12 | 6984 | 915 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 585 | 0 | 1346 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 38 | 214 | 0 | 0 | 0 | 194 | 0 | 300 | 0 | 3 | 6 | 170 | 41 | 32 | 16 | 34 | 0 | 0 | 4 | 131 | 1 | 0 | 200 | 6 | 130 | 180 | 0 | 365 | 940 | 0 | 6235 | 13219 | 87.04
11:00 | 0 | 50 | 17 | 160 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 0 | 135 | 32 | 15 | 0 | 35 | 58 | 24 | 16 | 390 | 304 | 0 | 0 | 17 | 24 | 322 | 0 | 0 | 29 | 90 | 21 | 15 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 14 | 0 | 48 | 12 | 4 | 40 | 64 | 3 | 580 | 0 | 0 | 0 | 0 | 34 | 162 | 0 | 0 | 0 | 900 | 19 | 23 | 30 | 8 | 0 | 200 | 285 | 30 | 200 | 35 | 37 | 50 | 51 | 9 | 13 | 88 | 62 | 8 | 65 | 0 | 285 | 320 | 0 | 34 | 40 | 20 | 5 | 163 | 16 | 0 | 83 | 30 | 0 | 18 | 165 | 17 | 77 | 135 | 31 | 2 | 40 | 12 | 6823 | 914 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 567 | 0 | 1356 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 93 | 0 | 51 | 214 | 0 | 0 | 0 | 194 | 0 | 335 | 0 | 5 | 6 | 164 | 56 | 0 | 9 | 34 | 0 | 0 | 7 | 166 | 1 | 0 | 170 | 6 | 130 | 180 | 0 | 364 | 840 | 0 | 6190 | 13013 | 87.03
12:00 | 0 | 50 | 17 | 110 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 35 | 0 | 132 | 32 | 95 | 0 | 35 | 62 | 22 | 16 | 450 | 301 | 0 | 0 | 17 | 29 | 316 | 0 | 0 | 31 | 90 | 20 | 14 | 0 | 0 | 31 | 15 | 0 | 0 | 0 | 17 | 16 | 6 | 62 | 48 | 4 | 40 | 96 | 4 | 592 | 17 | 0 | 0 | 4 | 68 | 162 | 0 | 0 | 0 | 943 | 19 | 23 | 48 | 8 | 0 | 230 | 285 | 30 | 190 | 35 | 55 | 50 | 51 | 8 | 11 | 114 | 70 | 43 | 69 | 24 | 305 | 320 | 0 | 34 | 39 | 20 | 5 | 163 | 16 | 0 | 83 | 28 | 0 | 18 | 164 | 17 | 77 | 134 | 33 | 2 | 45 | 12 | 7296 | 915 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 539 | 0 | 1364 | 0 | 0 | 0 | 33 | 3 | 46 | 15 | 0 | 0 | 99 | 0 | 56 | 170 | 0 | 0 | 0 | 203 | 0 | 353 | 0 | 6 | 6 | 163 | 55 | 35 | 29 | 41 | 0 | 0 | 7 | 172 | 1 | 0 | 170 | 7 | 130 | 180 | 0 | 364 | 800 | 0 | 6300 | 13596 | 87.03
13:00 | 8 | 50 | 17 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 47 | 0 | 146 | 61 | 205 | 4 | 35 | 65 | 22 | 16 | 450 | 275 | 0 | 0 | 17 | 29 | 313 | 0 | 0 | 30 | 90 | 24 | 14 | 0 | 0 | 88 | 15 | 13 | 0 | 6 | 63 | 30 | 55 | 70 | 75 | 4 | 40 | 110 | 10 | 580 | 72 | 0 | 0 | 17 | 87 | 162 | 0 | 0 | 0 | 1182 | 19 | 23 | 90 | 8 | 0 | 235 | 285 | 30 | 186 | 31 | 55 | 50 | 51 | 9 | 11 | 114 | 70 | 53 | 61 | 24 | 310 | 320 | 0 | 34 | 38 | 20 | 5 | 163 | 16 | 0 | 82 | 28 | 0 | 18 | 165 | 33 | 76 | 134 | 33 | 2 | 44 | 12 | 8073 | 915 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 459 | 0 | 1359 | 0 | 0 | 0 | 35 | 4 | 45 | 35 | 10 | 0 | 80 | 0 | 53 | 170 | 0 | 0 | 0 | 202 | 0 | 322 | 0 | 5 | 6 | 164 | 55 | 35 | 30 | 34 | 0 | 0 | 4 | 162 | 1 | 0 | 220 | 7 | 120 | 220 | 0 | 361 | 800 | 0 | 6236 | 14309 | 87.03
14:00 | 8 | 34 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 149 | 90 | 238 | 55 | 35 | 72 | 22 | 16 | 450 | 301 | 0 | 0 | 17 | 29 | 309 | 0 | 0 | 26 | 90 | 24 | 14 | 0 | 0 | 108 | 16 | 58 | 0 | 14 | 64 | 40 | 55 | 87 | 88 | 3 | 40 | 110 | 10 | 582 | 75 | 0 | 11 | 17 | 87 | 162 | 0 | 0 | 0 | 1224 | 17 | 23 | 108 | 8 | 0 | 230 | 285 | 30 | 186 | 30 | 55 | 50 | 51 | 8 | 11 | 114 | 80 | 53 | 53 | 31 | 295 | 320 | 0 | 34 | 37 | 20 | 5 | 163 | 16 | 0 | 81 | 25 | 0 | 18 | 164 | 52 | 76 | 124 | 33 | 2 | 37 | 12 | 8375 | 915 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 409 | 0 | 1366 | 0 | 0 | 0 | 37 | 4 | 51 | 35 | 14 | 0 | 72 | 0 | 45 | 184 | 0 | 0 | 0 | 197 | 0 | 380 | 0 | 5 | 6 | 163 | 55 | 35 | 26 | 34 | 0 | 0 | 3 | 150 | 1 | 0 | 150 | 8 | 130 | 220 | 0 | 397 | 790 | 0 | 6196 | 14571 | 87.02
15:00 | 8 | 34 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 147 | 90 | 245 | 55 | 35 | 72 | 22 | 16 | 450 | 301 | 0 | 0 | 0 | 26 | 307 | 0 | 0 | 19 | 90 | 24 | 14 | 0 | 0 | 72 | 16 | 86 | 0 | 8 | 64 | 44 | 17 | 87 | 88 | 2 | 40 | 110 | 5 | 582 | 90 | 0 | 12 | 0 | 51 | 162 | 0 | 0 | 0 | 1224 | 13 | 23 | 115 | 8 | 0 | 224 | 285 | 30 | 199 | 30 | 55 | 50 | 51 | 12 | 16 | 114 | 70 | 53 | 44 | 40 | 305 | 320 | 81 | 30 | 37 | 15 | 5 | 163 | 16 | 0 | 83 | 25 | 0 | 18 | 164 | 52 | 75 | 114 | 31 | 1 | 30 | 12 | 8332 | 915 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 1367 | 0 | 0 | 0 | 70 | 14 | 52 | 35 | 6 | 0 | 63 | 0 | 35 | 204 | 0 | 0 | 0 | 193 | 0 | 403 | 0 | 4 | 6 | 163 | 53 | 35 | 5 | 34 | 0 | 0 | 2 | 82 | 0 | 0 | 236 | 7 | 128 | 220 | 0 | 388 | 820 | 0 | 5830 | 14162 | 87.01
16:00 | 8 | 34 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 146 | 90 | 260 | 55 | 35 | 61 | 22 | 16 | 450 | 267 | 0 | 0 | 35 | 28 | 316 | 0 | 0 | 11 | 132 | 24 | 14 | 0 | 0 | 17 | 16 | 98 | 0 | 13 | 65 | 44 | 17 | 48 | 24 | 1 | 40 | 51 | 8 | 580 | 107 | 0 | 15 | 2 | 75 | 162 | 0 | 0 | 0 | 1224 | 8 | 23 | 115 | 8 | 0 | 235 | 285 | 30 | 191 | 30 | 50 | 50 | 51 | 25 | 16 | 114 | 78 | 43 | 26 | 44 | 280 | 320 | 112 | 30 | 36 | 0 | 5 | 163 | 16 | 0 | 82 | 25 | 0 | 18 | 164 | 52 | 75 | 132 | 32 | 1 | 18 | 12 | 8214 | 916 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 1362 | 0 | 0 | 0 | 91 | 11 | 52 | 35 | 19 | 0 | 39 | 0 | 21 | 204 | 0 | 0 | 0 | 191 | 0 | 318 | 0 | 0 | 6 | 166 | 54 | 70 | 2 | 49 | 0 | 0 | 1.8 | 66 | 0 | 0 | 307 | 4 | 128 | 220 | 0 | 301 | 1100 | 0 | 5997.8 | 14211.8 | 87.01
17:00 | 8 | 34 | 16 | 120 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 54 | 0 | 148 | 90 | 195 | 55 | 35 | 72 | 22 | 18 | 450 | 271 | 0 | 0 | 35 | 28 | 318 | 0 | 0 | 3 | 160 | 18 | 14 | 0 | 0 | 17 | 16 | 106 | 0 | 6 | 67 | 44 | 17 | 48 | 12 | 0 | 40 | 34 | 10 | 580 | 17 | 0 | 32 | 8 | 34 | 162 | 0 | 0 | 0 | 1224 | 2 | 23 | 113 | 8 | 0 | 234 | 285 | 30 | 190 | 33 | 51 | 50 | 51 | 26 | 16 | 114 | 72 | 52.2 | 8 | 45 | 310 | 320 | 333 | 34 | 36 | 0 | 5 | 163 | 16 | 0 | 85 | 25 | 0 | 18 | 163 | 51 | 76 | 133 | 31 | 0 | 5.37 | 12 | 8294.57 | 915 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.51 | 0 | 1 | 1362 | 0 | 40 | 0 | 50 | 11 | 52 | 35 | 22 | 0 | 13 | 16 | 6.19 | 204 | 0 | 0 | 0 | 192 | 0 | 321 | 0 | 0.6 | 5.5 | 170 | 54 | 70 | 5 | 49 | 0 | 0 | 0.6 | 30 | 0 | 13 | 307 | 7 | 130 | 220 | 0 | 350 | 1200 | 0 | 6087.4 | 14381.97 | 87
18:00 | 8 | 34 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 0 | 149 | 113 | 195 | 30 | 55 | 72 | 22 | 42 | 450 | 303 | 0 | 0 | 35 | 28 | 317 | 0 | 0 | 0 | 56 | 24 | 18 | 0 | 0 | 17 | 30 | 59 | 0 | 5 | 67 | 44 | 17 | 48 | 12 | 0 | 40 | 34 | 18 | 586 | 17 | 0 | 44 | 8 | 34 | 162 | 0 | 0 | 0 | 1147 | 0 | 23 | 120 | 8 | 0 | 227 | 285 | 30 | 206 | 33 | 56 | 50 | 82 | 42 | 8 | 114 | 80 | 52.2 | 0 | 45 | 310 | 320 | 389 | 34 | 36 | 0 | 5 | 120 | 16 | 0 | 85 | 25 | 0 | 17 | 161 | 17 | 86 | 153 | 31 | 0 | 0.16 | 12 | 8244.36 | 915 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 0 | 25 | 1367 | 0 | 40 | 0 | 50 | 19 | 80 | 35 | 29 | 8 | 0 | 30 | 0 | 203 | 0 | 0 | 0 | 189 | 0 | 366 | 0 | 0.05 | 5.5 | 170 | 56 | 72 | 0 | 49 | 0 | 0 | 0 | 1 | 0 | 20 | 307 | 9 | 130 | 220 | 0 | 339 | 1100 | 0 | 6063.56 | 14307.92 | 87
19:00 | 8 | 105 | 50 | 120 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 54 | 0 | 149 | 107 | 195 | 32 | 55 | 162 | 22 | 51 | 450 | 285 | 0 | 0 | 35 | 28 | 250 | 0 | 0 | 0 | 0 | 24 | 21 | 0 | 0 | 45 | 100 | 50 | 0 | 7 | 67 | 48 | 17 | 90 | 88 | 0 | 40 | 40 | 15 | 585 | 72 | 0 | 38 | 13 | 52 | 162 | 0 | 0 | 0 | 1224 | 0 | 27 | 127 | 8 | 0 | 236 | 240 | 30 | 215 | 33 | 69 | 50 | 156 | 72 | 16 | 114 | 80 | 16 | 0 | 47 | 290 | 320 | 385 | 34 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 25 | 0 | 17 | 162 | 17 | 87 | 153 | 34 | 0 | 0 | 12 | 8691 | 869 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1367 | 0 | 46 | 0 | 85 | 21 | 86 | 70 | 30 | 17 | 0 | 30 | 0 | 196 | 0 | 0 | 0 | 150 | 0 | 321 | 0 | 0 | 5.5 | 172 | 56 | 90 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 10 | 130 | 220 | 0 | 363 | 1120 | 20 | 6226.5 | 14917.5 | 86.99
19:30 | 8 | 105 | 16 | 140 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 54 | 0 | 80 | 122 | 145 | 55 | 55 | 162 | 22 | 50 | 450 | 295 | 0 | 0 | 35 | 28 | 250 | 36 | 0 | 0 | 0 | 24 | 21 | 0 | 0 | 17 | 15 | 50 | 0 | 6 | 67 | 72 | 17 | 90 | 95 | 0 | 40 | 51 | 15 | 585 | 17 | 0 | 19 | 25.5 | 87 | 162 | 0 | 0 | 0 | 1224 | 0 | 35 | 132 | 8 | 0 | 235 | 240 | 30 | 181 | 33 | 69 | 50 | 156 | 82 | 16 | 114 | 76 | 16 | 0 | 47 | 300 | 320 | 385 | 34 | 39 | 0 | 5 | 120 | 16 | 0 | 85 | 25 | 0 | 17 | 162 | 17 | 87 | 153 | 33 | 0 | 0 | 12 | 8492.5 | 869 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1350 | 0 | 40 | 0 | 50 | 21 | 86 | 35 | 30 | 8 | 0 | 30 | 0 | 205 | 0 | 0 | 0 | 150 | 0 | 319 | 0 | 0 | 5.5 | 174 | 56 | 55 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 40 | 307 | 10 | 130 | 220 | 0 | 362 | 1220 | 17 | 6148.5 | 14641
20:00 | 8 | 105 | 16 | 140 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 54 | 0 | 92 | 123 | 95 | 55 | 55 | 162 | 22 | 50 | 450 | 290 | 0 | 0 | 35 | 0 | 250 | 185 | 0 | 0 | 0 | 25 | 20 | 0 | 0 | 0 | 15 | 50 | 0 | 3 | 34 | 40 | 0 | 48 | 12 | 0 | 40 | 34 | 15 | 585 | 17 | 0 | 19 | 0 | 34 | 162 | 0 | 0 | 0 | 1224 | 0 | 35 | 24 | 8 | 0 | 236 | 275 | 30 | 181 | 33 | 69 | 50 | 156 | 77 | 16 | 114 | 76 | 16 | 0 | 47 | 290 | 320 | 385 | 34 | 39 | 0 | 5 | 120 | 16 | 0 | 85 | 25 | 0 | 17 | 163 | 0 | 96 | 153 | 33 | 0 | 0 | 12 | 8155 | 868 | 200 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 68 | 1366 | 0 | 38 | 0 | 50 | 23 | 86 | 0 | 16 | 0 | 0 | 30 | 0 | 205 | 0 | 0 | 0 | 150 | 0 | 322 | 0 | 0 | 5.5 | 171 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 130 | 180 | 0 | 365 | 1220 | 0 | 6105.5 | 14260.5 | 86.99
21:00 | 8 | 105 | 34 | 160 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35 | 0 | 0 | 94 | 124 | 45 | 0 | 55 | 162 | 22 | 50 | 450 | 277 | 0 | 0 | 35 | 0 | 318 | 200 | 0 | 0 | 160 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 17 | 0 | 0 | 32 | 12 | 0 | 40 | 0 | 17 | 583 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 45 | 0 | 236 | 285 | 30 | 181 | 33 | 69 | 50 | 155 | 75 | 16 | 114 | 80 | 16 | 0 | 0 | 300 | 320 | 385 | 34 | 37 | 0 | 5 | 163 | 16 | 0 | 85 | 25 | 0 | 17 | 163 | 0 | 97 | 164 | 34 | 0 | 0 | 12 | 8185 | 915 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 68 | 1355 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 192 | 0 | 379 | 0 | 0 | 5.5 | 172 | 56 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 122 | 220 | 0 | 436 | 1244 | 0 | 6386.5 | 14571.5 | 86.98
22:00 | 0 | 87 | 25 | 160 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 96 | 77 | 45 | 0 | 35 | 162 | 22 | 16 | 450 | 297 | 0 | 0 | 35 | 16 | 326 | 204 | 0 | 0 | 108 | 25 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 48 | 12 | 0 | 40 | 0 | 17 | 576 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1160 | 0 | 51 | 10 | 45 | 0 | 235 | 285 | 30 | 183 | 30 | 53 | 50 | 155 | 77 | 16 | 88 | 76 | 0 | 0 | 0 | 310 | 320 | 394 | 34 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 25 | 0 | 17 | 164 | 0 | 98 | 164 | 34 | 0 | 0 | 12 | 7974 | 916 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 68 | 1356 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 5 | 0 | 191 | 0 | 386 | 0 | 0 | 2.5 | 171 | 57 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 130 | 220 | 0 | 440 | 1200 | 0 | 6535.5 | 14509.5 | 86.98
23:00 | 0 | 68 | 16 | 160 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 5 | 0 | 74 | 62 | 15 | 0 | 0 | 126 | 22 | 16 | 450 | 310 | 0 | 0 | 35 | 32 | 320 | 202 | 0 | 0 | 108 | 21 | 15 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 48 | 12 | 0 | 40 | 0 | 31 | 529 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1160 | 0 | 51 | 10 | 73 | 0 | 235 | 285 | 30 | 202 | 36 | 38 | 50 | 155 | 75 | 17 | 88 | 78 | 0 | 0 | 0 | 290 | 320 | 394 | 35 | 40 | 0 | 5 | 163 | 8 | 0 | 85 | 20 | 0 | 17 | 164 | 0 | 99 | 164 | 34 | 0 | 0 | 12 | 7732 | 915 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 34 | 1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 12 | 0 | 191 | 0 | 414 | 0 | 0 | 2.5 | 174 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 130 | 220 | 0 | 460 | 1060 | 0 | 6343.5 | 14075.5 | 86.97
Total KWH | 100800 | 1059840 | 362400 | 6853200 | 0 | 0 | 0 | 0 | 9262800 | 0 | 0 | 324000 | 919440 | 0 | 3091968 | 2129280 | 2346251 | 410544 | 597939 | 1648800 | 480240 | 457920 | 9472000 | 6977280 | 0 | 0 | 477891 | 639100 | 7226394 | 900000 | 0 | 202974 | 2032800 | 560400 | 327960 | 0 | 0 | 666164 | 707564 | 769920 | 0 | 79680 | 731837 | 615600 | 248809 | 1509120 | 615360 | 26758 | 956160 | 1034577 | 405120 | 11032727.27 | 431564 | 0 | 192000 | 165882.6 | 1069709 | 3810302 | 0 | 0 | 0 | 26896361 | 133515 | 855880 | 1565672 | 568727 | 0 | 5458800 | 6844000 | 756960 | 4610000 | 793368 | 980160 | 1203000 | 1838880 | 799680 | 321120 | 2399700 | 1653120 | 694685 | 462718 | 479360 | 7244000 | 7678600 | 7285000 | 564408 | 912000 | 400200 | 116496 | 3483245 | 336960 | 0 | 2016000 | 649440 | 0 | 418000 | 4397700 | 566280 | 1802400 | 3050400 | 1019520 | 13700 | 289000 | 298320 | 185788449.87 | 22010327 | 6044832 | 0 | 76320 | 90368 | 0 | 0 | 0 | 0 | 0 | 0 | 627120 | 8574545 | 615840 | 31305278 | 0 | 275942 | 0 | 984672 | 137862 | 769056 | 446016 | 192493 | 24226 | 655790 | 162803 | 311248 | 4861364 | 0 | 28600 | 0 | 4639755 | 0 | 8658036 | 0 | 30360 | 127080 | 4114000 | 1284655 | 714593 | 142457 | 835641 | 0 | 0 | 33670.56 | 973440 | 3451 | 139392 | 5957000 | 187094 | 3001000 | 5023410 | 0 | 8006472 | 25534545.45 | 186000 | 147786754.01 | 333575203.88

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13596 | MW | 12:00 Hr. | Energy Generated |  |  | 333.5752 |  | MKWHr.
| Day Peak Demand |  |  | 13707.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.704 |  | MKWHr.
| Evening Peak Generation |  |  | 14917.5 | MW | 19:00 Hr. | Energy Demand |  |  | 335.2792 |  | MKWHr.
| Evening Peak Demand |  |  | 15035.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 36 |  | °C
| Minimum Generation of the Day |  |  | 11826 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1026.45 |  | MMCFD
| Maximum Generation of the Day |  |  | 14917.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.5746 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.6994 | 0 | 15.9599 | 0 | 0 | 0.20297 | 0 | 0 | 58.8622 | Gas | 137.4194 | Gas | 445094190.77
| Chattogram Zone |  |  | 4.2154 | 37.9291 | 8.7581 | 0 | 0.95616 | 0.16027 | 0 | 0.07968 | 52.0987 | Coal | 91.4003 | Coal | 590501605.4901
| Cumilla Zone |  |  | 21.4119 | 0 | 8.7581 | 0 | 0 | 0.46272 | 1.6531 | 0 | 32.2858 | HFO | 44.8447 | HFO | 794377340.452
| Mymensingh Zone |  |  | 1.0195 | 0 | 5.7174 | 0 | 0 | 0.3027 | 0 | 0 | 7.0396 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.502 | Hydro | 0.95616 | Hydro | 95616
| Khulna Zone |  |  | 6.0448 | 8.5745 | 0.78253 | 0 | 0 | 0.62712 | 22.0103 | 0 | 38.0394 | Solar | 3.9062 | Solar | 62986740.3716
| Barishal Zone |  |  | 8.2115 | 39.498 | 0.32539 | 0 | 0 | 0.003451 | 0 | 0 | 48.0384 | Import | 54.9687 | Import | 298887544.93
| Rajshahi Zone |  |  | 18.3148 | 0 | 2.9931 | 0 | 0 | 0.9974 | 31.3053 | 0 | 53.6106 | Wind | 0.07968 | Wind | 1166515.2
| Rangpur Zone |  |  | 0 | 5.3987 | 1.5502 | 0 | 0 | 1.1496 | 0 | 0 | 8.0985
| Total |  |  | 137.4194 | 91.4003 | 44.8447 | 0 | 0.95616 | 3.9062 | 54.9687 | 0.07968 | 333.5752
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 445094190.77 |  | Hydro | 95616
|  |  |  | Coal | 590501605.4901 |  | Solar | 62986740.3716
|  |  |  | HFO | 794377340.452 |  | Import | 298887544.93
|  |  |  | HSD | 0 |  | Wind | 1166515.2
[5 empty] | Total: | 219,31,09,553 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0103 | Peak Hr Flow | 869.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 12425945.549 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.3053 | Peak Hr Flow | 1367.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 766 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6531 | Peak Hr Flow | 80.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 1026 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.9687 | Peak Hr Flow | 2316.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5268
|  |  |  | Chattogram |  | 0 |  | 1497
|  |  |  | Cumilla |  | 0 |  | 1458
|  |  |  | Mymensingh |  | 113 |  | 1248
|  |  |  | Sylhet |  | 0 |  | 530
|  |  |  | Khulna |  | 0 |  | 1824
|  |  |  | Barishal |  | 0 |  | 451
|  |  |  | Rajshahi |  | 0 |  | 1471
|  |  |  | Rangpur |  | 0 |  | 791
|  |  |  | Total |  | 113 |  | 14538
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1227.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:06 | 15:45 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Blast wall construction | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:06 | 15:44 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Blast wall construction | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:08 | 15:55 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast wall construction | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:08 | 15:54 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast wall construction | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:21 | 14:50 | Chandraghona-Kaptai 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual Maintenance
| 08:54 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Oil centrifuging Work
| 08:55 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Oil centrifuging work
| 09:46 | 14:25 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
BUS Isolator Maintenance Purposed.
| 10:08 | 14:08 | BSRM-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Disk
Cleaning and from BSRM 230/33kV end Due to Emergency Maintenance
| 10:50 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 10:58 |  | Bibiyana-3 400 MW tripped due to high vibration at the auxiliary cooling water pump.
| 11:05 | 16:50 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to TR-2 33 KV. CB maintenance
| 12:25 | 13:45 | Hathazari 230/132/33kV S/S MT-02 HT Forced S/D
| 12:25 | 13:45 | Hathazari 230/132/33kV S/S MT-02 LT Forced S/D
| 13:18 | 14:13 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Forced S/D Due to Work on other end.
| 14:02 | 14:12 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to TR-2 33 KV. CB maintenance
| 14:10 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 14:10 |  | Bibiyana-3 400 MW GT was sync.
| 14:20 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Isolator (Q89B) red hot maintenance purposed. and from BSRM 230/33kV end Due to Line
maintenance
| 14:30 |  | Rampal 1320 MW (BIFPCL) Tripped
| 15:59 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
| 15:59 |  | Bibiyana-3 400 MW ST sync.
| 16:13 | 16:47 | Gollamari 132/33kV S/S Tr-2 LT Forced S/D Due to kite remove work at 33kV site
| 16:14 | 16:46 | Gollamari 132/33kV S/S Tr-2 HT Forced S/D Due to Kite Remove Work
| 19:00 |  | Evening Peak Gen.14917 MW
| 19:19 |  | Siddhirganj GT2 was sync..
| 19:46 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U#2
| 19:46 |  | Rampal 1320 MW (BIFPCL) unit-2 sync.
| 21:57 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 22:29 | 23:19 | Narail 132/33kV S/S TR2 (413-T) LT Tripped showing Overcurrent protection-p 142 relays | [7 empty] | 31.0MW load
|  |  | Due to Trip for R-phase fault,overcurrent trip & earth fault. | [7 empty] | interrup.
| 22:29 | 23:16 | Narail 132/33kV S/S TR1 (403-T) LT Tripped showing Overcurrent protection-p142 relays Due | [7 empty] | 31.0MW load
|  |  | to Trip for B-phase fault,overcurrent trip & earth fault. | [7 empty] | interrup.
| 01:22 |  | Meghnaghat CCPP(Summit)-2 GT Synchronized with remarks:- None
| 01:22 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 02:07 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 05:11 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 05:11 |  | BIPTC S/S 20DF24 Tripped showing Impedance 21R relays Due to Tripped by Impedance 21R
| 05:11 |  | Meghnaghat CCPP(Summit)-2 ST Synchronized with remarks:- None
| 05:55 |  | BIPTC S/S 20DF11 Tripped showing 87.1 Differential Relay relays Due to ACF Backup
protection CPR04 fault
| 07:05 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ghorashal 230kV end Due to Shutdown
requisition from Dhamrai 132/33 kV SS for Insulator Disk cleaning. and from Ishurdi
230/132kVend.
| 07:35 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 132kV Bushing (R-Ph) & 132kV DS
(B-PH) Red Hot Maintenance work
| 07:35 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to 132kV Bushing (R-Ph) & 132kV DS
(B-PH) Red Hot Maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 6853200 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 320 | 9262800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9472000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 6977280 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 32 | 410544 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 900000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 7226394 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 100800 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 107 | 2129280 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 597939 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 477891 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 560400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 327960 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 480240 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 639100 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 362400 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 2346251 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3091968 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1059840 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 51 | 457920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1648800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 202974 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 919440 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 0 | 2032800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2558 | 58862221
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 13 | 165882.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133515 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 192000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 956160 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 162 | 3810302 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 52 | 1069709 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 48 | 615600 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 67 | 731837 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1509120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 405120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 769920 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26758 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 707564 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 248809 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 40 | 1034577 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 615360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 45 | 666164 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 72 | 431564 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26896361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 79680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 585 | 11032727.27 | U2 may be started
Chattogram Area Total |  |  |  |  | 4915.22 | 2753 | 52098729.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 215 | 4610000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 236 | 5458800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 240 | 6844000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 793368 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 756960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 568727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 27 | 855880 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 127 | 1565672 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 47 | 479360 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1203000 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 1838880 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1653120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 694685 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 321120 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2399700 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 72 | 799680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 980160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 462718 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1536 | 32285830
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 1019520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 3050400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1802400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 289000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298320 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 566280 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 303 | 7039620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 912000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 400200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3483245 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 34 | 564408 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116496 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 25 | 649440 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2016000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 162 | 4397700 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 418000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 336960 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7244000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 7285000 | cooling water temperature High due to IDCT Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7678600 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1541 | 35502049
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 869 | 22010327 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 76320 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 90368 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 228 | 6044832 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 66 | 615840 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 627120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 8574545 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1163 | 38039352
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 363 | 8006472 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 139392 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 187094 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 130 | 3001000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 25534545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5023410 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 20 | 186000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5957000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3451 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2218 | 48038364.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 46 | 275942 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 21 | 137862 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 30 | 192493 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 196 | 4861364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 28600 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 150 | 4639755 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 321 | 8658036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 162803 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 127080 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 17 | 24226 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 769056 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 85 | 984672 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 446016 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1367 | 31305278 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 311248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 655790 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2424.5 | 53610581
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1284655 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 172 | 4114000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 103 | 835641 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33670.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 714593 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 142457 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 973440 | -
Rangpur Area Total |  |  |  |  | 950 | 421 | 8098456.56
Eastern Grid Total |  |  |  |  | 16921.242 | 8691 | 185788449.87
Western Grid Total |  |  |  |  | 11614.5 | 6226.5 | 147786754.01
National Grid Total |  |  |  |  | 28535.742 | 14917.5 | 333575203.88
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-03-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9888.23 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4537.2 | MW
i) Dhaka area |  |  | 5268.23 |  | MW | i) Khulna area |  |  |  | 1824 | MW
ii) Chattogram area |  |  | 1497 |  | MW | ii) Barishal area |  |  |  | 451.2 | MW
iii) Cumilla area |  |  | 1458 |  | MW | iii) Rajshahi area |  |  |  | 1471 | MW
iv) Mymensingh area |  |  | 1135 |  | MW | iv) Rangpur area |  |  |  | 791 | MW
v) Sylhet area |  |  | 530 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14425.43 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 66 | 09:00 | 133 | Payra | 30 | 22:00
2 | AKSML | 11 | 05:00 | 68 | Jamalpur | 123 | 19:00 | 134 | Postogola | 54 | 19:00
3 | Aftabnagar | 38 | 18:30 | 69 | Jashore | 155 | 19:00 | 135 | Purbachal | 19 | 00:00
4 | Agargaon | 115 | 13:00 | 70 | Jhenaidah | 134 | 18:00 | 136 | Purbasadipur | 119 | 13:00
5 | Agrabad | 92 | 14:00 | 71 | Joydebpur | 145 | 17:00 | 137 | Rahanpur | 29 | 18:30
6 | Amnura | 43 | 13:00 | 72 | Joypurhat | 62 | 13:00 | 138 | Rahim | 22 | 15:00
7 | Ashuganj | 103 | 16:00 | 73 | Juldah | 15 | 13:00 | 139 | Rajbari | 78 | 21:00
8 | BSRM | 202 | 17:00 | 74 | KSRM | 28 | 23:00 | 140 | Rajendrapur | 136 | 15:00
9 | Bagerhat | 86 | 22:00 | 75 | Kabirpur | 271 | 17:00 | 141 | Rajshahi | 107 | 21:00
10 | Bajitpur | 46 | 00:00 | 76 | Kachua | 90 | 21:00 | 142 | Rajshahi-230 | 82 | 21:00
11 | Bakulia | 96 | 19:00 | 77 | Kallyanpur | 117 | 21:00 | 143 | Ramganj | 122 | 21:00
12 | Banani | 31.2 | 14:00 | 78 | Kalurghat | 43 | 14:00 | 144 | Rampur | 40 | 19:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kamrangirchar | 56 | 09:00 | 145 | Rangamati | 17 | 19:00
14 | Barapukuria | 61 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 131 | 17:00
15 | Barguna | 20 | 19:00 | 81 | Kazla | 96 | 00:00 | 147 | Ruppur | 7.4 | 15:00
16 | Barishal | 113 | 19:00 | 82 | Keranigonj | 85 | 21:00 | 148 | SSM | 8 | 10:00
17 | Barishal-230 | 98 | 21:00 | 83 | Khagrachori | 32 | 18:30 | 149 | Saidpur | 112 | 14:00
18 | Baroaulia | 58 | 22:00 | 84 | Khosba | 38 | 20:00 | 150 | Satkhira | 136 | 18:30
19 | Baroirhat | 61 | 19:00 | 85 | Khulna | 72 | 19:00 | 151 | Satmasjid | 104 | 19:00
20 | Bashundhara | 185 | 19:30 | 86 | Khulshi | 179 | 14:00 | 152 | Savar | 216 | 16:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 146 | 00:00 | 153 | SevenRings | 19.15 | 07:00
22 | Beanibazar | 60 | 18:30 | 88 | Kodda | 288 | 07:00 | 154 | ShahCement | 39 | 12:00
23 | Benapole | 72 | 18:30 | 89 | Kulaura | 48 | 19:00 | 155 | Shahjadpur | 95 | 21:00
24 | Bhaluka | 151 | 16:00 | 90 | Kurigram | 60 | 17:00 | 156 | Shahjibazar | 136 | 21:00
25 | Bhandaria | 51 | 21:00 | 91 | Kushtia | 140 | 00:00 | 157 | Shahmirpur | 57 | 00:00
26 | Bhangura | 42 | 14:00 | 92 | Lalbag | 64 | 13:00 | 158 | Shariatpur | 83 | 20:00
27 | Bheramara(GK) | 58 | 19:00 | 93 | Lalmonirhat | 55 | 17:00 | 159 | Sherpur | 162 | 19:30
28 | Bhulta | 272 | 17:00 | 94 | MI_Cement | 18 | 17:00 | 160 | Shikalbaha | 24 | 23:00
29 | Bog-Sherpur | 82 | 04:00 | 95 | Madanganj | 42 | 15:00 | 161 | Shitalakhya | 85.1 | 14:00
30 | Bogura | 144 | 00:00 | 96 | Madaripur | 123 | 21:00 | 162 | Sholosohor | 45 | 14:00
31 | Borhanuddin | 82 | 21:00 | 97 | Madartek | 90.11 | 20:00 | 163 | Shyampur | 184 | 10:00
32 | Brahmanbaria | 135 | 19:00 | 98 | Madunaghat | 49 | 13:00 | 164 | Siddhirganj | 126 | 10:00
33 | Cantonment | 134 | 13:00 | 99 | Magura | 69 | 19:30 | 165 | Sirajganj | 112 | 19:30
34 | Chandpur | 74 | 21:00 | 100 | Mahasthangarh | 68 | 19:30 | 166 | Sonargaon | 102 | 23:00
35 | Chandraghona | 35 | 19:00 | 101 | Manikganj | 147 | 19:30 | 167 | Sreemongol | 79 | 21:00
36 | Chapai | 63 | 03:00 | 102 | Maniknagar | 72 | 12:00 | 168 | Sreepur | 106 | 15:00
37 | Charsaidpur | 47 | 02:00 | 103 | Matarbari | 48 | 19:00 | 169 | Srinagar | 49.4 | 21:00
38 | Chauddagram | 77 | 18:30 | 104 | Matuail | 72 | 12:00 | 170 | Sunamganj | 54 | 20:00
39 | Chhatak | 26 | 18:30 | 105 | Millgate | 87 | 14:00 | 171 | Sylhet | 37 | 21:00
40 | Chowmuhani | 232 | 18:30 | 106 | Mirpur | 145 | 19:30 | 172 | Sylhet-132 | 105 | 20:00
41 | Chuadanga | 118 | 03:00 | 107 | Mirsorai | 10 | 00:00 | 173 | TK | 31.5 | 18:30
42 | Coxsbazar | 113 | 00:00 | 108 | Mirzapur | 49 | 19:00 | 174 | Tangail | 198 | 18:30
43 | Cumilla(N) | 172 | 19:00 | 109 | Mithapukur | 56 | 17:00 | 175 | Thakurgaon | 87 | 13:00
44 | Cumilla(S) | 175 | 14:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 132 | 18:30
45 | Daudkandi | 152 | 20:00 | 111 | Mogbazar | 148.7 | 13:00 | 177 | Ullahpara | 33 | 14:00
46 | Dhaka | 60 | 13:00 | 112 | Mongla | 45 | 19:00 | 178 | Ullon | 49 | 19:00
47 | Dhamrai | 124 | 10:00 | 113 | Motijheel | 40 | 15:00 | 179 | Uttara | 90 | 16:00
48 | Dhanmondi | 149 | 13:00 | 114 | Muktagacha | 39 | 19:00 | 180 | UttaraNew | 56 | 19:00
49 | Dohazari | 100 | 21:00 | 115 | Munshiganj | 117 | 21:00 | 181 | Zigatola | 81 | 19:00
50 | Faridpur | 166 | 21:00 | 116 | Muradnagar | 28 | 18:30
51 | Fatullah | 99 | 15:00 | 117 | Mymensingh | 206 | 20:00
52 | Fenchuganj | 36 | 21:00 | 118 | Naogaon | 131 | 13:00
53 | Feni | 118 | 19:00 | 119 | Narail | 63 | 22:00
54 | GPH | 91 | 02:00 | 120 | Narinda | 87 | 13:00
55 | Ghatail | 86 | 19:30 | 121 | Narshingdi | 175 | 01:00
56 | Ghorashal | 14 | 00:00 | 122 | Natore | 153 | 04:00
57 | Ghorashal-230 | 85 | 00:00 | 123 | Nawabganj | 63.2 | 21:00
58 | Goalpara | 36 | 19:00 | 124 | Netrakona | 134 | 03:00
59 | Gollamari | 90 | 19:30 | 125 | New | 88 | 14:00
60 | Gopalganj | 113 | 22:00 | 126 | Niamatpur | 101 | 13:00
61 | Gulshan | 124 | 14:00 | 127 | Noapara | 49 | 20:00
62 | Halishahar | 78 | 11:00 | 128 | PHP | 8 | 16:00
63 | HaripurSBU | 178 | 17:00 | 129 | Pabna | 118 | 03:00
64 | Hasnabad | 102 | 17:00 | 130 | Palashbari | 108 | 13:00
65 | Hathazari | 77 | 21:00 | 131 | Panchagarh | 49 | 17:00
66 | Ishurdi | 75 | 14:00 | 132 | Patuakhali | 73.2 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14380 | 27 |  | 14408.22
1:00 | 13542 | 130 |  | 13677.85
2:00 | 13134 | 110 |  | 13248.95
3:00 | 13175 | 100 |  | 13279.5
4:00 | 13442 | 40 |  | 13483.8
5:00 | 12469 | 0 |  | 12469
6:00 | 11909 | 0 |  | 11909
7:00 | 11826 | 0 |  | 11826
8:00 | 12283 | 0 |  | 12283
9:00 | 12802 | 44 |  | 12847.98
10:00 | 13219 | 53 |  | 13274.39
11:00 | 13013 | 263 |  | 13287.84
12:00 | 13596 | 107 |  | 13707.82
13:00 | 14309 | 119 |  | 14433.36
14:00 | 14571 | 113 |  | 14689.09
15:00 | 14162 | 143 |  | 14311.44
16:00 | 14211.8 | 114 |  | 14330.93
17:00 | 14381.97 | 53 |  | 14436.97
18:00 | 14307.92 | 89 |  | 14400.92
19:00 | 14917.5 | 113 |  | 15035.5
19:30 | 14641 | 96 |  | 14741
20:00 | 14260.5 | 86 |  | 14350.5
21:00 | 14571.5 | 0 |  | 14571.5
22:00 | 14509.5 | 0 |  | 14509.5
23:00 | 14075.5 | 0 |  | 14075.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7970 | 6410 | 14380 | DAILY GENERATION CURVE
00:30 | 7713.5 | 6247.5 | 13961
01:00 | 7457 | 6085 | 13542 | 16-03-2025
01:30 | 7310 | 6028 | 13338
02:00 | 7163 | 5971 | 13134
02:30 | 7199.5 | 5955 | 13154.5
03:00 | 7236 | 5939 | 13175
03:30 | 7288 | 6020.5 | 13308.5
04:00 | 7340 | 6102 | 13442
04:30 | 7009.5 | 5946 | 12955.5
05:00 | 6679 | 5790 | 12469
05:30 | 6536 | 5653 | 12189
06:00 | 6393 | 5516 | 11909
06:30 | 6333 | 5534.5 | 11867.5
07:00 | 6273 | 5553 | 11826
07:30 | 6362.5 | 5692 | 12054.5
08:00 | 6452 | 5831 | 12283
08:30 | 6584 | 5958.5 | 12542.5
09:00 | 6716 | 6086 | 12802
09:30 | 6850 | 6160.5 | 13010.5
10:00 | 6984 | 6235 | 13219
10:30 | 6903.5 | 6212.5 | 13116
11:00 | 6823 | 6190 | 13013
11:30 | 7059.5 | 6245 | 13304.5
12:00 | 7296 | 6300 | 13596
12:30 | 7684.5 | 6268 | 13952.5
13:00 | 8073 | 6236 | 14309
13:30 | 8224 | 6216 | 14440
14:00 | 8375 | 6196 | 14571
14:30 | 8353.5 | 6013 | 14366.5
15:00 | 8332 | 5830 | 14162
15:30 | 8273 | 5913.9 | 14186.9
16:00 | 8214 | 5997.8 | 14211.8
16:30 | 8254.285 | 6042.6 | 14296.885
17:00 | 8294.57 | 6087.4 | 14381.97
17:30 | 8269.465 | 6075.48 | 14344.945
18:00 | 8244.36 | 6063.56 | 14307.92
18:30 | 8467.68 | 6145.03 | 14612.71
19:00 | 8691 | 6226.5 | 14917.5
19:30 | 8492.5 | 6148.5 | 14641
20:00 | 8155 | 6105.5 | 14260.5
20:30 | 8170 | 6246 | 14416 |  | Executive Engineer
21:00 | 8185 | 6386.5 | 14571.5 |  | Network Operation Division
21:30 | 8079.5 | 6461 | 14540.5
22:00 | 7974 | 6535.5 | 14509.5
22:30 | 7853 | 6439.5 | 14292.5
23:00 | 7732 | 6343.5 | 14075.5

## En-Curve
QF-LDC-12
Date | 16-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3983 | 1659 | 920 | 0 | 76 | 1364 | 40 | 3689 | 0 | 712 | 1937 | 0 | 0 | 0 | 27 | DAILY ENERGY CURVE
00:30 | 3889 | 1606.5 | 919.5 | 0 | 75 | 1318 | 40 | 3573 | 0 | 697 | 1842.5 | 0 | 0 | 0.5 | 78.5 | 16-03-2025
01:00 | 3795 | 1554 | 919 | 0 | 74 | 1272 | 40 | 3457 | 0 | 682 | 1748 | 0 | 0 | 1 | 130
01:30 | 3629 | 1557.5 | 919 | 0 | 70 | 1270 | 40 | 3448 | 0 | 674.5 | 1729.5 | 0 | 0 | 0.5 | 120 | Energy Generated | 333.5752 |  | MKWHr
02:00 | 3463 | 1561 | 919 | 0 | 66 | 1268 | 40 | 3439 | 0 | 667 | 1711 | 0 | 0 | 0 | 110 | Energy not Served | 1.704 |  | MKWHr
02:30 | 3509 | 1613.5 | 919 | 0 | 67 | 1314.5 | 40 | 3563 | 0 | 580 | 1544.5 | 0 | 0 | 4 | 105 | Total Energy Requirement | 335.2792 |  | MKWHr
03:00 | 3555 | 1666 | 919 | 0 | 68 | 1361 | 40 | 3687 | 0 | 493 | 1378 | 0 | 0 | 8 | 100
03:30 | 3764 | 1658.5 | 919 | 0 | 69 | 1368 | 40 | 3805.5 | 0 | 432.5 | 1244 | 0 | 0 | 8 | 70
04:00 | 3973 | 1651 | 919 | 0 | 70 | 1375 | 40 | 3924 | 0 | 372 | 1110 | 0 | 0 | 8 | 40
04:30 | 4002.5 | 1673 | 919.5 | 0 | 70 | 1298 | 40 | 3754.5 | 0 | 277.5 | 912 | 0 | 0 | 8.5 | 20
05:00 | 4032 | 1695 | 920 | 0 | 70 | 1221 | 40 | 3585 | 0 | 183 | 714 | 0 | 0 | 9 | 0
05:30 | 4029 | 1627 | 919.5 | 0 | 67 | 1167 | 40 | 3515.5 | 0 | 177.5 | 642 | 0 | 0 | 4.5 | 0
06:00 | 4026 | 1559 | 919 | 0 | 64 | 1113 | 40 | 3446 | 0 | 172 | 570 | 0 | 0 | 0 | 0
06:30 | 4015.5 | 1545.5 | 919.5 | 0 | 61 | 1123.5 | 40 | 3448.5 | 21.5 | 155.5 | 537 | 0 | 0 | 0 | 0
07:00 | 4005 | 1532 | 920 | 0 | 58 | 1134 | 40 | 3451 | 43 | 139 | 504 | 0 | 0 | 0 | 0
07:30 | 4026 | 1553.5 | 894 | 0 | 60 | 1125.5 | 40 | 3604 | 86 | 139 | 526 | 0 | 0 | 0.5 | 0
08:00 | 4047 | 1575 | 868 | 0 | 62 | 1117 | 40 | 3757 | 129 | 139 | 548 | 0 | 0 | 1 | 0
08:30 | 4039.5 | 1634 | 868 | 0 | 59 | 1169 | 40 | 3813.5 | 206 | 140 | 573 | 0 | 0 | 0.5 | 22
09:00 | 4032 | 1693 | 868 | 0 | 56 | 1221 | 40 | 3870 | 283 | 141 | 598 | 0 | 0 | 0 | 44
09:30 | 3954.5 | 1644.5 | 891.5 | 0 | 59 | 1283.5 | 40 | 3810.5 | 380.5 | 168.5 | 778 | 0 | 0 | 0 | 48.5
10:00 | 3877 | 1596 | 915 | 0 | 62 | 1346 | 40 | 3751 | 478 | 196 | 958 | 0 | 0 | 0 | 53
10:30 | 3704 | 1614.5 | 914.5 | 0 | 62 | 1351 | 40 | 3696 | 528 | 219 | 987 | 0 | 0 | 0 | 158
11:00 | 3531 | 1633 | 914 | 0 | 62 | 1356 | 40 | 3641 | 578 | 242 | 1016 | 0 | 0 | 0 | 263
11:30 | 3517.5 | 1672 | 914.5 | 0 | 66 | 1360 | 40 | 3633.5 | 605 | 268.5 | 1227.5 | 0 | 0 | 0 | 185
12:00 | 3504 | 1711 | 915 | 0 | 70 | 1364 | 40 | 3626 | 632 | 295 | 1439 | 0 | 0 | 0 | 107
12:30 | 3478.5 | 1725 | 915 | 0 | 70 | 1361.5 | 40 | 3723.5 | 608 | 344.5 | 1683.5 | 0 | 0 | 3 | 113
13:00 | 3453 | 1739 | 915 | 0 | 70 | 1359 | 40 | 3821 | 584 | 394 | 1928 | 0 | 0 | 6 | 119
13:30 | 3484.5 | 1744.5 | 915 | 0 | 75 | 1362.5 | 40 | 3795.5 | 551.5 | 414 | 2047.5 | 0 | 0 | 10 | 116
14:00 | 3516 | 1750 | 915 | 0 | 80 | 1366 | 40 | 3770 | 519 | 434 | 2167 | 0 | 0 | 14 | 113
14:30 | 3570.5 | 1752 | 915 | 0 | 75 | 1366.5 | 40 | 3618 | 440.5 | 442 | 2136 | 0 | 0 | 11 | 128
15:00 | 3625 | 1754 | 915 | 0 | 70 | 1367 | 40 | 3466 | 362 | 450 | 2105 | 0 | 0 | 8 | 143
15:30 | 3593.5 | 1725 | 915.5 | 0 | 74 | 1364.5 | 40 | 3599 | 298.4 | 478.5 | 2088 | 0 | 0 | 10.5 | 128.5
16:00 | 3562 | 1696 | 916 | 0 | 78 | 1362 | 40 | 3732 | 234.8 | 507 | 2071 | 0 | 0 | 13 | 114
16:30 | 3674.5 | 1715.75 | 915.5 | 0 | 75 | 1362 | 40 | 3808.5 | 162.035 | 552 | 1982.1 | 0 | 0 | 9.5 | 83.5
17:00 | 3787 | 1735.5 | 915 | 0 | 72 | 1362 | 40 | 3885 | 89.27 | 597 | 1893.2 | 0 | 0 | 6 | 53
17:30 | 3841.5 | 1736 | 915 | 0 | 76 | 1364.5 | 40 | 3795 | 45.745 | 585 | 1940.7 | 0 | 0 | 5.5 | 71
18:00 | 3896 | 1736.5 | 915 | 0 | 80 | 1367 | 40 | 3705 | 2.22 | 573 | 1988.2 | 0 | 0 | 5 | 89
18:30 | 3764.5 | 1745.5 | 892 | 0 | 80 | 1367 | 40 | 3766 | 1.11 | 605 | 2345.6 | 0 | 0 | 6 | 101
19:00 | 3633 | 1754.5 | 869 | 0 | 80 | 1367 | 40 | 3827 | 0 | 637 | 2703 | 0 | 0 | 7 | 113
19:30 | 3632 | 1739.5 | 869 | 0 | 76 | 1350 | 40 | 3928 | 0 | 636 | 2364.5 | 0 | 0 | 6 | 96
20:00 | 3821 | 1656.5 | 868 | 0 | 76 | 1366 | 40 | 4064 | 0 | 577 | 1789 | 0 | 0 | 3 | 86
20:30 | 3975 | 1714 | 891.5 | 0 | 78 | 1360.5 | 40 | 4213.5 | 0 | 508.5 | 1633.5 | 0 | 0 | 1.5 | 43
21:00 | 4129 | 1771.5 | 915 | 0 | 80 | 1355 | 40 | 4363 | 0 | 440 | 1478 | 0 | 0 | 0 | 0
21:30 | 4158 | 1803.5 | 915.5 | 0 | 78 | 1355.5 | 40 | 4387.5 | 0 | 368.5 | 1433 | 0 | 0 | 1 | 0
22:00 | 4187 | 1835.5 | 916 | 0 | 76 | 1356 | 40 | 4412 | 0 | 297 | 1388 | 0 | 0 | 2 | 0
22:30 | 4194 | 1853 | 915.5 | 0 | 77 | 1357 | 40 | 4360.5 | 0 | 275.5 | 1219 | 0 | 0 | 1 | 0
23:00 | 4201 | 1870.5 | 915 | 0 | 78 | 1358 | 40 | 4309 | 0 | 254 | 1050 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 02:00 | 369 | 16:00 | Payra | 414 | 02:00 | 405 | 16:00
Ashuganj | 395 | 13:00 | 380 | 14:00 | Rahanpur | 396 | 02:00 | 386 | 11:00
Bhulta | 398 | 18:00 | 375 | 11:00 | Rampal | 401 | 02:00 | 374 | 16:00
Bibiana | 393 | 04:00 | 380 | 11:00
BIPTC | 396 | 05:00 | 390 | 15:00
Bogura | 382 | 02:00 | 370 | 04:00
Gopalganj | 398 | 06:00 | 377 | 16:00
Kaliakoir | 365 | 02:00 | 348 | 12:00
Madunaghat | 400 | 02:00 | 386 | 22:00
Meghnaghat | 389 | 02:00 | 371 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 03:00 | 214 | 12:00 | Keranigonj | 224 | 02:00 | 212 | 14:00
AKSML | 233 | 00:00 | 223 | 22:00 | Khulna(S) | 231 | 02:00 | 215 | 16:00
Aminbazar | 226 | 03:00 | 215 | 15:00 | Madunaghat | 235 | 19:00 | 226 | 22:00
Ashuganj | 230 | 03:00 | 219 | 14:00 | Madunaghat-400 | 235 | 02:00 | 227 | 22:00
Ashuganj-400 | 229 | 06:00 | 222 | 13:00 | Maniknagar | 221 | 03:00 | 209 | 16:00
Baghabari | 233 | 02:00 | 225 | 11:00 | Meghnaghat | 230 | 02:00 | 219 | 15:00
Barapukuria | 224 | 19:00 | 216 | 09:00 | Meghnaghat-400 | 225 | 02:00 | 215 | 14:00
Barapukuria-230 | 224 | 19:00 | 216 | 09:00 | Mirsorai | 231 | 16:00 | 221 | 11:00
Barishal | 234 | 10:00 | 223 | 16:00 | Rajshahi | 234 | 03:00 | 222 | 14:00
Bheramara | 234 | 06:00 | 223 | 14:00 | Rampal | 230 | 02:00 | 213 | 16:00
Bhulta | 223 | 06:00 | 209 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 04:00 | 219 | 13:00 | Rampura | 222 | 06:00 | 208 | 12:00
BIPTC | 236 | 06:00 | 222 | 14:00 | Shikalbaha | 234 | 02:00 | 223 | 21:00
Bogura | 234 | 02:00 | 226 | 09:00 | Shyampur | 223 | 02:00 | 212 | 14:00
Bogura-400 | 234 | 02:00 | 226 | 09:00 | Siddhirganj | 221 | 03:00 | 213 | 12:00
Borhanuddin | 239 | 07:00 | 232 | 22:00 | Sirajgonj | 238 | 02:00 | 232 | 12:00
BSRM | 229 | 02:00 | 219 | 23:00 | Sreepur | 229 | 02:00 | 219 | 12:00
Cumilla(N) | 222 | 02:00 | 213 | 12:00 | Tongi | 223 | 04:00 | 210 | 12:00
Faridpur | 230 | 02:00 | 218 | 15:00
Fenchuganj | 229 | 05:00 | 224 | 16:00
Ghorashal | 230 | 00:00 | 220 | 10:00
Ghorashal-230 | 224 | 02:00 | 212 | 12:00
Gopalganj | 229 | 02:00 | 217 | 16:00
GPH | 232 | 02:00 | 224 | 23:00
Haripur | 222 | 01:00 | 209 | 14:00
Hasnabad | 223 | 02:00 | 212 | 14:00
Hathazari | 235 | 19:00 | 227 | 23:00
Ishurdi | 235 | 02:00 | 225 | 14:00
Jhenaidah | 229 | 06:00 | 214 | 15:00
Kaliakoir | 227 | 02:00 | 214 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 06:00 | 121 | 11:00 | Madunaghat | 135 | 19:00 | 129 | 21:00
Agargaon | 135 | 02:00 | 126 | 12:00 | Magura | 132 | 06:00 | 120 | 14:00
Agrabad | 135 | 18:00 | 128 | 09:00 | Mahasthangarh | 131 | 02:00 | 123 | 09:00
AKS | 132 | 03:00 | 126 | 09:00 | Manikganj | 128 | 19:30 | 119 | 15:00
Aminbazar | 132 | 01:00 | 122 | 16:00 | Maniknagar | 130 | 03:00 | 121 | 12:00
Amnura | 135 | 00:00 | 125 | 12:00 | Matarbari | 122 | 13:00 | 113 | 21:00
Ashuganj | 137 | 17:00 | 130 | 11:00 | Matuail | 129 | 04:00 | 121 | 11:00
Bagerhat | 130 | 06:00 | 115 | 16:00 | Millgate | 132 | 01:00 | 122 | 11:00
Bajitpur | 129 | 06:00 | 120 | 13:00 | Mirpur | 131 | 02:00 | 122 | 17:00
Bakulia | 137 | 18:30 | 128 | 23:00 | Mirzapur | 126 | 01:00 | 120 | 12:00
Banani | 132 | 04:00 | 121 | 11:00 | Mithapukur | 133 | 18:30 | 121 | 09:00
Bangabhaban | 130 | 02:00 | 120 | 16:00 | MI_Cement | 129 | 02:00 | 121.5 | 12:00
Barapukuria | 138 | 18:30 | 130 | 09:00 | Modern | 0 | 00:00 | 0 | 00:00
Barguna | 135 | 00:00 | 129 | 22:00 | Mogbazar | 132 | 04:00 | 122 | 12:00
Barishal | 130 | 06:00 | 120 | 22:00 | Mongla | 134 | 05:00 | 115 | 17:00
Barishal-230 | 130 | 02:00 | 122 | 16:00 | Motijheel | 130 | 02:00 | 120 | 16:00
Baroaulia | 134 | 00:00 | 128 | 22:00 | Muktagacha | 132 | 16:00 | 122 | 19:00
Baroirhat | 125 | 02:00 | 117 | 23:00 | Munshiganj | 129 | 03:00 | 122 | 12:00
Bashundhara | 132 | 02:00 | 121 | 11:00 | Muradnagar | 126 | 21:00 | 117 | 14:00
BashundharaCement | 128 | 01:00 | 120 | 12:00 | Mymensingh | 133 | 08:00 | 108 | 12:00
Beanibazar | 132 | 02:00 | 126 | 15:00 | Naogaon | 128 | 01:00 | 120 | 08:00
Benapole | 128 | 06:00 | 114 | 14:00 | Narail | 131 | 06:00 | 118 | 18:00
Bhaluka | 125 | 01:00 | 116 | 12:00 | Narinda | 130 | 03:00 | 121 | 12:00
Bhandaria | 125 | 07:00 | 111 | 22:00 | Narshingdi | 132 | 20:00 | 113 | 13:00
Bhangura | 132 | 02:00 | 126 | 14:00 | Natore | 132 | 06:00 | 125 | 14:00
Bheramara | 136 | 06:00 | 130 | 14:00 | Nawabganj | 132 | 03:00 | 123 | 11:00
Bheramara(GK) | 135 | 03:00 | 130 | 14:00 | Netrakona | 121 | 05:00 | 106 | 12:00
Bhulta | 126 | 20:00 | 115 | 14:00 | New | 133 | 18:00 | 122 | 11:00
Bog-Sherpur | 131 | 02:00 | 124 | 09:00 | Niamatpur | 134 | 06:00 | 129 | 09:00
Bogura | 134 | 18:30 | 126 | 09:00 | Noapara | 132 | 06:00 | 119 | 16:00
Bogura-230 | 134 | 02:00 | 127 | 09:00 | Pabna | 133 | 02:00 | 128 | 12:00
Brahmanbaria | 131 | 20:00 | 119 | 12:00 | Palashbari | 129 | 02:00 | 119 | 09:00
Cantonment | 135 | 03:00 | 125 | 15:00 | Panchagarh | 139 | 19:00 | 119 | 09:00
Chandpur | 125 | 18:30 | 112 | 00:00 | Patuakhali | 136 | 00:00 | 131 | 16:00
Chandraghona | 134 | 19:00 | 129 | 11:00 | Payra | 137 | 02:00 | 132 | 21:00
Chapai | 132 | 19:30 | 126 | 12:00 | PHP | 124 | 02:00 | 115 | 13:00
Charsaidpur | 129 | 02:00 | 122 | 12:00 | Postogola | 131 | 02:00 | 123 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 123 | 02:00 | 116 | 14:00 | Purbachal | 132 | 02:00 | 120 | 14:00
Chhatak | 133 | 03:00 | 125 | 18:30 | Purbasadipur | 133 | 18:30 | 117 | 09:00
Chowmuhani | 120 | 18:00 | 109 | 14:00 | Rahanpur | 138 | 05:00 | 131 | 09:00
Chuadanga | 127 | 08:00 | 117 | 16:00 | Rahanpur-400 | 135 | 01:00 | 131 | 12:00
Coxsbazar | 122 | 01:00 | 114 | 22:00 | Rahim | 129 | 02:00 | 122 | 14:00
Cumilla(N) | 127 | 02:00 | 120 | 14:00 | Rajbari | 128 | 06:00 | 118 | 22:00
Cumilla(S) | 130 | 02:00 | 118 | 14:00 | Rajendrapur | 136 | 19:30 | 117 | 12:00
Daudkandi | 124 | 21:00 | 115 | 23:00 | Rajshahi | 133 | 18:30 | 127 | 14:00
Dhaka | 132 | 03:00 | 121 | 11:00 | Rajshahi-230 | 135 | 02:00 | 120 | 12:00
Dhamrai | 127 | 01:00 | 120 | 11:00 | Ramganj | 118 | 18:00 | 107 | 14:00
Dhanmondi | 132.6 | 06:00 | 122 | 12:00 | Rampur | 134 | 03:00 | 127 | 23:00
Dohazari | 130 | 13:00 | 121 | 21:00 | Rampura | 132 | 06:00 | 122 | 11:00
Faridpur | 129 | 04:00 | 122 | 22:00 | Rangamati | 134 | 18:00 | 128 | 22:00
Fatullah | 130 | 03:00 | 122 | 15:00 | Rangpur | 132 | 19:00 | 121 | 08:00
Fenchuganj | 133 | 04:00 | 130 | 14:00 | Ruppur | 136 | 06:00 | 131 | 14:00
Feni | 124 | 18:00 | 116 | 14:00 | Saidpur | 133 | 18:30 | 120 | 09:00
Ghatail | 126 | 06:00 | 119 | 14:00 | Satkhira | 130 | 06:00 | 113 | 19:00
Ghorashal | 135 | 19:00 | 127 | 10:00 | Satmasjid | 135 | 03:00 | 126 | 12:00
Goalpara | 134 | 02:00 | 121 | 14:00 | Savar | 132 | 04:00 | 122 | 16:00
Gollamari | 134 | 06:00 | 122 | 16:00 | SevenRings | 135 | 02:00 | 127 | 12:00
Gopalganj | 133 | 02:00 | 122 | 16:00 | ShahCement | 129 | 02:00 | 122 | 12:00
Gopalganj-400 | 135 | 02:00 | 126 | 18:00 | Shahjadpur | 136 | 01:00 | 131 | 08:00
Gulshan | 131 | 02:00 | 121 | 12:00 | Shahjibazar | 130 | 20:00 | 123 | 12:00
Halishahar | 135 | 19:00 | 127 | 21:00 | Shahmirpur | 137 | 19:00 | 130 | 11:00
Haripur | 130 | 03:00 | 122 | 15:00 | Shariatpur | 132 | 07:00 | 123 | 19:00
HaripurSBU | 130 | 03:00 | 123 | 13:00 | Sherpur | 135 | 09:00 | 122 | 19:00
Hasnabad | 131 | 04:00 | 30 | 03:00 | Shikalbaha | 126 | 19:00 | 118 | 23:00
Hathazari | 136 | 18:30 | 130 | 20:00 | Shikalbaha-230 | 138 | 18:30 | 129 | 23:00
Ishurdi | 137 | 06:00 | 132 | 14:00 | Shitalakhya | 129 | 02:00 | 121.5 | 12:00
Jaldhaka | 135 | 18:30 | 118 | 09:00 | Sholosohor | 135 | 19:00 | 129 | 22:00
Jamalpur | 138 | 10:00 | 126 | 02:00 | Shyampur | 135 | 18:00 | 125 | 10:00
Jashore | 127 | 06:00 | 116 | 20:00 | Shyampur-230 | 129 | 02:00 | 122 | 12:00
Jhenaidah | 133 | 06:00 | 121 | 14:00 | Siddhirganj | 129 | 01:00 | 122 | 12:00
Jhenaidah-230 | 133 | 06:00 | 122 | 14:00 | Sirajganj | 130 | 06:00 | 122 | 09:00
Joydebpur | 138 | 19:30 | 120 | 13:00 | Sonargaon | 128 | 02:00 | 120 | 13:00
Joypurhat | 127 | 02:00 | 116 | 09:00 | Sreemongol | 128 | 06:00 | 124 | 14:00
Juldah | 135 | 00:00 | 128 | 23:00 | Sreepur | 128 | 02:00 | 121 | 12:00
Kabirpur | 133 | 19:30 | 120 | 11:00 | Srinagar | 131 | 02:00 | 122 | 15:00
Kachua | 123 | 18:00 | 115 | 13:00 | SSM | 139 | 18:30 | 130 | 08:00
Kaliakoir | 131 | 02:00 | 122 | 11:00 | Sunamganj | 132 | 00:00 | 123 | 22:00
Kallyanpur | 131 | 01:00 | 123 | 15:00 | Sylhet | 132 | 03:00 | 126 | 17:00
Kalurghat | 135 | 00:00 | 129 | 23:00 | Sylhet-132 | 133 | 03:00 | 128 | 15:00
Kamrangirchar | 130 | 01:00 | 122 | 15:00 | Tangail | 126 | 01:00 | 118 | 14:00
Kaptai | 132 | 02:00 | 123 | 15:00 | Thakurgaon | 138 | 19:00 | 116 | 09:00
Kazla | 130 | 03:00 | 121 | 12:00 | TK | 137 | 18:30 | 130 | 21:00
Keranigonj | 132 | 02:00 | 123 | 15:00 | Tongi | 134 | 03:00 | 126 | 12:00
Khagrachori | 132 | 01:00 | 126 | 22:00 | Ullahpara | 130 | 01:00 | 125 | 09:00
Khosba | 124 | 03:00 | 117 | 14:00 | Ullon | 132 | 06:00 | 121 | 11:00
Khulna | 130 | 07:00 | 119 | 16:00 | Uttara | 132 | 03:00 | 122 | 11:00
Khulna(S) | 134 | 02:00 | 122 | 16:00 | UttaraNew | 132 | 19:00 | 122 | 16:00
Khulshi | 133 | 01:00 | 126 | 23:00 | Zigatola | 132 | 03:00 | 123 | 15:00
Kishoreganj | 126 | 18:30 | 118 | 12:00
Kodda | 131 | 19:00 | 119 | 12:00
KSRM | 134 | 02:00 | 128 | 21:00
Kulaura | 132 | 01:00 | 128 | 23:00
Kurigram | 132 | 19:00 | 119 | 09:00
Kushtia | 134 | 06:00 | 125 | 14:00
Lalbag | 132 | 02:00 | 122 | 15:00
Lalmonirhat | 130 | 18:30 | 120 | 14:00
Madanganj | 128 | 01:00 | 120 | 12:00
Madaripur | 133 | 06:00 | 127 | 16:00
Madartek | 132 | 06:00 | 122 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division