## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-03-2025 | [28 empty] | Date: | 17-03-2025 | [28 empty] | Date: | 17-03-2025 | [28 empty] | Date: | 17-03-2025 | [28 empty] | Date: | 17-03-2025 | [18 empty] | Date: | 17-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 160 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 24 | 0 | 91 | 30 | 64 | 0 | 0 | 72 | 22 | 16 | 450 | 290 | 0 | 0 | 35 | 31 | 320 | 206 | 0 | 0 | 108 | 21 | 20 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 21 | 426 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1160 | 0 | 51 | 10 | 65 | 0 | 235 | 285 | 27 | 181 | 33 | 20 | 50 | 84 | 58 | 17 | 114 | 78 | 19 | 0 | 0 | 305 | 320 | 385 | 0 | 39 | 0 | 5 | 163 | 8 | 0 | 85 | 25 | 0 | 17 | 164 | 0 | 48 | 58 | 34 | 0 | 0 | 12 | 7287 | 915 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 34 | 1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 7 | 0 | 185 | 0 | 380 | 0 | 0 | 2.5 | 173 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 130 | 220 | 0 | 492 | 1050 | 0 | 6312.5 | 13599.5 | 86.97
01:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 34 | 0 | 105 | 16 | 64 | 0 | 0 | 35 | 22 | 0 | 450 | 264 | 0 | 0 | 17 | 32 | 320 | 202 | 0 | 0 | 35 | 21 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 21 | 505 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1160 | 0 | 51 | 10 | 45 | 0 | 235 | 285 | 10 | 188 | 33 | 41 | 50 | 53 | 39 | 17 | 114 | 72 | 52 | 0 | 0 | 285 | 320 | 385 | 0 | 39 | 0 | 5 | 163 | 8 | 0 | 85 | 25 | 0 | 17 | 164 | 0 | 48 | 58 | 34 | 0 | 0 | 12 | 7111 | 913 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 34 | 1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 6 | 0 | 140 | 0 | 307 | 0 | 0 | 2.5 | 174 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 522 | 1040 | 0 | 6162.5 | 13273.5 | 86.96
02:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 35 | 0 | 105 | 16 | 64 | 0 | 0 | 35 | 22 | 0 | 340 | 285 | 62 | 0 | 17 | 32 | 260 | 205 | 0 | 0 | 35 | 21 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 21 | 517 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 0 | 51 | 10 | 45 | 0 | 235 | 285 | 10 | 191 | 33 | 51 | 50 | 51 | 28 | 17 | 114 | 68 | 52 | 0 | 0 | 285 | 320 | 385 | 0 | 40 | 0 | 5 | 120 | 8 | 0 | 85 | 25 | 0 | 17 | 164 | 0 | 49 | 58 | 34 | 0 | 0 | 12 | 6933 | 916 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 34 | 1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 6 | 0 | 140 | 0 | 308 | 0 | 0 | 2.5 | 174 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 130 | 180 | 0 | 523 | 990 | 0 | 5931.5 | 12864.5 | 86.96
03:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 35 | 0 | 105 | 48 | 64 | 0 | 17 | 17 | 22 | 0 | 340 | 275 | 62 | 0 | 17 | 32 | 260 | 206 | 0 | 0 | 35 | 21 | 20 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 23 | 515 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1120 | 0 | 51 | 10 | 45 | 0 | 235 | 285 | 10 | 191 | 30 | 51 | 50 | 51 | 29 | 17 | 114 | 68 | 52 | 0 | 0 | 290 | 320 | 385 | 0 | 40 | 0 | 5 | 120 | 8 | 0 | 85 | 25 | 0 | 17 | 164 | 0 | 49 | 81 | 35 | 0 | 0 | 12 | 7008 | 916 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 34 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 22 | 0 | 140 | 0 | 308 | 0 | 0 | 2.5 | 176 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 130 | 180 | 0 | 581 | 1010 | 0 | 6088.5 | 13096.5 | 86.95
04:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 35 | 0 | 105 | 47 | 0 | 0 | 35 | 17 | 22 | 0 | 380 | 268 | 62 | 0 | 0 | 25 | 315 | 207 | 0 | 0 | 35 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 33 | 500 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1091 | 0 | 51 | 0 | 45 | 0 | 235 | 285 | 10 | 194 | 30 | 51 | 50 | 51 | 28 | 17 | 114 | 70 | 52 | 0 | 0 | 275 | 320 | 385 | 0 | 40 | 0 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 0 | 78 | 132 | 35 | 0 | 0 | 12 | 7028 | 917 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 86 | 0 | 140 | 0 | 309 | 0 | 0 | 2.5 | 178 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 130 | 220 | 0 | 571 | 1100 | 0 | 6080.5 | 13108.5 | 86.95
05:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 35 | 0 | 105 | 31 | 0 | 0 | 35 | 17 | 22 | 0 | 380 | 300 | 62 | 0 | 0 | 25 | 310 | 202 | 0 | 0 | 35 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 33 | 510 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 951 | 0 | 51 | 0 | 16 | 0 | 235 | 285 | 5 | 197 | 30 | 51 | 50 | 51 | 29 | 17 | 114 | 70 | 52 | 0 | 0 | 290 | 320 | 335 | 0 | 40 | 0 | 5 | 120 | 16 | 0 | 86 | 30 | 0 | 17 | 164 | 0 | 79 | 136 | 35 | 0 | 0 | 12 | 6806 | 916 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 0 | 1010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 153 | 0 | 140 | 0 | 321 | 0 | 0 | 2.5 | 175 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 130 | 220 | 0 | 476 | 920 | 0 | 5560.5 | 12366.5 | 86.94
06:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 35 | 0 | 105 | 31 | 0 | 0 | 17 | 17 | 22 | 0 | 340 | 263 | 123 | 0 | 0 | 32 | 310 | 203 | 0 | 0 | 35 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 33 | 567 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 16 | 0 | 210 | 285 | 5 | 182 | 30 | 40 | 50 | 51 | 29 | 17 | 70 | 68 | 25 | 0 | 0 | 285 | 320 | 335 | 0 | 40 | 0 | 5 | 120 | 16 | 0 | 86 | 30 | 0 | 17 | 165 | 0 | 55 | 116 | 35 | 0 | 0 | 12 | 6526 | 916 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 170 | 0 | 140 | 0 | 308 | 0 | 0 | 2.5 | 173 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 130 | 180 | 0 | 444 | 880 | 0 | 5197.5 | 11723.5 | 86.94
07:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 35 | 0 | 105 | 31 | 0 | 0 | 0 | 17 | 22 | 0 | 340 | 301 | 125 | 0 | 0 | 32 | 310 | 205 | 0 | 3 | 17 | 25 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 11 | 560 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 850 | 2 | 51 | 0 | 16 | 0 | 180 | 285 | 5 | 198 | 33 | 17 | 50 | 51 | 20 | 17 | 70 | 54 | 25 | 6 | 0 | 290 | 320 | 335 | 0 | 40 | 0 | 5 | 120 | 16 | 0 | 86 | 30 | 0 | 17 | 165 | 0 | 55 | 115 | 44 | 0 | 5.68 | 12 | 6487.68 | 916 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.93 | 408 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3.07 | 150 | 0 | 170 | 0 | 140 | 0 | 328 | 0 | 0.32 | 2.5 | 173 | 60 | 0 | 5 | 0 | 0 | 0 | 0.4 | 21 | 0.03 | 0 | 200 | 8 | 130 | 180 | 0 | 446 | 850 | 0 | 5236.25 | 11723.93 | 86.93
08:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 35 | 0 | 112 | 31 | 0 | 0 | 0 | 17 | 22 | 0 | 340 | 303 | 142 | 0 | 0 | 32 | 315 | 197 | 0 | 6 | 35 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 4 | 563 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 865 | 7 | 51 | 0 | 16 | 0 | 180 | 285 | 5 | 201 | 33 | 16 | 50 | 51 | 9 | 17 | 52 | 64 | 8 | 5 | 0 | 300 | 320 | 385 | 0 | 40 | 0 | 5 | 163 | 16 | 0 | 86 | 30 | 0 | 17 | 165 | 0 | 79 | 135 | 43 | 1 | 16.43 | 12 | 6683.43 | 867 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.54 | 409 | 0 | 822.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 17.47 | 150 | 0 | 170 | 0 | 140 | 0 | 414 | 0 | 1.76 | 2.5 | 171 | 58 | 0 | 7 | 0 | 0 | 0 | 1.6 | 70 | 0.08 | 0 | 200 | 7 | 130 | 220 | 0 | 447 | 860 | 0 | 5408.72 | 12092.15 | 86.93
09:00 | 0 | 0 | 12 | 160 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 0 | 132 | 31 | 0 | 0 | 0 | 17 | 22 | 0 | 450 | 298 | 223 | 0 | 0 | 30 | 310 | 144 | 0 | 18 | 35 | 25 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 855 | 12 | 51 | 0 | 43 | 0 | 240 | 285 | 12 | 203 | 33 | 0 | 50 | 51 | 9 | 17 | 52 | 62 | 8 | 9 | 0 | 310 | 320 | 387 | 0 | 39 | 0 | 5 | 163 | 16 | 0 | 86 | 30 | 0 | 17 | 165 | 0 | 79 | 136 | 33 | 1 | 28.84 | 12 | 6973.84 | 867 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.96 | 412 | 0 | 914.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 13.58 | 166 | 0 | 165 | 0 | 142 | 0 | 414 | 0 | 1.52 | 5.5 | 172 | 58 | 0 | 17 | 0 | 0 | 0 | 2.4 | 76 | 0.1 | 0 | 220 | 6 | 130 | 220 | 0 | 446 | 900 | 0 | 5596.09 | 12569.93 | 86.92
10:00 | 0 | 0 | 17 | 160 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 7 | 38 | 0 | 149 | 46 | 15 | 0 | 17 | 35 | 22 | 0 | 450 | 282 | 304 | 0 | 17 | 28 | 314 | 143 | 0 | 26 | 35 | 24 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 3 | 80 | 0 | 7 | 575 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 852 | 15 | 51 | 5 | 110 | 0 | 240 | 285 | 42 | 182 | 33 | 0 | 50 | 51 | 9 | 17 | 88 | 66 | 10 | 41 | 0 | 305 | 320 | 372 | 0 | 39 | 0 | 5 | 163 | 16 | 0 | 86 | 30 | 0 | 17 | 165 | 0 | 79 | 136 | 28 | 1 | 29.75 | 12 | 7374.75 | 914 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.33 | 378 | 0 | 1053.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 15.31 | 183 | 0 | 161 | 0 | 154 | 0 | 414 | 0 | 1.57 | 5.5 | 175 | 58 | 0 | 26 | 0 | 0 | 0 | 5.8 | 88 | 0.26 | 0 | 164 | 6 | 120 | 220 | 0 | 445 | 850 | 0 | 5739.11 | 13113.86 | 86.92
11:00 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 51 | 0 | 149 | 92 | 45 | 0 | 35 | 54 | 22 | 9 | 450 | 305 | 365 | 0 | 17 | 24 | 261 | 142 | 0 | 26 | 100 | 24 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 48 | 0 | 4 | 60 | 0 | 2 | 665 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 795 | 18 | 51 | 50 | 110 | 0 | 235 | 285 | 40 | 181 | 30 | 0 | 50 | 51 | 9 | 17 | 88 | 62 | 43 | 52 | 1 | 290 | 320 | 339 | 0 | 39 | 0 | 5 | 163 | 16 | 0 | 83 | 30 | 0 | 17 | 165 | 0 | 79 | 135 | 27 | 0 | 10.71 | 12 | 7475.71 | 915 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.84 | 378 | 0 | 1160.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 15.64 | 178 | 0 | 150 | 0 | 155 | 0 | 414 | 0 | 1.32 | 5.5 | 174 | 57 | 0 | 15 | 0 | 0 | 0 | 0 | 166 | 0.39 | 0 | 150 | 6 | 120 | 200 | 0 | 445 | 820 | 0 | 5803.76 | 13279.47 | 86.91
12:00 | 0 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 51 | 0 | 143 | 86 | 46 | 0 | 55 | 90 | 22 | 16 | 450 | 299 | 440 | 0 | 30 | 24 | 287 | 96 | 0 | 14 | 125 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 74 | 12 | 3 | 46 | 0 | 2 | 683 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 856 | 18 | 51 | 68 | 45 | 0 | 225 | 285 | 7 | 186 | 32 | 0 | 50 | 51 | 9 | 14 | 98 | 64 | 52 | 56 | 48 | 315 | 320 | 375 | 0 | 38 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 165 | 0 | 79 | 135 | 27 | 2 | 4.89 | 12 | 7895.89 | 914 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.65 | 377 | 0 | 1161.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 8.75 | 172 | 0 | 145 | 0 | 149 | 0 | 414 | 0 | 0 | 5.5 | 176 | 58 | 0 | 37 | 0 | 0 | 0 | 0 | 62 | 0.6 | 0 | 150 | 7 | 130 | 200 | 0 | 444 | 660 | 0 | 5536.36 | 13432.25 | 86.91
13:00 | 0 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 47 | 0 | 148 | 62 | 195 | 25 | 55 | 90 | 22 | 22 | 450 | 283 | 540 | 0 | 35 | 24 | 263 | 97 | 0 | 22 | 125 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 0 | 0 | 95 | 36 | 3 | 46 | 0 | 9 | 680 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 800 | 17 | 51 | 82 | 45 | 0 | 235 | 285 | 5 | 185 | 31 | 0 | 50 | 51 | 9 | 16 | 114 | 72 | 52 | 36 | 47 | 305 | 320 | 344 | 0 | 38 | 0 | 0 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 165 | 35 | 55 | 135 | 17 | 0 | 24.78 | 12 | 8144.78 | 913 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.31 | 376 | 0 | 1160.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5.94 | 171 | 0 | 141 | 0 | 148 | 0 | 414 | 0 | 0 | 5.5 | 139 | 57 | 0 | 36 | 0 | 0 | 0 | 0 | 187 | 0.54 | 0 | 150 | 7 | 130 | 200 | 0 | 444 | 650 | 0 | 5577.44 | 13722.22 | 86.9
14:00 | 8 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 47 | 0 | 143 | 80 | 260 | 55 | 55 | 90 | 22 | 31 | 450 | 262 | 583 | 0 | 35 | 24 | 280 | 97 | 0 | 2 | 108 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 100 | 36 | 3 | 46 | 0 | 5 | 778 | 0 | 0 | 0 | 1 | 0 | 162 | 0 | 0 | 0 | 805 | 14 | 51 | 113 | 45 | 0 | 236 | 285 | 5 | 183 | 31 | 0 | 50 | 51 | 9 | 17 | 114 | 74 | 52 | 48 | 24 | 285 | 320 | 338 | 0 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 162 | 53 | 78 | 135 | 10 | 2 | 17.39 | 8 | 8406.39 | 914 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.76 | 379 | 0 | 1209.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 37.23 | 165 | 0 | 137 | 0 | 144 | 0 | 414 | 0 | 4.54 | 5.5 | 163 | 58 | 0 | 32 | 0 | 0 | 0 | 0 | 162 | 0.49 | 0 | 150 | 8 | 118 | 206 | 0 | 446 | 680 | 0 | 5666.88 | 14073.27 | 86.9
15:00 | 8 | 17 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 148 | 60 | 145 | 15 | 55 | 90 | 22 | 17 | 450 | 275 | 583 | 0 | 35 | 24 | 311 | 96 | 0 | 3 | 60 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 46 | 0 | 0 | 100 | 12 | 2 | 46 | 0 | 2 | 854 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 804 | 10 | 51 | 70 | 45 | 0 | 236 | 285 | 5 | 183 | 31 | 0 | 50 | 51 | 9 | 17 | 114 | 72 | 52 | 27 | 24 | 265 | 320 | 350 | 0 | 39 | 0 | 5 | 120 | 16 | 0 | 85 | 28 | 0 | 17 | 161 | 33 | 78 | 135 | 10 | 2 | 13.82 | 6 | 8145.82 | 913 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.14 | 378 | 0 | 1119.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18.09 | 164 | 0 | 137 | 0 | 140 | 0 | 350 | 0 | 1.57 | 2.5 | 172 | 58 | 0 | 26 | 0 | 0 | 0 | 0 | 122 | 0.36 | 0 | 150 | 8 | 118 | 182 | 0 | 362 | 660 | 0 | 5284.37 | 13430.19 | 86.89
16:00 | 8 | 52 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 135 | 46 | 145 | 15 | 35 | 90 | 22 | 16 | 450 | 304 | 584 | 0 | 17 | 14 | 316 | 97 | 0 | 2 | 51 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 46 | 0 | 0 | 100 | 12 | 1 | 46 | 0 | 4 | 856 | 0 | 0 | 0 | 8 | 0 | 207 | 0 | 0 | 0 | 800 | 6 | 51 | 70 | 45 | 0 | 228 | 285 | 5 | 204 | 27 | 1 | 50 | 51 | 21 | 17 | 114 | 76 | 52 | 21 | 24 | 310 | 320 | 372 | 5 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 161 | 17 | 78 | 135 | 10 | 1 | 14.58 | 8 | 8283.58 | 914 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.85 | 377 | 0 | 1117.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 25.23 | 163 | 0 | 136 | 0 | 138 | 0 | 350 | 0 | 2.17 | 2.5 | 174 | 58 | 0 | 17 | 0 | 0 | 0 | 0 | 78 | 0.24 | 0 | 150 | 8 | 118 | 209 | 0 | 0 | 700 | 0 | 4937.1 | 13220.68 | 86.89
17:00 | 8 | 52 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 132 | 80 | 145 | 15 | 35 | 90 | 22 | 32 | 450 | 270 | 583 | 0 | 17 | 14 | 320 | 94 | 0 | 1 | 70 | 23 | 21 | 0 | 0 | 8 | 30 | 0 | 0 | 1 | 46 | 0 | 0 | 100 | 12 | 0 | 46 | 11 | 8 | 852 | 5 | 0 | 0 | 8 | 10 | 214 | 0 | 0 | 0 | 758 | 2 | 51 | 70 | 45 | 0 | 236 | 285 | 5 | 183 | 35 | 56 | 50 | 51 | 27 | 17 | 70 | 74 | 52 | 7 | 24 | 305 | 320 | 350 | 5 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 161 | 17 | 78 | 135 | 9 | 0 | 4.73 | 12 | 8291.73 | 914 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.4 | 379 | 17 | 1112.32 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 7 | 160 | 0 | 137 | 0 | 140 | 0 | 414 | 0 | 0.81 | 2.5 | 177 | 58 | 13 | 7 | 12 | 0 | 0 | 1.3 | 29 | 0.07 | 0 | 245 | 7 | 118 | 209 | 0 | 0 | 700 | 0 | 5010.4 | 13302.13 | 86.88
18:00 | 8 | 70 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 0 | 134 | 108 | 95 | 15 | 55 | 90 | 22 | 48 | 380 | 307 | 583 | 0 | 17 | 14 | 318 | 89 | 0 | 0 | 70 | 22 | 21 | 0 | 0 | 17 | 30 | 9 | 0 | 0 | 46 | 16 | 0 | 100 | 12 | 0 | 46 | 17 | 23 | 856 | 17 | 0 | 0 | 8 | 17 | 214 | 0 | 0 | 0 | 700 | 0 | 51 | 70 | 45 | 0 | 236 | 285 | 5 | 187 | 35 | 94 | 50 | 88 | 36 | 17 | 52 | 78 | 25 | 0 | 24 | 305 | 320 | 350 | 5 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 17 | 97 | 162 | 7 | 0 | 0.38 | 12 | 8383.38 | 914 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 377 | 17 | 1113.19 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0.75 | 158 | 0 | 137 | 0 | 138 | 0 | 414 | 0 | 0.07 | 2.5 | 176 | 58 | 35 | 0 | 45 | 0 | 0 | 0 | 1 | 0 | 0 | 241 | 9 | 118 | 210 | 0 | 0 | 750 | 0 | 5059.43 | 13442.81 | 86.88
19:00 | 8 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 54 | 0 | 131 | 110 | 95 | 15 | 55 | 90 | 22 | 50 | 450 | 275 | 585 | 0 | 17 | 14 | 320 | 94 | 0 | 0 | 70 | 24.5 | 21 | 0 | 0 | 17 | 30 | 12 | 0 | 0 | 51 | 24 | 0 | 100 | 12 | 0 | 46 | 18 | 19 | 852 | 17 | 0 | 0 | 8 | 24 | 214 | 0 | 0 | 0 | 870 | 0 | 51 | 70 | 83 | 0 | 236 | 285 | 5 | 181 | 35 | 94 | 50 | 155 | 55 | 17 | 52 | 78 | 25 | 0 | 24 | 290 | 320 | 350 | 5 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 17 | 98 | 163 | 11 | 0 | 0 | 12 | 8766.5 | 867 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 17 | 1369.1 | 0 | 24 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 156 | 0 | 137 | 0 | 141 | 0 | 414 | 0 | 0 | 2.5 | 173 | 61 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 118 | 208 | 0 | 0 | 730 | 0 | 5506.6 | 14273.1 | 86.87
19:30 | 0 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 0 | 131 | 95 | 0 | 0 | 55 | 90 | 22 | 17 | 450 | 255 | 583 | 0 | 17 | 20 | 320 | 61 | 0 | 0 | 70 | 24.5 | 21 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 51 | 24 | 0 | 100 | 12 | 0 | 46 | 22 | 22 | 855 | 0 | 0 | 0 | 8 | 51 | 214 | 0 | 0 | 0 | 950 | 0 | 51 | 70 | 83 | 0 | 236 | 285 | 5 | 182 | 35 | 94 | 50 | 155 | 55 | 17 | 34 | 72 | 8 | 0 | 24 | 265 | 320 | 350 | 5 | 39 | 0 | 5 | 163 | 16 | 0 | 85 | 28 | 0 | 17 | 165 | 17 | 98 | 164 | 12 | 0 | 0 | 12 | 8545.5 | 867 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 17 | 1357.82 | 0 | 49 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 157 | 0 | 136 | 0 | 142 | 0 | 414 | 0 | 0 | 5 | 171 | 61 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 118 | 200 | 0 | 0 | 900 | 0 | 5691.82 | 14237.32
20:00 | 0 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 0 | 132 | 80 | 0 | 0 | 55 | 90 | 22 | 0 | 450 | 266 | 583 | 0 | 17 | 22 | 326 | 86 | 0 | 0 | 70 | 24.5 | 21 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 51 | 24 | 0 | 72 | 12 | 0 | 46 | 0 | 23 | 853 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 970 | 0 | 51 | 40 | 83 | 0 | 236 | 285 | 5 | 181 | 35 | 94 | 50 | 120 | 54 | 17 | 34 | 70 | 0 | 0 | 0 | 270 | 320 | 350 | 5 | 40 | 0 | 5 | 163 | 16 | 0 | 85 | 28 | 0 | 17 | 164 | 0 | 98 | 154 | 14 | 0 | 0 | 12 | 8348.5 | 867 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 1360.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 136 | 0 | 142 | 0 | 414 | 0 | 0 | 5.5 | 171 | 61 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 118 | 205 | 0 | 0 | 1000 | 0 | 5643.57 | 13992.07 | 86.87
21:00 | 0 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 54 | 0 | 132 | 80 | 0 | 0 | 55 | 126 | 22 | 0 | 450 | 310 | 583 | 0 | 17 | 20 | 320 | 68 | 0 | 0 | 70 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 24 | 0 | 72 | 43 | 0 | 46 | 0 | 23 | 856 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 871 | 0 | 51 | 24 | 157 | 0 | 236 | 285 | 5 | 198 | 35 | 94 | 50 | 122 | 56 | 17 | 54 | 78 | 0 | 0 | 0 | 310 | 320 | 356 | 5 | 40 | 0 | 5 | 163 | 16 | 0 | 85 | 28 | 0 | 18 | 165 | 0 | 98 | 155 | 14 | 0 | 0 | 12 | 8464.5 | 914 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 136 | 0 | 142 | 0 | 414 | 0 | 0 | 5.5 | 168 | 61 | 35 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 126 | 210 | 0 | 0 | 1220 | 0 | 6028.5 | 14493 | 86.86
22:00 | 0 | 88 | 25 | 120 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 54 | 0 | 135 | 80 | 0 | 0 | 35 | 126 | 22 | 0 | 450 | 312 | 583 | 0 | 17 | 20 | 310 | 40 | 0 | 0 | 70 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 51 | 24 | 0 | 100 | 48 | 0 | 46 | 0 | 25 | 855 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 951 | 0 | 51 | 33 | 157 | 0 | 236 | 285 | 5 | 191 | 36 | 92 | 50 | 146 | 56 | 17 | 70 | 86 | 0 | 0 | 0 | 310 | 320 | 357 | 5 | 40 | 0 | 5 | 163 | 16 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 89 | 155 | 11 | 0 | 0 | 12 | 8561 | 914 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 1361 | 0 | 0 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 153 | 0 | 0 | 0 | 0 | 5.5 | 165 | 61 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 212 | 0 | 0 | 1150 | 0 | 5667.5 | 14228.5 | 86.86
23:00 | 0 | 70 | 17 | 120 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 54 | 0 | 149 | 62 | 0 | 0 | 0 | 126 | 22 | 0 | 450 | 303 | 583 | 0 | 17 | 21 | 310 | 40 | 0 | 0 | 52 | 21 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 51 | 24 | 0 | 100 | 48 | 0 | 46 | 0 | 27 | 876 | 0 | 0 | 0 | 8 | 0 | 183 | 0 | 0 | 0 | 950 | 0 | 51 | 70 | 157 | 0 | 235 | 285 | 5 | 176 | 33 | 70 | 50 | 155 | 57 | 17 | 70 | 82 | 0 | 0 | 0 | 305 | 320 | 347 | 5 | 40 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 89 | 156 | 11 | 0 | 0 | 12 | 8429 | 914 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 1371 | 0 | 0 | 0 | 110 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 145 | 0 | 174 | 0 | 0 | 0 | 0 | 5.5 | 167 | 61 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 122 | 220 | 0 | 40 | 1150 | 0 | 5875.5 | 14304.5 | 86.85
Total KWH | 46800 | 671040 | 475200 | 3175300 | 0 | 0 | 0 | 0 | 9388800 | 0 | 0 | 190440 | 1101240 | 0 | 3114720 | 1387200 | 1482622 | 185922 | 662061 | 1578240 | 561600 | 279360 | 9795000 | 6951855 | 8540482 | 0 | 400447 | 568200 | 7325921 | 3349000 | 0 | 127185 | 1494000 | 547800 | 468360 | 0 | 0 | 50182 | 100364 | 120960 | 0 | 100800 | 513955 | 143652 | 0 | 170688 | 365760 | 22320 | 1083540 | 81964 | 397440 | 16698181.82 | 30109 | 0 | 0 | 85372.2 | 93672 | 4177593 | 0 | 0 | 0 | 21807270 | 119340 | 1120052 | 1078909 | 1488727 | 0 | 5687300 | 6916000 | 231840 | 4649000 | 781200 | 978240 | 1185020 | 1887360 | 679560 | 389120 | 2053140 | 1708800 | 758021 | 314055 | 245632 | 7192000 | 7653800 | 9108000 | 70200 | 935000 | 0 | 105264 | 3630027 | 354360 | 0 | 2048640 | 688992 | 0 | 413000 | 3392130 | 207360 | 1783200 | 3031200 | 504960 | 7850 | 176750 | 284400 | 183771067.02 | 21934545 | 4063392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538560 | 11301820 | 176640 | 26938909 | 0 | 28286 | 0 | 372672 | 0 | 0 | 88704 | 0 | 0 | 372016 | 30338 | 180000 | 4114909 | 0 | 3275209 | 0 | 3781736 | 0 | 7917018 | 0 | 14820 | 89442 | 4152000 | 1354909 | 375481 | 225719 | 513129 | 0 | 0 | 18013.44 | 1069200 | 3313 | 0 | 5301000 | 208475 | 3000000 | 4974550 | 0 | 7402896 | 22181818.18 | 0 | 135999519.62 | 319770586.64

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-03-2025 | during | 18-03-2025 | during | 18-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 260 | 260 | 120 | 120 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 310 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 96 | 68 | 208.13 | 208.13 | 80 | 80 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 287 | 320 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 86 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 24.5 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 20 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 46 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 143 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 126 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 14 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 51 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 440 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 70 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2896 | 3004.5 | 5272.5 | 5240.5 | 3884.3 | 3852.3
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 214 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 64 | 82 | 64 | 82 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 74 | 72 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 23 | 2 | 30 | 2 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.97 | 0 | 3.97 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 43 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 856 | 871 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 0 | 2 | 5 | 2 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 683 | 856 | 875 | 875 | 875 | 875 | -
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1870 | 2208 | 3693.69 | 3719.72 | 3693.69 | 3719.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 186 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 225 | 236 | 235 | 235 | 235 | 235 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 35 | 46.94 | 46.94 | 35 | 35 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 7 | 5 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 157 | 195 | 195 | 83 | 83 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 68 | 24 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 48 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 122 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 78 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 17 | 20.83 | 20.83 | 17 | 17
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 54 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 56 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 94 | 115 | 115 | 16 | 16 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 33 | 0 | 33 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1341 | 1462 | 2256.97 | 2223.97 | 1851.2 | 1818.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-03-2025 | during | 18-03-2025 | during | 18-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 27 | 14 | 210 | 210 | 34 | 34 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 155 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 79 | 98 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 4.89 | 0 | 39.87 | 0 | 39.87 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 259.89 | 279 | 643.57 | 601.5 | 467.57 | 425.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 40 | 38 | 38 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 5 | 40 | 40 | 35 | 35 | Gas shortage
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 28 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 165 | 165 | 165 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 356 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | machine problem
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1529 | 1511 | 1611 | 1611 | 1540 | 1540
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 914 | 914 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 142 | 98 | 410 | 410 | 220 | 220 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81.65 | 0 | 84 | 0 | 84 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 377 | 592 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1514.65 | 1604 | 3596.2 | 3512.2 | 2224.02 | 2140.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 444 | 0 | 20 | 450 | 420 | 420 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 10 | 10.12 | 10.12 | 6 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 126 | 130.1 | 130.1 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 660 | 1220 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 200 | 210 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1591.6 | 1873 | 2192.22 | 2621.22 | 2536 | 2539
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 172 | 156 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 145 | 136 | 220 | 220 | 150 | 150 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 149 | 142 | 220 | 220 | 160 | 160 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.52 | 0 | 5.52 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1161.86 | 1376 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 8.75 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 41 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2097.11 | 2229.5 | 3173.05 | 3012.53 | 2886.67 | 2726.15
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 61 | 56 | 56 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 176 | 168 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 58 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 62 | 0 | 156 | 0 | 156 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 333 | 322 | 655.4 | 468 | 620.42 | 433.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 13432.25 | 14493 | 23094.6 | 23010.64 | 19703.87 | 19193.91
Forecast Scenario (18-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13600 |  | 0 |  | 13600
|  |  |  | 1:00 | 13480 |  | 0 |  | 13480
|  |  |  | 2:00 | 13050 |  | 0 |  | 13050
|  |  |  | 3:00 | 13270 |  | 0 |  | 13270
|  |  |  | 4:00 | 13280 |  | 0 |  | 13280
|  |  |  | 5:00 | 12420 |  | 0 |  | 12420
|  |  |  | 6:00 | 11720 |  | 0 |  | 11720
|  |  |  | 7:00 | 11720 |  | 0 |  | 11720
|  |  |  | 8:00 | 12090 |  | 0 |  | 12090
|  |  |  | 9:00 | 12630 |  | 0 |  | 12630
|  |  |  | 10:00 | 13270 |  | 0 |  | 13270
|  |  |  | 11:00 | 13350 |  | 0 |  | 13350
|  |  |  | 12:00 | 13480 |  | 0 |  | 13480
|  |  |  | 13:00 | 13770 |  | 0 |  | 13770
|  |  |  | 14:00 | 14130 |  | 0 |  | 14130
|  |  |  | 15:00 | 13490 |  | 0 |  | 13490
|  |  |  | 16:00 | 13270 |  | 0 |  | 13270
|  |  |  | 17:00 | 13340 |  | 0 |  | 13340
|  |  |  | 18:00 | 13420 |  | 0 |  | 13420
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14450 |  | 0 |  | 14450
|  |  |  | 19:30 | 14300 |  | 0 |  | 14300
|  |  |  | 20:00 | 14100 |  | 0 |  | 14100
|  |  |  | 21:00 | 14300 |  | 0 |  | 14300
|  |  |  | 22:00 | 14300 |  | 0 |  | 14300
|  |  |  | 23:00 | 13900 |  | 0 |  | 13900
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 13480.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14450.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14450.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 319.83 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:27 hrs on 18-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13432.25 | MW | 12:00 Hr. | Energy Generated |  |  | 319.7706 |  | MKWHr.
| Day Peak Demand |  |  | 13488.68 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.493 |  | MKWHr.
| Evening Peak Generation |  |  | 14493 | MW | 21:00 Hr. | Energy Demand |  |  | 321.2636 |  | MKWHr.
| Evening Peak Demand |  |  | 14493 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.8 |  | °C
| Minimum Generation of the Day |  |  | 11723.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1110 |  | MMCFD
| Maximum Generation of the Day |  |  | 14493 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9715 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 50.6723 | 0 | 13.0693 | 0 | 0 | 0.12718 | 0 | 0 | 63.8688 | Gas | 145.2167 | Gas | 475976551.92
| Chattogram Zone |  |  | 4.575 | 38.5055 | 1.7567 | 0 | 1.0835 | 0.14166 | 0 | 0.1008 | 46.1632 | Coal | 90.1999 | Coal | 588570705.109
| Cumilla Zone |  |  | 22.4483 | 0 | 7.6809 | 0 | 0 | 0.31405 | 1.7088 | 0 | 32.152 | HFO | 29.3982 | HFO | 525198570.944
| Mymensingh Zone |  |  | 0.50496 | 0 | 5.3062 | 0 | 0 | 0.1846 | 0 | 0 | 5.9957 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.5914 | Hydro | 1.0835 | Hydro | 108354
| Khulna Zone |  |  | 4.0634 | 11.3018 | 0.17664 | 0 | 0 | 0.53856 | 21.9345 | 0 | 38.015 | Solar | 3.1891 | Solar | 52972396.5084
| Barishal Zone |  |  | 8.183 | 34.8857 | 0 | 0 | 0 | 0.003313 | 0 | 0 | 43.0721 | Import | 50.5823 | Import | 265209813.75
| Rajshahi Zone |  |  | 19.1783 | 0 | 0.52 | 0 | 0 | 0.56684 | 26.9389 | 0 | 47.2041 | Wind | 0.1008 | Wind | 1475712
| Rangpur Zone |  |  | 0 | 5.5069 | 0.88861 | 0 | 0 | 1.3129 | 0 | 0 | 7.7085
| Total |  |  | 145.2167 | 90.1999 | 29.3982 | 0 | 1.0835 | 3.1891 | 50.5823 | 0.1008 | 319.7706
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 475976551.92 |  | Hydro | 108354
|  |  |  | Coal | 588570705.109 |  | Solar | 52972396.5084
|  |  |  | HFO | 525198570.944 |  | Import | 265209813.75
|  |  |  | HSD | 0 |  | Wind | 1475712
[5 empty] | Total: | 190,95,12,104 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9345 | Peak Hr Flow | 914.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10592290 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.9389 | Peak Hr Flow | 1376.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 598 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7088 | Peak Hr Flow | 78.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 990 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.5823 | Peak Hr Flow | 2368.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5116
|  |  |  | Chattogram |  | 0 |  | 1470
|  |  |  | Cumilla |  | 0 |  | 1360
|  |  |  | Mymensingh |  | 0 |  | 1125
|  |  |  | Sylhet |  | 0 |  | 516
|  |  |  | Khulna |  | 0 |  | 1689
|  |  |  | Barishal |  | 0 |  | 458
|  |  |  | Rajshahi |  | 0 |  | 1392
|  |  |  | Rangpur |  | 0 |  | 800
|  |  |  | Total |  | 0 |  | 13926
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 792 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1227.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:54 | 15:15 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D
| 08:55 | 15:15 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Fire wall Construction
works.
| 09:09 | 12:18 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to IDRNPP Project work.
|  | 10:05 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 10:05 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 10:48 |  | Ghorasal Unit-7 365 MW was forced shutdown at 10:48 hrs due to air compressor trip.
| 10:52 | 14:10 | New Tongi S/S T1(403T) LT Scheduled S/D Due to 33 KV T1-A incoming panel relocation work
| 10:55 | 13:50 | New Tongi S/S T1(403T) HT Scheduled S/D Due to T1-A 33kv incoming panel relocation work
| 11:35 |  | Ghorashal Unit-7 365 MW GT was sync at 11:35hr
| 11:43 |  | Siddhirganj GT-1 was shutdown at 11:43 hrs due to gas shortage.
| 12:00 |  | Day peak Generation is 13428 MW
| 12:45 | 13:36 | Sreepur 230/132/33kV S/S 132 kV BUS-2 Forced S/D Due to Bird nest Cleaning
|  | 13:33 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
| 13:36 | 13:36 | Sreepur 230/132/33kV S/S 132 kV BUS-2 Forced S/D Due to Bird nest Cleaning
| 13:40 | 14:00 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Forced S/D Due to Bird nest Cleaning
| 14:31 | 15:40 | Sunamganj 132/33kV S/S Tr-1 HT Tripped showing RET670 REC650 relays Due to Mechanical | [7 empty] | 2.0MW load
|  |  | Faulty | [7 empty] | interrup.
| 15:05 |  | Patuakhali 1320 MW (RNPL) unit-1 tripped.
| 15:06 | 15:21 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Tripped showing MCGG relays Due to Tripped | [7 empty] | 24.0MW load
|  |  | due to O/C & E/F | [7 empty] | interrup.
|  | 15:15 | Bogura 132/33kV S/S Transformer-2 HT is restored.
|  | 15:17 | Bogura 132/33kV S/S Transformer-2 LT is restored.
|  | 16:22 | Hathazari 230/132/33kV S/S MT-02 HT is restored.
| 16:28 | 17:00 | Chandpur 132/33kV S/S 402T LT Tripped showing E/F relays Due to E/F | [7 empty] | 12.0MW load
interrup.
| 16:28 | 17:16 | Chandpur 132/33kV S/S 422T LT Tripped showing O/C & E/F relays Due to 33kv T-5 bus | [7 empty] | 14.0MW load
|  |  | coupler DS heavy flashing | [7 empty] | interrup.
| 16:28 | 17:16 | Chandpur 132/33kV S/S 422T HT Tripped showing O/C relays Due to O/C | [7 empty] | 14.0MW load
interrup.
| 16:50 | 17:15 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing 33kV CB tripping relays Due to | [7 empty] | 50.0MW load
|  |  | 33kV khalil Mondol Hat feeder fault | [7 empty] | interrup.
| 16:50 | 17:15 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing 33kV CB Tripping relays Due to | [7 empty] | 50.0MW load
|  |  | 33kV khalil Mondol Hat feeder fault | [7 empty] | interrup.
| 19:00 |  | Sirajganj 68 MW Solar 132/33 kV Transformer S/D.
| 21:00 |  | Evening Peak Generation: 14492 MW.
| 21:09 |  | Sirajgonj 400 MW CCPP Unit-4 Tripped
| 21:09 |  | Sirajganj 400 MW CCPP Unit-4 tripped. | [7 empty] | 400MW generation
interrup.
| 22:57 |  | Patuakhali 1320 MW (RNPL) unit-1 was sync.
| 23:30 |  | Sirajganj 68 MW Solar 132/33 kV Transformer syn.
| 01:20 |  | Sirajganj 400 MW CCPP Unit-4 GT sync.
| 01:20 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
| 01:59 |  | SS Power unit-2 was shut down due to tube leakage at the boiler.
| 02:22 |  | Sirajganj 400 MW CCPP Unit-4 ST sync.
| 02:22 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 06:00 |  | Min. Gen. 11366 MW
| 06:10 | 07:56 | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to 33 kv bus red hot removed | [7 empty] | 15.0MW load
interrup.
| 06:11 | 07:55 | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 06:42 |  | Bogura 132/33kV S/S Transformer-2 LT Project Work S/D Due to 33 kV bus Spacer Change | [7 empty] | 35.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:42 |  | Bogura 132/33kV S/S Transformer-2 HT Project Work S/D Due to 33 kV bus Spacer Change | [7 empty] | 35.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:42 |  | Bogura 132/33kV S/S Transformer-1 LT Project Work S/D Due to 33 kV bus Spacer Change | [7 empty] | 35.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:42 |  | Bogura 132/33kV S/S Transformer-1 HT Project Work S/D Due to 33 kV bus Spacer Change | [7 empty] | 35.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:00 |  | Chandpur 132/33kV S/S 33 kV T-5 section Scheduled S/D Due to 33 Kv Bus coupler DS | [7 empty] | 23.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 07:00 |  | Chandpur 132/33kV S/S 33 kV T-2 section Scheduled S/D Due to 33 Kv Bus coupler DS | [7 empty] | 4.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 07:13 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Scheduled S/D from Ghorashal 230kV end Due to Shutdown
requisition from Dhamrai 132/33 kV SS for Insulator Disk cleaning . and from Ishurdi
230/132kVend.
| 07:16 |  | Ashuganj North CCPP was shutdown due to machine vibration related maintenance work.
| 07:35 |  | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to S/D taken by T-2, Sec 33kV (Y-Ph)
Bushing & 33kV CT (B-Ph) Clamp Side Hot Spot Maintenance Work
| 07:35 |  | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to S/D taken by T-2, Sec 33kV (Y-Ph)
Bushing & 33kV CT (B-Ph) Clamp Side Hot Spot Maintenance Work
| 07:41 |  | Shahjibazar 132/33kV S/S SPCL 86 MW Tripped showing N/A relays Due to N/A
| 07:41 |  | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Shahjibazar 132/33kV end Due to due
to 86 SPCL & Sreemongal-01 trip, sreemoingal-ckt-02 was source out
| 07:41 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distanve
relay relays Due to stromy weather and from Shahjibazar 132/33kV end showing distance,
(zone-01. C phase, ABC trip, D-0, R-0.01) relays Due to N/A
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 3175300 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 9388800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9795000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 310 | 6951855 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 185922 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 68 | 3349000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7325921 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 46800 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 190440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 1387200 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 662061 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 400447 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24.5 | 547800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 468360 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 561600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 568200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 475200 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 1482622 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3114720 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 671040 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 279360 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1578240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 127185 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1101240 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 8540482 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1494000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3004.5 | 63868795
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 85372.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119340 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1083540 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 4177593 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 93672 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 143652 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 513955 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 72 | 170688 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 397440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 120960 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 22320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 100364 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 81964 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 43 | 365760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 50182 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 30109 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 871 | 21807270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 100800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 856 | 16698181.82 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4915.22 | 2208 | 46163163.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 198 | 4649000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 236 | 5687300 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6916000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 781200 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 231840 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 157 | 1488727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1120052 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 24 | 1078909 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 245632 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1185020 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 122 | 1887360 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1708800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 758021 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 389120 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 54 | 2053140 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 679560 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 978240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 314055 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1462 | 32151976
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 14 | 504960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 3031200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1783200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 176750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 284400 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 207360 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 279 | 5995720
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 935000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3630027 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 5 | 70200 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 105264 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 28 | 688992 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2048640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 165 | 3392130 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 413000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 354360 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7192000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 356 | 9108000 | FGMO not available due to Air Compressor problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7653800 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2368.568 | 1511 | 35591413
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 914 | 21934545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 98 | 4063392 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 176640 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 538560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 592 | 11301820 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1604 | 38014957
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 7402896 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 208475 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 126 | 3000000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1220 | 22181818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 210 | 4974550 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5301000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3313 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1873 | 43072052.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 28286 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 4114909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 136 | 3275209 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 142 | 3781736 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 7917018 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 30338 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 89442 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 372672 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 88704 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 14820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1376 | 26938909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 180000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 372016 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2229.5 | 47204059
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 61 | 1354909 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 168 | 4152000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 58 | 513129 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 18013.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 375481 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 225719 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1069200 | -
Rangpur Area Total |  |  |  |  | 950 | 322 | 7708451.44
Eastern Grid Total |  |  |  |  | 16921.242 | 8464.5 | 183771067.02
Western Grid Total |  |  |  |  | 11614.5 | 6028.5 | 135999519.62
National Grid Total |  |  |  |  | 28535.742 | 14493 | 319770586.64
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9587.2 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4338.1 | MW
i) Dhaka area |  |  | 5115.7 |  | MW | i) Khulna area |  |  |  | 1689 | MW
ii) Chattogram area |  |  | 1470.5 |  | MW | ii) Barishal area |  |  |  | 457.5 | MW
iii) Cumilla area |  |  | 1360 |  | MW | iii) Rajshahi area |  |  |  | 1391.6 | MW
iv) Mymensingh area |  |  | 1125 |  | MW | iv) Rangpur area |  |  |  | 800 | MW
v) Sylhet area |  |  | 516 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13925.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 74 | 18:30 | 133 | Payra | 30 | 21:00
2 | AKSML | 23 | 17:00 | 68 | Jamalpur | 128 | 18:00 | 134 | Postogola | 53 | 15:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jashore | 138 | 23:00 | 135 | Purbachal | 19 | 00:00
4 | Agargaon | 118 | 13:00 | 70 | Jhenaidah | 126 | 00:00 | 136 | Purbasadipur | 117 | 18:00
5 | Agrabad | 92 | 15:00 | 71 | Joydebpur | 146 | 10:00 | 137 | Rahanpur | 31 | 22:00
6 | Amnura | 42 | 19:30 | 72 | Joypurhat | 69 | 22:00 | 138 | Rahim | 33 | 14:00
7 | Ashuganj | 90 | 23:00 | 73 | Juldah | 15 | 13:00 | 139 | Rajbari | 74 | 03:00
8 | BSRM | 199 | 23:00 | 74 | KSRM | 28 | 16:00 | 140 | Rajendrapur | 118 | 13:00
9 | Bagerhat | 92 | 19:00 | 75 | Kabirpur | 240 | 19:00 | 141 | Rajshahi | 102 | 00:00
10 | Bajitpur | 45 | 23:00 | 76 | Kachua | 81 | 22:00 | 142 | Rajshahi-230 | 79 | 04:00
11 | Bakulia | 95 | 14:00 | 77 | Kallyanpur | 108 | 13:00 | 143 | Ramganj | 116 | 21:00
12 | Banani | 32 | 13:00 | 78 | Kalurghat | 44 | 11:00 | 144 | Rampur | 40 | 18:30
13 | Bangabhaban | 17 | 10:00 | 79 | Kamrangirchar | 71 | 13:00 | 145 | Rangamati | 16 | 19:00
14 | Barapukuria | 60 | 15:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 140 | 18:00
15 | Barguna | 20 | 19:00 | 81 | Kazla | 99 | 13:00 | 147 | Ruppur | 6.6 | 10:00
16 | Barishal | 112 | 19:30 | 82 | Keranigonj | 79 | 13:00 | 148 | SSM | 3 | 13:00
17 | Barishal-230 | 98 | 19:30 | 83 | Khagrachori | 30 | 18:00 | 149 | Saidpur | 111 | 17:00
18 | Baroaulia | 66 | 14:00 | 84 | Khosba | 32 | 14:00 | 150 | Satkhira | 139 | 19:00
19 | Baroirhat | 59 | 20:00 | 85 | Khulna | 68 | 19:00 | 151 | Satmasjid | 100 | 20:00
20 | Bashundhara | 183 | 13:00 | 86 | Khulshi | 171 | 15:00 | 152 | Savar | 237 | 15:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 135 | 00:00 | 153 | SevenRings | 21.05 | 20:00
22 | Beanibazar | 64 | 18:30 | 88 | Kodda | 321 | 14:00 | 154 | ShahCement | 39 | 05:00
23 | Benapole | 68 | 00:00 | 89 | Kulaura | 40 | 18:30 | 155 | Shahjadpur | 85 | 10:00
24 | Bhaluka | 141 | 12:00 | 90 | Kurigram | 64 | 17:00 | 156 | Shahjibazar | 125 | 00:00
25 | Bhandaria | 52 | 22:00 | 91 | Kushtia | 134 | 00:00 | 157 | Shahmirpur | 54.5 | 00:00
26 | Bhangura | 40 | 03:00 | 92 | Lalbag | 65 | 13:00 | 158 | Shariatpur | 82 | 21:00
27 | Bheramara(GK) | 52 | 00:00 | 93 | Lalmonirhat | 50 | 19:30 | 159 | Sherpur | 162 | 18:00
28 | Bhulta | 272 | 13:00 | 94 | MI_Cement | 18.3 | 15:00 | 160 | Shikalbaha | 29 | 23:00
29 | Bog-Sherpur | 76 | 01:00 | 95 | Madanganj | 40 | 14:00 | 161 | Shitalakhya | 87.2 | 15:00
30 | Bogura | 146 | 04:00 | 96 | Madaripur | 109 | 21:00 | 162 | Sholosohor | 42 | 15:00
31 | Borhanuddin | 83 | 23:00 | 97 | Madartek | 87.9 | 00:00 | 163 | Shyampur | 160 | 03:00
32 | Brahmanbaria | 121 | 18:30 | 98 | Madunaghat | 49 | 14:00 | 164 | Siddhirganj | 130 | 11:00
33 | Cantonment | 136 | 13:00 | 99 | Magura | 59 | 00:00 | 165 | Sirajganj | 102 | 20:00
34 | Chandpur | 64 | 01:00 | 100 | Mahasthangarh | 70 | 22:00 | 166 | Sonargaon | 103 | 00:00
35 | Chandraghona | 35 | 19:00 | 101 | Manikganj | 137 | 13:00 | 167 | Sreemongol | 72 | 00:00
36 | Chapai | 66 | 22:00 | 102 | Maniknagar | 72 | 13:00 | 168 | Sreepur | 102 | 10:00
37 | Charsaidpur | 47 | 11:00 | 103 | Matarbari | 46 | 22:00 | 169 | Srinagar | 44.1 | 00:00
38 | Chauddagram | 75 | 21:00 | 104 | Matuail | 72 | 11:00 | 170 | Sunamganj | 46 | 21:00
39 | Chhatak | 27 | 18:30 | 105 | Millgate | 108 | 14:00 | 171 | Sylhet | 34 | 19:00
40 | Chowmuhani | 243 | 18:30 | 106 | Mirpur | 138 | 14:00 | 172 | Sylhet-132 | 101 | 16:00
41 | Chuadanga | 111 | 03:00 | 107 | Mirsorai | 10 | 00:00 | 173 | TK | 32 | 18:30
42 | Coxsbazar | 129 | 21:00 | 108 | Mirzapur | 44 | 19:00 | 174 | Tangail | 176 | 04:00
43 | Cumilla(N) | 153 | 23:00 | 109 | Mithapukur | 62 | 04:00 | 175 | Thakurgaon | 91 | 19:00
44 | Cumilla(S) | 175 | 16:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 168 | 08:00
45 | Daudkandi | 140 | 21:00 | 111 | Mogbazar | 149.2 | 14:00 | 177 | Ullahpara | 33 | 08:00
46 | Dhaka | 60 | 13:00 | 112 | Mongla | 42 | 01:00 | 178 | Ullon | 47 | 00:00
47 | Dhamrai | 126 | 14:00 | 113 | Motijheel | 39 | 12:00 | 179 | Uttara | 91 | 13:00
48 | Dhanmondi | 149 | 13:00 | 114 | Muktagacha | 32 | 18:00 | 180 | UttaraNew | 54 | 12:00
49 | Dohazari | 104 | 19:00 | 115 | Munshiganj | 110 | 00:00 | 181 | Zigatola | 74 | 00:00
50 | Faridpur | 158 | 21:00 | 116 | Muradnagar | 25 | 00:00
51 | Fatullah | 96 | 12:00 | 117 | Mymensingh | 198 | 18:00
52 | Fenchuganj | 28 | 18:30 | 118 | Naogaon | 131 | 22:00
53 | Feni | 116 | 22:00 | 119 | Narail | 59 | 22:00
54 | GPH | 91 | 09:00 | 120 | Narinda | 88.5 | 13:00
55 | Ghatail | 78 | 18:00 | 121 | Narshingdi | 166 | 14:00
56 | Ghorashal | 14 | 00:00 | 122 | Natore | 137 | 00:00
57 | Ghorashal-230 | 79 | 14:00 | 123 | Nawabganj | 56 | 00:00
58 | Goalpara | 34 | 00:00 | 124 | Netrakona | 135 | 18:00
59 | Gollamari | 92 | 20:00 | 125 | New | 71.7 | 23:00
60 | Gopalganj | 112 | 21:00 | 126 | Niamatpur | 100 | 22:00
61 | Gulshan | 126 | 13:00 | 127 | Noapara | 60.5 | 15:00
62 | Halishahar | 75 | 10:00 | 128 | PHP | 7 | 00:00
63 | HaripurSBU | 185 | 12:00 | 129 | Pabna | 111 | 03:00
64 | Hasnabad | 98 | 00:00 | 130 | Palashbari | 114 | 18:00
65 | Hathazari | 81 | 21:00 | 131 | Panchagarh | 52 | 19:00
66 | Ishurdi | 66 | 03:00 | 132 | Patuakhali | 75.8 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13599.5 | 125 |  | 13730.13
1:00 | 13273.5 | 198 |  | 13480.5
2:00 | 12864.5 | 178 |  | 13050.5
3:00 | 13096.5 | 166 |  | 13269.5
4:00 | 13108.5 | 164 |  | 13279.5
5:00 | 12366.5 | 52 |  | 12420.5
6:00 | 11723.5 | 0 |  | 11723.5
7:00 | 11723.93 | 0 |  | 11723.93
8:00 | 12092.15 | 0 |  | 12092.15
9:00 | 12569.93 | 61 |  | 12633.93
10:00 | 13113.86 | 153 |  | 13273.86
11:00 | 13279.47 | 75 |  | 13357.47
12:00 | 13432.25 | 54 |  | 13488.68
13:00 | 13722.22 | 53 |  | 13777.22
14:00 | 14073.27 | 57 |  | 14133.27
15:00 | 13430.19 | 60 |  | 13493.19
16:00 | 13220.68 | 50 |  | 13272.68
17:00 | 13302.13 | 47 |  | 13351.25
18:00 | 13442.81 | 0 |  | 13442.81
19:00 | 14273.1 | 0 |  | 14273.1
19:30 | 14237.32 | 0 |  | 14237.32
20:00 | 13992.07 | 0 |  | 13992.07
21:00 | 14493 | 0 |  | 14493
22:00 | 14228.5 | 0 |  | 14228.5
23:00 | 14304.5 | 0 |  | 14304.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7287 | 6312.5 | 13599.5 | DAILY GENERATION CURVE
00:30 | 7199 | 6237.5 | 13436.5
01:00 | 7111 | 6162.5 | 13273.5 | 17-03-2025
01:30 | 7022 | 6047 | 13069
02:00 | 6933 | 5931.5 | 12864.5
02:30 | 6970.5 | 6010 | 12980.5
03:00 | 7008 | 6088.5 | 13096.5
03:30 | 7018 | 6084.5 | 13102.5
04:00 | 7028 | 6080.5 | 13108.5
04:30 | 6917 | 5820.5 | 12737.5
05:00 | 6806 | 5560.5 | 12366.5
05:30 | 6666 | 5379 | 12045
06:00 | 6526 | 5197.5 | 11723.5
06:30 | 6506.84 | 5216.875 | 11723.715
07:00 | 6487.68 | 5236.25 | 11723.93
07:30 | 6585.555 | 5322.485 | 11908.04
08:00 | 6683.43 | 5408.72 | 12092.15
08:30 | 6828.635 | 5502.405 | 12331.04
09:00 | 6973.84 | 5596.09 | 12569.93
09:30 | 7174.295 | 5667.6 | 12841.895
10:00 | 7374.75 | 5739.11 | 13113.86
10:30 | 7425.23 | 5771.435 | 13196.665
11:00 | 7475.71 | 5803.76 | 13279.47
11:30 | 7685.8 | 5670.06 | 13355.86
12:00 | 7895.89 | 5536.36 | 13432.25
12:30 | 8020.335 | 5556.9 | 13577.235
13:00 | 8144.78 | 5577.44 | 13722.22
13:30 | 8275.585 | 5622.16 | 13897.745
14:00 | 8406.39 | 5666.88 | 14073.27
14:30 | 8276.105 | 5475.625 | 13751.73
15:00 | 8145.82 | 5284.37 | 13430.19
15:30 | 8214.7 | 5110.735 | 13325.435
16:00 | 8283.58 | 4937.1 | 13220.68
16:30 | 8287.655 | 4973.75 | 13261.405
17:00 | 8291.73 | 5010.4 | 13302.13
17:30 | 8337.555 | 5034.915 | 13372.47
18:00 | 8383.38 | 5059.43 | 13442.81
18:30 | 8574.94 | 5283.015 | 13857.955
19:00 | 8766.5 | 5506.6 | 14273.1
19:30 | 8545.5 | 5691.82 | 14237.32
20:00 | 8348.5 | 5643.57 | 13992.07
20:30 | 8406.5 | 5836.035 | 14242.535 |  | Executive Engineer
21:00 | 8464.5 | 6028.5 | 14493 |  | Network Operation Division
21:30 | 8512.75 | 5848 | 14360.75
22:00 | 8561 | 5667.5 | 14228.5
22:30 | 8495 | 5771.5 | 14266.5
23:00 | 8429 | 5875.5 | 14304.5

## En-Curve
QF-LDC-12
Date | 17-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4120 | 1813.5 | 915 | 0 | 78 | 1365 | 40 | 4223 | 0 | 180 | 865 | 0 | 0 | 0 | 125 | DAILY ENERGY CURVE
00:30 | 4056 | 1770 | 914 | 0 | 75 | 1343.5 | 40 | 4275 | 0 | 119.5 | 843.5 | 0 | 0 | 0 | 161.5 | 17-03-2025
01:00 | 3992 | 1726.5 | 913 | 0 | 72 | 1322 | 40 | 4327 | 0 | 59 | 822 | 0 | 0 | 0 | 198
01:30 | 3974 | 1671.5 | 914.5 | 0 | 70 | 1265.5 | 40 | 4253 | 0 | 59 | 821.5 | 0 | 0 | 0 | 188 | Energy Generated | 319.7706 |  | MKWHr
02:00 | 3956 | 1616.5 | 916 | 0 | 68 | 1209 | 40 | 4179 | 0 | 59 | 821 | 0 | 0 | 0 | 178 | Energy not Served | 1.493 |  | MKWHr
02:30 | 3965.5 | 1617.5 | 916 | 0 | 68 | 1213 | 40 | 4253 | 0 | 75 | 832.5 | 0 | 0 | 0 | 172 | Total Energy Requirement | 321.2636 |  | MKWHr
03:00 | 3975 | 1618.5 | 916 | 0 | 68 | 1217 | 40 | 4327 | 0 | 91 | 844 | 0 | 0 | 0 | 166
03:30 | 4039.5 | 1653 | 916.5 | 0 | 69 | 1164.5 | 40 | 4317.5 | 0 | 90.5 | 812 | 0 | 0 | 0 | 165
04:00 | 4104 | 1687.5 | 917 | 0 | 70 | 1112 | 40 | 4308 | 0 | 90 | 780 | 0 | 0 | 0 | 164
04:30 | 4078.5 | 1694.5 | 916.5 | 0 | 70 | 1061 | 40 | 4029 | 0 | 82 | 766 | 0 | 0 | 0 | 108
05:00 | 4053 | 1701.5 | 916 | 0 | 70 | 1010 | 40 | 3750 | 0 | 74 | 752 | 0 | 0 | 0 | 52
05:30 | 4024.5 | 1673.5 | 916 | 0 | 69 | 913.5 | 40 | 3666 | 0 | 74 | 668 | 0 | 0 | 0.5 | 26
06:00 | 3996 | 1645.5 | 916 | 0 | 68 | 817 | 40 | 3582 | 0 | 74 | 584 | 0 | 0 | 1 | 0
06:30 | 4009.5 | 1659 | 916 | 0 | 61 | 820.5 | 40 | 3564.5 | 28.715 | 65 | 559 | 0 | 0 | 0.5 | 0
07:00 | 4023 | 1672.5 | 916 | 0 | 54 | 824 | 40 | 3547 | 57.43 | 56 | 534 | 0 | 0 | 0 | 0
07:30 | 4086.5 | 1725 | 891.5 | 0 | 59 | 823.385 | 40 | 3560 | 121.655 | 65 | 536 | 0 | 0 | 0 | 0
08:00 | 4150 | 1777.5 | 867 | 0 | 64 | 822.77 | 40 | 3573 | 185.88 | 74 | 538 | 0 | 0 | 0 | 0
08:30 | 4161 | 1890 | 867 | 0 | 63 | 868.4 | 40 | 3605.5 | 219.64 | 76 | 540.5 | 0 | 0 | 0 | 30.5
09:00 | 4172 | 2002.5 | 867 | 0 | 62 | 914.03 | 40 | 3638 | 253.4 | 78 | 543 | 0 | 0 | 0 | 61
09:30 | 4150 | 2083 | 890.5 | 0 | 64 | 983.685 | 60 | 3567.5 | 325.71 | 88 | 629.5 | 0 | 0 | 0 | 107
10:00 | 4128 | 2163.5 | 914 | 0 | 66 | 1053.34 | 80 | 3497 | 398.02 | 98 | 716 | 0 | 0 | 0 | 153
10:30 | 3984 | 2181 | 914.5 | 0 | 64 | 1106.705 | 70 | 3490.5 | 422.46 | 158.5 | 804 | 0 | 0 | 1 | 114
11:00 | 3840 | 2198.5 | 915 | 0 | 62 | 1160.07 | 60 | 3484 | 446.9 | 219 | 892 | 0 | 0 | 2 | 75
11:30 | 3904 | 2196.5 | 914.5 | 0 | 63 | 1160.965 | 53 | 3444 | 387.895 | 259 | 965 | 0 | 0 | 8 | 64.5
12:00 | 3968 | 2194.5 | 914 | 0 | 64 | 1161.86 | 46 | 3404 | 328.89 | 299 | 1038 | 0 | 0 | 14 | 54
12:30 | 3936 | 2232.5 | 913.5 | 0 | 68 | 1161.005 | 46 | 3350 | 381.73 | 300 | 1174 | 0 | 0 | 14.5 | 53.5
13:00 | 3904 | 2270.5 | 913 | 0 | 72 | 1160.15 | 46 | 3296 | 434.57 | 301 | 1310 | 0 | 0 | 15 | 53
13:30 | 3890 | 2276 | 913.5 | 0 | 73 | 1184.755 | 46 | 3377.5 | 426.99 | 293.5 | 1400.5 | 0 | 0 | 16 | 55
14:00 | 3876 | 2281.5 | 914 | 0 | 74 | 1209.36 | 46 | 3459 | 419.41 | 286 | 1491 | 0 | 0 | 17 | 57
14:30 | 3858 | 2241.5 | 913.5 | 0 | 73 | 1164.535 | 46 | 3448.5 | 358.195 | 259 | 1371.5 | 0 | 0 | 18 | 58.5
15:00 | 3840 | 2201.5 | 913 | 0 | 72 | 1119.71 | 46 | 3438 | 296.98 | 232 | 1252 | 0 | 0 | 19 | 60
15:30 | 3877 | 2272.5 | 913.5 | 0 | 74 | 1118.41 | 46 | 3276.5 | 270.025 | 238 | 1225.5 | 0 | 0 | 14 | 55
16:00 | 3914 | 2343.5 | 914 | 0 | 76 | 1117.11 | 46 | 3115 | 243.07 | 244 | 1199 | 0 | 0 | 9 | 50
16:30 | 3933.5 | 2325 | 914 | 0 | 75 | 1114.715 | 46 | 3142 | 166.19 | 270.5 | 1269.5 | 0 | 0 | 5 | 48.5
17:00 | 3953 | 2306.5 | 914 | 0 | 74 | 1112.32 | 46 | 3169 | 89.31 | 297 | 1340 | 0 | 0 | 1 | 47
17:30 | 3939 | 2298.5 | 914 | 0 | 76 | 1112.755 | 46 | 3163.5 | 46.215 | 335.5 | 1440.5 | 0 | 0 | 0.5 | 23.5
18:00 | 3925 | 2290.5 | 914 | 0 | 78 | 1113.19 | 46 | 3158 | 3.12 | 374 | 1541 | 0 | 0 | 0 | 0
18:30 | 3927.5 | 2320.75 | 890.5 | 0 | 78 | 1241.145 | 46 | 3326 | 1.56 | 414.5 | 1612 | 0 | 0 | 0 | 0
19:00 | 3930 | 2351 | 867 | 0 | 78 | 1369.1 | 46 | 3494 | 0 | 455 | 1683 | 0 | 0 | 0 | 0
19:30 | 3899 | 2307.5 | 867 | 0 | 72 | 1357.82 | 46 | 3752 | 0 | 465 | 1471 | 0 | 0 | 0 | 0
20:00 | 3935 | 2332 | 867 | 0 | 70 | 1360.07 | 46 | 3869 | 0 | 355 | 1158 | 0 | 0 | 0 | 0
20:30 | 3938 | 2412.5 | 890.5 | 0 | 74 | 1368.035 | 46 | 3972 | 0 | 355 | 1186.5 | 0 | 0 | 0 | 0
21:00 | 3941 | 2493 | 914 | 0 | 78 | 1376 | 46 | 4075 | 0 | 355 | 1215 | 0 | 0 | 0 | 0
21:30 | 3725 | 2494.75 | 914 | 0 | 82 | 1368.5 | 46 | 4057.5 | 0 | 346.5 | 1321 | 0 | 0 | 5.5 | 0
22:00 | 3509 | 2496.5 | 914 | 0 | 86 | 1361 | 46 | 4040 | 0 | 338 | 1427 | 0 | 0 | 11 | 0
22:30 | 3500 | 2495 | 914 | 0 | 84 | 1366 | 46 | 4074 | 0 | 307 | 1468 | 0 | 0 | 12.5 | 0
23:00 | 3491 | 2493.5 | 914 | 0 | 82 | 1371 | 46 | 4108 | 0 | 276 | 1509 | 0 | 0 | 14 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 18:30 | 374 | 00:00 | Payra | 416 | 07:00 | 407 | 00:00
Ashuganj | 412 | 18:00 | 377 | 11:00 | Rahanpur | 401 | 06:00 | 384 | 20:00
Bhulta | 405 | 18:00 | 381 | 12:00 | Rampal | 405 | 18:30 | 387 | 00:00
Bibiana | 395 | 06:00 | 385 | 00:00
BIPTC | 396 | 04:00 | 387 | 16:00
Bogura | 387 | 06:00 | 367 | 20:00
Gopalganj | 403 | 18:00 | 384 | 00:00
Kaliakoir | 377 | 16:00 | 354 | 09:00
Madunaghat | 399 | 19:00 | 386 | 00:00
Meghnaghat | 400 | 18:30 | 38 | 04:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 18:30 | 217 | 00:00 | Keranigonj | 227 | 18:00 | 215 | 00:00
AKSML | 233 | 18:00 | 225 | 02:00 | Khulna(S) | 232 | 06:00 | 221 | 21:00
Aminbazar | 230 | 18:00 | 217 | 00:00 | Madunaghat | 235 | 18:00 | 228 | 00:00
Ashuganj | 232 | 18:00 | 222 | 12:00 | Madunaghat-400 | 235 | 19:00 | 226 | 00:00
Ashuganj-400 | 232 | 18:00 | 222 | 12:00 | Maniknagar | 229 | 18:30 | 213 | 12:00
Baghabari | 235 | 05:00 | 131 | 08:00 | Meghnaghat | 237 | 18:30 | 222 | 00:00
Barapukuria | 225 | 06:00 | 216 | 18:00 | Meghnaghat-400 | 231 | 18:30 | 218 | 00:00
Barapukuria-230 | 225 | 06:00 | 216 | 18:00 | Mirsorai | 231 | 18:00 | 220 | 12:00
Barishal | 235 | 07:00 | 225 | 00:00 | Rajshahi | 234 | 05:00 | 221 | 20:00
Bheramara | 235 | 05:00 | 222 | 11:00 | Rampal | 231 | 06:00 | 220 | 00:00
Bhulta | 229 | 18:00 | 214 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 19:00 | 221 | 00:00 | Rampura | 228 | 18:30 | 211 | 12:00
BIPTC | 237 | 05:00 | 222 | 11:00 | Shikalbaha | 232 | 18:00 | 224 | 00:00
Bogura | 236 | 06:00 | 225 | 20:00 | Shyampur | 231 | 18:30 | 216 | 00:00
Bogura-400 | 238 | 07:00 | 225 | 20:00 | Siddhirganj | 224 | 17:00 | 218 | 00:00
Borhanuddin | 240 | 18:00 | 233 | 00:00 | Sirajgonj | 240 | 05:00 | 234 | 11:00
BSRM | 231 | 18:30 | 221 | 12:00 | Sreepur | 232 | 18:30 | 223 | 12:00
Cumilla(N) | 228 | 18:00 | 215 | 00:00 | Tongi | 223 | 19:00 | 211 | 00:00
Faridpur | 234 | 17:00 | 221 | 00:00
Fenchuganj | 232 | 18:30 | 223 | 12:00
Ghorashal | 225 | 01:00 | 220 | 00:00
Ghorashal-230 | 226 | 18:00 | 214 | 12:00
Gopalganj | 232 | 18:00 | 221 | 00:00
GPH | 232 | 18:00 | 224 | 12:00
Haripur | 230 | 18:30 | 215 | 12:00
Hasnabad | 228 | 18:00 | 216 | 00:00
Hathazari | 238 | 18:30 | 227 | 00:00
Ishurdi | 236 | 05:00 | 225 | 11:00
Jhenaidah | 230 | 06:00 | 218 | 21:00
Kaliakoir | 232 | 18:00 | 219 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 18:30 | 124 | 11:00 | Madunaghat | 134 | 18:00 | 129 | 00:00
Agargaon | 138 | 18:30 | 129 | 00:00 | Magura | 132 | 06:00 | 124 | 12:00
Agrabad | 133 | 06:00 | 129 | 02:00 | Mahasthangarh | 132 | 06:00 | 124 | 20:00
AKS | 129 | 10:00 | 126 | 01:00 | Manikganj | 129 | 18:30 | 120 | 08:00
Aminbazar | 135 | 18:00 | 126 | 00:00 | Maniknagar | 133 | 18:30 | 123 | 12:00
Amnura | 136 | 06:00 | 124 | 04:00 | Matarbari | 123 | 11:00 | 112 | 00:00
Ashuganj | 136 | 18:30 | 131 | 00:00 | Matuail | 134 | 18:00 | 124 | 12:00
Bagerhat | 126 | 05:00 | 116 | 21:00 | Millgate | 136 | 18:30 | 125 | 09:00
Bajitpur | 131 | 18:00 | 125 | 00:00 | Mirpur | 135 | 18:30 | 124 | 00:00
Bakulia | 134 | 18:00 | 129 | 00:00 | Mirzapur | 129 | 13:00 | 121 | 09:00
Banani | 135 | 18:30 | 122 | 12:00 | Mithapukur | 132 | 06:00 | 124 | 17:00
Bangabhaban | 132 | 19:00 | 123 | 12:00 | MI_Cement | 135 | 18:30 | 124 | 12:00
Barapukuria | 138 | 06:00 | 131 | 18:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 06:00 | 130 | 00:00 | Mogbazar | 135 | 07:00 | 125 | 11:00
Barishal | 130 | 07:00 | 121 | 00:00 | Mongla | 130 | 05:00 | 118 | 21:00
Barishal-230 | 132 | 07:00 | 124 | 00:00 | Motijheel | 132 | 19:00 | 123 | 12:00
Baroaulia | 134 | 18:00 | 129 | 00:00 | Muktagacha | 133 | 03:00 | 121 | 17:00
Baroirhat | 127 | 18:30 | 118 | 00:00 | Munshiganj | 133 | 18:00 | 123 | 12:00
Bashundhara | 134 | 18:30 | 123 | 12:00 | Muradnagar | 129 | 18:30 | 119 | 00:00
BashundharaCement | 132 | 19:00 | 123 | 00:00 | Mymensingh | 136 | 12:00 | 114 | 18:00
Beanibazar | 130 | 06:00 | 127 | 00:00 | Naogaon | 131 | 01:00 | 119 | 21:00
Benapole | 129 | 06:00 | 118 | 21:00 | Narail | 134 | 06:00 | 123 | 13:00
Bhaluka | 125 | 04:00 | 119 | 09:00 | Narinda | 134 | 06:00 | 123 | 13:00
Bhandaria | 126 | 08:00 | 115 | 00:00 | Narshingdi | 131 | 18:00 | 117 | 11:00
Bhangura | 133 | 05:00 | 126 | 11:00 | Natore | 133 | 05:00 | 126 | 20:00
Bheramara | 136 | 05:00 | 128 | 14:00 | Nawabganj | 138 | 18:00 | 127 | 00:00
Bheramara(GK) | 136 | 04:00 | 129 | 11:00 | Netrakona | 124 | 06:00 | 112 | 00:00
Bhulta | 130 | 18:30 | 120 | 00:00 | New | 135 | 18:00 | 125 | 12:00
Bog-Sherpur | 132 | 06:00 | 124 | 20:00 | Niamatpur | 136 | 06:00 | 128 | 19:00
Bogura | 134 | 05:00 | 126 | 21:00 | Noapara | 132 | 05:00 | 122 | 21:00
Bogura-230 | 134 | 06:00 | 126 | 20:00 | Pabna | 134 | 05:00 | 127 | 11:00
Brahmanbaria | 128 | 18:30 | 121 | 12:00 | Palashbari | 128 | 03:00 | 119 | 17:00
Cantonment | 138 | 18:30 | 128 | 00:00 | Panchagarh | 139 | 22:00 | 122 | 09:00
Chandpur | 131 | 18:00 | 113 | 00:00 | Patuakhali | 135 | 14:00 | 130 | 00:00
Chandraghona | 133 | 18:00 | 129 | 00:00 | Payra | 136 | 07:00 | 133 | 00:00
Chapai | 132 | 04:00 | 126 | 21:00 | PHP | 127 | 18:30 | 116 | 00:00
Charsaidpur | 134 | 18:30 | 124 | 00:00 | Postogola | 137 | 18:00 | 127 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 130 | 03:00 | 117 | 00:00 | Purbachal | 135 | 18:30 | 123 | 12:00
Chhatak | 130 | 06:00 | 126 | 00:00 | Purbasadipur | 132 | 22:00 | 119 | 09:00
Chowmuhani | 122 | 20:00 | 108 | 00:00 | Rahanpur | 137 | 06:00 | 130 | 20:00
Chuadanga | 131 | 05:00 | 121 | 22:00 | Rahanpur-400 | 137 | 06:00 | 131 | 19:00
Coxsbazar | 122 | 21:00 | 112 | 00:00 | Rahim | 132 | 18:00 | 124 | 12:00
Cumilla(N) | 131 | 18:30 | 121 | 00:00 | Rajbari | 130 | 17:00 | 121 | 00:00
Cumilla(S) | 130 | 06:00 | 120 | 00:00 | Rajendrapur | 133 | 18:30 | 125 | 08:00
Daudkandi | 128 | 18:00 | 117 | 00:00 | Rajshahi | 133 | 05:00 | 127 | 20:00
Dhaka | 135 | 18:00 | 124 | 11:00 | Rajshahi-230 | 135 | 05:00 | 120 | 19:00
Dhamrai | 132 | 18:00 | 122 | 00:00 | Ramganj | 123 | 18:30 | 107 | 00:00
Dhanmondi | 136 | 18:30 | 125 | 12:00 | Rampur | 133 | 18:00 | 127 | 11:00
Dohazari | 128 | 17:00 | 122 | 00:00 | Rampura | 136 | 18:30 | 124 | 12:00
Faridpur | 131 | 18:30 | 124 | 00:00 | Rangamati | 133 | 18:00 | 128 | 00:00
Fatullah | 135 | 18:30 | 125 | 12:00 | Rangpur | 131 | 23:00 | 120 | 18:00
Fenchuganj | 134 | 04:00 | 130 | 00:00 | Ruppur | 137 | 04:00 | 130 | 11:00
Feni | 125 | 18:30 | 117 | 00:00 | Saidpur | 135 | 22:00 | 121 | 18:00
Ghatail | 128 | 05:00 | 119 | 16:00 | Satkhira | 129 | 06:00 | 117 | 21:00
Ghorashal | 135 | 18:30 | 129 | 11:00 | Satmasjid | 139 | 18:30 | 128 | 00:00
Goalpara | 134 | 06:00 | 124 | 21:00 | Savar | 135 | 18:30 | 122 | 09:00
Gollamari | 133 | 06:00 | 125 | 21:00 | SevenRings | 137 | 18:30 | 129 | 11:00
Gopalganj | 133 | 06:00 | 125 | 21:00 | ShahCement | 134 | 18:30 | 124 | 00:00
Gopalganj-400 | 136 | 17:00 | 129 | 00:00 | Shahjadpur | 134 | 23:00 | 132 | 00:00
Gulshan | 134 | 06:00 | 124 | 12:00 | Shahjibazar | 131 | 18:30 | 124 | 00:00
Halishahar | 132 | 04:00 | 128 | 00:00 | Shahmirpur | 134 | 17:00 | 130 | 00:00
Haripur | 135 | 18:30 | 125 | 06:00 | Shariatpur | 134 | 06:00 | 125 | 00:00
HaripurSBU | 135 | 18:30 | 124 | 13:00 | Sherpur | 137 | 12:00 | 121 | 00:00
Hasnabad | 133 | 18:00 | 127 | 00:00 | Shikalbaha | 123 | 06:00 | 119 | 00:00
Hathazari | 136 | 18:30 | 130 | 00:00 | Shikalbaha-230 | 136 | 05:00 | 130 | 00:00
Ishurdi | 138 | 05:00 | 131 | 11:00 | Shitalakhya | 135 | 18:30 | 124 | 12:00
Jaldhaka | 132 | 14:00 | 119 | 09:00 | Sholosohor | 133 | 06:00 | 130 | 00:00
Jamalpur | 139 | 12:00 | 123 | 00:00 | Shyampur | 134 | 18:00 | 125 | 00:00
Jashore | 131 | 01:00 | 120 | 21:00 | Shyampur-230 | 135 | 18:30 | 125 | 00:00
Jhenaidah | 133 | 06:00 | 125 | 11:00 | Siddhirganj | 134 | 18:30 | 125 | 12:00
Jhenaidah-230 | 134 | 06:00 | 125 | 12:00 | Sirajganj | 130 | 05:00 | 124 | 09:00
Joydebpur | 137 | 18:00 | 125 | 00:00 | Sonargaon | 134 | 18:30 | 121 | 07:00
Joypurhat | 131 | 01:00 | 117 | 20:00 | Sreemongol | 129 | 05:00 | 125 | 00:00
Juldah | 134 | 17:00 | 129 | 11:00 | Sreepur | 130 | 18:30 | 124 | 00:00
Kabirpur | 132 | 18:30 | 121 | 09:00 | Srinagar | 137 | 18:30 | 127 | 00:00
Kachua | 131 | 18:00 | 114 | 00:00 | SSM | 139 | 18:00 | 130 | 16:00
Kaliakoir | 133 | 18:00 | 125 | 09:00 | Sunamganj | 130 | 07:00 | 125 | 00:00
Kallyanpur | 134 | 18:00 | 126 | 00:00 | Sylhet | 130 | 04:00 | 127 | 01:00
Kalurghat | 134 | 18:30 | 129 | 12:00 | Sylhet-132 | 132 | 06:00 | 128 | 00:00
Kamrangirchar | 138 | 18:00 | 126 | 00:00 | Tangail | 128 | 12:00 | 118 | 09:00
Kaptai | 136 | 18:00 | 132 | 1:00 | Thakurgaon | 138 | 22:00 | 119 | 09:00
Kazla | 133 | 19:00 | 123 | 12:00 | TK | 136 | 18:00 | 129 | 00:00
Keranigonj | 136 | 18:00 | 127 | 00:00 | Tongi | 134 | 18:30 | 128 | 00:00
Khagrachori | 131 | 06:00 | 127 | 00:00 | Ullahpara | 132 | 05:00 | 125 | 11:00
Khosba | 128 | 18:00 | 120 | 00:00 | Ullon | 134 | 19:00 | 124 | 12:00
Khulna | 129 | 05:00 | 120 | 21:00 | Uttara | 133 | 17:00 | 123 | 00:00
Khulna(S) | 134 | 06:00 | 125 | 21:00 | UttaraNew | 134 | 18:00 | 123 | 09:00
Khulshi | 131 | 17:00 | 126 | 09:00 | Zigatola | 137 | 18:30 | 128 | 00:00
Kishoreganj | 128 | 07:00 | 121 | 00:00
Kodda | 131 | 18:00 | 121 | 08:00
KSRM | 134 | 18:00 | 128 | 00:00
Kulaura | 132 | 07:00 | 129 | 00:00
Kurigram | 134 | 22:00 | 121 | 09:00
Kushtia | 135 | 06:00 | 126 | 13:00
Lalbag | 137 | 18:30 | 127 | 00:00
Lalmonirhat | 130 | 14:00 | 118 | 18:00
Madanganj | 132 | 19:00 | 123 | 00:00
Madaripur | 134 | 17:00 | 127 | 00:00
Madartek | 134 | 18:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division