## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-03-2025 | during | 19-03-2025 | during | 19-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 120 | 120 | 120 | 120 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 271 | 260 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 98 | 96 | 208.13 | 208.13 | 80 | 80 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 308 | 315 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 47 | 121 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 20 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 20 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 20 | 20 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 277 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 31 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 18 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 8 | 108 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2968 | 3068 | 5131.5 | 5100.5 | 3883.3 | 3852.3
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 56 | 80 | 56 | 80 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 2 | 32 | 2 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 106 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 1 | 0 | 3.25 | 0 | 3.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 0 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 854 | 856 | 875 | 875 | 875 | 875 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1809 | 1889 | 3188.97 | 3217.72 | 3073.97 | 3102.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 240 | 0 | 0 | machine problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 23 | 35 | 46.94 | 46.94 | 35 | 35 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 47 | 55 | 55 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 187 | 195 | 195 | 145 | 145 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 30 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 25 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 0 | 0 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 71 | 170 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 80 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 54 | 97 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 56 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 61 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 0 | 0 | 0 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1148 | 1373 | 1825.97 | 2065.97 | 1744.2 | 1744.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-03-2025 | during | 19-03-2025 | during | 19-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 7 | 210 | 210 | 11 | 11 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 166 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 109 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.96 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 239.96 | 294 | 652.7 | 601.5 | 453.7 | 402.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 40 | 38 | 39 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 5 | 5 | 40 | 40 | 5 | 5 | Gas shortage
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 165 | 165 | 165 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 22 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 350 | 380 | 380 | 352 | 352 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1502 | 1491 | 1611 | 1612 | 1510 | 1510
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 912 | 914 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 134 | 138 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 383 | 462 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1514 | 1531 | 3602.2 | 3512.2 | 2105.02 | 2015.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 465 | 323 | 660 | 660 | 420 | 420 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 10 | 10.12 | 10.12 | 6 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 126 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 1200 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1646.69 | 2180 | 2832.12 | 2831.12 | 2536 | 2539
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 172 | 155 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 149 | 155 | 220 | 220 | 190 | 190 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 152 | 152 | 220 | 220 | 190 | 190 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 90 | 90 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.89 | 0 | 5.52 | 0 | 5.52 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 909 | 1511.17 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.91 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 106 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1969.3 | 2392.67 | 3175.05 | 3014.53 | 2958.26 | 2797.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 62 | 61 | 61 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 172 | 170 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 84 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 34 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 40 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 201 | 0 | 185 | 0 | 185 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 481.9 | 350 | 694.4 | 473 | 654.42 | 433.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 13278.85 | 14568.67 | 22713.91 | 22428.54 | 18918.87 | 18396.5
Forecast Scenario (19-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13980 |  | 0 |  | 13980
|  |  |  | 1:00 | 13410 |  | 0 |  | 13410
|  |  |  | 2:00 | 12940 |  | 0 |  | 12940
|  |  |  | 3:00 | 13220 |  | 0 |  | 13220
|  |  |  | 4:00 | 12870 |  | 0 |  | 12870
|  |  |  | 5:00 | 12120 |  | 0 |  | 12120
|  |  |  | 6:00 | 11360 |  | 0 |  | 11360
|  |  |  | 7:00 | 11410 |  | 0 |  | 11410
|  |  |  | 8:00 | 11960 |  | 0 |  | 11960
|  |  |  | 9:00 | 12440 |  | 0 |  | 12440
|  |  |  | 10:00 | 12900 |  | 0 |  | 12900
|  |  |  | 11:00 | 12830 |  | 0 |  | 12830
|  |  |  | 12:00 | 13370 |  | 0 |  | 13370
|  |  |  | 13:00 | 13400 |  | 0 |  | 13400
|  |  |  | 14:00 | 13640 |  | 0 |  | 13640
|  |  |  | 15:00 | 13780 |  | 0 |  | 13780
|  |  |  | 16:00 | 13920 |  | 0 |  | 13920
|  |  |  | 17:00 | 13770 |  | 0 |  | 13770
|  |  |  | 18:00 | 13840 |  | 0 |  | 13840
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14390 |  | 0 |  | 14390
|  |  |  | 19:30 | 14410 |  | 0 |  | 14410
|  |  |  | 20:00 | 14400 |  | 0 |  | 14400
|  |  |  | 21:00 | 14560 |  | 0 |  | 14560
|  |  |  | 22:00 | 14300 |  | 0 |  | 14300
|  |  |  | 23:00 | 14350 |  | 0 |  | 14350
Probable Maximum Temperature: |  |  | 34.40°C
Probable Maximum Demand at Day Peak: |  |  | 13370.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14560.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14560.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 319.16 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:28 hrs on 19-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-03-2025 | [28 empty] | Date: | 18-03-2025 | [28 empty] | Date: | 18-03-2025 | [28 empty] | Date: | 18-03-2025 | [28 empty] | Date: | 18-03-2025 | [18 empty] | Date: | 18-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 0 | 149 | 31 | 0 | 0 | 0 | 126 | 22 | 0 | 450 | 285 | 583 | 0 | 17 | 22 | 300 | 39 | 0 | 0 | 52 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 51 | 0 | 0 | 100 | 24 | 0 | 46 | 0 | 30 | 865 | 0 | 0 | 0 | 8 | 0 | 175 | 0 | 0 | 0 | 910 | 0 | 51 | 70 | 100 | 0 | 200 | 285 | 5 | 208 | 36 | 51 | 50 | 155 | 35 | 17 | 70 | 80 | 0 | 0 | 0 | 295 | 320 | 349 | 5 | 40 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 50 | 57 | 11 | 0 | 0 | 12 | 7971 | 914 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 1360 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 162 | 0 | 191 | 0 | 0 | 0 | 0 | 2.5 | 169 | 62 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 118 | 220 | 0 | 165 | 1050 | 0 | 5854.5 | 13825.5 | 86.85
01:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 0 | 135 | 16 | 0 | 0 | 0 | 90 | 22 | 0 | 450 | 293 | 583 | 0 | 0 | 22 | 303 | 40 | 0 | 0 | 52 | 22 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 48 | 24 | 0 | 46 | 0 | 30 | 875 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 108 | 0 | 200 | 285 | 5 | 220 | 36 | 24 | 50 | 120 | 36 | 17 | 70 | 78 | 0 | 0 | 0 | 285 | 320 | 323 | 5 | 40 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 17 | 164 | 0 | 49 | 58 | 11 | 0 | 0 | 9 | 7574 | 915 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 0 | 1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 194 | 0 | 200 | 0 | 0 | 0 | 0 | 2.5 | 170 | 61 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 118 | 220 | 0 | 240 | 950 | 0 | 5650.5 | 13224.5 | 86.84
02:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 0 | 113 | 16 | 0 | 0 | 0 | 17 | 22 | 0 | 450 | 310 | 583 | 0 | 0 | 22 | 303 | 41 | 0 | 0 | 52 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 24 | 0 | 46 | 0 | 30 | 868 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 614 | 0 | 51 | 0 | 108 | 0 | 200 | 285 | 5 | 220 | 36 | 17 | 50 | 120 | 27 | 17 | 70 | 72 | 0 | 0 | 0 | 295 | 320 | 328 | 5 | 40 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 17 | 164 | 0 | 48 | 58 | 11 | 0 | 0 | 12 | 7186 | 914 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453 | 0 | 1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 199 | 0 | 203 | 0 | 98 | 0 | 0 | 2.5 | 168 | 61 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 128 | 220 | 0 | 309 | 950 | 0 | 5583.5 | 12769.5 | 86.84
03:00 | 0 | 34 | 8 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 0 | 105 | 48 | 0 | 0 | 17 | 17 | 22 | 0 | 450 | 312 | 583 | 0 | 0 | 22 | 303 | 41 | 0 | 0 | 52 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 48 | 24 | 0 | 46 | 0 | 30 | 866 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 108 | 0 | 200 | 285 | 5 | 202 | 36 | 17 | 50 | 120 | 28 | 17 | 70 | 74 | 0 | 0 | 0 | 315 | 320 | 329 | 5 | 40 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 17 | 165 | 0 | 49 | 86 | 11 | 0 | 0 | 12 | 7278 | 914 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 0 | 1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 194 | 0 | 200 | 0 | 214 | 0 | 0 | 2.5 | 169 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 128 | 220 | 0 | 379 | 950 | 0 | 5748.5 | 13026.5 | 86.83
04:00 | 0 | 34 | 8 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 0 | 105 | 47 | 0 | 0 | 35 | 0 | 22 | 0 | 400 | 276 | 583 | 0 | 0 | 22 | 290 | 41 | 0 | 0 | 17 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 100 | 12 | 0 | 46 | 0 | 30 | 820 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 583 | 0 | 51 | 0 | 108 | 0 | 150 | 285 | 5 | 182 | 36 | 47 | 50 | 100 | 27 | 17 | 70 | 72 | 0 | 0 | 0 | 290 | 320 | 345 | 5 | 40 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 17 | 164 | 0 | 78 | 133 | 11 | 0 | 0 | 12 | 7117 | 913 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 188 | 0 | 190 | 0 | 300 | 0 | 0 | 2.5 | 170 | 62 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 10 | 122 | 180 | 0 | 535 | 850 | 0 | 5752.5 | 12869.5 | 86.83
05:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 54 | 0 | 105 | 16 | 0 | 0 | 35 | 0 | 22 | 0 | 400 | 300 | 583 | 0 | 0 | 22 | 282 | 40 | 0 | 0 | 17 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 70 | 12 | 0 | 46 | 0 | 33 | 752 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 490 | 0 | 51 | 0 | 108 | 0 | 150 | 285 | 5 | 194 | 36 | 50 | 50 | 100 | 28 | 17 | 70 | 58 | 0 | 0 | 0 | 300 | 320 | 353 | 5 | 40 | 0 | 5 | 120 | 22 | 0 | 85 | 30 | 0 | 17 | 164 | 17 | 79 | 135 | 11 | 0 | 0 | 12 | 6927 | 914 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 180 | 0 | 150 | 0 | 300 | 0 | 0 | 2.5 | 172 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 134 | 180 | 0 | 563 | 600 | 0 | 5193.5 | 12120.5 | 86.82
06:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 17 | 0 | 105 | 16 | 0 | 0 | 17 | 0 | 22 | 0 | 400 | 292 | 583 | 0 | 0 | 22 | 282 | 40 | 0 | 0 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 33 | 750 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 405 | 0 | 51 | 0 | 108 | 0 | 150 | 285 | 5 | 188 | 36 | 24 | 50 | 68 | 28 | 17 | 35 | 62 | 0 | 0 | 0 | 310 | 320 | 340 | 5 | 40 | 0 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 17 | 48 | 115 | 17 | 0 | 0 | 12 | 6554 | 914 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 175 | 0 | 150 | 0 | 350 | 0 | 0 | 2.5 | 175 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 122 | 180 | 0 | 271 | 550 | 0 | 4812.5 | 11366.5 | 86.82
07:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 25 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 311 | 583 | 0 | 0 | 22 | 285 | 40 | 0 | 3 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 1 | 0 | 7 | 0 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 14 | 751 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 405 | 1 | 51 | 0 | 108 | 0 | 55 | 285 | 5 | 214 | 36 | 17 | 50 | 68 | 0 | 17 | 34 | 58 | 0 | 6 | 0 | 305 | 320 | 375 | 5 | 40 | 0 | 5 | 120 | 16 | 0 | 85 | 30 | 0 | 17 | 164 | 17 | 53 | 118 | 18 | 0 | 4.56 | 12 | 6453.56 | 914 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.91 | 415 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 4.84 | 190 | 0 | 173 | 0 | 150 | 0 | 414 | 0 | 0.37 | 2.5 | 174 | 62 | 0 | 4 | 0 | 0 | 0 | 0.8 | 19 | 0.04 | 0 | 150 | 7 | 134 | 180 | 0 | 311 | 550 | 0 | 4959.46 | 11413.02 | 86.81
08:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 40 | 0 | 121 | 48 | 0 | 0 | 0 | 35 | 22 | 0 | 420 | 307 | 583 | 0 | 0 | 22 | 290 | 101 | 0 | 10 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 7 | 0 | 0 | 0 | 24 | 0 | 1 | 46 | 0 | 4 | 754 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 500 | 6 | 51 | 0 | 108 | 0 | 0 | 285 | 10 | 190 | 36 | 17 | 50 | 68 | 0 | 17 | 35 | 56 | 0 | 5 | 0 | 315 | 320 | 347 | 5 | 40 | 0 | 5 | 163 | 16 | 0 | 0 | 25 | 0 | 17 | 164 | 17 | 79 | 135 | 18 | 0 | 11.39 | 12 | 6701.39 | 872 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.81 | 415 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 17.86 | 183 | 0 | 165 | 0 | 163 | 0 | 414 | 0 | 1.59 | 5.5 | 171 | 62 | 0 | 15 | 0 | 0 | 0 | 2.9 | 69 | 0.14 | 0 | 250 | 7 | 128 | 220 | 0 | 419 | 550 | 0 | 5264.8 | 11966.19 | 86.81
09:00 | 0 | 52 | 16 | 120 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 54 | 0 | 132 | 48 | 0 | 0 | 0 | 35 | 22 | 0 | 420 | 291 | 583 | 0 | 0 | 22 | 324 | 99 | 0 | 18 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 3 | 755 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 500 | 12 | 51 | 0 | 112 | 0 | 0 | 285 | 44 | 182 | 37 | 17 | 50 | 68 | 0 | 17 | 35 | 56 | 0 | 18 | 0 | 300 | 320 | 345 | 5 | 40 | 0 | 5 | 163 | 16 | 0 | 85 | 28 | 0 | 17 | 165 | 17 | 79 | 136 | 15 | 1 | 25.4 | 12 | 6969.4 | 864 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 421 | 0 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 31.77 | 179 | 0 | 162 | 0 | 163 | 0 | 360 | 0 | 3.38 | 5.5 | 170 | 62 | 0 | 28 | 0 | 0 | 0 | 4.9 | 126 | 0.32 | 0 | 250 | 6 | 120 | 180 | 0 | 525 | 600 | 0 | 5431.87 | 12401.27 | 86.8
10:00 | 0 | 52 | 16 | 120 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 33 | 0 | 132 | 48 | 275 | 0 | 17 | 72 | 22 | 0 | 420 | 296 | 500 | 0 | 0 | 22 | 321 | 98 | 0 | 25 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 89 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 2 | 751 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 500 | 16 | 51 | 0 | 145 | 0 | 0 | 285 | 46 | 182 | 27 | 17 | 50 | 68 | 0 | 17 | 35 | 60 | 0 | 47 | 0 | 300 | 320 | 345 | 5 | 40 | 0 | 5 | 120 | 16 | 0 | 84 | 30 | 0 | 17 | 165 | 17 | 79 | 135 | 10 | 2 | 42.85 | 12 | 7302.85 | 865 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 415 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 51.45 | 176 | 0 | 160 | 0 | 162 | 0 | 414 | 0 | 4.24 | 5.5 | 172 | 62 | 0 | 36 | 0 | 0 | 0 | 6.6 | 170 | 0.27 | 0 | 307 | 6 | 120 | 220 | 0 | 312 | 600 | 0 | 5471.06 | 12773.91 | 86.8
11:00 | 0 | 52 | 16 | 120 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 18 | 0 | 132 | 47 | 275 | 0 | 35 | 72 | 22 | 0 | 420 | 305 | 500 | 0 | 0 | 16 | 316 | 96 | 0 | 30 | 0 | 22 | 14 | 0 | 0 | 0 | 0 | 109 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 2 | 757 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 500 | 18 | 51 | 0 | 145 | 0 | 0 | 285 | 48 | 204 | 32 | 40 | 50 | 68 | 0 | 17 | 35 | 70 | 0 | 53 | 0 | 290 | 320 | 384 | 5 | 39 | 0 | 5 | 120 | 16 | 0 | 81 | 30 | 0 | 15 | 165 | 0 | 59 | 135 | 7 | 2 | 46.47 | 12 | 7341.47 | 865 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 384 | 0 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 60.89 | 173 | 0 | 152 | 0 | 156 | 0 | 350 | 0 | 5.43 | 5.5 | 168 | 62 | 0 | 40 | 0 | 0 | 0 | 7.6 | 193 | 0.57 | 0 | 233 | 4 | 126 | 220 | 0 | 320 | 650 | 0 | 5403.99 | 12745.46 | 86.79
12:00 | 0 | 52 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 132 | 47 | 277 | 0 | 35 | 72 | 22 | 0 | 420 | 271 | 583 | 0 | 0 | 20 | 308 | 98 | 0 | 32 | 8 | 22 | 14 | 0 | 0 | 0 | 0 | 106 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 2 | 854 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 19 | 51 | 0 | 182 | 0 | 0 | 285 | 48 | 182 | 23 | 51 | 50 | 71 | 0 | 17 | 54 | 74 | 0 | 60 | 0 | 310 | 320 | 350 | 5 | 39 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 15 | 165 | 0 | 59 | 115 | 5 | 2 | 46.96 | 12 | 7666.96 | 912 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 383 | 0 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 57.91 | 172 | 0 | 149 | 0 | 152 | 0 | 414 | 0 | 3.89 | 5.5 | 172 | 61 | 0 | 40 | 0 | 0 | 0 | 7.9 | 201 | 0.69 | 0 | 230 | 5 | 126 | 220 | 0 | 465 | 600 | 0 | 5611.89 | 13278.85 | 86.79
13:00 | 0 | 52 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 149 | 60 | 277 | 0 | 35 | 72 | 22 | 0 | 420 | 301 | 583 | 0 | 0 | 20 | 309 | 95 | 0 | 31 | 35 | 22 | 20 | 0 | 0 | 0 | 0 | 107 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 4 | 855 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 17 | 51 | 0 | 184 | 0 | 0 | 285 | 48 | 191 | 30 | 53 | 50 | 100 | 0 | 17 | 70 | 74 | 0 | 56 | 0 | 295 | 360 | 350 | 5 | 38 | 0 | 5 | 163 | 16 | 0 | 84 | 30 | 0 | 15 | 163 | 0 | 78 | 125 | 5 | 2 | 47.67 | 12 | 7879.67 | 912 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 451 | 0 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 60.78 | 170 | 0 | 147 | 0 | 148 | 0 | 414 | 0 | 5.12 | 5.5 | 171 | 61 | 0 | 40 | 0 | 0 | 0 | 5.8 | 195 | 0.55 | 0 | 250 | 6 | 126 | 220 | 0 | 281 | 570 | 0 | 5463.75 | 13343.42 | 86.78
14:00 | 0 | 35 | 16 | 120 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 18 | 0 | 148 | 60 | 261 | 0 | 35 | 72 | 22 | 0 | 420 | 301 | 583 | 0 | 0 | 20 | 308 | 94 | 0 | 28 | 35 | 22 | 20 | 0 | 0 | 0 | 0 | 109 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 4 | 855 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 15 | 51 | 0 | 184 | 0 | 0 | 285 | 47 | 210 | 31 | 51 | 50 | 100 | 0 | 17 | 70 | 56 | 0 | 47 | 0 | 315 | 320 | 388 | 5 | 38 | 0 | 2 | 163 | 22 | 0 | 84 | 30 | 0 | 17 | 162 | 0 | 78 | 124 | 5 | 2 | 44.49 | 12 | 7848.49 | 912 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 460 | 0 | 1003.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 54.31 | 169 | 0 | 142 | 0 | 145 | 0 | 414 | 0 | 4.97 | 5.5 | 168 | 62 | 0 | 37 | 0 | 0 | 0 | 6.6 | 184 | 0.51 | 0 | 307 | 7 | 128 | 220 | 0 | 311 | 700 | 0 | 5732.86 | 13581.35 | 86.78
15:00 | 8 | 35 | 16 | 120 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 18 | 0 | 146 | 60 | 264 | 0 | 35 | 72 | 22 | 2 | 420 | 303 | 583 | 0 | 17 | 20 | 308 | 94 | 0 | 21 | 70 | 14 | 20 | 0 | 0 | 0 | 0 | 109 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 4 | 855 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 12 | 51 | 3 | 175 | 0 | 0 | 285 | 44 | 196 | 34 | 51 | 50 | 128 | 0 | 17 | 97 | 70 | 0 | 24 | 0 | 315 | 320 | 359 | 5 | 38 | 0 | 0 | 163 | 22 | 0 | 84 | 30 | 0 | 15 | 162 | 0 | 78 | 114 | 6 | 2 | 37.07 | 12 | 7871.07 | 912 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 462 | 0 | 1205.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 43.5 | 167 | 0 | 141 | 0 | 141 | 0 | 414 | 0 | 3.91 | 5.5 | 173 | 62 | 0 | 30 | 0 | 0 | 0 | 5.6 | 144 | 0.39 | 0 | 307 | 7 | 128 | 220 | 0 | 320 | 700 | 0 | 5844.21 | 13715.28 | 86.77
16:00 | 8 | 35 | 16 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 18 | 0 | 146 | 105 | 264 | 48 | 35 | 72 | 22 | 26 | 420 | 285 | 583 | 0 | 35 | 20 | 308 | 96 | 0 | 13 | 108 | 20 | 20 | 0 | 0 | 0 | 0 | 106 | 0 | 13 | 0 | 0 | 0 | 36 | 0 | 1 | 86 | 0 | 5 | 855 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 7 | 51 | 43 | 175 | 0 | 0 | 285 | 44 | 183 | 34 | 50 | 50 | 155 | 17 | 17 | 97 | 54 | 0 | 19 | 0 | 300 | 320 | 351 | 5 | 38 | 0 | 0 | 163 | 22 | 0 | 84 | 30 | 0 | 15 | 165 | 0 | 78 | 123 | 4 | 1 | 24.16 | 12 | 8150.16 | 912 | 124 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 462 | 0 | 1225.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 28.21 | 162 | 0 | 141 | 0 | 142 | 0 | 414 | 0 | 2.54 | 5.5 | 170 | 62 | 0 | 19 | 0 | 0 | 0 | 3.7 | 93 | 0.22 | 0 | 307 | 6 | 118 | 220 | 0 | 320 | 700 | 0 | 5727.55 | 13877.71 | 86.77
17:00 | 8 | 35 | 16 | 120 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 18 | 0 | 147 | 121 | 210 | 55 | 35 | 72 | 22 | 31 | 420 | 302 | 583 | 0 | 17 | 20 | 310 | 96 | 0 | 5 | 108 | 20 | 20 | 0 | 0 | 0 | 0 | 109 | 0 | 7 | 0 | 0 | 0 | 36 | 0 | 0 | 46 | 0 | 7 | 856 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 505 | 2 | 51 | 50 | 185 | 0 | 0 | 285 | 45 | 196 | 34 | 52 | 50 | 157 | 27 | 17 | 97 | 76 | 0 | 7 | 0 | 300 | 320 | 367 | 5 | 38 | 0 | 5 | 163 | 22 | 0 | 84 | 30 | 0 | 17 | 165 | 0 | 78 | 135 | 5 | 0 | 9.16 | 11 | 8059.16 | 912 | 123 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 405 | 0 | 1312.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 10.4 | 151 | 0 | 141 | 0 | 143 | 0 | 414 | 0 | 0.95 | 5.5 | 169 | 62 | 34 | 8 | 35 | 0 | 0 | 1.5 | 33 | 0.1 | 0 | 307 | 6 | 126 | 220 | 0 | 320 | 700 | 0 | 5684.2 | 13743.36 | 86.76
18:00 | 8 | 70 | 25 | 120 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 54 | 18 | 0 | 149 | 121 | 160 | 40 | 55 | 100 | 22 | 31 | 420 | 282 | 583 | 0 | 17 | 20 | 307 | 99 | 0 | 0 | 108 | 20 | 20 | 0 | 0 | 0 | 0 | 109 | 0 | 7 | 13 | 0 | 0 | 36 | 0 | 0 | 46 | 0 | 21 | 855 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 505 | 0 | 51 | 50 | 185 | 0 | 0 | 285 | 44 | 183 | 31 | 55 | 50 | 169 | 31 | 17 | 97 | 80 | 0 | 0 | 24 | 300 | 320 | 290 | 5 | 38 | 0 | 5 | 163 | 22 | 0 | 84 | 28 | 0 | 15 | 165 | 0 | 95 | 161 | 4 | 0 | 0.45 | 6 | 8063.45 | 912 | 123 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 412 | 0 | 1360.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 143 | 0 | 147 | 0 | 414 | 0 | 0.05 | 5.5 | 171 | 62 | 70 | 0 | 105 | 0 | 0 | 0.1 | 2 | 0 | 0 | 307 | 8 | 126 | 220 | 0 | 322 | 700 | 0 | 5779.09 | 13842.54 | 86.76
19:00 | 0 | 88 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 18 | 0 | 149 | 121 | 95 | 40 | 55 | 162 | 22 | 31 | 420 | 307 | 583 | 0 | 17 | 20 | 313 | 96 | 0 | 0 | 108 | 21 | 20 | 0 | 0 | 0 | 0 | 108 | 0 | 5 | 34 | 7 | 0 | 36 | 0 | 0 | 46 | 0 | 20 | 857 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 550 | 0 | 51 | 50 | 185 | 0 | 0 | 285 | 47 | 201 | 31 | 69 | 50 | 170 | 55 | 17 | 97 | 74 | 0 | 0 | 24 | 290 | 320 | 385 | 5 | 40 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 15 | 165 | 0 | 107 | 173 | 5 | 0 | 0 | 12 | 8338 | 866 | 138 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474 | 0 | 1512.22 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 0 | 5.5 | 171 | 62 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 130 | 220 | 0 | 325 | 750 | 0 | 6052.72 | 14390.72 | 86.75
19:30 | 0 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 18 | 0 | 149 | 121 | 45 | 40 | 55 | 162 | 22 | 31 | 420 | 271 | 583 | 0 | 0 | 20 | 315 | 99 | 0 | 0 | 108 | 20 | 20 | 0 | 0 | 0 | 0 | 56 | 0 | 5 | 34 | 8 | 0 | 90 | 4 | 0 | 46 | 0 | 20 | 857 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 550 | 0 | 51 | 50 | 187 | 0 | 0 | 285 | 46 | 184 | 31 | 68 | 50 | 170 | 55 | 17 | 97 | 76 | 0 | 0 | 24 | 290 | 320 | 349 | 5 | 40 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 15 | 165 | 0 | 107 | 173 | 6 | 0 | 0 | 12 | 8214 | 867 | 138 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 0 | 1509.18 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 153 | 0 | 151 | 0 | 414 | 0 | 0 | 5.5 | 173 | 62 | 72 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 323 | 900 | 0 | 6197.68 | 14411.68
20:00 | 0 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 18 | 0 | 149 | 121 | 15 | 15 | 55 | 162 | 22 | 31 | 420 | 276 | 583 | 0 | 0 | 20 | 312 | 99 | 0 | 0 | 108 | 20 | 20 | 0 | 0 | 0 | 0 | 51 | 0 | 2 | 34 | 24 | 0 | 100 | 12 | 0 | 46 | 0 | 20 | 856 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 550 | 0 | 51 | 50 | 187 | 0 | 0 | 285 | 47 | 182 | 32 | 69 | 50 | 170 | 54 | 17 | 97 | 74 | 0 | 0 | 24 | 295 | 320 | 349 | 5 | 40 | 0 | 5 | 163 | 22 | 0 | 85 | 30 | 0 | 15 | 165 | 0 | 108 | 173 | 8 | 0 | 0 | 12 | 8191 | 867 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 1510.05 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 153 | 0 | 150 | 0 | 414 | 0 | 0 | 5.5 | 171 | 62 | 72 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 323 | 930 | 0 | 6209.55 | 14400.55 | 86.75
21:00 | 0 | 105 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 18 | 0 | 149 | 121 | 0 | 0 | 55 | 162 | 22 | 31 | 420 | 260 | 583 | 0 | 0 | 20 | 315 | 96 | 0 | 0 | 108 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 36 | 0 | 46 | 0 | 20 | 856 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 0 | 51 | 30 | 187 | 0 | 0 | 285 | 47 | 182 | 35 | 61 | 50 | 170 | 56 | 17 | 97 | 80 | 0 | 0 | 25 | 290 | 320 | 350 | 5 | 40 | 0 | 5 | 163 | 22 | 0 | 86 | 30 | 0 | 15 | 165 | 0 | 109 | 166 | 7 | 0 | 0 | 12 | 8115 | 914 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 17 | 1511.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 155 | 0 | 152 | 0 | 414 | 0 | 0 | 5.5 | 170 | 62 | 34 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 323 | 1200 | 0 | 6453.67 | 14568.67 | 86.74
22:00 | 0 | 88 | 25 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 128 | 92 | 0 | 0 | 55 | 108 | 22 | 31 | 420 | 279 | 583 | 0 | 0 | 20 | 303 | 97 | 0 | 0 | 70 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 36 | 0 | 46 | 0 | 24 | 856 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 187 | 0 | 0 | 285 | 48 | 182 | 35 | 51 | 50 | 170 | 56 | 17 | 97 | 84 | 0 | 0 | 25 | 285 | 320 | 350 | 5 | 42 | 0 | 5 | 163 | 22 | 0 | 86 | 30 | 0 | 15 | 165 | 0 | 109 | 166 | 5 | 0 | 0 | 12 | 7887 | 914 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447 | 0 | 1516.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 155 | 0 | 156 | 0 | 414 | 0 | 0 | 5.5 | 172 | 65 | 34 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 118 | 220 | 0 | 323 | 1230 | 0 | 6434.3 | 14321.3 | 86.74
23:00 | 0 | 70 | 17 | 120 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 18 | 0 | 114 | 92 | 5 | 0 | 0 | 72 | 22 | 31 | 420 | 294 | 583 | 0 | 0 | 18 | 303 | 101 | 0 | 0 | 70 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 36 | 0 | 46 | 0 | 29 | 859 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 189 | 0 | 0 | 285 | 50 | 187 | 30 | 39 | 50 | 170 | 56 | 17 | 97 | 86 | 0 | 0 | 25 | 310 | 320 | 348 | 5 | 41 | 0 | 5 | 163 | 22 | 0 | 86 | 30 | 0 | 0 | 164 | 0 | 109 | 156 | 5 | 0 | 0 | 12 | 7756 | 914 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 1357.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 156 | 0 | 414 | 0 | 0 | 2.5 | 172 | 64 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 323 | 1120 | 0 | 6106.59 | 13862.59 | 86.73
Total KWH | 32976 | 1082880 | 358080 | 2893700 | 0 | 0 | 0 | 0 | 9471600 | 0 | 0 | 294120 | 717840 | 0 | 3130704 | 1502400 | 2424535 | 233138 | 595856 | 1608480 | 555840 | 275520 | 9956000 | 7053556 | 13620000 | 0 | 104851 | 487700 | 7306476 | 1967000 | 0 | 214414 | 1204800 | 500400 | 469440 | 0 | 0 | 0 | 0 | 1162560 | 0 | 145440 | 206185 | 35328 | 0 | 1090560 | 243840 | 15961 | 1095540 | 0 | 421920 | 19949090.91 | 0 | 0 | 0 | 0 | 0 | 3998312 | 0 | 0 | 0 | 13832726 | 123660 | 1089460 | 379709 | 3646545 | 0 | 1281500 | 6926000 | 793440 | 4750000 | 811368 | 985920 | 1199180 | 2989920 | 573720 | 413120 | 1727100 | 1680960 | 0 | 337055 | 152864 | 7317000 | 7731600 | 8867000 | 191664 | 939000 | 0 | 94656 | 3665782 | 480384 | 0 | 1958400 | 700320 | 0 | 354000 | 4395060 | 122760 | 1830000 | 3019200 | 186240 | 15350 | 337660 | 287520 | 182614885.91 | 21799272 | 3802752 | 0 | 0 | 56320 | 0 | 0 | 0 | 0 | 0 | 0 | 588960 | 10610910 | 31200 | 27331182 | 0 | 0 | 0 | 50688 | 0 | 50512 | 0 | 0 | 0 | 722090 | 0 | 414000 | 4094000 | 0 | 4087564 | 0 | 4074127 | 0 | 8432218 | 0 | 35340 | 107082 | 4168000 | 1425163 | 410830 | 289293 | 808656 | 0 | 0 | 54686.16 | 1429920 | 3732 | 0 | 6219000 | 198220 | 2928000 | 5179320 | 0 | 8152727 | 19728000 | 0 | 137283764.16 | 319898650.07

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13278.85 | MW | 12:00 Hr. | Energy Generated |  |  | 319.8987 |  | MKWHr.
| Day Peak Demand |  |  | 13374.85 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.306 |  | MKWHr.
| Evening Peak Generation |  |  | 14568.67 | MW | 21:00 Hr. | Energy Demand |  |  | 321.2047 |  | MKWHr.
| Evening Peak Demand |  |  | 14568.67 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.8 |  | °C
| Minimum Generation of the Day |  |  | 11366.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1083.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 14568.67 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9739 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 54.2817 | 0 | 13.5662 | 0 | 0 | 0.21441 | 0 | 0 | 68.0623 | Gas | 149.3969 | Gas | 486473005.27
| Chattogram Zone |  |  | 4.4202 | 33.7818 | 2.7385 | 0 | 1.0955 | 0.13962 | 0 | 0.14544 | 42.3211 | Coal | 84.0856 | Coal | 539654755.8078
| Cumilla Zone |  |  | 20.9106 | 0 | 6.8092 | 0 | 0 | 0.33705 | 1.681 | 0 | 29.7379 | HFO | 29.7816 | HFO | 539100258.62
| Mymensingh Zone |  |  | 0.18624 | 0 | 5.2595 | 0 | 0 | 0.35301 | 0 | 0 | 5.7987 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.6949 | Hydro | 1.0955 | Hydro | 109554
| Khulna Zone |  |  | 3.8028 | 10.6109 | 0.08752 | 0 | 0 | 0.58896 | 21.7993 | 0 | 36.8894 | Solar | 4.5821 | Solar | 75800976.3876
| Barishal Zone |  |  | 8.3055 | 34.0997 | 0 | 0 | 0 | 0.003732 | 0 | 0 | 42.409 | Import | 50.8114 | Import | 267769606.08
| Rajshahi Zone |  |  | 20.795 | 0 | 0.1012 | 0 | 0 | 1.1714 | 27.3312 | 0 | 49.3988 | Wind | 0.14544 | Wind | 2129241.6
| Rangpur Zone |  |  | 0 | 5.5932 | 1.2195 | 0 | 0 | 1.7739 | 0 | 0 | 8.5865
| Total |  |  | 149.3969 | 84.0856 | 29.7816 | 0 | 1.0955 | 4.5821 | 50.8114 | 0.14544 | 319.8987
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 486473005.27 |  | Hydro | 109554
|  |  |  | Coal | 539654755.8078 |  | Solar | 75800976.3876
|  |  |  | HFO | 539100258.62 |  | Import | 267769606.08
|  |  |  | HSD | 0 |  | Wind | 2129241.6
[5 empty] | Total: | 191,10,37,397 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7993 | Peak Hr Flow | 914.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34115533.16 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.3312 | Peak Hr Flow | 1511.17 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 718 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.681 | Peak Hr Flow | 80.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 878 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.8114 | Peak Hr Flow | 2505.17 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5172
|  |  |  | Chattogram |  | 0 |  | 1412
|  |  |  | Cumilla |  | 0 |  | 1415
|  |  |  | Mymensingh |  | 0 |  | 1109
|  |  |  | Sylhet |  | 0 |  | 496
|  |  |  | Khulna |  | 0 |  | 1625
|  |  |  | Barishal |  | 0 |  | 442
|  |  |  | Rajshahi |  | 0 |  | 1441
|  |  |  | Rangpur |  | 0 |  | 800
|  |  |  | Total |  | 0 |  | 13912
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Shahjibazar 132/33kV S/S SPCL 86 MW is restored.
|  | 08:01 | Shahjibazar-Sreemangal 132kV Ckt-2 is restored.
| 08:15 | 16:57 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Blast wall construction | [7 empty] | 5.0MW load
interrup.
| 08:15 | 16:57 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Blast wall construction | [7 empty] | 5.0MW load
interrup.
| 08:20 | 15:20 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast wall construction | [7 empty] | 20.0MW load
interrup.
| 08:20 | 15:20 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast wall construction | [7 empty] | 20.0MW load
interrup.
|  | 08:50 | Bogura 132/33kV S/S Transformer-1 LT is restored.
|  | 08:50 | Bogura 132/33kV S/S Transformer-1 HT is restored.
|  | 08:52 | Bogura 132/33kV S/S Transformer-2 LT is restored.
|  | 08:52 | Bogura 132/33kV S/S Transformer-2 HT is restored.
| 08:56 | 14:54 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Line maintenance.
| 09:38 | 11:22 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Forced S/D
| 09:38 | 11:21 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Forced S/D
| 09:45 | 16:06 | GPH 230/33kV S/S BSRM CKT-1 Scheduled S/D Due to for rust cleaning
|  | 09:50 | Feni 132/33kV S/S T-2(415T) HT is restored.
|  | 09:50 | Feni 132/33kV S/S T-2(415T) LT is restored.
|  | 10:47 | Chandpur 132/33kV S/S 33 kV T-5 section is restored.
|  | 10:47 | Chandpur 132/33kV S/S 33 kV T-2 section is restored.
| 10:53 | 13:01 | BIPTC S/S 20DF24 Scheduled S/D Due to Tripped by Impedance 21R
| 11:10 | 11:48 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Forced S/D Due to Project work for Rajendrapur line
bay commissioning.
| 11:45 | 12:20 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing O/c, E/F relays Due to Wzpdcl | [7 empty] | 56.0MW load
|  |  | dopdopia 2 feeder fault and fire. | [7 empty] | interrup.
| 11:46 | 13:45 | Sirajganj 132/33kV S/S Solar Park 1 Scheduled S/D Due to SCADA Commissioning at Solar
park end.
| 12:15 | 12:39 | Sreepur 230/132/33kV S/S 132 kV BUS-2 Forced S/D Due to Project work for Rajendrapur
line Commissioning
| 13:55 | 15:45 | Sirajganj 132/33kV S/S Solar Park 2 Scheduled S/D Due to SCADA Commissioning at Solar
park end..
|  | 14:33 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
| 21:00 |  | Evening peak Generation is 14568 MW
| 22:56 | 00:05 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Forced S/D Due to Keranihat REB red hot | [7 empty] | 60.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 22:56 | 00:05 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Forced S/D Due to Keranihat REB redhot | [7 empty] | 60.0MW load
|  |  | maintenance at bus side D/S. | [7 empty] | interrup.
| 05:32 |  | Bheramara 410 MW CCPP tripped due to a fire at GT and ST underground cable.
| 06:00 |  | Minimum generation 11151 MW
| 06:00 |  | Minimum Generation: 11151 MW.
| 06:22 | 07:46 | Bheramara P/S-Ishurdi 132 kV Ckt-1 Forced S/D from Ishurdi 132/33kV end.
| 06:22 | 07:46 | Bheramara P/S-Ishurdi 132 kV Ckt-2 Forced S/D from Ishurdi 132/33kV end.
| 07:20 |  | Bheramara P/S-Kustia 132 kV Ckt-1 Forced S/D from Kushtia 132/33kV end Due to Shout down
by ALDC
| 07:22 |  | Bheramara P/S-Kustia 132 kV Ckt-2 Forced S/D from Kushtia 132/33kV end Due to Shout down
by ALDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2893700 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9471600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9956000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 260 | 7053556 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 233138 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 96 | 1967000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 7306476 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 32976 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 294120 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 121 | 1502400 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 595856 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 104851 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 500400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 469440 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 555840 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 487700 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 358080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 2424535 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3130704 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1082880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 31 | 275520 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1608480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 214414 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 18 | 717840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 13620000 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1204800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6085.764 | 3068 | 68062306
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 123660 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1095540 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3998312 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 35328 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 206185 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1090560 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 421920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 1162560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 15961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 243840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13832726 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 145440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 856 | 19949090.91 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 1889 | 42321122.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4750000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 1281500 | GT under hot commissioning load will vary.
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6926000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 811368 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 793440 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 187 | 3646545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1089460 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 30 | 379709 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 25 | 152864 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1199180 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 2989920 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1680960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 413120 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1727100 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 573720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 61 | 985920 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 337055 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1373 | 29737861
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 7 | 186240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 166 | 3019200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 109 | 1830000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 337660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 287520 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 122760 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 294 | 5798730
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 939000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3665782 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 5 | 191664 | Gas shortage
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 94656 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 700320 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1958400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 165 | 4395060 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 354000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 480384 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7317000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8867000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7731600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1491 | 36694866
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 914 | 21799272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 56320 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 138 | 3802752 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 31200 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 588960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 462 | 10610910 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1531 | 36889414
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 323 | 8152727 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 198220 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 120 | 2928000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 19728000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5179320 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6219000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3732 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2180 | 42408999
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 155 | 4094000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 155 | 4087564 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 152 | 4074127 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8432218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 107082 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 50512 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 50688 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1511.17 | 27331182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 414000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 722090 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2392.67 | 49398803
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1425163 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4168000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 84 | 808656 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 54686.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 34 | 410830 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 289293 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1429920 | -
Rangpur Area Total |  |  |  |  | 950 | 350 | 8586548.16
Eastern Grid Total |  |  |  |  | 16921.242 | 8115 | 182614885.91
Western Grid Total |  |  |  |  | 11614.5 | 6453.67 | 137283764.16
National Grid Total |  |  |  |  | 28535.742 | 14568.67 | 319898650.07
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9604.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4307.3 | MW
i) Dhaka area |  |  | 5172.29 |  | MW | i) Khulna area |  |  |  | 1625 | MW
ii) Chattogram area |  |  | 1412 |  | MW | ii) Barishal area |  |  |  | 441.5 | MW
iii) Cumilla area |  |  | 1415 |  | MW | iii) Rajshahi area |  |  |  | 1440.8 | MW
iv) Mymensingh area |  |  | 1109 |  | MW | iv) Rangpur area |  |  |  | 800 | MW
v) Sylhet area |  |  | 496 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13911.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 76 | 10:00 | 133 | Payra | 30 | 21:00
2 | AKSML | 24 | 17:00 | 68 | Jamalpur | 112 | 19:00 | 134 | Postogola | 51 | 16:00
3 | Aftabnagar | 34 | 00:00 | 69 | Jashore | 140 | 19:30 | 135 | Purbachal | 18 | 00:00
4 | Agargaon | 105 | 13:00 | 70 | Jhenaidah | 123 | 19:00 | 136 | Purbasadipur | 121 | 18:00
5 | Agrabad | 90 | 12:00 | 71 | Joydebpur | 142 | 16:00 | 137 | Rahanpur | 32 | 19:00
6 | Amnura | 43 | 20:00 | 72 | Joypurhat | 66 | 21:00 | 138 | Rahim | 35 | 16:00
7 | Ashuganj | 90 | 23:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 68 | 19:00
8 | BSRM | 204 | 05:00 | 74 | KSRM | 23 | 18:30 | 140 | Rajendrapur | 118 | 16:00
9 | Bagerhat | 83 | 00:00 | 75 | Kabirpur | 259 | 17:00 | 141 | Rajshahi | 100 | 22:00
10 | Bajitpur | 46 | 18:00 | 76 | Kachua | 81 | 21:00 | 142 | Rajshahi-230 | 79 | 21:00
11 | Bakulia | 94 | 19:30 | 77 | Kallyanpur | 105 | 19:30 | 143 | Ramganj | 112 | 00:00
12 | Banani | 28 | 11:00 | 78 | Kalurghat | 40 | 10:00 | 144 | Rampur | 39 | 00:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kamrangirchar | 67.5 | 12:00 | 145 | Rangamati | 16 | 18:30
14 | Barapukuria | 63 | 10:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 132 | 17:00
15 | Barguna | 22 | 22:00 | 81 | Kazla | 95 | 16:00 | 147 | Ruppur | 7 | 10:00
16 | Barishal | 105 | 00:00 | 82 | Keranigonj | 77 | 16:00 | 148 | SSM | 14 | 06:00
17 | Barishal-230 | 94 | 14:00 | 83 | Khagrachori | 30 | 18:30 | 149 | Saidpur | 109 | 10:00
18 | Baroaulia | 62 | 10:00 | 84 | Khosba | 34 | 21:00 | 150 | Satkhira | 128 | 18:30
19 | Baroirhat | 61 | 19:30 | 85 | Khulna | 64 | 18:30 | 151 | Satmasjid | 100 | 19:30
20 | Bashundhara | 164 | 14:00 | 86 | Khulshi | 176 | 12:00 | 152 | Savar | 216 | 10:00
21 | BashundharaCement | 8 | 12:00 | 87 | Kishoreganj | 130 | 19:30 | 153 | SevenRings | 19.45 | 20:00
22 | Beanibazar | 60 | 18:30 | 88 | Kodda | 314 | 21:00 | 154 | ShahCement | 40 | 19:30
23 | Benapole | 67 | 00:00 | 89 | Kulaura | 36 | 19:00 | 155 | Shahjadpur | 81 | 19:30
24 | Bhaluka | 145 | 18:00 | 90 | Kurigram | 65 | 18:00 | 156 | Shahjibazar | 117 | 00:00
25 | Bhandaria | 51 | 22:00 | 91 | Kushtia | 126 | 16:00 | 157 | Shahmirpur | 57 | 09:00
26 | Bhangura | 39 | 14:00 | 92 | Lalbag | 62 | 13:00 | 158 | Shariatpur | 78 | 00:00
27 | Bheramara(GK) | 54 | 19:00 | 93 | Lalmonirhat | 52 | 18:00 | 159 | Sherpur | 160 | 18:00
28 | Bhulta | 269 | 03:00 | 94 | MI_Cement | 18.1 | 23:00 | 160 | Shikalbaha | 28 | 15:00
29 | Bog-Sherpur | 80 | 03:00 | 95 | Madanganj | 39 | 19:30 | 161 | Shitalakhya | 81.5 | 15:00
30 | Bogura | 159 | 22:00 | 96 | Madaripur | 107 | 00:00 | 162 | Sholosohor | 41 | 15:00
31 | Borhanuddin | 83 | 22:00 | 97 | Madartek | 83.67 | 00:00 | 163 | Shyampur | 160 | 14:00
32 | Brahmanbaria | 122 | 21:00 | 98 | Madunaghat | 48 | 18:30 | 164 | Siddhirganj | 116 | 08:00
33 | Cantonment | 138 | 13:00 | 99 | Magura | 62 | 19:00 | 165 | Sirajganj | 106 | 20:00
34 | Chandpur | 67 | 21:00 | 100 | Mahasthangarh | 68 | 21:00 | 166 | Sonargaon | 102 | 03:00
35 | Chandraghona | 34 | 19:00 | 101 | Manikganj | 119 | 20:00 | 167 | Sreemongol | 63 | 19:00
36 | Chapai | 64 | 23:00 | 102 | Maniknagar | 68 | 13:00 | 168 | Sreepur | 98 | 10:00
37 | Charsaidpur | 49 | 15:00 | 103 | Matarbari | 48 | 00:00 | 169 | Srinagar | 41.59 | 20:00
38 | Chauddagram | 76 | 18:30 | 104 | Matuail | 69 | 09:00 | 170 | Sunamganj | 45 | 20:00
39 | Chhatak | 27 | 21:00 | 105 | Millgate | 105 | 10:00 | 171 | Sylhet | 36 | 14:00
40 | Chowmuhani | 230 | 20:00 | 106 | Mirpur | 131 | 20:00 | 172 | Sylhet-132 | 101 | 15:00
41 | Chuadanga | 98 | 18:30 | 107 | Mirsorai | 10 | 01:00 | 173 | TK | 31 | 00:00
42 | Coxsbazar | 125 | 18:30 | 108 | Mirzapur | 46 | 22:00 | 174 | Tangail | 182 | 13:00
43 | Cumilla(N) | 164 | 16:00 | 109 | Mithapukur | 60 | 03:00 | 175 | Thakurgaon | 92 | 19:00
44 | Cumilla(S) | 171 | 15:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 110 | 00:00
45 | Daudkandi | 141 | 19:00 | 111 | Mogbazar | 135.4 | 14:00 | 177 | Ullahpara | 32 | 08:00
46 | Dhaka | 52 | 13:00 | 112 | Mongla | 33 | 05:00 | 178 | Ullon | 46 | 20:00
47 | Dhamrai | 128 | 19:00 | 113 | Motijheel | 35 | 14:00 | 179 | Uttara | 84 | 13:00
48 | Dhanmondi | 134 | 13:00 | 114 | Muktagacha | 38 | 18:00 | 180 | UttaraNew | 52 | 00:00
49 | Dohazari | 98 | 18:30 | 115 | Munshiganj | 102 | 00:00 | 181 | Zigatola | 66 | 16:00
50 | Faridpur | 144 | 19:00 | 116 | Muradnagar | 26 | 18:30
51 | Fatullah | 96 | 12:00 | 117 | Mymensingh | 202 | 18:00
52 | Fenchuganj | 27 | 21:00 | 118 | Naogaon | 128 | 00:00
53 | Feni | 118 | 21:00 | 119 | Narail | 56 | 00:00
54 | GPH | 96 | 03:00 | 120 | Narinda | 80 | 15:00
55 | Ghatail | 80 | 17:00 | 121 | Narshingdi | 172 | 22:00
56 | Ghorashal | 14 | 11:00 | 122 | Natore | 143 | 19:30
57 | Ghorashal-230 | 82 | 21:00 | 123 | Nawabganj | 51.4 | 20:00
58 | Goalpara | 34 | 00:00 | 124 | Netrakona | 141 | 18:00
59 | Gollamari | 88 | 00:00 | 125 | New | 83.5 | 15:00
60 | Gopalganj | 103 | 00:00 | 126 | Niamatpur | 107 | 21:00
61 | Gulshan | 110 | 12:00 | 127 | Noapara | 46 | 20:00
62 | Halishahar | 72 | 10:00 | 128 | PHP | 3 | 00:00
63 | HaripurSBU | 185 | 04:00 | 129 | Pabna | 104 | 03:00
64 | Hasnabad | 95 | 16:00 | 130 | Palashbari | 110 | 18:00
65 | Hathazari | 80 | 19:30 | 131 | Panchagarh | 53 | 18:00
66 | Ishurdi | 68 | 19:30 | 132 | Patuakhali | 74 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13825.5 | 148 |  | 13980.16
1:00 | 13224.5 | 178 |  | 13410.5
2:00 | 12769.5 | 163 |  | 12939.5
3:00 | 13026.5 | 190 |  | 13225.5
4:00 | 12869.5 | 0 |  | 12869.5
5:00 | 12120.5 | 0 |  | 12120.5
6:00 | 11366.5 | 0 |  | 11366.5
7:00 | 11413.02 | 0 |  | 11413.02
8:00 | 11966.19 | 0 |  | 11966.19
9:00 | 12401.27 | 45 |  | 12448.27
10:00 | 12773.91 | 123 |  | 12902.91
11:00 | 12745.46 | 89 |  | 12838.46
12:00 | 13278.85 | 92 |  | 13374.85
13:00 | 13343.42 | 62 |  | 13408.42
14:00 | 13581.35 | 65 |  | 13649.35
15:00 | 13715.28 | 70 |  | 13788.28
16:00 | 13877.71 | 48 |  | 13927.71
17:00 | 13743.36 | 33 |  | 13777.36
18:00 | 13842.54 | 0 |  | 13842.54
19:00 | 14390.72 | 0 |  | 14390.72
19:30 | 14411.68 | 0 |  | 14411.68
20:00 | 14400.55 | 0 |  | 14400.55
21:00 | 14568.67 | 0 |  | 14568.67
22:00 | 14321.3 | 0 |  | 14321.3
23:00 | 13862.59 | 0 |  | 13862.59
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7971 | 5854.5 | 13825.5 | DAILY GENERATION CURVE
00:30 | 7772.5 | 5752.5 | 13525
01:00 | 7574 | 5650.5 | 13224.5 | 18-03-2025
01:30 | 7380 | 5617 | 12997
02:00 | 7186 | 5583.5 | 12769.5
02:30 | 7232 | 5666 | 12898
03:00 | 7278 | 5748.5 | 13026.5
03:30 | 7197.5 | 5750.5 | 12948
04:00 | 7117 | 5752.5 | 12869.5
04:30 | 7022 | 5473 | 12495
05:00 | 6927 | 5193.5 | 12120.5
05:30 | 6740.5 | 5003 | 11743.5
06:00 | 6554 | 4812.5 | 11366.5
06:30 | 6503.78 | 4885.98 | 11389.76
07:00 | 6453.56 | 4959.46 | 11413.02
07:30 | 6577.475 | 5112.13 | 11689.605
08:00 | 6701.39 | 5264.8 | 11966.19
08:30 | 6835.395 | 5348.335 | 12183.73
09:00 | 6969.4 | 5431.87 | 12401.27
09:30 | 7136.125 | 5451.465 | 12587.59
10:00 | 7302.85 | 5471.06 | 12773.91
10:30 | 7322.16 | 5437.525 | 12759.685
11:00 | 7341.47 | 5403.99 | 12745.46
11:30 | 7504.215 | 5507.94 | 13012.155
12:00 | 7666.96 | 5611.89 | 13278.85
12:30 | 7773.315 | 5537.82 | 13311.135
13:00 | 7879.67 | 5463.75 | 13343.42
13:30 | 7864.08 | 5598.305 | 13462.385
14:00 | 7848.49 | 5732.86 | 13581.35
14:30 | 7859.78 | 5788.535 | 13648.315
15:00 | 7871.07 | 5844.21 | 13715.28
15:30 | 8010.615 | 5785.88 | 13796.495
16:00 | 8150.16 | 5727.55 | 13877.71
16:30 | 8104.66 | 5705.875 | 13810.535
17:00 | 8059.16 | 5684.2 | 13743.36
17:30 | 8061.305 | 5731.645 | 13792.95
18:00 | 8063.45 | 5779.09 | 13842.54
18:30 | 8200.725 | 5915.905 | 14116.63
19:00 | 8338 | 6052.72 | 14390.72
19:30 | 8214 | 6197.68 | 14411.68
20:00 | 8191 | 6209.55 | 14400.55
20:30 | 8153 | 6331.61 | 14484.61 |  | Executive Engineer
21:00 | 8115 | 6453.67 | 14568.67 |  | Network Operation Division
21:30 | 8001 | 6443.985 | 14444.985
22:00 | 7887 | 6434.3 | 14321.3
22:30 | 7821.5 | 6270.445 | 14091.945
23:00 | 7756 | 6106.59 | 13862.59

## En-Curve
QF-LDC-12
Date | 18-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3521 | 2412.5 | 914 | 0 | 80 | 1360 | 46 | 4027 | 0 | 177 | 1274 | 0 | 0 | 14 | 148 | DAILY ENERGY CURVE
00:30 | 3547 | 2393.5 | 914.5 | 0 | 79 | 1359 | 46 | 4015.5 | 0 | 135 | 1020 | 0 | 0 | 15.5 | 163 | 18-03-2025
01:00 | 3573 | 2374.5 | 915 | 0 | 78 | 1358 | 46 | 4004 | 0 | 93 | 766 | 0 | 0 | 17 | 178
01:30 | 3636.5 | 2390 | 914.5 | 0 | 75 | 1288 | 46 | 3838.5 | 0 | 93 | 707 | 0 | 0 | 8.5 | 170.5 | Energy Generated | 319.8987 |  | MKWHr
02:00 | 3700 | 2405.5 | 914 | 0 | 72 | 1218 | 46 | 3673 | 0 | 93 | 648 | 0 | 0 | 0 | 163 | Energy not Served | 1.306 |  | MKWHr
02:30 | 3744 | 2416.5 | 914 | 0 | 73 | 1211.5 | 46 | 3710.5 | 0 | 117.5 | 664.5 | 0 | 0 | 0.5 | 176.5 | Total Energy Requirement | 321.2047 |  | MKWHr
03:00 | 3788 | 2427.5 | 914 | 0 | 74 | 1205 | 46 | 3748 | 0 | 142 | 681 | 0 | 0 | 1 | 190
03:30 | 3795.5 | 2352 | 913.5 | 0 | 73 | 1145.5 | 46 | 3733.5 | 0 | 124 | 762 | 0 | 0 | 3 | 95
04:00 | 3803 | 2276.5 | 913 | 0 | 72 | 1086 | 46 | 3719 | 0 | 106 | 843 | 0 | 0 | 5 | 0
04:30 | 3786.5 | 2295 | 913.5 | 0 | 65 | 1017 | 46 | 3463 | 0 | 82 | 822 | 0 | 0 | 5 | 0
05:00 | 3770 | 2313.5 | 914 | 0 | 58 | 948 | 46 | 3207 | 0 | 58 | 801 | 0 | 0 | 5 | 0
05:30 | 3779 | 2311 | 914 | 0 | 60 | 932.5 | 46 | 2992 | 0 | 49.5 | 655.5 | 0 | 0 | 4 | 0
06:00 | 3788 | 2308.5 | 914 | 0 | 62 | 917 | 46 | 2777 | 0 | 41 | 510 | 0 | 0 | 3 | 0
06:30 | 3808.5 | 2280 | 914 | 0 | 60 | 918 | 46 | 2797.5 | 27.76 | 41 | 492 | 0 | 0 | 5 | 0
07:00 | 3829 | 2251.5 | 914 | 0 | 58 | 919 | 46 | 2818 | 55.52 | 41 | 474 | 0 | 0 | 7 | 0
07:30 | 3798.5 | 2287.5 | 893 | 0 | 57 | 916.5 | 46 | 2969.5 | 125.105 | 57 | 532.5 | 0 | 0 | 7 | 0
08:00 | 3768 | 2323.5 | 872 | 0 | 56 | 914 | 46 | 3121 | 194.69 | 73 | 591 | 0 | 0 | 7 | 0
08:30 | 3760.5 | 2348 | 868 | 0 | 56 | 911 | 46 | 3202 | 287.73 | 94.5 | 605 | 0 | 0 | 5 | 22.5
09:00 | 3753 | 2372.5 | 864 | 0 | 56 | 908 | 46 | 3283 | 380.77 | 116 | 619 | 0 | 0 | 3 | 45
09:30 | 3770 | 2349 | 864.5 | 0 | 58 | 911.5 | 46 | 3201 | 467.59 | 116 | 800 | 0 | 0 | 4 | 84
10:00 | 3787 | 2325.5 | 865 | 0 | 60 | 915 | 46 | 3119 | 554.41 | 116 | 981 | 0 | 0 | 5 | 123
10:30 | 3754.5 | 2317 | 865 | 0 | 65 | 914 | 46 | 3096.5 | 597.185 | 115.5 | 985.5 | 0 | 0 | 3.5 | 106
11:00 | 3722 | 2308.5 | 865 | 0 | 70 | 913 | 46 | 3074 | 639.96 | 115 | 990 | 0 | 0 | 2 | 89
11:30 | 3710.5 | 2387 | 888.5 | 0 | 72 | 911 | 46 | 3225.5 | 651.655 | 119 | 996 | 0 | 0 | 5 | 90.5
12:00 | 3699 | 2465.5 | 912 | 0 | 74 | 909 | 46 | 3377 | 663.35 | 123 | 1002 | 0 | 0 | 8 | 92
12:30 | 3718.5 | 2478.5 | 912 | 0 | 74 | 910.5 | 46 | 3314 | 654.135 | 143 | 1049 | 0 | 0 | 11.5 | 77
13:00 | 3738 | 2491.5 | 912 | 0 | 74 | 912 | 46 | 3251 | 644.92 | 163 | 1096 | 0 | 0 | 15 | 62
13:30 | 3740 | 2503 | 912 | 0 | 65 | 957.985 | 46 | 3363 | 617.9 | 154.5 | 1087 | 0 | 0 | 16 | 63.5
14:00 | 3742 | 2514.5 | 912 | 0 | 56 | 1003.97 | 46 | 3475 | 590.88 | 146 | 1078 | 0 | 0 | 17 | 65
14:30 | 3716.5 | 2504.5 | 912 | 0 | 63 | 1104.64 | 46 | 3483 | 522.675 | 163.5 | 1116 | 0 | 0 | 16.5 | 67.5
15:00 | 3691 | 2494.5 | 912 | 0 | 70 | 1205.31 | 46 | 3491 | 454.47 | 181 | 1154 | 0 | 0 | 16 | 70
15:30 | 3676.5 | 2481 | 912 | 0 | 62 | 1215.345 | 66 | 3489.5 | 375.15 | 225.5 | 1279 | 0 | 0 | 14.5 | 59
16:00 | 3662 | 2467.5 | 912 | 0 | 54 | 1225.38 | 86 | 3488 | 295.83 | 270 | 1404 | 0 | 0 | 13 | 48
16:30 | 3678 | 2485 | 912 | 0 | 65 | 1269.065 | 66 | 3406 | 203.47 | 280 | 1436 | 0 | 0 | 10 | 40.5
17:00 | 3694 | 2502.5 | 912 | 0 | 76 | 1312.75 | 46 | 3324 | 111.11 | 290 | 1468 | 0 | 0 | 7 | 33
17:30 | 3651 | 2500 | 912 | 0 | 78 | 1336.595 | 46 | 3329 | 57.355 | 334 | 1542 | 0 | 0 | 7 | 16.5
18:00 | 3608 | 2497.5 | 912 | 0 | 80 | 1360.44 | 46 | 3334 | 3.6 | 378 | 1616 | 0 | 0 | 7 | 0
18:30 | 3677.5 | 2507.5 | 889 | 0 | 77 | 1436.33 | 46 | 3415 | 1.8 | 412 | 1648.5 | 0 | 0 | 6 | 0
19:00 | 3747 | 2517.5 | 866 | 0 | 74 | 1512.22 | 46 | 3496 | 0 | 446 | 1681 | 0 | 0 | 5 | 0
19:30 | 3700 | 2481.5 | 867 | 0 | 76 | 1509.18 | 46 | 3633 | 0 | 473 | 1621 | 0 | 0 | 5 | 0
20:00 | 3695 | 2493.5 | 867 | 0 | 74 | 1510.05 | 46 | 3661 | 0 | 472 | 1580 | 0 | 0 | 2 | 0
20:30 | 3700.5 | 2483.5 | 890.5 | 0 | 77 | 1510.61 | 46 | 3826.5 | 0 | 457 | 1492 | 0 | 0 | 1 | 0
21:00 | 3706 | 2473.5 | 914 | 0 | 80 | 1511.17 | 46 | 3992 | 0 | 442 | 1404 | 0 | 0 | 0 | 0
21:30 | 3711.5 | 2483 | 914 | 0 | 82 | 1513.985 | 46 | 4002 | 0 | 388 | 1304.5 | 0 | 0 | 0 | 0
22:00 | 3717 | 2492.5 | 914 | 0 | 84 | 1516.8 | 46 | 4012 | 0 | 334 | 1205 | 0 | 0 | 0 | 0
22:30 | 3701 | 2514.5 | 914 | 0 | 85 | 1436.945 | 46 | 3929 | 0 | 321 | 1144.5 | 0 | 0 | 0 | 0
23:00 | 3685 | 2536.5 | 914 | 0 | 86 | 1357.09 | 46 | 3846 | 0 | 308 | 1084 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 06:00 | 366 | 00:00 | Payra | 417 | 06:00 | 409 | 21:00
Ashuganj | 404 | 6:00 | 384 | 15:00 | Rahanpur | 398 | 06:00 | 381 | 17:00
Bhulta | 398 | 06:00 | 372 | 14:00 | Rampal | 407 | 06:00 | 390 | 22:00
Bibiana | 394 | 04:00 | 387 | 15:00
BIPTC | 398 | 16:00 | 389 | 16:00
Bogura | 384 | 06:00 | 363 | 22:00
Gopalganj | 406 | 06:00 | 390 | 22:00
Kaliakoir | 372 | 18:00 | 343 | 14:00
Madunaghat | 397 | 06:00 | 386 | 15:00
Meghnaghat | 400 | 06:00 | 383 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 18:30 | 217 | 14:00 | Keranigonj | 230 | 18:30 | 216 | 14:00
AKSML | 231 | 18:00 | 222 | 14:00 | Khulna(S) | 235 | 06:00 | 220 | 21:00
Aminbazar | 230 | 05:00 | 218 | 14:00 | Madunaghat | 234 | 18:00 | 225 | 14:00
Ashuganj | 234 | 18:00 | 223 | 15:00 | Madunaghat-400 | 233 | 05:00 | 226 | 15:00
Ashuganj-400 | 234 | 6:00 | 218 | 15:00 | Maniknagar | 225 | 03:00 | 214 | 14:00
Baghabari | 235 | 05:00 | 225 | 22:00 | Meghnaghat | 234 | 04:00 | 224 | 14:00
Barapukuria | 224 | 00:00 | 214 | 17:00 | Meghnaghat-400 | 230 | 06:00 | 219 | 14:00
Barapukuria-230 | 224 | 1:00 | 214 | 17:00 | Mirsorai | 228 | 06:00 | 217 | 13:00
Barishal | 236 | 06:00 | 228 | 22:00 | Rajshahi | 234 | 02:00 | 221 | 14:00
Bheramara | 236 | 02:00 | 223 | 14:00 | Rampal | 233 | 06:00 | 222 | 21:00
Bhulta | 227 | 06:00 | 214 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 18:00 | 221 | 14:00 | Rampura | 227 | 06:00 | 212 | 14:00
BIPTC | 237 | 02:00 | 222 | 14:00 | Shikalbaha | 230 | 05:00 | 222 | 14:00
Bogura | 235 | 05:00 | 223 | 17:00 | Shyampur | 228 | 06:00 | 216 | 14:00
Bogura-400 | 234 | 05:00 | 223 | 17:00 | Siddhirganj | 228 | 04:00 | 216 | 14:00
Borhanuddin | 240 | 09:00 | 235 | 22:00 | Sirajgonj | 241 | 06:00 | 234 | 22:00
BSRM | 227 | 04:00 | 218 | 15:00 | Sreepur | 233 | 04:00 | 222 | 14:00
Cumilla(N) | 226 | 18:30 | 216 | 13:00 | Tongi | 222 | 06:00 | 212 | 13:00
Faridpur | 235 | 06:00 | 225 | 14:00
Fenchuganj | 232 | 18:00 | 225 | 07:00
Ghorashal | 230 | 18:00 | 220 | 14:00
Ghorashal-230 | 228 | 18:30 | 215 | 14:00
Gopalganj | 233 | 06:00 | 225 | 14:00
GPH | 229 | 06:00 | 223 | 14:00
Haripur | 228 | 18:30 | 214 | 14:00
Hasnabad | 226 | 03:00 | 218 | 15:00
Hathazari | 232 | 01:00 | 226 | 13:00
Ishurdi | 237 | 02:00 | 224 | 19:00
Jhenaidah | 231 | 06:00 | 217 | 21:00
Kaliakoir | 232 | 18:00 | 216 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 125 | 14:00 | Madunaghat | 133 | 18:00 | 128 | 15:00
Agargaon | 138 | 06:00 | 128 | 14:00 | Magura | 133 | 06:00 | 123 | 21:00
Agrabad | 131 | 05:00 | 125 | 14:00 | Mahasthangarh | 132 | 00:00 | 121 | 17:00
AKS | 129 | 03:00 | 125 | 12:00 | Manikganj | 129 | 20:00 | 119 | 07:00
Aminbazar | 135 | 18:00 | 127 | 14:00 | Maniknagar | 133 | 06:00 | 124 | 13:00
Amnura | 135 | 05:00 | 124 | 17:00 | Matarbari | 122 | 10:00 | 112 | 21:00
Ashuganj | 135 | 04:00 | 131 | 14:00 | Matuail | 132 | 05:00 | 124 | 14:00
Bagerhat | 131 | 07:00 | 119 | 19:00 | Millgate | 135 | 18:00 | 125 | 14:00
Bajitpur | 132 | 05:00 | 124 | 14:00 | Mirpur | 134 | 06:00 | 125 | 14:00
Bakulia | 133 | 18:00 | 127 | 14:00 | Mirzapur | 131 | 04:00 | 120 | 14:00
Banani | 135 | 03:00 | 124 | 14:00 | Mithapukur | 132 | 00:00 | 120 | 17:00
Bangabhaban | 132 | 03:00 | 123 | 14:00 | MI_Cement | 134 | 18:30 | 123 | 14:00
Barapukuria | 139 | 00:00 | 129 | 16:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 06:00 | 130 | 21:00 | Mogbazar | 136 | 03:00 | 128 | 12:00
Barishal | 131 | 06:00 | 125 | 00:00 | Mongla | 131 | 08:00 | 120 | 19:00
Barishal-230 | 132 | 06:00 | 126 | 00:00 | Motijheel | 132 | 03:00 | 123 | 14:00
Baroaulia | 132 | 02:00 | 127 | 15:00 | Muktagacha | 132 | 05:00 | 120 | 00:00
Baroirhat | 125 | 18:30 | 117 | 14:00 | Munshiganj | 133 | 18:00 | 123 | 14:00
Bashundhara | 135 | 03:00 | 124 | 14:00 | Muradnagar | 127 | 18:00 | 119 | 15:00
BashundharaCement | 131 | 19:00 | 123 | 14:00 | Mymensingh | 133 | 05:00 | 114 | 14:00
Beanibazar | 132 | 06:00 | 127 | 14:00 | Naogaon | 128 | 05:00 | 118 | 17:00
Benapole | 130 | 06:00 | 114 | 21:00 | Narail | 132 | 03:00 | 123 | 19:00
Bhaluka | 128 | 05:00 | 118 | 14:00 | Narinda | 133 | 6:00 | 124 | 13:00
Bhandaria | 126 | 12:00 | 116 | 00:00 | Narshingdi | 129 | 18:00 | 117 | 22:00
Bhangura | 133 | 02:00 | 127 | 14:00 | Natore | 132 | 00:00 | 124 | 17:00
Bheramara | 136 | 02:00 | 129 | 14:00 | Nawabganj | 137 | 03:00 | 128 | 14:00
Bheramara(GK) | 136 | 04:00 | 128 | 21:00 | Netrakona | 126 | 05:00 | 112 | 14:00
Bhulta | 128 | 05:00 | 118 | 14:00 | New | 136 | 18:30 | 125 | 14:00
Bog-Sherpur | 131 | 05:00 | 122 | 17:00 | Niamatpur | 135 | 04:00 | 127 | 18:00
Bogura | 133 | 00:00 | 124 | 18:00 | Noapara | 134 | 07:00 | 123 | 19:00
Bogura-230 | 133 | 00:00 | 125 | 17:00 | Pabna | 136 | 06:00 | 127 | 15:00
Brahmanbaria | 130 | 06:00 | 121 | 14:00 | Palashbari | 129 | 00:00 | 117 | 17:00
Cantonment | 138 | 06:00 | 128 | 14:00 | Panchagarh | 141 | 00:00 | 119 | 16:00
Chandpur | 127 | 19:30 | 117 | 14:00 | Patuakhali | 135 | 07:00 | 131 | 00:00
Chandraghona | 133 | 06:00 | 127 | 14:00 | Payra | 136 | 07:00 | 133 | 22:00
Chapai | 133 | 01:00 | 124 | 18:00 | PHP | 124 | 18:30 | 116 | 12:00
Charsaidpur | 133 | 18:00 | 124 | 14:00 | Postogola | 137 | 18:00 | 126 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 123 | 04:00 | 20 | 02:00 | Purbachal | 137 | 06:00 | 126 | 14:00
Chhatak | 133 | 05:00 | 127 | 13:00 | Purbasadipur | 133 | 00:00 | 116 | 13:00
Chowmuhani | 119 | 18:00 | 110 | 13:00 | Rahanpur | 136 | 04:00 | 129 | 18:00
Chuadanga | 133 | 06:00 | 120 | 19:00 | Rahanpur-400 | 136 | 05:00 | 130 | 17:00
Coxsbazar | 121 | 09:00 | 113 | 21:00 | Rahim | 131 | 05:00 | 124 | 15:00
Cumilla(N) | 128 | 18:30 | 122 | 13:00 | Rajbari | 130 | 06:00 | 123 | 22:00
Cumilla(S) | 130 | 01:00 | 119 | 14:00 | Rajendrapur | 134 | 18:30 | 121 | 15:00
Daudkandi | 125 | 18:00 | 117 | 14:00 | Rajshahi | 134 | 06:00 | 126 | 21:00
Dhaka | 136 | 04:00 | 125 | 14:00 | Rajshahi-230 | 135 | 03:00 | 119 | 17:00
Dhamrai | 129 | 03:00 | 120 | 14:00 | Ramganj | 121 | 18:30 | 110 | 13:00
Dhanmondi | 137 | 06:00 | 127 | 15:00 | Rampur | 131 | 06:00 | 125 | 14:00
Dohazari | 128 | 09:00 | 122 | 14:00 | Rampura | 136 | 04:00 | 125 | 14:00
Faridpur | 131 | 07:00 | 126 | 14:00 | Rangamati | 131 | 05:00 | 126 | 14:00
Fatullah | 134 | 18:30 | 124 | 15:00 | Rangpur | 133 | 00:00 | 119 | 17:00
Fenchuganj | 133 | 02:00 | 131 | 05:00 | Ruppur | 137 | 03:00 | 130 | 15:00
Feni | 124 | 19:30 | 114 | 15:00 | Saidpur | 134 | 00:00 | 120 | 13:00
Ghatail | 130 | 03:00 | 116 | 17:00 | Satkhira | 132 | 14:00 | 119 | 19:00
Ghorashal | 136 | 04:00 | 130 | 11:00 | Satmasjid | 137 | 04:00 | 129 | 13:00
Goalpara | 133 | 09:00 | 123 | 19:00 | Savar | 135 | 18:00 | 126 | 14:00
Gollamari | 135 | 06:00 | 126 | 19:00 | SevenRings | 136 | 03:00 | 128 | 14:00
Gopalganj | 135 | 06:00 | 127 | 21:00 | ShahCement | 133 | 18:00 | 124 | 14:00
Gopalganj-400 | 138 | 06:00 | 132 | 14:00 | Shahjadpur | 138 | 01:00 | 129 | 16:00
Gulshan | 136 | 06:00 | 125 | 14:00 | Shahjibazar | 130 | 06:00 | 124 | 07:00
Halishahar | 130 | 00:00 | 127 | 14:00 | Shahmirpur | 133 | 03:00 | 128 | 14:00
Haripur | 134 | 18:30 | 125 | 15:00 | Shariatpur | 135 | 05:00 | 128 | 14:00
HaripurSBU | 134 | 18:30 | 125 | 15:00 | Sherpur | 135 | 10:00 | 118 | 00:00
Hasnabad | 133 | 03:00 | 126 | 14:00 | Shikalbaha | 122 | 00:00 | 118 | 14:00
Hathazari | 134 | 17:00 | 129 | 13:00 | Shikalbaha-230 | 134 | 05:00 | 128 | 14:00
Ishurdi | 138 | 02:00 | 130 | 22:00 | Shitalakhya | 134 | 18:30 | 123 | 14:00
Jaldhaka | 132 | 00:00 | 117 | 16:00 | Sholosohor | 132 | 05:00 | 127 | 14:00
Jamalpur | 137 | 10:00 | 120 | 00:00 | Shyampur | 132 | 04:00 | 125 | 14:00
Jashore | 131 | 06:00 | 120 | 19:00 | Shyampur-230 | 133 | 06:00 | 124 | 14:00
Jhenaidah | 134 | 05:00 | 124 | 19:00 | Siddhirganj | 132 | 05:00 | 124 | 14:00
Jhenaidah-230 | 134 | 05:00 | 124 | 21:00 | Sirajganj | 130 | 00:00 | 122 | 17:00
Joydebpur | 136 | 18:00 | 122 | 13:00 | Sonargaon | 132 | 18:30 | 122 | 14:00
Joypurhat | 125 | 05:00 | 114 | 17:00 | Sreemongol | 131 | 06:00 | 126 | 14:00
Juldah | 132 | 00:00 | 127 | 14:00 | Sreepur | 131 | 04:00 | 123 | 14:00
Kabirpur | 135 | 18:00 | 122 | 14:00 | Srinagar | 137 | 06:00 | 128 | 14:00
Kachua | 126 | 18:00 | 115 | 13:00 | SSM | 137 | 07:00 | 132 | 00:00
Kaliakoir | 134 | 18:00 | 123 | 14:00 | Sunamganj | 131 | 05:00 | 126 | 14:00
Kallyanpur | 135 | 07:00 | 126 | 13:00 | Sylhet | 132 | 06:00 | 127 | 15:00
Kalurghat | 133 | 18:00 | 128 | 14:00 | Sylhet-132 | 132 | 03:00 | 129 | 14:00
Kamrangirchar | 136 | 06:00 | 128 | 14:00 | Tangail | 126 | 04:00 | 117 | 17:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 140 | 00:00 | 116 | 16:00
Kazla | 133 | 06:00 | 123 | 15:00 | TK | 134 | 01:00 | 128 | 14:00
Keranigonj | 138 | 18:30 | 128 | 14:00 | Tongi | 134 | 05:00 | 128 | 13:00
Khagrachori | 131 | 06:00 | 126 | 14:00 | Ullahpara | 132 | 05:00 | 124 | 17:00
Khosba | 127 | 18:30 | 118 | 14:00 | Ullon | 136 | 06:00 | 125 | 14:00
Khulna | 131 | 05:00 | 123 | 18:30 | Uttara | 135 | 07:00 | 125 | 14:00
Khulna(S) | 135 | 06:00 | 126 | 19:30 | UttaraNew | 135 | 18:30 | 125 | 14:00
Khulshi | 131 | 18:00 | 124 | 14:00 | Zigatola | 137 | 18:30 | 128 | 15:00
Kishoreganj | 131 | 05:00 | 120 | 14:00
Kodda | 134 | 18:00 | 121 | 07:00
KSRM | 132 | 00:00 | 128 | 15:00
Kulaura | 134 | 07:00 | 129 | 14:00
Kurigram | 131 | 00:00 | 118 | 13:00
Kushtia | 135 | 05:00 | 126 | 19:00
Lalbag | 137 | 18:00 | 127 | 14:00
Lalmonirhat | 130 | 00:00 | 119 | 13:00
Madanganj | 131 | 19:00 | 123 | 14:00
Madaripur | 135 | 09:00 | 130 | 00:00
Madartek | 135 | 04:00 | 124 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division