## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-03-2025 | during | 21-03-2025 | during | 21-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 120 | 120 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 22 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 407 | 412 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 311 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 52 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 99 | 98 | 208.13 | 208.13 | 105 | 105 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 270 | 335 | 335 | 290 | 290 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 46 | 110 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 20.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 12 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 13 | 16 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 42 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 29 | 16 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 1 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2834 | 2753.5 | 5128.5 | 5100.5 | 3741.3 | 3713.3
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 162 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 21 | 79 | 56 | 80 | 56 | 80 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 73 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 17 | 30 | 32 | 30 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.2 | 0 | 4.2 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 60 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 430 | 550 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 9 | 0 | 17 | 3 | 17 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 800 | 780 | 785 | 785 | 875 | 875 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1612 | 1841 | 3026.92 | 3015.72 | 3116.92 | 3105.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 198 | 175 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 7 | 307 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 36 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 35 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 158 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 113 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 32 | 24 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 35 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 100 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 80 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 17 | 17 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 79 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 56 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 94 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 47 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1324 | 1515 | 2410.99 | 2345.99 | 2274.49 | 2209.49
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-03-2025 | during | 21-03-2025 | during | 21-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 136 | 175 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 108 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 30.1 | 0 | 40 | 0 | 40 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 14 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 267.1 | 295 | 643.6 | 601.5 | 443.6 | 401.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 40 | 38 | 39 | 38 | 39 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 155 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 5 | 5 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 164 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 352 | 375 | 380 | 380 | 352 | 352 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1502 | 1518 | 1613 | 1614 | 1551 | 1552
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 896 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Power evacuation problem in PGCB switchyard
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 21.46 | 0 | 87 | 0 | 87 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 382 | 409 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1299.46 | 1305 | 3601.2 | 3514.2 | 1904.02 | 1817.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 378 | 377.5 | 660 | 660 | 660 | 660 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 94 | 110 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 847 | 972 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.24 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1745.24 | 1996.5 | 2832.12 | 2831.12 | 2792.12 | 2791.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 185 | 182 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 201 | 186 | 220 | 220 | 200 | 200 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 197 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 402 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 2.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.46 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1268 | 1267.73 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 16.28 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 20 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2296.24 | 2249.23 | 3102.28 | 2935.53 | 3020.49 | 2853.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 65 | 61 | 63 | 63 | 65 | 65 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 171 | 170 | 170 | 170 | 175 | 175 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 16.5 | 0 | 16.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 166 | 0 | 100 | 0 | 100 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 444.2 | 336 | 617.9 | 495 | 590.92 | 468.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 13324.24 | 13809.23 | 22976.51 | 22453.56 | 19434.86 | 18911.91
Forecast Scenario (21-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13390 |  | 0 |  | 13390
|  |  |  | 1:00 | 12820 |  | 0 |  | 12820
|  |  |  | 2:00 | 12500 |  | 0 |  | 12500
|  |  |  | 3:00 | 12680 |  | 0 |  | 12680
|  |  |  | 4:00 | 12600 |  | 0 |  | 12600
|  |  |  | 5:00 | 11710 |  | 0 |  | 11710
|  |  |  | 6:00 | 11060 |  | 0 |  | 11060
|  |  |  | 7:00 | 10670 |  | 0 |  | 10670
|  |  |  | 8:00 | 10870 |  | 0 |  | 10870
|  |  |  | 9:00 | 11210 |  | 0 |  | 11210
|  |  |  | 10:00 | 11280 |  | 0 |  | 11280
|  |  |  | 11:00 | 11580 |  | 0 |  | 11580
|  |  |  | 12:00 | 12270 |  | 0 |  | 12270
|  |  |  | 13:00 | 12770 |  | 0 |  | 12770
|  |  |  | 14:00 | 12100 |  | 0 |  | 12100
|  |  |  | 15:00 | 12230 |  | 0 |  | 12230
|  |  |  | 16:00 | 12520 |  | 0 |  | 12520
|  |  |  | 17:00 | 12630 |  | 0 |  | 12630
|  |  |  | 18:00 | 12730 |  | 0 |  | 12730
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 13640 |  | 0 |  | 13640
|  |  |  | 19:30 | 13660 |  | 0 |  | 13660
|  |  |  | 20:00 | 13740 |  | 0 |  | 13740
|  |  |  | 21:00 | 13900 |  | 0 |  | 13900
|  |  |  | 22:00 | 13890 |  | 0 |  | 13890
|  |  |  | 23:00 | 13630 |  | 0 |  | 13630
Probable Maximum Temperature: |  |  | 33.70°C
Probable Maximum Demand at Day Peak: |  |  | 12270.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 298.42 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:21 hrs on 21-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-03-2025 | [28 empty] | Date: | 20-03-2025 | [28 empty] | Date: | 20-03-2025 | [28 empty] | Date: | 20-03-2025 | [28 empty] | Date: | 20-03-2025 | [18 empty] | Date: | 20-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 38 | 120 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 36 | 0 | 0 | 142 | 95 | 0 | 0 | 72 | 22 | 16 | 420 | 290 | 583 | 0 | 0 | 15 | 271 | 103 | 0 | 0 | 142 | 20.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 98 | 60 | 0 | 46 | 0 | 21 | 826 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 127 | 0 | 4 | 285 | 20 | 182 | 33 | 30 | 45 | 68 | 36 | 17 | 79 | 82 | 52 | 0 | 41 | 300 | 320 | 347 | 5 | 41 | 0 | 5 | 152 | 22 | 0 | 85 | 30 | 0 | 18 | 165 | 17 | 49 | 58 | 10 | 0 | 0 | 12 | 7632.5 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 51 | 1354.13 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 183 | 0 | 197 | 0 | 414 | 0 | 0 | 5 | 176 | 65 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 88 | 220 | 0 | 405 | 1108 | 0 | 6303.63 | 13936.13 | 86.61
01:00 | 0 | 105 | 43 | 120 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 18 | 0 | 0 | 142 | 95 | 0 | 0 | 17 | 22 | 16 | 420 | 267 | 583 | 0 | 0 | 15 | 270 | 103 | 0 | 0 | 108 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 98 | 24 | 0 | 46 | 0 | 26 | 826 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 167 | 0 | 38 | 285 | 20 | 182 | 33 | 17 | 45 | 34 | 27 | 18 | 79 | 74 | 52 | 0 | 41 | 280 | 320 | 347 | 5 | 41 | 0 | 5 | 152 | 22 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 49 | 58 | 11 | 0 | 0 | 12 | 7443 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 17 | 1360.73 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 184 | 0 | 199 | 0 | 414 | 0 | 0 | 5.5 | 174 | 64 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 88 | 220 | 0 | 378 | 1105 | 0 | 6071.73 | 13514.73 | 86.6
02:00 | 0 | 105 | 43 | 120 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 18 | 0 | 0 | 142 | 65 | 0 | 0 | 17 | 22 | 16 | 420 | 278 | 583 | 0 | 0 | 15 | 270 | 103 | 0 | 0 | 108 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 98 | 24 | 0 | 46 | 0 | 28 | 828 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 168 | 0 | 8 | 285 | 20 | 182 | 33 | 16 | 50 | 17 | 27 | 18 | 79 | 76 | 52 | 0 | 41 | 295 | 320 | 302 | 5 | 41 | 0 | 5 | 134 | 22 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 49 | 58 | 10 | 0 | 0 | 12 | 7339 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1360.78 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 185 | 0 | 198 | 0 | 320 | 0 | 0 | 5.5 | 175 | 64 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 88 | 220 | 0 | 378 | 1046 | 0 | 5822.78 | 13161.78 | 86.6
03:00 | 0 | 105 | 43 | 120 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 18 | 0 | 0 | 143 | 65 | 0 | 17 | 17 | 22 | 0 | 380 | 312 | 583 | 0 | 0 | 15 | 270 | 103 | 0 | 0 | 108 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 87 | 24 | 0 | 46 | 0 | 30 | 830 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 168 | 0 | 13 | 285 | 20 | 185 | 33 | 16 | 50 | 17 | 28 | 18 | 79 | 68 | 52 | 0 | 41 | 300 | 320 | 334 | 5 | 41 | 0 | 5 | 136 | 22 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 68 | 68 | 12 | 0 | 0 | 12 | 7375 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 1360.56 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 189 | 0 | 201 | 0 | 387 | 0 | 0 | 5.5 | 174 | 64 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 10 | 88 | 180 | 0 | 379 | 1048 | 0 | 5891.56 | 13266.56 | 86.59
04:00 | 0 | 105 | 43 | 120 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 18 | 0 | 0 | 144 | 0 | 0 | 35 | 17 | 22 | 0 | 420 | 270 | 583 | 0 | 0 | 15 | 264 | 104 | 0 | 0 | 90 | 21.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 87 | 24 | 0 | 46 | 0 | 30 | 828 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 168 | 0 | 29 | 285 | 20 | 182 | 33 | 46 | 50 | 17 | 28 | 18 | 79 | 74 | 52 | 0 | 41 | 300 | 320 | 336 | 5 | 41 | 0 | 5 | 154 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 68 | 135 | 12 | 0 | 0 | 12 | 7460.5 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 1355.01 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 190 | 0 | 191 | 0 | 318 | 0 | 0 | 5.5 | 171 | 65 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 88 | 220 | 0 | 378.3 | 1120 | 0 | 5988.31 | 13448.81 | 86.59
05:00 | 0 | 105 | 43 | 120 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 18 | 0 | 0 | 112 | 0 | 0 | 35 | 17 | 22 | 0 | 420 | 289 | 583 | 0 | 0 | 15 | 260 | 103 | 0 | 0 | 52 | 21.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 87 | 24 | 0 | 46 | 0 | 30 | 756 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 505 | 0 | 51 | 0 | 168 | 0 | 28 | 285 | 20 | 188 | 33 | 50 | 50 | 17 | 27 | 18 | 79 | 76 | 52 | 0 | 41 | 285 | 320 | 287 | 5 | 41 | 0 | 5 | 141 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 69 | 135 | 12 | 0 | 0 | 12 | 7074.5 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 1172.79 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 193 | 0 | 189 | 0 | 326 | 0 | 0 | 5.5 | 174 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 88 | 220 | 0 | 378 | 1000 | 0 | 5509.79 | 12584.29 | 86.58
06:00 | 0 | 70 | 25 | 120 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 18 | 0 | 0 | 64 | 0 | 0 | 17 | 0 | 17 | 0 | 420 | 300 | 583 | 0 | 0 | 15 | 258 | 104 | 0 | 0 | 11 | 21.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 46 | 0 | 30 | 703 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 0 | 43 | 0 | 168 | 0 | 38 | 285 | 20 | 182 | 33 | 24 | 50 | 17 | 28 | 18 | 79 | 68 | 52 | 0 | 41 | 290 | 320 | 289 | 5 | 41 | 0 | 5 | 133 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 69 | 136 | 12 | 0 | 0 | 12 | 6681.5 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 1015.24 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 197 | 0 | 189 | 0 | 319 | 0 | 0 | 2.5 | 173 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 88 | 220 | 0 | 379 | 900 | 0 | 5239.24 | 11920.74 | 86.58
07:00 | 0 | 70 | 43 | 120 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 18 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 311 | 583 | 0 | 0 | 15 | 256 | 39 | 0 | 2 | 0 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 12 | 1 | 46 | 0 | 12 | 703 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 3 | 43 | 0 | 177 | 0 | 6 | 285 | 21 | 217 | 33 | 17 | 50 | 17 | 0 | 18 | 52 | 66 | 52 | 9 | 33 | 310 | 320 | 408 | 5 | 41 | 0 | 5 | 143 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 79 | 127 | 12 | 0 | 4.39 | 12 | 6668.39 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 384 | 0 | 1014.06 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 3 | 0 | 1.98 | 199 | 0 | 202 | 0 | 160 | 0 | 362 | 0 | 0.14 | 2.5 | 173 | 65 | 0 | 3 | 0 | 0 | 0 | 0.6 | 14 | 0.04 | 0 | 200 | 7 | 110 | 220 | 0 | 379 | 895 | 0 | 5307.82 | 11976.21 | 86.57
08:00 | 0 | 88 | 43 | 120 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 18 | 0 | 0 | 110 | 0 | 0 | 0 | 30 | 17 | 0 | 450 | 284 | 583 | 0 | 0 | 15 | 258 | 102 | 0 | 0 | 24 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 12 | 2 | 46 | 0 | 5 | 804 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 451 | 8 | 43 | 0 | 185 | 0 | 9 | 285 | 32 | 182 | 33 | 16 | 50 | 17 | 0 | 18 | 52 | 68 | 52 | 19 | 38 | 290 | 320 | 350 | 5 | 41 | 0 | 5 | 153 | 22 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 69 | 136 | 12 | 0 | 12.35 | 12 | 6914.35 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 384 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 21 | 0 | 9.08 | 188 | 0 | 199 | 0 | 167 | 0 | 322 | 0 | 1.02 | 2.5 | 173 | 64 | 0 | 11 | 0 | 0 | 0 | 2.1 | 36 | 0.1 | 0 | 270 | 7 | 88 | 220 | 0 | 378 | 965 | 0 | 5501.3 | 12415.65 | 86.57
09:00 | 0 | 105 | 42 | 120 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 20 | 0 | 0 | 110 | 0 | 0 | 0 | 35 | 17 | 0 | 450 | 309 | 583 | 0 | 0 | 13 | 272 | 102 | 0 | 12 | 51 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 12 | 3 | 46 | 0 | 3 | 800 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 13 | 43 | 0 | 185 | 0 | 5 | 285 | 45 | 193 | 30 | 17 | 40 | 17 | 0 | 18 | 52 | 64 | 52 | 39 | 32 | 295 | 320 | 362 | 5 | 41 | 0 | 5 | 150 | 22 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 69 | 136 | 9 | 1 | 23.62 | 12 | 7085.62 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.51 | 382 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 32 | 0 | 5.14 | 187 | 0 | 201 | 0 | 185 | 0 | 329 | 0 | 0.51 | 2.5 | 175 | 64 | 0 | 20 | 0 | 0 | 0 | 4 | 90 | 0.1 | 0 | 270 | 6 | 96 | 220 | 0 | 379 | 997 | 0 | 5647.26 | 12732.88 | 86.56
10:00 | 0 | 105 | 42 | 120 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 36 | 0 | 0 | 109 | 45 | 0 | 17 | 35 | 22 | 0 | 450 | 309 | 583 | 0 | 25 | 16 | 278 | 100 | 0 | 3 | 76 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 48 | 12 | 3 | 46 | 0 | 3 | 800 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 16 | 51 | 5 | 185 | 0 | 6 | 285 | 46 | 203 | 30 | 17 | 40 | 17 | 0 | 18 | 67 | 58 | 52 | 50 | 32 | 315 | 320 | 382 | 5 | 40 | 0 | 5 | 155 | 22 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 69 | 136 | 5 | 1 | 32.37 | 12 | 7311.37 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.59 | 381 | 0 | 1161 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 3 | 0 | 8.57 | 187 | 0 | 200 | 0 | 200 | 0 | 414 | 0 | 0.71 | 5.5 | 173 | 64 | 0 | 27 | 0 | 0 | 0 | 5.5 | 136 | 0.2 | 0 | 224 | 6 | 96 | 220 | 0 | 378 | 913 | 0 | 5768.57 | 13079.94 | 86.56
11:00 | 8 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 36 | 0 | 0 | 46 | 145 | 12 | 17 | 35 | 22 | 9 | 450 | 299 | 583 | 0 | 35 | 16 | 280 | 100 | 0 | 5 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 48 | 48 | 4 | 46 | 0 | 2 | 790 | 35 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 17 | 51 | 58 | 177 | 0 | 11 | 285 | 44 | 195 | 32 | 35 | 40 | 17 | 0 | 17 | 79 | 66 | 52 | 51 | 32 | 315 | 320 | 380 | 5 | 40 | 0 | 5 | 151 | 22 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 69 | 136 | 5 | 2 | 22.27 | 12 | 7368.27 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.98 | 384 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 32.79 | 187 | 0 | 201 | 0 | 200 | 0 | 396 | 0 | 2.65 | 5.5 | 173 | 64 | 0 | 32 | 0 | 0 | 0 | 6.7 | 157 | 0.52 | 0 | 200 | 6 | 94 | 220 | 0 | 378 | 850 | 0 | 5714.14 | 13082.41 | 86.55
12:00 | 8 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 36 | 0 | 0 | 46 | 145 | 52 | 17 | 35 | 22 | 29 | 450 | 301 | 583 | 0 | 35 | 13 | 280 | 99 | 0 | 1 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 21 | 0 | 73 | 12 | 4 | 46 | 0 | 2 | 800 | 35 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 430 | 18 | 51 | 113 | 187 | 0 | 7 | 285 | 45 | 198 | 35 | 54 | 40 | 17 | 1 | 17 | 79 | 64 | 52 | 47 | 32 | 310 | 320 | 352 | 5 | 40 | 0 | 5 | 150 | 22 | 0 | 85 | 30 | 0 | 18 | 165 | 14 | 69 | 136 | 5 | 1 | 30.1 | 12 | 7539.1 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.46 | 382 | 0 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16.28 | 185 | 0 | 201 | 0 | 197 | 0 | 402 | 0 | 1.46 | 5.5 | 171 | 65 | 0 | 35 | 0 | 0 | 0 | 7.2 | 166 | 0.24 | 0 | 200 | 6 | 94 | 220 | 0 | 378 | 847 | 0 | 5785.14 | 13324.24 | 86.54
13:00 | 8 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 36 | 0 | 0 | 60 | 245 | 55 | 35 | 90 | 22 | 56 | 450 | 248 | 583 | 0 | 35 | 16 | 275 | 101 | 0 | 2 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 72 | 0 | 73 | 12 | 4 | 46 | 0 | 7 | 800 | 35 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 18 | 51 | 133 | 185 | 0 | 6 | 285 | 44 | 183 | 35 | 56 | 40 | 17 | 9 | 18 | 79 | 70 | 52 | 50 | 32 | 295 | 320 | 348 | 5 | 40 | 0 | 5 | 144 | 22 | 0 | 84 | 30 | 0 | 18 | 164 | 54.5 | 69 | 133 | 5 | 0 | 44.21 | 12 | 7840.71 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 383 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 10.21 | 180 | 0 | 199 | 0 | 205 | 0 | 321 | 0 | 0.93 | 5.5 | 173 | 65 | 35 | 33 | 34 | 0 | 0 | 6.7 | 128 | 0.27 | 0 | 200 | 6 | 94 | 180 | 0 | 378 | 800 | 0 | 5696.61 | 13537.32 | 86.53
14:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 18 | 0 | 0 | 60 | 245 | 55 | 35 | 90 | 22 | 75 | 450 | 284 | 500 | 0 | 35 | 16 | 275 | 38 | 0 | 14 | 90 | 18 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 64 | 0 | 85 | 12 | 1 | 46 | 0 | 3 | 800 | 35 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 500 | 16 | 51 | 138 | 187 | 0 | 44 | 285 | 45 | 183 | 35 | 54 | 40 | 17 | 9 | 18 | 79 | 68 | 52 | 40 | 40 | 305 | 320 | 299 | 5 | 39 | 0 | 5 | 135 | 22 | 0 | 85 | 20 | 0 | 18 | 165 | 54.5 | 69 | 136 | 5 | 2 | 9.51 | 12 | 7661.01 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.89 | 382 | 0 | 1324.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 2.74 | 173 | 0 | 196 | 0 | 203 | 0 | 323 | 0 | 0.19 | 5.5 | 174 | 64 | 35 | 29 | 34 | 0 | 0 | 6.2 | 140 | 0.45 | 0 | 250 | 7 | 110 | 220 | 0 | 378 | 781 | 0 | 5818.07 | 13479.08 | 86.52
15:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 5 | 410 | 0 | 0 | 17 | 18 | 0 | 0 | 60 | 195 | 30 | 35 | 90 | 22 | 83 | 450 | 287 | 500 | 0 | 35 | 16 | 250 | 39 | 0 | 5 | 90 | 20 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 17 | 72 | 0 | 85 | 12 | 2 | 46 | 0 | 2 | 800 | 35 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 500 | 11 | 51 | 137 | 187 | 0 | 72 | 285 | 47 | 191 | 35 | 55 | 42 | 17 | 9 | 18 | 79 | 74 | 52 | 36 | 40 | 290 | 320 | 299 | 5 | 39 | 0 | 5 | 133 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 54.5 | 69 | 136 | 5 | 0 | 14.87 | 12 | 7610.37 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.22 | 383 | 0 | 1219.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 5.04 | 181 | 0 | 194 | 0 | 203 | 0 | 328 | 0 | 0.42 | 2.5 | 173 | 61 | 35 | 24 | 34 | 0 | 0 | 5.1 | 115 | 0.35 | 0 | 200 | 6 | 120 | 180 | 0 | 379 | 779 | 0 | 5585.57 | 13195.94 | 86.51
16:00 | 8 | 60 | 33 | 0 | 0 | 0 | 0 | 19 | 411 | 0 | 0 | 17 | 18 | 0 | 0 | 85 | 195 | 30 | 35 | 90 | 22 | 87 | 450 | 296 | 500 | 0 | 35 | 16 | 250 | 39 | 0 | 10 | 90 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 71 | 0 | 74 | 12 | 1 | 46 | 0 | 5 | 800 | 24 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 500 | 7 | 51 | 100 | 187 | 0 | 101 | 285 | 47 | 200 | 36 | 46 | 42 | 17 | 9 | 18 | 79 | 66 | 52 | 22 | 40 | 310 | 320 | 329 | 5 | 40 | 0 | 5 | 135 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 54.5 | 69 | 136 | 5 | 0 | 3.39 | 12 | 7658.89 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4 | 381 | 0 | 1221.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.93 | 181 | 0 | 192 | 0 | 203 | 0 | 348 | 0 | 0.28 | 2.5 | 173 | 61 | 35 | 13 | 34 | 0 | 0 | 2.9 | 66 | 0.18 | 0 | 200 | 6 | 120 | 180 | 0 | 380 | 780 | 0 | 5514.34 | 13173.23 | 86.5
17:00 | 8 | 88 | 33 | 0 | 0 | 0 | 0 | 22 | 409 | 0 | 0 | 17 | 19 | 0 | 0 | 95 | 195 | 30 | 35 | 90 | 22 | 87 | 450 | 284 | 540 | 0 | 35 | 16 | 275 | 101 | 0 | 2 | 90 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 74 | 36 | 0 | 46 | 0 | 11 | 794 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 500 | 2 | 51 | 70 | 187 | 0 | 114 | 285 | 50 | 185 | 36 | 34 | 37 | 17 | 22 | 18 | 79 | 68 | 52 | 7 | 47 | 315 | 320 | 300 | 5 | 40 | 0 | 5 | 139 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 54.5 | 69 | 155 | 0 | 0 | 4.03 | 12 | 7758.53 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.67 | 410 | 0 | 1209.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 181 | 0 | 189 | 0 | 199 | 0 | 324 | 0 | 0.26 | 2.5 | 173 | 62 | 50 | 5 | 62 | 0 | 0 | 1.1 | 15 | 0.07 | 0 | 200 | 7 | 120 | 220 | 0 | 379 | 833 | 0 | 5555.32 | 13313.85 | 86.49
18:00 | 8 | 100 | 42 | 0 | 0 | 0 | 0 | 22 | 390 | 0 | 0 | 24 | 36 | 0 | 0 | 126 | 160 | 30 | 35 | 144 | 22 | 87 | 370 | 269 | 540 | 0 | 35 | 16 | 240 | 101 | 0 | 0 | 90 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 80 | 36 | 0 | 46 | 0 | 13 | 792 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 500 | 0 | 51 | 70 | 187 | 0 | 130 | 285 | 51 | 182 | 36 | 37 | 35 | 17 | 45 | 18 | 79 | 74 | 52 | 0 | 47 | 305 | 320 | 300 | 5 | 40 | 0 | 5 | 133 | 16 | 0 | 85 | 20 | 0 | 18 | 164 | 54.5 | 107 | 165 | 0 | 0 | 0.11 | 12 | 7771.61 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 410 | 17 | 1218.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 180 | 0 | 180 | 0 | 321 | 0 | 0.01 | 2.5 | 175 | 61 | 73 | 0 | 110 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 8 | 120 | 220 | 0 | 378.17 | 900 | 0 | 5652.89 | 13424.5 | 86.48
19:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 22 | 411 | 0 | 0 | 54 | 54 | 0 | 0 | 110 | 30 | 0 | 35 | 162 | 22 | 78 | 420 | 291 | 540 | 0 | 17 | 16 | 270 | 98 | 0 | 0 | 70 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 79 | 0 | 88 | 60 | 0 | 46 | 0 | 17 | 794 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 550 | 0 | 51 | 12 | 180 | 0 | 162 | 285 | 52 | 182 | 36 | 56 | 35 | 66 | 52 | 18 | 79 | 70 | 8 | 0 | 47 | 275 | 320 | 348 | 5 | 40 | 0 | 5 | 137 | 16 | 0 | 85 | 30 | 0 | 18 | 165 | 17 | 107 | 165 | 0 | 0 | 0 | 12 | 7828 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 17 | 1219.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 185 | 0 | 197 | 0 | 384 | 0 | 0 | 2.5 | 171 | 61 | 74 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 10 | 110 | 220 | 0 | 378 | 850 | 0 | 5668.03 | 13496.03 | 86.47
19:30 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 22 | 412 | 0 | 0 | 17 | 54 | 0 | 0 | 110 | 15 | 0 | 17 | 126 | 22 | 16 | 420 | 286 | 540 | 0 | 0 | 16 | 270 | 98 | 0 | 0 | 70 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 79 | 0 | 88 | 60 | 0 | 46 | 0 | 17 | 792 | 0 | 0 | 0 | 1 | 0 | 162 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 187 | 0 | 222 | 285 | 52 | 182 | 36 | 94 | 35 | 100 | 55 | 18 | 70 | 74 | 8 | 0 | 47 | 285 | 320 | 357 | 5 | 40 | 0 | 5 | 150 | 16 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 108 | 166 | 0 | 0 | 0 | 12 | 7794 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 17 | 1279.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 188 | 0 | 197 | 0 | 390 | 0 | 0 | 2.5 | 172 | 61 | 74 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 10 | 110 | 220 | 0 | 377 | 950 | 0 | 5805.99 | 13599.99
20:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 22 | 411 | 0 | 0 | 30 | 54 | 0 | 0 | 110 | 15 | 0 | 17 | 126 | 22 | 16 | 420 | 292 | 540 | 0 | 0 | 16 | 270 | 98 | 0 | 0 | 70 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 79 | 0 | 88 | 60 | 0 | 46 | 0 | 18 | 792 | 0 | 0 | 0 | 5 | 0 | 161 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 187 | 0 | 260 | 285 | 51 | 182 | 36 | 92 | 35 | 100 | 54 | 18 | 52 | 70 | 8 | 0 | 24 | 295 | 320 | 348 | 5 | 40 | 0 | 5 | 149 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 166 | 0 | 0 | 0 | 12 | 7794 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 1269.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 188 | 0 | 197 | 0 | 392 | 0 | 0 | 2.5 | 173 | 61 | 74 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 10 | 110 | 220 | 0 | 379 | 945 | 0 | 5772.39 | 13566.39 | 86.46
21:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 22 | 412 | 0 | 0 | 17 | 54 | 0 | 0 | 110 | 15 | 0 | 17 | 108 | 22 | 16 | 450 | 311 | 583 | 0 | 0 | 16 | 270 | 98 | 0 | 0 | 70 | 20.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 79 | 0 | 88 | 60 | 0 | 46 | 0 | 17 | 780 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 158 | 0 | 307 | 285 | 35 | 175 | 36 | 94 | 35 | 100 | 56 | 19 | 52 | 80 | 8 | 0 | 24 | 305 | 320 | 375 | 5 | 40 | 0 | 5 | 155 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 175 | 0 | 0 | 0 | 12 | 7922.5 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 1267.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 186 | 0 | 197 | 0 | 414 | 0 | 0 | 2.5 | 170 | 61 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 377.5 | 972 | 0 | 5886.73 | 13809.23 | 86.45
22:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 22 | 411 | 0 | 0 | 17 | 54 | 0 | 0 | 110 | 15 | 0 | 17 | 108 | 22 | 16 | 450 | 302 | 583 | 0 | 0 | 16 | 264 | 102 | 0 | 0 | 70 | 20.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 79 | 0 | 88 | 60 | 0 | 46 | 0 | 21 | 746 | 0 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 552 | 0 | 43 | 0 | 76 | 0 | 364 | 285 | 10 | 157 | 36 | 67 | 35 | 114 | 56 | 19 | 52 | 80 | 34 | 0 | 0 | 315 | 320 | 352 | 5 | 41 | 0 | 5 | 159 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 166 | 0 | 0 | 0 | 12 | 7777.5 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1270.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 184 | 0 | 197 | 0 | 383 | 0 | 0 | 2.5 | 173 | 61 | 35 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 120 | 220 | 0 | 377 | 1000 | 0 | 5862.61 | 13640.11 | 86.44
23:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 22 | 377 | 0 | 0 | 17 | 54 | 0 | 0 | 121 | 15 | 0 | 17 | 108 | 22 | 16 | 450 | 303 | 583 | 0 | 0 | 16 | 260 | 102 | 0 | 0 | 70 | 20.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 51 | 81 | 0 | 88 | 60 | 0 | 46 | 0 | 31 | 570 | 0 | 0 | 0 | 8 | 0 | 161 | 0 | 0 | 0 | 552 | 0 | 43 | 0 | 78 | 0 | 365 | 285 | 10 | 171 | 36 | 33 | 30 | 120 | 38 | 20 | 52 | 82 | 34 | 0 | 0 | 305 | 320 | 350 | 5 | 41 | 0 | 5 | 153 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 166 | 0 | 0 | 0 | 12 | 7540.5 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 1258.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 183 | 0 | 197 | 0 | 400 | 0 | 0 | 2.5 | 170 | 61 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 377 | 1001 | 0 | 5855.02 | 13395.52 | 86.43
Total KWH | 70128 | 2215680 | 932160 | 0 | 0 | 0 | 0 | 190272.73 | 9504000 | 0 | 0 | 312480 | 753120 | 0 | 0 | 2401920 | 2085305 | 330836 | 463712 | 1533600 | 543100 | 703680 | 10175500 | 7045527 | 13535455 | 0 | 335365 | 359500 | 6427666 | 2264000 | 0 | 51567 | 1832400 | 446400 | 333360 | 0 | 0 | 0 | 0 | 0 | 0 | 42720 | 447100 | 1139224 | 0 | 1821120 | 770880 | 23520 | 1108680 | 0 | 370080 | 18800000 | 190691 | 0 | 0 | 38977.2 | 0 | 3860632 | 0 | 0 | 0 | 12381817 | 127845 | 1049432 | 1182618 | 3997818 | 0 | 2607600 | 6898000 | 805920 | 4578000 | 819864 | 976320 | 990790 | 969600 | 584640 | 430220 | 1703160 | 1696320 | 1080264 | 358172.73 | 652280 | 7312500 | 7690300 | 8482000 | 202896 | 966000 | 0 | 112560 | 3473836 | 354624 | 0 | 2023680 | 662304 | 0 | 435000 | 4407000 | 393840 | 1812000 | 3129600 | 126720 | 7700 | 204000 | 298080 | 179445678.66 | 21444363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406800 | 9600000 | 82080 | 29672728 | 0 | 0 | 0 | 0 | 0 | 75968 | 0 | 0 | 0 | 122680 | 0 | 99752 | 4524727 | 0 | 4766527 | 0 | 4860873 | 0 | 8673090 | 0 | 9540 | 94878 | 4228000 | 1475345 | 583145 | 223256 | 867100 | 0 | 0 | 48205.92 | 1020960 | 2722.5 | 0 | 5891000 | 199836 | 2434000 | 5181980 | 0 | 9137454 | 23045818 | 0 | 138772828.42 | 318218507.08

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13324.24 | MW | 12:00 Hr. | Energy Generated |  |  | 318.2185 |  | MKWHr.
| Day Peak Demand |  |  | 13507.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.063 |  | MKWHr.
| Evening Peak Generation |  |  | 13809.23 | MW | 21:00 Hr. | Energy Demand |  |  | 320.2815 |  | MKWHr.
| Evening Peak Demand |  |  | 13809.23 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 11920.74 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1038.71 |  | MMCFD
| Maximum Generation of the Day |  |  | 13936.13 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.0206 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 50.8248 | 0 | 13.9704 | 0 | 0 | 0.051567 | 0 | 0 | 64.8467 | Gas | 144.2185 | Gas | 470142783.6855
| Chattogram Zone |  |  | 4.2307 | 31.1818 | 4.408 | 0 | 1.1087 | 0.15136 | 0 | 0.04272 | 41.1233 | Coal | 84.5594 | Coal | 535061830.33
| Cumilla Zone |  |  | 22.1776 | 0 | 7.1489 | 0 | 0 | 0.35817 | 1.6963 | 0 | 31.381 | HFO | 32.7691 | HFO | 578915357.124
| Mymensingh Zone |  |  | 0.12672 | 0 | 5.6335 | 0 | 0 | 0.2117 | 0 | 0 | 5.9719 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1227 | Hydro | 1.1087 | Hydro | 110868
| Khulna Zone |  |  | 0 | 9.6 | 0.08208 | 0 | 0 | 0.4068 | 21.4444 | 0 | 31.5332 | Solar | 2.7067 | Solar | 45482961.5104
| Barishal Zone |  |  | 7.8158 | 38.0743 | 0 | 0 | 0 | 0.0027225 | 0 | 0 | 45.8928 | Import | 52.8134 | Import | 285540611.37
| Rajshahi Zone |  |  | 22.9201 | 0 | 0.075968 | 0 | 0 | 0.23197 | 29.6727 | 0 | 52.9008 | Wind | 0.04272 | Wind | 625420.8
| Rangpur Zone |  |  | 0 | 5.7033 | 1.4502 | 0 | 0 | 1.2924 | 0 | 0 | 8.446
| Total |  |  | 144.2185 | 84.5594 | 32.7691 | 0 | 1.1087 | 2.7067 | 52.8134 | 0.04272 | 318.2185
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 470142783.6855 |  | Hydro | 110868
|  |  |  | Coal | 535061830.33 |  | Solar | 45482961.5104
|  |  |  | HFO | 578915357.124 |  | Import | 285540611.37
|  |  |  | HSD | 0 |  | Wind | 625420.8
[5 empty] | Total: | 191,58,79,832 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4444 | Peak Hr Flow | 896.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 11662800.083 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.6727 | Peak Hr Flow | 1267.73 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 712 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6963 | Peak Hr Flow | 80.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 896 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.8134 | Peak Hr Flow | 2243.73 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4963
|  |  |  | Chattogram |  | 0 |  | 1476
|  |  |  | Cumilla |  | 0 |  | 1348
|  |  |  | Mymensingh |  | 0 |  | 1078
|  |  |  | Sylhet |  | 0 |  | 458
|  |  |  | Khulna |  | 0 |  | 1525
|  |  |  | Barishal |  | 0 |  | 444
|  |  |  | Rajshahi |  | 0 |  | 1234
|  |  |  | Rangpur |  | 0 |  | 790
|  |  |  | Total |  | 0 |  | 13316
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:35 | 17:33 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Fire wall Construction
Works.
| 08:35 | 17:33 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Fire wall Construction
Works.
| 08:36 | 17:31 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Fire wall Construction
Works.
| 08:36 | 17:31 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Fire wall Construction
Works.
| 08:46 | 14:43 | Chandraghona-Kaptai 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end.
|  | 09:09 | Dhamrai 132/33kV S/S Transformer-2 HT is restored.
| 09:28 | 16:50 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to Oil leakage problem of ATR-02 solving
| 09:30 | 16:49 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to The solving oil leakage problem of
ATR-02
|  | 10:18 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
|  | 10:18 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
| 10:20 | 11:22 | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D Due to Oil leakage maintenance Work.
| 10:20 | 11:23 | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to Oil leakage maintenance Work.
| 10:30 |  | At Bhola Boharuddin 230/33KV 120/140 MVA Txr S/D has restored.
| 11:02 | 14:13 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to metering work of 33 KV CP.
| 11:02 | 13:12 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to metering work of 33 KV CP.
| 12:00 |  | Day Peak 13324 MW
| 12:42 |  | Ashugonj North 360 MW ST was sync.
| 12:56 | 13:31 | Panchagar-Thakurgaon 132kV Ckt-1 Forced S/D from Panchagarh 132/33kV end Due to Removing
kite from 132 kv transmissin line ckt -01 ,B Phase ( Thakurgaon to Panchagarh)
| 13:20 | 15:08 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to metering work of 33 KV CP.
| 13:20 | 15:08 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to metering work of 33 KV CP.
|  | 13:25 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
| 14:08 |  | Full interruption (around 99MW) is occurring under Millgate substation as both
Tongi-Millgate circuit 1 & 2 tripped showing distance relay.
| 14:08 | 15:48 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-2 Tripped showing Z4/DEF.SEND relays. | [7 empty] | 36.0MW load
interrup.
| 14:08 | 15:30 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-1 Tripped showing PH B/DEF RCV 87L/2ND HR | [7 empty] | 48.0MW load
|  |  | BLKD Z1/5th HR BLKD Z3/Dist.SEND relays. | [7 empty] | interrup.
|  | 14:44 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
|  | 14:58 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
| 15:15 | 17:13 | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Oil leakage of TR -01
| 15:15 | 17:14 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Oil leakage of TR -01.
| 15:30 | 15:30 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-1 Forced S/D
| 16:39 | 17:41 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to 33 kv bus bar Fault | [7 empty] | 25.0MW load
interrup.
| 16:39 | 17:42 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Forced S/D Due to 33 kv bus bar Fault | [7 empty] | 25.0MW load
interrup.
| 18:35 | 23:48 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to 33kv side CT (R phase) red-hot | [7 empty] | 15.0MW load
interrup.
| 18:35 | 23:48 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to 33kv side CT (R phase) red-hot . | [7 empty] | 15.0MW load
interrup.
| 06:38 |  | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to S/D taken by PBS-Feni for 33kV T-2
bus side Hot spot Maintenance work
| 06:38 |  | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to S/D taken by PBS-Feni for 33kV T-2
bus side Hot spot Maintenance work
| 07:10 |  | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Buchholz Relay Oil Leakage
Maintenance Work of T-3.
| 07:10 |  | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Buchholz Relay Oil Leakage
Maintenance Work of T-3.
| 07:26 |  | Maniknagar 132/33kV S/S Transformer GT-2 HT Scheduled S/D Due to Maintenance Work for
High Temperature
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 22 | 190272.73 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 412 | 9504000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10175500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 311 | 7045527 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 330836 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 98 | 2264000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6427666 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 70128 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 312480 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 110 | 2401920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 463712 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 335365 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 446400 | Low water level
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 12 | 333360 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 543100 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 16 | 359500 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 932160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 2085305 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2215680 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 703680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1533600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 51567 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 753120 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 13535455 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1832400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6085.764 | 2753.5 | 64846733.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 38977.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127845 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1108680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 162 | 3860632 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 79 | 1139224 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 447100 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1821120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 370080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 770880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 190691 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 550 | 12381817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 42720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 780 | 18800000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 1841 | 41123286.2
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 175 | 4578000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 307 | 2607600 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6898000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 819864 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 35 | 805920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 158 | 3997818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1049432 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 1182618 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 24 | 652280 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 990790 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 969600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1696320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 1080264 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 430220 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1703160 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 584640 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 976320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 358172.73 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1515 | 31381018.73
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 126720 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 175 | 3129600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 1812000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 204000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 393840 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 295 | 5971940
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 966000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3473836 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 5 | 202896 | Gas shortage
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 112560 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 662304 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2023680 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 4407000 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 435000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 354624 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7312500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 375 | 8482000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7690300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1518 | 36122700
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 896 | 21444363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 82080 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 406800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 409 | 9600000 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1305 | 31533243
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 377.5 | 9137454 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 199836 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2434000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 972 | 23045818 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5181980 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5891000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2722.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1996.5 | 45892810.5
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4524727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 186 | 4766527 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4860873 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8673090 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 94878 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 75968 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 9540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1267.73 | 29672728 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 99752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 122680 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2249.23 | 52900763
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 61 | 1475345 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4228000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 867100 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48205.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 583145 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 223256 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1020960 | -
Rangpur Area Total |  |  |  |  | 950 | 336 | 8446011.92
Eastern Grid Total |  |  |  |  | 16921.242 | 7922.5 | 179445678.66
Western Grid Total |  |  |  |  | 11614.5 | 5886.73 | 138772828.42
National Grid Total |  |  |  |  | 28535.742 | 13809.23 | 318218507.08
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9322.15 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3993 | MW
i) Dhaka area |  |  | 4962.55 |  | MW | i) Khulna area |  |  |  | 1524.8 | MW
ii) Chattogram area |  |  | 1475.6 |  | MW | ii) Barishal area |  |  |  | 444 | MW
iii) Cumilla area |  |  | 1348 |  | MW | iii) Rajshahi area |  |  |  | 1234.2 | MW
iv) Mymensingh area |  |  | 1078 |  | MW | iv) Rangpur area |  |  |  | 790 | MW
v) Sylhet area |  |  | 458 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13315.15 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 79 | 18:00 | 133 | Payra | 30 | 21:00
2 | AKSML | 24.3 | 13:00 | 68 | Jamalpur | 117 | 18:00 | 134 | Postogola | 51 | 13:00
3 | Aftabnagar | 34 | 00:00 | 69 | Jashore | 137 | 00:00 | 135 | Purbachal | 18 | 00:00
4 | Agargaon | 108 | 13:00 | 70 | Jhenaidah | 117 | 00:00 | 136 | Purbasadipur | 124 | 13:00
5 | Agrabad | 92 | 15:00 | 71 | Joydebpur | 142 | 09:00 | 137 | Rahanpur | 29 | 04:00
6 | Amnura | 42 | 00:00 | 72 | Joypurhat | 64 | 00:00 | 138 | Rahim | 35 | 04:00
7 | Ashuganj | 112.5 | 18:30 | 73 | Juldah | 13 | 01:00 | 139 | Rajbari | 68 | 03:00
8 | BSRM | 198 | 23:00 | 74 | KSRM | 32 | 05:00 | 140 | Rajendrapur | 118 | 09:00
9 | Bagerhat | 83 | 00:00 | 75 | Kabirpur | 266 | 16:00 | 141 | Rajshahi | 97 | 04:00
10 | Bajitpur | 48 | 20:00 | 76 | Kachua | 81 | 18:30 | 142 | Rajshahi-230 | 74 | 00:00
11 | Bakulia | 100 | 19:00 | 77 | Kallyanpur | 102 | 00:00 | 143 | Ramganj | 124 | 18:30
12 | Banani | 26 | 11:00 | 78 | Kalurghat | 42 | 14:00 | 144 | Rampur | 41 | 23:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kamrangirchar | 73.15 | 13:00 | 145 | Rangamati | 16 | 18:30
14 | Barapukuria | 70 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 151 | 18:00
15 | Barguna | 20 | 00:00 | 81 | Kasba | 34 | 00:00 | 147 | Ruppur | 6.4 | 08:00
16 | Barishal | 94 | 00:00 | 82 | Kazla | 101 | 13:00 | 148 | SSM | 9 | 23:00
17 | Barishal-230 | 102 | 19:00 | 83 | Keranigonj | 75 | 00:00 | 149 | Saidpur | 118 | 17:00
18 | Baroaulia | 64 | 13:00 | 84 | Khagrachori | 32 | 18:00 | 150 | Satkhira | 129 | 18:30
19 | Baroirhat | 62 | 18:30 | 85 | Khulna | 59 | 19:00 | 151 | Satmasjid | 94 | 12:00
20 | Bashundhara | 180 | 13:00 | 86 | Khulshi | 167 | 23:00 | 152 | Savar | 204 | 10:00
21 | BashundharaCement | 8 | 16:00 | 87 | Kishoreganj | 122 | 00:00 | 153 | SevenRings | 20.2 | 03:00
22 | Beanibazar | 50 | 00:00 | 88 | Kodda | 296 | 10:00 | 154 | ShahCement | 37 | 23:00
23 | Benapole | 66 | 00:00 | 89 | Kulaura | 34 | 13:00 | 155 | Shahjadpur | 82 | 09:00
24 | Bhaluka | 138 | 10:00 | 90 | Kurigram | 61 | 17:00 | 156 | Shahjibazar | 120 | 00:00
25 | Bhandaria | 50 | 00:00 | 91 | Kushtia | 114 | 18:00 | 157 | Shahmirpur | 60 | 00:00
26 | Bhangura | 38 | 03:00 | 92 | Lalbag | 64 | 13:00 | 158 | Shariatpur | 75 | 00:00
27 | Bheramara(GK) | 46 | 00:00 | 93 | Lalmonirhat | 57 | 17:00 | 159 | Sherpur | 160 | 18:00
28 | Bhulta | 266 | 23:00 | 94 | MI_Cement | 18.2 | 17:00 | 160 | Shikalbaha | 29 | 00:00
29 | Bog-Sherpur | 66 | 03:00 | 95 | Madanganj | 44 | 21:00 | 161 | Shitalakhya | 80.8 | 11:00
30 | Bogura | 167 | 03:00 | 96 | Madaripur | 98 | 21:00 | 162 | Sholosohor | 43 | 12:00
31 | Borhanuddin | 82 | 22:00 | 97 | Madartek | 86.09 | 00:00 | 163 | Shyampur | 196 | 10:00
32 | Brahmanbaria | 122 | 00:00 | 98 | Madunaghat | 50 | 18:30 | 164 | Siddhirganj | 124 | 10:00
33 | Cantonment | 142 | 13:00 | 99 | Magura | 54 | 00:00 | 165 | Sirajganj | 98 | 09:00
34 | Chandpur | 65 | 21:00 | 100 | Mahasthangarh | 74 | 21:00 | 166 | Sonargaon | 120 | 23:00
35 | Chandraghona | 36 | 18:30 | 101 | Manikganj | 112 | 00:00 | 167 | Sreemongol | 63 | 21:00
36 | Chapai | 67 | 00:00 | 102 | Maniknagar | 68 | 12:00 | 168 | Sreepur | 102 | 12:00
37 | Charsaidpur | 49 | 11:00 | 103 | Matarbari | 49 | 19:00 | 169 | Srinagar | 40 | 21:00
38 | Chauddagram | 76 | 00:00 | 104 | Matuail | 71 | 12:00 | 170 | Sunamganj | 46 | 20:00
39 | Chhatak | 26 | 23:00 | 105 | Millgate | 105 | 11:00 | 171 | Sylhet | 34 | 22:00
40 | Chowmuhani | 235 | 18:30 | 106 | Mirpur | 129 | 14:00 | 172 | Sylhet-132 | 91 | 00:00
41 | Chuadanga | 101 | 03:00 | 107 | Mirsorai | 10 | 00:00 | 173 | TK | 22.7 | 21:00
42 | Coxsbazar | 135 | 19:00 | 108 | Mirzapur | 44 | 07:00 | 174 | Tangail | 168 | 07:00
43 | Cumilla(N) | 159 | 01:00 | 109 | Mithapukur | 56 | 17:00 | 175 | Thakurgaon | 96 | 17:00
44 | Cumilla(S) | 175 | 22:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 138 | 16:00
45 | Daudkandi | 145 | 21:00 | 111 | Mogbazar | 134.7 | 12:00 | 177 | Ullahpara | 32 | 09:00
46 | Dhaka | 54 | 11:00 | 112 | Mongla | 36 | 10:00 | 178 | Ullon | 48 | 20:00
47 | Dhamrai | 132 | 10:00 | 113 | Motijheel | 36 | 12:00 | 179 | Uttara | 80 | 12:00
48 | Dhanmondi | 140 | 12:00 | 114 | Muktagacha | 32 | 18:00 | 180 | UttaraNew | 31 | 02:00
49 | Dohazari | 109 | 22:00 | 115 | Munshiganj | 106 | 00:00 | 181 | Zigatola | 66 | 00:00
50 | Faridpur | 135 | 00:00 | 116 | Muradnagar | 26 | 00:00
51 | Fatullah | 96 | 12:00 | 117 | Mymensingh | 197 | 18:00
52 | Fenchuganj | 24 | 18:00 | 118 | Naogaon | 122 | 04:00
53 | Feni | 119 | 18:30 | 119 | Narail | 52 | 00:00
54 | GPH | 95 | 19:30 | 120 | Narinda | 82 | 13:00
55 | Ghatail | 70 | 13:00 | 121 | Narshingdi | 170 | 01:00
56 | Ghorashal | 14 | 11:00 | 122 | Natore | 135 | 04:00
57 | Ghorashal-230 | 87 | 14:00 | 123 | Nawabganj | 47.4 | 00:00
58 | Goalpara | 34 | 00:00 | 124 | Netrakona | 142 | 18:00
59 | Gollamari | 90 | 19:00 | 125 | New | 88.6 | 12:00
60 | Gopalganj | 96 | 19:00 | 126 | Niamatpur | 100 | 08:00
61 | Gulshan | 110 | 11:00 | 127 | Noapara | 43 | 19:00
62 | Halishahar | 72 | 14:00 | 128 | PHP | 6 | 05:00
63 | HaripurSBU | 187 | 11:00 | 129 | Pabna | 107 | 03:00
64 | Hasnabad | 81 | 00:00 | 130 | Palashbari | 100 | 18:00
65 | Hathazari | 79 | 20:00 | 131 | Panchagarh | 53 | 18:00
66 | Ishurdi | 62 | 03:00 | 132 | Patuakhali | 71 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13936.13 | 186 |  | 14130.5
1:00 | 13514.73 | 126 |  | 13646.4
2:00 | 13161.78 | 124 |  | 13291.78
3:00 | 13266.56 | 148 |  | 13421.56
4:00 | 13448.81 | 79 |  | 13531.81
5:00 | 12584.29 | 55 |  | 12641.29
6:00 | 11920.74 | 10 |  | 11930.74
7:00 | 11976.21 | 0 |  | 11976.21
8:00 | 12415.65 | 45 |  | 12462.65
9:00 | 12732.88 | 30 |  | 12763.88
10:00 | 13079.94 | 90 |  | 13173.94
11:00 | 13082.41 | 188 |  | 13278.41
12:00 | 13324.24 | 175 |  | 13507.24
13:00 | 13537.32 | 197 |  | 13743.32
14:00 | 13479.08 | 215 |  | 13704.08
15:00 | 13195.94 | 184 |  | 13387.94
16:00 | 13173.23 | 125 |  | 13304.23
17:00 | 13313.85 | 86 |  | 13403.85
18:00 | 13424.5 | 0 |  | 13424.5
19:00 | 13496.03 | 0 |  | 13496.03
19:30 | 13599.99 | 0 |  | 13599.99
20:00 | 13566.39 | 0 |  | 13566.39
21:00 | 13809.23 | 0 |  | 13809.23
22:00 | 13640.11 | 0 |  | 13640.11
23:00 | 13395.52 | 0 |  | 13395.52
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7632.5 | 6303.63 | 13936.13 | DAILY GENERATION CURVE
00:30 | 7537.75 | 6187.68 | 13725.43
01:00 | 7443 | 6071.73 | 13514.73 | 20-03-2025
01:30 | 7391 | 5947.255 | 13338.255
02:00 | 7339 | 5822.78 | 13161.78
02:30 | 7357 | 5857.17 | 13214.17
03:00 | 7375 | 5891.56 | 13266.56
03:30 | 7417.75 | 5939.935 | 13357.685
04:00 | 7460.5 | 5988.31 | 13448.81
04:30 | 7267.5 | 5749.05 | 13016.55
05:00 | 7074.5 | 5509.79 | 12584.29
05:30 | 6878 | 5374.515 | 12252.515
06:00 | 6681.5 | 5239.24 | 11920.74
06:30 | 6674.945 | 5273.53 | 11948.475
07:00 | 6668.39 | 5307.82 | 11976.21
07:30 | 6791.37 | 5404.56 | 12195.93
08:00 | 6914.35 | 5501.3 | 12415.65
08:30 | 6999.985 | 5574.28 | 12574.265
09:00 | 7085.62 | 5647.26 | 12732.88
09:30 | 7198.495 | 5707.915 | 12906.41
10:00 | 7311.37 | 5768.57 | 13079.94
10:30 | 7339.82 | 5741.355 | 13081.175
11:00 | 7368.27 | 5714.14 | 13082.41
11:30 | 7453.685 | 5749.64 | 13203.325
12:00 | 7539.1 | 5785.14 | 13324.24
12:30 | 7689.905 | 5740.875 | 13430.78
13:00 | 7840.71 | 5696.61 | 13537.32
13:30 | 7750.86 | 5757.34 | 13508.2
14:00 | 7661.01 | 5818.07 | 13479.08
14:30 | 7635.69 | 5701.82 | 13337.51
15:00 | 7610.37 | 5585.57 | 13195.94
15:30 | 7634.63 | 5549.955 | 13184.585
16:00 | 7658.89 | 5514.34 | 13173.23
16:30 | 7708.71 | 5534.83 | 13243.54
17:00 | 7758.53 | 5555.32 | 13313.85
17:30 | 7765.07 | 5604.105 | 13369.175
18:00 | 7771.61 | 5652.89 | 13424.5
18:30 | 7799.805 | 5660.46 | 13460.265
19:00 | 7828 | 5668.03 | 13496.03
19:30 | 7794 | 5805.99 | 13599.99
20:00 | 7794 | 5772.39 | 13566.39
20:30 | 7858.25 | 5829.56 | 13687.81 |  | Executive Engineer
21:00 | 7922.5 | 5886.73 | 13809.23 |  | Network Operation Division
21:30 | 7850 | 5874.67 | 13724.67
22:00 | 7777.5 | 5862.61 | 13640.11
22:30 | 7659 | 5858.815 | 13517.815
23:00 | 7540.5 | 5855.02 | 13395.52

## En-Curve
QF-LDC-12
Date | 20-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3593 | 2410.5 | 903 | 0 | 82 | 1354.13 | 46 | 3963 | 0 | 549.5 | 1035 | 0 | 0 | 0 | 186 | DAILY ENERGY CURVE
00:30 | 3611.5 | 2412.5 | 899 | 0 | 78 | 1357.43 | 46 | 3902 | 0 | 535 | 884 | 0 | 0 | 0 | 156 | 20-03-2025
01:00 | 3630 | 2414.5 | 895 | 0 | 74 | 1360.73 | 46 | 3841 | 0 | 520.5 | 733 | 0 | 0 | 0 | 126
01:30 | 3549.5 | 2420 | 896 | 0 | 75 | 1360.755 | 46 | 3788 | 0 | 520.5 | 682.5 | 0 | 0 | 0 | 125 | Energy Generated | 318.2185 |  | MKWHr
02:00 | 3469 | 2425.5 | 897 | 0 | 76 | 1360.78 | 46 | 3735 | 0 | 520.5 | 632 | 0 | 0 | 0 | 124 | Energy not Served | 2.063 |  | MKWHr
02:30 | 3516 | 2406 | 896 | 0 | 72 | 1360.67 | 46 | 3754.5 | 0 | 521 | 642 | 0 | 0 | 0 | 136 | Total Energy Requirement | 320.2815 |  | MKWHr
03:00 | 3563 | 2386.5 | 895 | 0 | 68 | 1360.56 | 46 | 3774 | 0 | 521.5 | 652 | 0 | 0 | 0 | 148
03:30 | 3539.5 | 2415.75 | 895 | 0 | 71 | 1357.785 | 46 | 3842.65 | 0 | 513 | 677 | 0 | 0 | 0 | 113.5
04:00 | 3516 | 2445 | 895 | 0 | 74 | 1355.01 | 46 | 3911.3 | 0 | 504.5 | 702 | 0 | 0 | 0 | 79
04:30 | 3494 | 2440 | 895 | 0 | 75 | 1263.9 | 46 | 3688.15 | 0 | 452.5 | 662 | 0 | 0 | 0 | 67
05:00 | 3472 | 2435 | 895 | 0 | 76 | 1172.79 | 46 | 3465 | 0 | 400.5 | 622 | 0 | 0 | 0 | 55
05:30 | 3469.5 | 2430.5 | 895 | 0 | 72 | 1094.015 | 46 | 3358 | 0 | 309.5 | 578 | 0 | 0 | 0 | 32.5
06:00 | 3467 | 2426 | 895 | 0 | 68 | 1015.24 | 46 | 3251 | 0 | 218.5 | 534 | 0 | 0 | 0 | 10
06:30 | 3513.5 | 2418.75 | 895.5 | 0 | 67 | 1014.65 | 46 | 3250 | 25.575 | 233.5 | 484 | 0 | 0 | 0 | 5
07:00 | 3560 | 2411.5 | 896 | 0 | 66 | 1014.06 | 46 | 3249 | 51.15 | 248.5 | 434 | 0 | 0 | 0 | 0
07:30 | 3515 | 2437 | 872.5 | 0 | 67 | 1067.03 | 46 | 3369 | 94.9 | 279.5 | 448 | 0 | 0 | 0 | 22.5
08:00 | 3470 | 2462.5 | 849 | 0 | 68 | 1120 | 46 | 3489 | 138.65 | 310.5 | 462 | 0 | 0 | 0 | 45
08:30 | 3511.5 | 2480 | 849 | 0 | 66 | 1120 | 46 | 3503 | 203.765 | 329 | 466 | 0 | 0 | 0 | 37.5
09:00 | 3553 | 2497.5 | 849 | 0 | 64 | 1120 | 46 | 3517 | 268.88 | 347.5 | 470 | 0 | 0 | 0 | 30
09:30 | 3619.5 | 2516.5 | 872.5 | 0 | 61 | 1140.5 | 46 | 3450 | 308.41 | 360.5 | 531.5 | 0 | 0 | 0 | 60
10:00 | 3686 | 2535.5 | 896 | 0 | 58 | 1161 | 46 | 3383 | 347.94 | 373.5 | 593 | 0 | 0 | 0 | 90
10:30 | 3616.5 | 2514.5 | 896.5 | 0 | 62 | 1159 | 46 | 3311 | 375.425 | 352.25 | 748 | 0 | 0 | 0 | 139
11:00 | 3547 | 2493.5 | 897 | 0 | 66 | 1157 | 46 | 3239 | 402.91 | 331 | 903 | 0 | 0 | 0 | 188
11:30 | 3534.5 | 2497 | 896.5 | 0 | 65 | 1212.5 | 46 | 3256 | 385.825 | 333.5 | 972 | 0 | 0 | 4.5 | 181.5
12:00 | 3522 | 2500.5 | 896 | 0 | 64 | 1268 | 46 | 3273 | 368.74 | 336 | 1041 | 0 | 0 | 9 | 175
12:30 | 3469.5 | 2445.5 | 896 | 0 | 67 | 1293.5 | 46 | 3261 | 355.03 | 377 | 1210.75 | 0 | 0 | 9.5 | 186
13:00 | 3417 | 2390.5 | 896 | 0 | 70 | 1319 | 46 | 3249 | 341.32 | 418 | 1380.5 | 0 | 0 | 10 | 197
13:30 | 3369.5 | 2393 | 896.5 | 0 | 69 | 1321.55 | 46 | 3289 | 342.65 | 383 | 1390 | 0 | 0 | 8 | 206
14:00 | 3322 | 2395.5 | 897 | 0 | 68 | 1324.1 | 46 | 3329 | 343.98 | 348 | 1399.5 | 0 | 0 | 6 | 215
14:30 | 3349.5 | 2363 | 896.5 | 0 | 71 | 1272.02 | 46 | 3302 | 311.99 | 352 | 1366 | 0 | 0 | 7.5 | 199.5
15:00 | 3377 | 2330.5 | 896 | 0 | 74 | 1219.94 | 46 | 3275 | 280 | 356 | 1332.5 | 0 | 0 | 9 | 184
15:30 | 3421.5 | 2359 | 896.5 | 0 | 70 | 1220.545 | 46 | 3275 | 221.54 | 367.5 | 1300.5 | 0 | 0 | 6.5 | 154.5
16:00 | 3466 | 2387.5 | 897 | 0 | 66 | 1221.15 | 46 | 3275 | 163.08 | 379 | 1268.5 | 0 | 0 | 4 | 125
16:30 | 3472 | 2432.5 | 896.5 | 0 | 67 | 1215.51 | 46 | 3313 | 108.03 | 405.5 | 1285.5 | 0 | 0 | 2 | 105.5
17:00 | 3478 | 2477.5 | 896 | 0 | 68 | 1209.87 | 46 | 3351 | 52.98 | 432 | 1302.5 | 0 | 0 | 0 | 86
17:30 | 3440.5 | 2424 | 896 | 0 | 71 | 1214.405 | 46 | 3383.585 | 27.685 | 458 | 1408 | 0 | 0 | 0 | 43
18:00 | 3403 | 2370.5 | 896 | 0 | 74 | 1218.94 | 46 | 3416.17 | 2.39 | 484 | 1513.5 | 0 | 0 | 0 | 0
18:30 | 3506.5 | 2383.5 | 872 | 0 | 72 | 1219.235 | 46 | 3438.085 | 1.195 | 487 | 1434.75 | 0 | 0 | 0 | 0
19:00 | 3610 | 2396.5 | 848 | 0 | 70 | 1219.53 | 46 | 3460 | 0 | 490 | 1356 | 0 | 0 | 0 | 0
19:30 | 3698 | 2421.5 | 848 | 0 | 74 | 1279.49 | 46 | 3554 | 0 | 504 | 1175 | 0 | 0 | 0 | 0
20:00 | 3726 | 2443.5 | 848 | 0 | 70 | 1269.89 | 46 | 3552 | 0 | 464 | 1147 | 0 | 0 | 0 | 0
20:30 | 3771 | 2481.75 | 872 | 0 | 75 | 1268.81 | 46 | 3589.25 | 0 | 464 | 1120 | 0 | 0 | 0 | 0
21:00 | 3816 | 2520 | 896 | 0 | 80 | 1267.73 | 46 | 3626.5 | 0 | 464 | 1093 | 0 | 0 | 0 | 0
21:30 | 3811 | 2466 | 892 | 0 | 80 | 1268.92 | 46 | 3626.25 | 0 | 452 | 1082.5 | 0 | 0 | 0 | 0
22:00 | 3806 | 2412 | 888 | 0 | 80 | 1270.11 | 46 | 3626 | 0 | 440 | 1072 | 0 | 0 | 0 | 0
22:30 | 3797 | 2411.5 | 889 | 0 | 81 | 1264.315 | 46 | 3538 | 0 | 447 | 1043.5 | 0 | 0 | 0.5 | 0
23:00 | 3788 | 2411 | 890 | 0 | 82 | 1258.52 | 46 | 3450 | 0 | 454 | 1015 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 18:30 | 292 | 05:00 | Payra | 416 | 18:30 | 409 | 00:00
Ashuganj | 410 | 18:00 | 373 | 09::00 | Rahanpur | 395 | 06:00 | 383 | 04:00
Bhulta | 405 | 18:00 | 373 | 10:00 | Rampal | 405 | 06:00 | 393 | 00:00
Bibiana | 394 | 13:00 | 386 | 10:00
BIPTC | 398 | 22:00 | 391 | 01:00
Bogura | 382 | 06:00 | 366 | 12:00
Gopalganj | 402 | 06:00 | 391 | 00:00
Kaliakoir | 378 | 18:00 | 356 | 09:00
Madunaghat | 396 | 19:00 | 388 | 10:00
Meghnaghat | 401 | 18:30 | 383 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 18:30 | 219 | 10:00 | Keranigonj | 232 | 18:30 | 216 | 10:00
AKSML | 234 | 18:00 | 223 | 10:00 | Khulna(S) | 233 | 06:00 | 223 | 00:00
Aminbazar | 229 | 05:00 | 222 | 15:00 | Madunaghat | 233 | 18:00 | 226 | 10:00
Ashuganj | 232 | 18:00 | 221 | 10:00 | Madunaghat-400 | 234 | 19:00 | 228 | 10:00
Ashuganj-400 | 232 | 18:00 | 221 | 10:00 | Maniknagar | 229 | 18:00 | 214 | 10:00
Baghabari | 234 | 05:00 | 225 | 09:00 | Meghnaghat | 236 | 18:00 | 224 | 10:00
Barapukuria | 222 | 00:00 | 213 | 12:00 | Meghnaghat-400 | 233 | 18:30 | 219 | 10:00
Barapukuria-230 | 222 | 00:00 | 213 | 12:00 | Mirsorai | 229 | 18:30 | 219 | 10:00
Barishal | 236 | 06:00 | 230 | 00:00 | Rajshahi | 232 | 05:00 | 221 | 10:00
Bheramara | 235 | 05:00 | 223 | 10:00 | Rampal | 232 | 06:00 | 223 | 00:00
Bhulta | 231 | 18:00 | 214 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 18:00 | 222 | 10:00 | Rampura | 229 | 18:30 | 212 | 10:00
BIPTC | 237 | 05:00 | 222 | 10:00 | Shikalbaha | 266 | 15:00 | 224 | 10:00
Bogura | 234 | 18:30 | 223 | 12:00 | Shyampur | 229 | 18:00 | 217 | 10:00
Bogura-400 | 234 | 06:00 | 223 | 12:00 | Siddhirganj | 227 | 18:00 | 218 | 10:00
Borhanuddin | 240 | 06:00 | 236 | 00:00 | Sirajgonj | 239 | 04:00 | 233 | 10:00
BSRM | 230 | 18:30 | 219 | 10:00 | Sreepur | 231 | 18:00 | 216 | 00:00
Cumilla(N) | 226 | 18:30 | 216 | 10:00 | Tongi | 225 | 18:30 | 210 | 09:00
Faridpur | 234 | 18:30 | 225 | 00:00
Fenchuganj | 233 | 18:00 | 225 | 01:00
Ghorashal | 235 | 00:00 | 230 | 01:00
Ghorashal-230 | 230 | 18:30 | 213 | 10:00
Gopalganj | 232 | 06:00 | 225 | 00:00
GPH | 232 | 18:30 | 222 | 10:00
Haripur | 225 | 05:00 | 216 | 10:00
Hasnabad | 227 | 18:30 | 219 | 10:00
Hathazari | 233 | 18:00 | 226 | 07:00
Ishurdi | 236 | 05:00 | 224 | 10:00
Jhenaidah | 230 | 05:00 | 220 | 19:30
Kaliakoir | 235 | 18:00 | 220 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 18:00 | 126 | 08:00 | Madunaghat | 133 | 18:30 | 129 | 09:00
Agargaon | 139 | 18:30 | 129 | 10:00 | Magura | 132 | 05:00 | 124 | 00:00
Agrabad | 132 | 18:00 | 126 | 10:00 | Mahasthangarh | 131 | 18:30 | 121 | 09:00
AKS | 129 | 04:00 | 126 | 00:00 | Manikganj | 129 | 18:00 | 122 | 09:00
Aminbazar | 136 | 18:00 | 129 | 00:00 | Maniknagar | 135 | 18:30 | 125 | 10:00
Amnura | 135 | 05:00 | 126 | 00:00 | Matarbari | 121 | 07:00 | 111 | 19:00
Ashuganj | 137 | 18:30 | 132 | 11:00 | Matuail | 134 | 18:00 | 124 | 10:00
Bagerhat | 130 | 06:00 | 120 | 18:00 | Millgate | 137 | 18:00 | 124 | 10:00
Bajitpur | 131 | 18:30 | 124 | 12:00 | Mirpur | 136 | 18:30 | 125 | 10:00
Bakulia | 132 | 05:00 | 128 | 10:00 | Mirzapur | 131 | 18:30 | 120 | 10:00
Banani | 136 | 18:30 | 125 | 10:00 | Mithapukur | 133 | 18:30 | 118 | 12:00
Bangabhaban | 134 | 18:30 | 125 | 10:00 | MI_Cement | 133.2 | 18:30 | 124 | 10:00
Barapukuria | 137 | 00:00 | 128 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 06:00 | 131 | 00:00 | Mogbazar | 135 | 02:00 | 125 | 10:00
Barishal | 131 | 06:00 | 125 | 00:00 | Mongla | 130 | 05:00 | 121 | 00:00
Barishal-230 | 131 | 06:00 | 126 | 00:00 | Motijheel | 134 | 18:30 | 125 | 10:00
Baroaulia | 132 | 18:30 | 128 | 11:00 | Muktagacha | 132 | 14:00 | 120 | 00:00
Baroirhat | 125 | 19:00 | 117 | 09:00 | Munshiganj | 133 | 18:00 | 123 | 09:00
Bashundhara | 135 | 18:30 | 123 | 10:00 | Muradnagar | 131 | 18:00 | 120 | 09:00
BashundharaCement | 134 | 18:30 | 124 | 11:00 | Mymensingh | 133 | 17:00 | 114 | 12:00
Beanibazar | 131 | 04:00 | 128 | 00:00 | Naogaon | 127 | 18:30 | 118 | 09:00
Benapole | 128 | 06:00 | 120 | 00:00 | Narail | 132 | 05:00 | 124 | 00:00
Bhaluka | 128 | 18:30 | 119 | 10:00 | Narinda | 135 | 18:30 | 125 | 10:00
Bhandaria | 126 | 09:00 | 116 | 00:00 | Narshingdi | 131 | 18:30 | 118 | 00:00
Bhangura | 133 | 00:00 | 126 | 10:00 | Natore | 132 | 05:00 | 125 | 10:00
Bheramara | 134 | 05:00 | 127 | 10:00 | Nawabganj | 138 | 18:30 | 129 | 10:00
Bheramara(GK) | 134 | 05:00 | 128 | 09:00 | Netrakona | 121 | 18:30 | 111 | 12:00
Bhulta | 129 | 18:00 | 119 | 10:00 | New | 141 | 18:00 | 124 | 10:00
Bog-Sherpur | 131 | 18:30 | 122 | 10:00 | Niamatpur | 133 | 05:00 | 129 | 09:00
Bogura | 132 | 06:00 | 125 | 09:00 | Noapara | 132 | 03:00 | 125 | 00:00
Bogura-230 | 133 | 18:30 | 125 | 10:00 | Pabna | 134 | 05:00 | 127 | 10:00
Brahmanbaria | 130 | 18:00 | 122 | 00:00 | Palashbari | 127 | 00:00 | 117 | 12:00
Cantonment | 139 | 18:30 | 129 | 10:00 | Panchagarh | 137 | 18:30 | 113 | 12:00
Chandpur | 126 | 19:30 | 113 | 10:00 | Patuakhali | 135 | 18:30 | 130 | 00:00
Chandraghona | 133 | 18:00 | 128 | 09:00 | Payra | 137 | 18:30 | 134 | 00:00
Chapai | 131 | 01:00 | 126 | 13:00 | PHP | 124 | 19:30 | 115 | 10:00
Charsaidpur | 134 | 18:30 | 124 | 10:00 | Postogola | 139 | 18:00 | 127 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 18:30 | 116 | 09:00 | Purbachal | 136 | 18:30 | 125 | 10:00
Chhatak | 132 | 05:00 | 128 | 00:00 | Purbasadipur | 130 | 00:00 | 112 | 12:00
Chowmuhani | 122 | 21:00 | 109 | 15:00 | Rahanpur | 135 | 06:00 | 130 | 03:00
Chuadanga | 132 | 05:00 | 122 | 00:00 | Rahanpur-400 | 135 | 05:00 | 131 | 00:00
Coxsbazar | 120 | 06:00 | 112 | 19:00 | Rahim | 135 | 18:00 | 126 | 09:00
Cumilla(N) | 129 | 18:30 | 122 | 09:00 | Rajbari | 130 | 18:30 | 124 | 00:00
Cumilla(S) | 129 | 03:00 | 121 | 10:00 | Rajendrapur | 131 | 18:30 | 118 | 10:00
Daudkandi | 128 | 18:30 | 119 | 00:00 | Rajshahi | 134 | 05:00 | 127 | 10:00
Dhaka | 135 | 18:00 | 126 | 10:00 | Rajshahi-230 | 134 | 06:00 | 120 | 04:00
Dhamrai | 133 | 18:30 | 121 | 10:00 | Ramganj | 126 | 21:00 | 107 | 10:00
Dhanmondi | 136 | 06:00 | 126 | 10:00 | Rampur | 133 | 18:00 | 127 | 10:00
Dohazari | 126 | 06:00 | 107 | 19:30 | Rampura | 137 | 18:30 | 125 | 10:00
Faridpur | 131 | 18:30 | 126 | 00:00 | Rangamati | 132 | 18:00 | 127 | 10:00
Fatullah | 135 | 18:30 | 125 | 10:00 | Rangpur | 131 | 18:30 | 118 | 12:00
Fenchuganj | 135 | 18:00 | 131 | 10:00 | Ruppur | 136 | 04:00 | 129 | 08:00
Feni | 125 | 20:00 | 114 | 09:00 | Saidpur | 132 | 18:30 | 117 | 12:00
Ghatail | 128 | 05:00 | 119 | 10:00 | Satkhira | 130 | 06:00 | 118 | 20:00
Ghorashal | 136 | 18:00 | 129 | 11:00 | Satmasjid | 139 | 18:30 | 129 | 12:00
Goalpara | 134 | 06:00 | 126 | 21:00 | Savar | 137 | 18:00 | 124 | 12:00
Gollamari | 134 | 18:00 | 127 | 01:00 | SevenRings | 137 | 18:30 | 127 | 10:00
Gopalganj | 134 | 06:00 | 128 | 00:00 | ShahCement | 134 | 18:30 | 124 | 10:00
Gopalganj-400 | 136 | 06:00 | 131 | 00:00 | Shahjadpur | 136 | 03:00 | 130 | 08:00
Gulshan | 136 | 18:30 | 125 | 10:00 | Shahjibazar | 132 | 18:00 | 125 | 00:00
Halishahar | 132 | 07:00 | 126 | 10:00 | Shahmirpur | 133 | 05:00 | 129 | 10:00
Haripur | 132 | 18:00 | 125 | 10:00 | Shariatpur | 135 | 06:00 | 128 | 01:00
HaripurSBU | 132 | 19:00 | 125 | 10:00 | Sherpur | 135 | 23:00 | 115 | 02:00
Hasnabad | 134 | 18:30 | 126 | 09:00 | Shikalbaha | 123 | 19:30 | 118 | 10:00
Hathazari | 134 | 18:00 | 130 | 07:00 | Shikalbaha-230 | 134 | 06:00 | 130 | 10:00
Ishurdi | 137 | 05:00 | 129 | 10:00 | Shitalakhya | 133.2 | 18:30 | 124 | 10:00
Jaldhaka | 130 | 00:00 | 114 | 12:00 | Sholosohor | 133 | 06:00 | 128 | 10:00
Jamalpur | 138 | 23:00 | 119 | 03:00 | Shyampur | 134 | 18:30 | 124 | 09:00
Jashore | 130 | 06:00 | 122 | 00:00 | Shyampur-230 | 134 | 18:00 | 124 | 10:00
Jhenaidah | 133 | 05:00 | 126 | 00:00 | Siddhirganj | 137 | 18:00 | 125 | 10:00
Jhenaidah-230 | 133 | 05:00 | 125 | 20:00 | Sirajganj | 131 | 18:30 | 121 | 09:00
Joydebpur | 130 | 13:00 | 121 | 10:00 | Sonargaon | 135 | 18:30 | 124 | 00:00
Joypurhat | 124 | 04:00 | 114 | 10:00 | Sreemongol | 132 | 18:00 | 126 | 00:00
Juldah | 133 | 19:00 | 130 | 05:00 | Sreepur | 130 | 18:00 | 122 | 10:00
Kabirpur | 136 | 18:00 | 121 | 10:00 | Srinagar | 137 | 18:00 | 129 | 09:00
Kachua | 125 | 19:30 | 114 | 09:00 | SSM | 136 | 19:30 | 131 | 16:00
Kaliakoir | 136 | 18:00 | 125 | 10:00 | Sunamganj | 130 | 04:00 | 127 | 00:00
Kallyanpur | 136 | 18:00 | 126 | 10:00 | Sylhet | 132 | 07:00 | 129 | 00:00
Kalurghat | 133 | 18:00 | 128 | 10:00 | Sylhet-132 | 134 | 18:00 | 130 | 00:00
Kamrangirchar | 137 | 18:00 | 129 | 09:00 | Tangail | 128 | 13:00 | 119 | 09:00
Kaptai | 136 | 6:00 | 122 | 18:00 | Thakurgaon | 135 | 18:30 | 111 | 12:00
Kasba | 128 | 18:00 | 120 | 10:00 | TK | 134 | 19:30 | 129 | 09:00
Kazla | 134 | 19:00 | 124 | 11:00 | Tongi | 137 | 19:30 | 125 | 09:00
Keranigonj | 140 | 18:30 | 129 | 10:00 | Ullahpara | 132 | 05:00 | 123 | 10:00
Khagrachori | 131 | 06:00 | 126 | 10:00 | Ullon | 135 | 18:30 | 126 | 10:00
Khulna | 131 | 05:00 | 125 | 00:00 | Uttara | 135 | 18:00 | 125 | 10:00
Khulna(S) | 134 | 06:00 | 127 | 00:00 | UttaraNew | 136 | 18:30 | 124 | 10:00
Khulshi | 131 | 06:00 | 125 | 10:00 | Zigatola | 140 | 18:00 | 129 | 10:00
Kishoreganj | 129 | 18:30 | 121 | 10:00
Kodda | 136 | 04:00 | 119 | 10:00
KSRM | 132 | 06:00 | 128 | 09:00
Kulaura | 134 | 18:30 | 130 | 00:00
Kurigram | 130 | 18:30 | 116 | 12:00
Kushtia | 132 | 03:00 | 127 | 00:00
Lalbag | 140 | 18:30 | 125 | 09:00
Lalmonirhat | 127 | 22:00 | 115 | 12:00
Madanganj | 134 | 18:30 | 124 | 11:00
Madaripur | 135 | 18:00 | 129 | 00:00
Madartek | 135 | 06:00 | 124 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division