## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-03-2025 | [28 empty] | Date: | 21-03-2025 | [28 empty] | Date: | 21-03-2025 | [28 empty] | Date: | 21-03-2025 | [28 empty] | Date: | 21-03-2025 | [18 empty] | Date: | 21-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 22 | 372 | 0 | 0 | 17 | 54 | 0 | 0 | 129 | 0 | 0 | 17 | 108 | 22 | 16 | 450 | 277 | 583 | 0 | 0 | 14 | 260 | 100 | 0 | 0 | 70 | 20.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 81 | 0 | 88 | 60 | 0 | 46 | 0 | 29 | 575 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 553 | 0 | 43 | 0 | 16 | 0 | 380 | 285 | 10 | 194 | 36 | 17 | 30 | 120 | 42 | 20 | 52 | 78 | 34 | 0 | 0 | 295 | 320 | 350 | 5 | 41 | 0 | 5 | 152 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 49 | 58 | 0 | 0 | 0 | 12 | 7276.5 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1265.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 182 | 0 | 189 | 0 | 393 | 0 | 0 | 2.5 | 162 | 61 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 378 | 992 | 0 | 5817.14 | 13093.64 | 86.42
01:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 18 | 0 | 0 | 129 | 0 | 0 | 17 | 72 | 22 | 16 | 380 | 297 | 500 | 0 | 0 | 14 | 260 | 102 | 0 | 0 | 70 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 51 | 81 | 0 | 88 | 36 | 0 | 46 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 553 | 0 | 43 | 0 | 8 | 0 | 370 | 285 | 10 | 211 | 36 | 17 | 20 | 140 | 28 | 20 | 88 | 78 | 34 | 0 | 0 | 300 | 320 | 350 | 5 | 41 | 0 | 5 | 152 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 49 | 58 | 0 | 0 | 0 | 12 | 7048 | 889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 1165.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 180 | 0 | 140 | 0 | 396 | 0 | 0 | 2.5 | 161 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 110 | 220 | 0 | 377 | 896 | 0 | 5479.45 | 12527.45 | 86.41
02:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 18 | 0 | 0 | 129 | 0 | 0 | 17 | 72 | 22 | 16 | 330 | 305 | 450 | 0 | 0 | 14 | 258 | 101 | 0 | 0 | 70 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 51 | 81 | 0 | 88 | 12 | 0 | 46 | 0 | 31 | 640 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 500 | 0 | 43 | 0 | 8 | 0 | 370 | 285 | 10 | 211 | 36 | 16 | 0 | 155 | 27 | 20 | 88 | 76 | 34 | 0 | 0 | 300 | 320 | 346 | 5 | 41 | 0 | 5 | 152 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 49 | 58 | 0 | 0 | 0 | 12 | 6909 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 1166.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 165 | 0 | 140 | 0 | 396 | 0 | 0 | 2.5 | 163 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 110 | 180 | 0 | 377 | 850 | 0 | 5340.24 | 12249.24 | 86.4
03:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 18 | 0 | 0 | 128 | 0 | 0 | 17 | 54 | 22 | 16 | 400 | 311 | 450 | 0 | 0 | 14 | 255 | 101 | 0 | 0 | 70 | 19.7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 51 | 81 | 0 | 48 | 12 | 0 | 46 | 0 | 32 | 770 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 533 | 0 | 43 | 0 | 8 | 0 | 330 | 285 | 10 | 208 | 36 | 17 | 0 | 155 | 28 | 20 | 88 | 72 | 34 | 0 | 0 | 305 | 320 | 394 | 5 | 41 | 0 | 5 | 156 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 78 | 74 | 0 | 0 | 0 | 12 | 7111.7 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 1114.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 159 | 0 | 376 | 0 | 0 | 2.5 | 161 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 10 | 110 | 180 | 0 | 378 | 859 | 0 | 5272.01 | 12383.71 | 86.39
04:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 18 | 0 | 0 | 128 | 0 | 0 | 0 | 35 | 22 | 0 | 400 | 272 | 550 | 0 | 0 | 10 | 250 | 36 | 0 | 0 | 70 | 19.7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 16 | 0 | 48 | 0 | 0 | 46 | 0 | 33 | 743 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 515 | 0 | 43 | 0 | 8 | 0 | 385 | 285 | 10 | 181 | 36 | 44 | 0 | 155 | 28 | 20 | 74 | 70 | 34 | 0 | 0 | 295 | 320 | 346 | 5 | 41 | 0 | 5 | 154 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 79 | 126 | 0 | 0 | 0 | 12 | 6992.7 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 1067.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 172 | 0 | 172 | 0 | 393 | 0 | 0 | 2.5 | 166 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 378 | 980 | 0 | 5513.11 | 12505.81 | 86.38
05:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 18 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 279 | 480 | 0 | 0 | 10 | 250 | 37 | 0 | 0 | 17 | 19.7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 34 | 656 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 0 | 43 | 0 | 8 | 0 | 375 | 285 | 10 | 182 | 36 | 50 | 0 | 136 | 28 | 20 | 34 | 68 | 16 | 0 | 0 | 290 | 320 | 286 | 5 | 41 | 0 | 5 | 137 | 16 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 79 | 126 | 0 | 0 | 0 | 12 | 6288.7 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 912.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 172 | 0 | 173 | 0 | 323 | 0 | 0 | 2.5 | 164 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 110 | 220 | 0 | 379 | 900 | 0 | 5131.22 | 11419.92 | 86.37
06:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 18 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 274 | 480 | 0 | 0 | 10 | 245 | 37 | 0 | 0 | 0 | 18.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 29 | 600 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 0 | 43 | 0 | 8 | 0 | 385 | 285 | 10 | 182 | 36 | 24 | 0 | 136 | 28 | 20 | 17 | 58 | 16 | 0 | 0 | 290 | 320 | 286 | 5 | 41 | 0 | 5 | 132 | 8 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 55 | 136 | 0 | 0 | 0 | 12 | 6004.5 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 829.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 170 | 0 | 175 | 0 | 320 | 0 | 0 | 2.5 | 166 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 110 | 180 | 0 | 379 | 680 | 0 | 4731.62 | 10736.12 | 86.36
07:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 18 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 283 | 480 | 0 | 0 | 10 | 245 | 38 | 0 | 1 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 18 | 602 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 2 | 43 | 0 | 8 | 0 | 330 | 285 | 10 | 190 | 36 | 17 | 0 | 100 | 0 | 20 | 17 | 58 | 8 | 1 | 0 | 295 | 320 | 294 | 5 | 41 | 0 | 5 | 132 | 16 | 0 | 41 | 30 | 0 | 18 | 164 | 0 | 55 | 136 | 0 | 0 | 0.23 | 12 | 5840.23 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 382 | 0 | 828.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0.37 | 174 | 0 | 171 | 0 | 175 | 0 | 329 | 0 | 0.03 | 2.5 | 165 | 63 | 0 | 2 | 0 | 0 | 0 | 0.6 | 11 | 0.03 | 0 | 150 | 7 | 116 | 180 | 0 | 379 | 612 | 0 | 4652.52 | 10492.75 | 86.35
08:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 18 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 283 | 480 | 0 | 0 | 10 | 245 | 37 | 0 | 1 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 12 | 600 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 7 | 43 | 0 | 8 | 0 | 330 | 285 | 10 | 201 | 36 | 17 | 0 | 85 | 0 | 20 | 17 | 56 | 0 | 18 | 0 | 310 | 320 | 218 | 5 | 41 | 0 | 5 | 136 | 16 | 0 | 41 | 30 | 0 | 18 | 164 | 0 | 69 | 136 | 0 | 0 | 2.5 | 12 | 5815.5 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4 | 380 | 0 | 826.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 2.75 | 174 | 0 | 167 | 0 | 180 | 0 | 350 | 0 | 0.27 | 2.5 | 165 | 60 | 0 | 9 | 0 | 0 | 0 | 1.9 | 26 | 0.06 | 0 | 150 | 6 | 120 | 180 | 0 | 377 | 618 | 0 | 4688.08 | 10503.58 | 86.34
09:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 285 | 480 | 0 | 0 | 10 | 245 | 39 | 0 | 10 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 20 | 604 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 13 | 43 | 0 | 8 | 0 | 330 | 285 | 10 | 202 | 36 | 17 | 0 | 85 | 0 | 20 | 17 | 56 | 0 | 16 | 0 | 315 | 320 | 320 | 5 | 41 | 0 | 5 | 138 | 16 | 0 | 41 | 30 | 0 | 18 | 164 | 0 | 69 | 136 | 0 | 0 | 5.09 | 12 | 6044.09 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 378 | 0 | 831.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3.28 | 174 | 0 | 163 | 0 | 180 | 0 | 350 | 0 | 0.28 | 2.5 | 167 | 60 | 0 | 14 | 0 | 0 | 0 | 2.8 | 52 | 0.35 | 0 | 200 | 6 | 120 | 180 | 0 | 378 | 621 | 0 | 4804.59 | 10848.68 | 86.33
10:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 283 | 480 | 0 | 0 | 10 | 246 | 38 | 0 | 5 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 14 | 608 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 400 | 16 | 43 | 0 | 8 | 0 | 330 | 285 | 10 | 182 | 36 | 16 | 0 | 85 | 0 | 20 | 17 | 58 | 0 | 52 | 0 | 300 | 320 | 295 | 5 | 41 | 0 | 5 | 134 | 16 | 0 | 41 | 30 | 0 | 18 | 165 | 0 | 69 | 137 | 0 | 1 | 7.85 | 12 | 6014.85 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 378 | 0 | 824.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 6.52 | 174 | 0 | 178 | 0 | 188 | 0 | 350 | 0 | 0.63 | 2.5 | 160 | 60 | 0 | 25 | 0 | 0 | 0 | 4.3 | 120 | 0.43 | 0 | 200 | 6 | 120 | 180 | 0 | 378 | 618 | 0 | 4976.41 | 10991.26 | 86.32
11:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 18 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 290 | 480 | 0 | 0 | 10 | 245 | 38 | 0 | 5 | 0 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 7 | 607 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 18 | 43 | 0 | 8 | 0 | 330 | 285 | 8 | 220 | 36 | 17 | 0 | 85 | 0 | 20 | 17 | 54 | 0 | 59 | 0 | 305 | 320 | 329 | 5 | 41 | 0 | 5 | 134 | 16 | 0 | 41 | 30 | 0 | 18 | 164 | 0 | 69 | 136 | 0 | 1 | 10.04 | 12 | 6139.04 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 378 | 0 | 827.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 4.68 | 174 | 0 | 185 | 0 | 190 | 0 | 350 | 0 | 0.49 | 2.5 | 151 | 62 | 0 | 22 | 0 | 0 | 0 | 3.5 | 56 | 0.57 | 0 | 200 | 6 | 120 | 180 | 0 | 377 | 619 | 0 | 4929.31 | 11068.35 | 86.31
12:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 18 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 285 | 480 | 0 | 0 | 11 | 245 | 99 | 0 | 6 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 19 | 603 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 18 | 43 | 0 | 8 | 0 | 355 | 285 | 5 | 218 | 36 | 20 | 0 | 86 | 0 | 20 | 29 | 64 | 0 | 64 | 0 | 320 | 320 | 350 | 5 | 42 | 0 | 5 | 151 | 16 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 69 | 136 | 0 | 1 | 13.94 | 12 | 6432.94 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 378 | 0 | 862.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 6.5 | 174 | 0 | 183 | 0 | 190 | 0 | 414 | 0 | 0.7 | 2.5 | 150 | 61 | 0 | 17 | 0 | 0 | 0 | 3.9 | 52 | 0.62 | 0 | 263 | 6 | 120 | 220 | 0 | 377 | 622 | 0 | 5110.83 | 11543.77 | 86.3
13:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 18 | 0 | 0 | 92 | 0 | 0 | 0 | 17 | 17 | 0 | 420 | 243 | 583 | 0 | 0 | 13 | 245 | 100 | 0 | 6 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 48 | 0 | 3 | 46 | 0 | 24 | 684 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 17 | 51 | 0 | 8 | 0 | 390 | 285 | 5 | 223 | 36 | 35 | 0 | 125 | 0 | 20 | 34 | 66 | 14 | 61 | 0 | 285 | 320 | 349 | 5 | 41 | 0 | 5 | 146 | 21 | 0 | 82 | 30 | 0 | 18 | 164 | 0 | 69 | 136 | 0 | 0 | 16.68 | 12 | 6760.68 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 379 | 0 | 921.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 4.89 | 174 | 0 | 180 | 0 | 187 | 0 | 414 | 0 | 0.3 | 0 | 151 | 62 | 0 | 16 | 0 | 0 | 0 | 4.6 | 107 | 0.56 | 0 | 307 | 6 | 120 | 220 | 0 | 377 | 692 | 0 | 5331.11 | 12091.79 | 86.29
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 18 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 297 | 480 | 0 | 0 | 14 | 245 | 38 | 0 | 14 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 24 | 0 | 3 | 46 | 0 | 30 | 608 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 16 | 51 | 0 | 8 | 0 | 330 | 285 | 5 | 199 | 35 | 35 | 0 | 85 | 0 | 20 | 34 | 62 | 25 | 51 | 0 | 275 | 320 | 380 | 5 | 41 | 0 | 5 | 133 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 55 | 105 | 0 | 0 | 8.92 | 12 | 6057.92 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 378 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 4.13 | 168 | 0 | 179 | 0 | 140 | 0 | 313 | 0 | 0.36 | 0 | 152 | 62 | 0 | 10 | 0 | 0 | 0 | 2.5 | 56 | 0.57 | 0 | 150 | 7 | 120 | 220 | 0 | 380 | 599 | 0 | 4733.56 | 10791.48 | 86.29
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 299 | 480 | 0 | 0 | 14 | 238 | 37 | 0 | 9 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 24 | 0 | 2 | 46 | 0 | 13 | 604 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 12 | 51 | 0 | 8 | 0 | 365 | 285 | 5 | 196 | 35 | 30 | 0 | 85 | 0 | 20 | 34 | 62 | 25 | 40 | 0 | 325 | 320 | 346 | 5 | 42 | 0 | 5 | 156 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 55 | 105 | 0 | 0 | 5.99 | 12 | 6155.99 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 380 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 3.09 | 166 | 0 | 179 | 0 | 140 | 0 | 414 | 0 | 0.3 | 0 | 121 | 62 | 0 | 7 | 0 | 0 | 0 | 3 | 42 | 0.4 | 0 | 150 | 6 | 112 | 220 | 0 | 378.8 | 600 | 0 | 4789.59 | 10945.58 | 86.28
16:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 300 | 480 | 0 | 0 | 14 | 243 | 37 | 0 | 6 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 27 | 602 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 400 | 7 | 51 | 0 | 8 | 0 | 360 | 285 | 5 | 204 | 36 | 31 | 0 | 51 | 3 | 20 | 34 | 62 | 25 | 22 | 0 | 305 | 320 | 382 | 5 | 41 | 0 | 5 | 137 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 55 | 65 | 0 | 0 | 3.01 | 12 | 6027.01 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 377 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 5.78 | 166 | 0 | 180 | 0 | 140 | 0 | 414 | 0 | 0.47 | 2.5 | 121 | 62 | 0 | 6 | 0 | 0 | 0 | 1.5 | 37 | 0.28 | 0 | 150 | 7 | 120 | 220 | 0 | 379.5 | 605 | 0 | 4744.03 | 10771.04 | 86.28
17:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 25 | 17 | 0 | 400 | 292 | 583 | 0 | 0 | 14 | 244 | 100 | 0 | 0 | 0 | 16.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 24 | 603 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 400 | 2 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 196 | 36 | 65 | 0 | 17 | 14 | 20 | 34 | 56 | 25 | 6 | 0 | 320 | 320 | 365 | 5 | 41 | 0 | 5 | 147 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 55 | 72 | 0 | 0 | 2.73 | 12 | 6200.23 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 377 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.58 | 166 | 0 | 181 | 0 | 180 | 0 | 414 | 0 | 0.25 | 2.5 | 122 | 62 | 25 | 3 | 20 | 0 | 0 | 0.8 | 17 | 0.06 | 0 | 200 | 6 | 116 | 220 | 0 | 379 | 622 | 0 | 4858.19 | 11058.42 | 86.27
18:00 | 0 | 88 | 43 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 12 | 0 | 0 | 0 | 128 | 0 | 0 | 13 | 35 | 17 | 16 | 300 | 285 | 450 | 0 | 30 | 14 | 243 | 101 | 0 | 0 | 35 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 26 | 657 | 0 | 0 | 0 | 5 | 0 | 162 | 0 | 0 | 0 | 430 | 0 | 10 | 10 | 8 | 0 | 355 | 230 | 5 | 185 | 36 | 74 | 0 | 24 | 31 | 20 | 70 | 60 | 25 | 0 | 0 | 310 | 320 | 356 | 5 | 41 | 0 | 5 | 156 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 59 | 110 | 0 | 0 | 0.04 | 12 | 6406.04 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 457 | 0 | 872 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 0 | 2.5 | 122 | 62 | 35 | 0 | 63 | 0 | 0 | 0 | 1 | 0 | 0 | 270 | 7 | 80 | 180 | 0 | 379 | 760 | 0 | 4959.5 | 11365.54 | 86.27
19:00 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 17 | 0 | 17 | 0 | 420 | 310 | 500 | 0 | 17 | 14 | 243 | 37 | 0 | 0 | 27 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 34 | 752 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 450 | 0 | 27 | 10 | 8 | 0 | 355 | 285 | 5 | 182 | 33 | 68 | 0 | 51 | 56 | 20 | 70 | 56 | 8 | 0 | 0 | 290 | 320 | 368 | 5 | 42 | 0 | 5 | 146 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 135 | 0 | 0 | 0 | 12 | 6638 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 180 | 0 | 175 | 0 | 414 | 0 | 0 | 2.5 | 120 | 63 | 28 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 108 | 220 | 0 | 467 | 700 | 0 | 5073.5 | 11711.5 | 86.26
19:30 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 313 | 500 | 0 | 0 | 14 | 244 | 61 | 0 | 0 | 17 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 34 | 754 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 192 | 33 | 68 | 0 | 17 | 56 | 20 | 52 | 56 | 8 | 0 | 0 | 310 | 320 | 347 | 5 | 42 | 0 | 5 | 153 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 136 | 0 | 0 | 0 | 12 | 6580 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 182 | 0 | 180 | 0 | 414 | 0 | 0 | 2.5 | 119 | 63 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 126 | 220 | 0 | 467 | 680 | 0 | 5039.5 | 11619.5
20:00 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 294 | 583 | 0 | 0 | 14 | 245 | 102 | 0 | 0 | 17 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 34 | 758 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 455 | 0 | 51 | 0 | 8 | 0 | 360 | 285 | 5 | 184 | 36 | 68 | 0 | 17 | 57 | 20 | 52 | 64 | 8 | 0 | 0 | 305 | 320 | 347 | 5 | 42 | 0 | 5 | 154 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 135 | 0 | 0 | 0 | 12 | 6744 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 182 | 0 | 180 | 0 | 414 | 0 | 0 | 2.5 | 119 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 110 | 220 | 0 | 552 | 742 | 0 | 4972.5 | 11716.5 | 86.26
21:00 | 0 | 50 | 43 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 29 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 307 | 583 | 0 | 0 | 14 | 245 | 101 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 23 | 759 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 457 | 0 | 51 | 0 | 8 | 0 | 360 | 285 | 10 | 200 | 36 | 68 | 0 | 27 | 58 | 20 | 52 | 62 | 8 | 0 | 0 | 315 | 320 | 380 | 5 | 42 | 0 | 5 | 157 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 135 | 0 | 0 | 0 | 12 | 6794 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 865.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 183 | 0 | 181 | 0 | 414 | 0 | 0 | 2.5 | 119 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 110 | 220 | 0 | 612 | 850 | 0 | 5154.66 | 11948.66 | 86.25
22:00 | 0 | 50 | 43 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 35 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 309 | 583 | 0 | 0 | 14 | 240 | 101 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 35 | 753 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 455 | 0 | 51 | 0 | 8 | 0 | 360 | 285 | 38 | 196 | 36 | 68 | 0 | 51 | 58 | 20 | 52 | 72 | 8 | 0 | 0 | 315 | 320 | 357 | 5 | 41 | 0 | 5 | 159 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 135 | 0 | 0 | 0 | 12 | 6846 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 862.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 182 | 0 | 180 | 0 | 414 | 0 | 0 | 2.5 | 121 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 116 | 220 | 0 | 620 | 845 | 0 | 5156.92 | 12002.92 | 86.25
23:00 | 0 | 50 | 43 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 35 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 296 | 583 | 0 | 0 | 14 | 240 | 103 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 756 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 456 | 0 | 51 | 0 | 8 | 0 | 359 | 285 | 53 | 183 | 36 | 68 | 0 | 51 | 58 | 20 | 52 | 70 | 8 | 0 | 0 | 300 | 320 | 357 | 5 | 41 | 0 | 5 | 153 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 135 | 0 | 0 | 0 | 9 | 6792 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456 | 0 | 863.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 181 | 0 | 175 | 0 | 414 | 0 | 0 | 2.5 | 125 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 108 | 110 | 0 | 625 | 846 | 0 | 5046.42 | 11838.42 | 86.24
Total KWH | 0 | 1622400 | 795840 | 0 | 0 | 0 | 0 | 0 | 9140400 | 0 | 0 | 35640 | 465120 | 0 | 0 | 1676640 | 0 | 0 | 103504 | 371520 | 419760 | 79680 | 8927000 | 7000698 | 12251818 | 0 | 47293 | 297100 | 5956584 | 1800000 | 0 | 78726 | 402000 | 411000 | 223560 | 0 | 0 | 0 | 0 | 0 | 0 | 450720 | 331932 | 301872 | 0 | 601920 | 94080 | 20039 | 1101660 | 0 | 647040 | 15774545.46 | 0 | 0 | 0 | 14131.8 | 0 | 3810348 | 0 | 0 | 0 | 10543635 | 125550 | 1043400 | 33454 | 217455 | 0 | 8809400 | 6858000 | 319200 | 4794000 | 848520 | 974400 | 106510 | 2220480 | 551040 | 459700 | 1068180 | 1521600 | 404650 | 380336 | 0 | 7376000 | 7655400 | 8678000 | 203256 | 986000 | 0 | 116112 | 3515236 | 425928 | 0 | 1443840 | 718656 | 0 | 432000 | 3854190 | 0 | 1452000 | 2808000 | 0 | 3450 | 75530 | 295680 | 156573359.26 | 21650909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576000 | 9832727 | 0 | 21748740 | 0 | 0 | 0 | 37152 | 0 | 0 | 0 | 0 | 0 | 166590 | 0 | 48752 | 4104455 | 0 | 4442818 | 0 | 4299355 | 0 | 9198327 | 0 | 4380 | 59454 | 3559000 | 1435199 | 104592 | 126196 | 321273 | 0 | 0 | 27837.48 | 578160 | 3859.5 | 0 | 4080000 | 182594 | 2716000 | 4890530 | 0 | 10186909 | 18449455 | 0 | 122831263.98 | 279404623.24

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-03-2025 | during | 22-03-2025 | during | 22-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 403 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 285 | 307 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 99 | 101 | 208.13 | 208.13 | 105 | 105 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 245 | 245 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 92 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 0 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 11 | 14 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 43 | 52.19 | 52.19 | 43 | 43 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 50 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 29 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 480 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2212 | 2305 | 5265.5 | 5240.5 | 3774.13 | 3749.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 161 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 19 | 23 | 2 | 32 | 2 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 400 | 457 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 52 | 5 | 10 | 5 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 603 | 759 | 770 | 770 | 770 | 770 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1252 | 1510 | 2979.47 | 3009.72 | 2979.47 | 3009.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 218 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 36 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 86 | 27 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 62 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 29 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 58 | 113 | 113 | 58 | 58 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 20 | 68 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1233 | 1245 | 2410.99 | 2345.99 | 2211.55 | 2146.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-03-2025 | during | 22-03-2025 | during | 22-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 136 | 135 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 45 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 13.94 | 0 | 30 | 0 | 30 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 231.94 | 192 | 632.7 | 601.5 | 432.7 | 401.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 42 | 42 | 38 | 39 | 38 | 39 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 43 | 43 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 157 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 5 | 5 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 164 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 380 | 385 | 385 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1504 | 1542 | 1659 | 1660 | 1542 | 1543
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 903 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Power evacuation problem in PGCB switchyard
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 62 | 0 | 62 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 378 | 457 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1372 | 1360 | 3576.2 | 3514.2 | 1984.02 | 1922.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 377 | 612 | 660 | 660 | 660 | 660 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 9 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 850 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 263 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1608.62 | 1801 | 2831.12 | 2831.12 | 2819.12 | 2819.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 174 | 167 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 183 | 183 | 220 | 220 | 200 | 200 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 181 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.7 | 0 | 3.5 | 0 | 3.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 862.61 | 865.16 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 6.5 | 0 | 35 | 0 | 35 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 13 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1846.31 | 1812.66 | 3064.03 | 2935.53 | 2982.24 | 2853.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 62 | 62 | 62 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 150 | 119 | 170 | 170 | 170 | 170 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 16.5 | 0 | 16.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 52 | 0 | 54 | 0 | 54 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 283.9 | 181 | 570.9 | 494 | 534.92 | 458.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 11543.77 | 11948.66 | 22989.91 | 22632.56 | 19260.15 | 18902.8
Forecast Scenario (22-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11670 |  | 0 |  | 11670
|  |  |  | 1:00 | 11000 |  | 0 |  | 11000
|  |  |  | 2:00 | 10870 |  | 0 |  | 10870
|  |  |  | 3:00 | 10930 |  | 0 |  | 10930
|  |  |  | 4:00 | 11290 |  | 0 |  | 11290
|  |  |  | 5:00 | 10370 |  | 0 |  | 10370
|  |  |  | 6:00 | 9690 |  | 0 |  | 9690
|  |  |  | 7:00 | 9720 |  | 0 |  | 9720
|  |  |  | 8:00 | 10160 |  | 0 |  | 10160
|  |  |  | 9:00 | 10280 |  | 0 |  | 10280
|  |  |  | 10:00 | 10470 |  | 0 |  | 10470
|  |  |  | 11:00 | 10740 |  | 0 |  | 10740
|  |  |  | 12:00 | 11240 |  | 0 |  | 11240
|  |  |  | 13:00 | 11800 |  | 0 |  | 11800
|  |  |  | 14:00 | 12370 |  | 0 |  | 12370
|  |  |  | 15:00 | 12410 |  | 0 |  | 12410
|  |  |  | 16:00 | 12370 |  | 0 |  | 12370
|  |  |  | 17:00 | 12410 |  | 0 |  | 12410
|  |  |  | 18:00 | 12580 |  | 0 |  | 12580
|  |  |  | 18:30 | 12900 |  | 0 |  | 12900
|  |  |  | 19:00 | 13620 |  | 0 |  | 13620
|  |  |  | 19:30 | 13480 |  | 0 |  | 13480
|  |  |  | 20:00 | 13520 |  | 0 |  | 13520
|  |  |  | 21:00 | 13870 |  | 0 |  | 13870
|  |  |  | 22:00 | 13710 |  | 0 |  | 13710
|  |  |  | 23:00 | 13330 |  | 0 |  | 13330
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 11240.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13870.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13870.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 280.42 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:03 hrs on 22-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11543.77 | MW | 12:00 Hr. | Energy Generated |  |  | 279.4046 |  | MKWHr.
| Day Peak Demand |  |  | 11543.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.263 |  | MKWHr.
| Evening Peak Generation |  |  | 11948.66 | MW | 21:00 Hr. | Energy Demand |  |  | 279.6676 |  | MKWHr.
| Evening Peak Demand |  |  | 11948.66 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 10492.75 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 965.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 13093.64 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.3145 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 46.4279 | 0 | 5.5996 | 0 | 0 | 0.078726 | 0 | 0 | 52.1063 | Gas | 139.6396 | Gas | 447186970.25
| Chattogram Zone |  |  | 4.4574 | 26.3182 | 1.3439 | 0 | 1.1017 | 0.14559 | 0 | 0.45072 | 33.8175 | Coal | 73.8615 | Coal | 455135925.2568
| Cumilla Zone |  |  | 23.4562 | 0 | 5.2522 | 0 | 0 | 0.38034 | 1.5216 | 0 | 30.6103 | HFO | 17.2145 | HFO | 317587823.956
| Mymensingh Zone |  |  | 0 | 0 | 4.5557 | 0 | 0 | 0.07898 | 0 | 0 | 4.6347 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.4046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.4046 | Hydro | 1.1017 | Hydro | 110166
| Khulna Zone |  |  | 0 | 9.8327 | 0 | 0 | 0 | 0.576 | 21.6509 | 0 | 32.0596 | Solar | 2.2154 | Solar | 35783140.9378
| Barishal Zone |  |  | 7.7891 | 32.7164 | 0 | 0 | 0 | 0.0038595 | 0 | 0 | 40.5093 | Import | 44.9212 | Import | 222485315.11
| Rajshahi Zone |  |  | 22.1044 | 0 | 0.037152 | 0 | 0 | 0.21972 | 21.7487 | 0 | 44.11 | Wind | 0.45072 | Wind | 6598540.8
| Rangpur Zone |  |  | 0 | 4.9942 | 0.42586 | 0 | 0 | 0.73219 | 0 | 0 | 6.1523
| Total |  |  | 139.6396 | 73.8615 | 17.2145 | 0 | 1.1017 | 2.2154 | 44.9212 | 0.45072 | 279.4046
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 447186970.25 |  | Hydro | 110166
|  |  |  | Coal | 455135925.2568 |  | Solar | 35783140.9378
|  |  |  | HFO | 317587823.956 |  | Import | 222485315.11
|  |  |  | HSD | 0 |  | Wind | 6598540.8
[5 empty] | Total: | 148,48,87,882 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6509 | Peak Hr Flow | 903.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35188436.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.7487 | Peak Hr Flow | 865.16 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 614 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5216 | Peak Hr Flow | 62.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 854 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.9212 | Peak Hr Flow | 1830.16 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4343
|  |  |  | Chattogram |  | 0 |  | 1320
|  |  |  | Cumilla |  | 0 |  | 1229
|  |  |  | Mymensingh |  | 0 |  | 870
|  |  |  | Sylhet |  | 0 |  | 383
|  |  |  | Khulna |  | 0 |  | 1326
|  |  |  | Barishal |  | 0 |  | 387
|  |  |  | Rajshahi |  | 0 |  | 990
|  |  |  | Rangpur |  | 0 |  | 691
|  |  |  | Total |  | 0 |  | 11539
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Tr-04 bushing maintenance work by
Energypac
| 08:02 | 08:15 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Tr-04 bushing maintenance work by
Energypac
| 08:03 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Tr-04 bushing maintenance work by
Energypac
| 08:27 | 10:57 | Maniknagar-Narinda 132kV Ckt-1 Scheduled S/D from Maniknagar 132/33kV end Due to High
Temperature Maintenance work
| 08:37 | 16:35 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Blast wall Work | [7 empty] | 5.0MW load
interrup.
| 08:37 | 16:34 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Blast wall Work | [7 empty] | 5.0MW load
interrup.
| 08:38 | 16:31 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast wall wark | [7 empty] | 10.0MW load
interrup.
| 08:38 | 16:30 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast wall Work | [7 empty] | 10.0MW load
interrup.
| 08:55 |  | Tongi 230/132/33kV S/S Tongi-Uttara Ckt Scheduled S/D Due to Shutdown taken by nldc
| 09:05 | 16:52 | Rahanpur 400/132kV S/S AT-01 LT Project Work S/D Due to For project work
| 09:05 | 16:52 | Rahanpur 400/132kV S/S AT-01 HT Project Work S/D Due to For Project work
| 09:17 | 11:42 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Forced S/D Due to 33KV PBS FEDER FAULT | [7 empty] | 20.0MW load
interrup.
| 09:17 | 11:41 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to 33kv PBS Feder fault | [7 empty] | 20.0MW load
interrup.
| 09:25 | 11:59 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to Oil Leakage from Buchholz Relay
Maintenance and Clearance Adjustment between B-Phase Bushing and Conductor
| 09:25 | 11:59 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D
|  | 09:36 | Narshingdi 132/33kV S/S T-3 HT is restored.
|  | 09:36 | Narshingdi 132/33kV S/S T-3 LT is restored.
|  | 09:46 | Maniknagar 132/33kV S/S Transformer GT-2 HT is restored.
| 09:55 | 12:22 | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to High Temperature
Maintenance work
|  | 10:05 | Feni 132/33kV S/S T-2(415T) LT is restored.
|  | 10:05 | Feni 132/33kV S/S T-2(415T) HT is restored.
| 11:19 |  | Bibiyana-III 400 MW CCPP, FGMO is ON with remarks:-
| 11:34 | 19:13 | Kodda 132/33kV S/S Bus-1 Scheduled S/D
| 12:00 |  | Day peak generation 11539 MW
|  | 14:35 | Hathazari 230/132/33kV S/S MT-02 LT is restored.
| 14:46 |  | Sreepur-Rajendrapur 132kV Ckt-1 was switched on at 14:46 hrs and put on loaded condition
for the first time at 15:05 hrs. Now, Rajendrapur 132/33kV T-2 and T-3 transformer are
taking load from Sreepur 230/132/33kV grid S/S through Sreepur-Rajendrapur 132kV Ckt-1
and Rajendrapur 132/33kV T-1 transformer is taking load from Kodda 132/33kV grid S/S
through Rajendrapur-Kodda 132kV Ckt-1.
|  | 14:46 | Kodda-Rajendrapur 132kV Ckt-2 is restored.
| 14:55 | 15:08 | Keranigonj 230/132/33kV S/S TR-1 LT Tripped showing Trip relay operated relays Due to PBS | [7 empty] | 26.0MW load
|  |  | 33kV feeder fault | [7 empty] | interrup.
|  | 15:02 | Rajendrapur 132/33kV S/S MTR-3 LT is restored.
|  | 17:29 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 17:30 | Khulna (C) S/S TR-1 425T LT is restored.
| 19:30 |  | Barishal Electric 307 MW PP tripped.
| 19:30 |  | Barisal 307 MW Tripped
| 20:28 |  | Kodda-Summit Kodda 149 MW PP (ACE Kodda) 132kV line was switched on.
| 21:00 |  | Evening Peak Gen. 11948 MW
| 23:33 |  | Bhola Nutan Biddyut CCPP GT-2 was shutdown due to turbine compressor problem.
| 23:41 | 23:57 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing Distance relay, | [7 empty] | 30.0MW load
|  |  | Zone-1, C-phase. relays. | [7 empty] | interrup. Kabirpur
132/33kV end
| 03:33 |  | Barishal Electric 307 MW PP was sync.
| 03:33 |  | Barisal 307 MW Synchronized
| 06:00 |  | Minimum generation 9361 MW
| 07:07 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33kv Feeder Redhot Repair | [7 empty] | 21.0MW load
interrup.
| 07:07 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to 33kv Feeder Redhot Repair | [7 empty] | 21.0MW load
interrup.
| 07:08 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Redhot Repair | [7 empty] | 21.0MW load
interrup.
| 07:08 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Redhot Repair | [7 empty] | 21.0MW load
interrup.
| 07:13 |  | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Installation of TR-3 Development work
| 07:13 |  | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Installation of TR-3 Development work
| 07:30 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to for 33kv hot-spot maintenance
| 07:30 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For 33kv Hot-spot maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9140400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8927000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 307 | 7000698 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 101 | 1800000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 245 | 5956584 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 35640 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 1676640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 103504 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 47293 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 411000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 223560 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 419760 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 14 | 297100 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 43 | 795840 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 1622400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 79680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 371520 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 78726 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 29 | 465120 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 12251818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 0 | 402000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2305 | 52106283
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 14131.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125550 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1101660 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3810348 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 301872 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 331932 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 601920 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 647040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 94080 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 457 | 10543635 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 52 | 450720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 759 | 15774545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 1510 | 33817473.26
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 200 | 4794000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8809400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6858000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 848520 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 319200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1043400 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 33454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 106510 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 27 | 2220480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1521600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 404650 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 459700 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1068180 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 551040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 974400 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 380336 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1245 | 30610325
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 135 | 2808000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 1452000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 75530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 295680 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 192 | 4634660
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 986000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3515236 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 5 | 203256 | Partial Shutdown due to maintenance
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116112 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718656 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1443840 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 3854190 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 425928 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7376000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 8678000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7655400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1542 | 35404618
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 903 | 21650909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Power evacuation problem in PGCB switchyard
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 576000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 457 | 9832727 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1360 | 32059636
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 612 | 10186909 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 9 | 182594 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2716000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 850 | 18449455 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4890530 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 4080000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3859.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1801 | 40509347.5
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 167 | 4104455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4442818 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 181 | 4299355 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9198327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 59454 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 37152 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 4380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 865.16 | 21748740 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 48752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 166590 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1812.66 | 44110023
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1435199 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 119 | 3559000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 321273 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27837.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 104592 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 126196 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 578160 | -
Rangpur Area Total |  |  |  |  | 950 | 181 | 6152257.48
Eastern Grid Total |  |  |  |  | 16921.242 | 6794 | 156573359.26
Western Grid Total |  |  |  |  | 11614.5 | 5154.66 | 122831263.98
National Grid Total |  |  |  |  | 28535.742 | 11948.66 | 279404623.24
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8145.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3393.5 | MW
i) Dhaka area |  |  | 4343.47 |  | MW | i) Khulna area |  |  |  | 1325.7 | MW
ii) Chattogram area |  |  | 1320 |  | MW | ii) Barishal area |  |  |  | 387 | MW
iii) Cumilla area |  |  | 1229 |  | MW | iii) Rajshahi area |  |  |  | 989.8 | MW
iv) Mymensingh area |  |  | 870 |  | MW | iv) Rangpur area |  |  |  | 691 | MW
v) Sylhet area |  |  | 383 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11538.97 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 68 | 18:00 | 133 | Payra | 28 | 00:00
2 | AKSML | 13 | 15:00 | 68 | Jamalpur | 100 | 04:00 | 134 | Postogola | 46 | 00:00
3 | Aftabnagar | 32 | 00:00 | 69 | Jashore | 117 | 21:00 | 135 | Purbachal | 17 | 00:00
4 | Agargaon | 87 | 13:00 | 70 | Jhenaidah | 99 | 19:00 | 136 | Purbasadipur | 117 | 13:00
5 | Agrabad | 86 | 00:00 | 71 | Joydebpur | 119 | 11:00 | 137 | Rahanpur | 21 | 00:00
6 | Amnura | 36 | 01:00 | 72 | Joypurhat | 60 | 00:00 | 138 | Rahim | 41 | 08:00
7 | Ashuganj | 88 | 00:00 | 73 | Juldah | 14 | 00:00 | 139 | Rajbari | 60 | 03:00
8 | BSRM | 200 | 23:00 | 74 | KSRM | 36 | 04:00 | 140 | Rajendrapur | 100 | 00:00
9 | Bagerhat | 74 | 00:00 | 75 | Kabirpur | 209 | 00:00 | 141 | Rajshahi | 87 | 03:00
10 | Bajitpur | 41 | 03:00 | 76 | Kachua | 73 | 00:00 | 142 | Rajshahi-230 | 63 | 00:00
11 | Bakulia | 90 | 01:00 | 77 | Kallyanpur | 93 | 00:00 | 143 | Ramganj | 114 | 00:00
12 | Banani | 20 | 20:00 | 78 | Kalurghat | 34 | 00:00 | 144 | Rampur | 40 | 00:00
13 | Bangabhaban | 4 | 16:00 | 79 | Kamrangirchar | 65.61 | 01:00 | 145 | Rangamati | 15 | 19:00
14 | Barapukuria | 63 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 127 | 18:30
15 | Barguna | 18 | 00:00 | 81 | Kasba | 32 | 00:00 | 147 | Ruppur | 5.2 | 10:00
16 | Barishal | 91 | 21:00 | 82 | Kazla | 87 | 00:00 | 148 | SSM | 11 | 04:00
17 | Barishal-230 | 88 | 00:00 | 83 | Keranigonj | 68 | 00:00 | 149 | Saidpur | 104 | 11:00
18 | Baroaulia | 59 | 00:00 | 84 | Khagrachori | 32 | 18:00 | 150 | Satkhira | 112 | 19:00
19 | Baroirhat | 56 | 00:00 | 85 | Khulna | 54 | 18:00 | 151 | Satmasjid | 82 | 13:00
20 | Bashundhara | 148 | 12:00 | 86 | Khulshi | 151 | 00:00 | 152 | Savar | 174 | 12:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 112 | 00:00 | 153 | SevenRings | 18.29 | 01:00
22 | Beanibazar | 45 | 04:00 | 88 | Kodda | 282 | 12:00 | 154 | ShahCement | 39 | 12:00
23 | Benapole | 58 | 21:00 | 89 | Kulaura | 30 | 13:00 | 155 | Shahjadpur | 64 | 09:00
24 | Bhaluka | 113 | 00:00 | 90 | Kurigram | 58 | 03:00 | 156 | Shahjibazar | 112 | 00:00
25 | Bhandaria | 48 | 00:00 | 91 | Kushtia | 100 | 16:00 | 157 | Shahmirpur | 52 | 00:00
26 | Bhangura | 30 | 03:00 | 92 | Lalbag | 58 | 01:00 | 158 | Shariatpur | 69 | 00:00
27 | Bheramara(GK) | 38 | 18:00 | 93 | Lalmonirhat | 56 | 17:00 | 159 | Sherpur | 138 | 17:00
28 | Bhulta | 256 | 00:00 | 94 | MI_Cement | 17.9 | 10:00 | 160 | Shikalbaha | 23 | 00:00
29 | Bog-Sherpur | 60 | 03:00 | 95 | Madanganj | 44 | 00:00 | 161 | Shitalakhya | 60.6 | 00:00
30 | Bogura | 160 | 04:00 | 96 | Madaripur | 90 | 00:00 | 162 | Sholosohor | 38 | 00:00
31 | Borhanuddin | 79 | 00:00 | 97 | Madartek | 76.69 | 00:00 | 163 | Shyampur | 170 | 01:00
32 | Brahmanbaria | 117 | 00:00 | 98 | Madunaghat | 47 | 00:00 | 164 | Siddhirganj | 106 | 11:00
33 | Cantonment | 116 | 13:00 | 99 | Magura | 46 | 19:00 | 165 | Sirajganj | 78 | 03:00
34 | Chandpur | 59 | 22:00 | 100 | Mahasthangarh | 70 | 03:00 | 166 | Sonargaon | 118 | 00:00
35 | Chandraghona | 32 | 21:00 | 101 | Manikganj | 101 | 21:00 | 167 | Sreemongol | 55 | 01:00
36 | Chapai | 55 | 04:00 | 102 | Maniknagar | 54 | 13:00 | 168 | Sreepur | 88 | 16:00
37 | Charsaidpur | 49 | 00:00 | 103 | Matarbari | 49 | 03:00 | 169 | Srinagar | 37 | 13:00
38 | Chauddagram | 72 | 00:00 | 104 | Matuail | 62 | 00:00 | 170 | Sunamganj | 41 | 00:00
39 | Chhatak | 26 | 00:00 | 105 | Millgate | 66 | 00:00 | 171 | Sylhet | 32 | 00:00
40 | Chowmuhani | 212 | 18:00 | 106 | Mirpur | 109 | 12:00 | 172 | Sylhet-132 | 84 | 00:00
41 | Chuadanga | 77 | 03:00 | 107 | Mirsorai | 9 | 00:00 | 173 | TK | 21.5 | 00:00
42 | Coxsbazar | 128 | 18:30 | 108 | Mirzapur | 40 | 04:00 | 174 | Tangail | 162 | 04:00
43 | Cumilla(N) | 156 | 00:00 | 109 | Mithapukur | 54 | 03:00 | 175 | Thakurgaon | 86 | 10:00
44 | Cumilla(S) | 169 | 00:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 120 | 00:00
45 | Daudkandi | 134 | 00:00 | 111 | Mogbazar | 104 | 12:00 | 177 | Ullahpara | 32 | 03:00
46 | Dhaka | 28 | 12:00 | 112 | Mongla | 30 | 19:00 | 178 | Ullon | 44 | 00:00
47 | Dhamrai | 114 | 09:00 | 113 | Motijheel | 28 | 12:00 | 179 | Uttara | 80 | 13:00
48 | Dhanmondi | 105 | 12:00 | 114 | Muktagacha | 31 | 03:00 | 180 | UttaraNew | 22 | 22:00
49 | Dohazari | 108 | 00:00 | 115 | Munshiganj | 99 | 00:00 | 181 | Zigatola | 60 | 00:00
50 | Faridpur | 120 | 00:00 | 116 | Muradnagar | 23 | 00:00
51 | Fatullah | 83 | 00:00 | 117 | Mymensingh | 168 | 03:00
52 | Fenchuganj | 25 | 22:00 | 118 | Naogaon | 113 | 04:00
53 | Feni | 106 | 00:00 | 119 | Narail | 45 | 19:00
54 | GPH | 94 | 12:00 | 120 | Narinda | 61 | 13:00
55 | Ghatail | 62 | 04:00 | 121 | Narshingdi | 148 | 23:00
56 | Ghorashal | 13 | 00:00 | 122 | Natore | 118 | 04:00
57 | Ghorashal-230 | 80 | 04:00 | 123 | Nawabganj | 44.4 | 13:00
58 | Goalpara | 30 | 00:00 | 124 | Netrakona | 131 | 04:00
59 | Gollamari | 86 | 23:00 | 125 | New | 68.3 | 00:00
60 | Gopalganj | 89 | 22:00 | 126 | Niamatpur | 86 | 00:00
61 | Gulshan | 74 | 19:00 | 127 | Noapara | 34 | 19:00
62 | Halishahar | 44.5 | 14:00 | 128 | PHP | 7 | 14:00
63 | HaripurSBU | 145 | 06:00 | 129 | Pabna | 94 | 03:00
64 | Hasnabad | 75 | 00:00 | 130 | Palashbari | 92 | 10:00
65 | Hathazari | 80 | 00:00 | 131 | Panchagarh | 48 | 18:00
66 | Ishurdi | 51 | 18:00 | 132 | Patuakhali | 65.5 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13093.64 | 36 |  | 13131.26
1:00 | 12527.45 | 47 |  | 12576.45
2:00 | 12249.24 | 26 |  | 12276.24
3:00 | 12383.71 | 41 |  | 12426.71
4:00 | 12505.81 | 30 |  | 12536.81
5:00 | 11419.92 | 26 |  | 11446.92
6:00 | 10736.12 | 19 |  | 10756.12
7:00 | 10492.75 | 14 |  | 10507.75
8:00 | 10503.58 | 24 |  | 10528.58
9:00 | 10848.68 | 0 |  | 10848.68
10:00 | 10991.26 | 0 |  | 10991.26
11:00 | 11068.35 | 0 |  | 11068.35
12:00 | 11543.77 | 0 |  | 11543.77
13:00 | 12091.79 | 0 |  | 12091.79
14:00 | 10791.48 | 0 |  | 10791.48
15:00 | 10945.58 | 0 |  | 10945.58
16:00 | 10771.04 | 0 |  | 10771.04
17:00 | 11058.42 | 0 |  | 11058.42
18:00 | 11365.54 | 0 |  | 11365.54
19:00 | 11711.5 | 0 |  | 11711.5
19:30 | 11619.5 | 0 |  | 11619.5
20:00 | 11716.5 | 0 |  | 11716.5
21:00 | 11948.66 | 0 |  | 11948.66
22:00 | 12002.92 | 0 |  | 12002.92
23:00 | 11838.42 | 0 |  | 11838.42
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7276.5 | 5817.14 | 13093.64 | DAILY GENERATION CURVE
00:30 | 7162.25 | 5648.295 | 12810.545
01:00 | 7048 | 5479.45 | 12527.45 | 21-03-2025
01:30 | 6978.5 | 5409.845 | 12388.345
02:00 | 6909 | 5340.24 | 12249.24
02:30 | 7010.35 | 5306.125 | 12316.475
03:00 | 7111.7 | 5272.01 | 12383.71
03:30 | 7052.2 | 5392.56 | 12444.76
04:00 | 6992.7 | 5513.11 | 12505.81
04:30 | 6640.7 | 5322.165 | 11962.865
05:00 | 6288.7 | 5131.22 | 11419.92
05:30 | 6146.6 | 4931.42 | 11078.02
06:00 | 6004.5 | 4731.62 | 10736.12
06:30 | 5922.365 | 4692.07 | 10614.435
07:00 | 5840.23 | 4652.52 | 10492.75
07:30 | 5827.865 | 4670.3 | 10498.165
08:00 | 5815.5 | 4688.08 | 10503.58
08:30 | 5929.795 | 4746.335 | 10676.13
09:00 | 6044.09 | 4804.59 | 10848.68
09:30 | 6029.47 | 4890.5 | 10919.97
10:00 | 6014.85 | 4976.41 | 10991.26
10:30 | 6076.945 | 4952.86 | 11029.805
11:00 | 6139.04 | 4929.31 | 11068.35
11:30 | 6285.99 | 5020.07 | 11306.06
12:00 | 6432.94 | 5110.83 | 11543.77
12:30 | 6596.81 | 5220.97 | 11817.78
13:00 | 6760.68 | 5331.11 | 12091.79
13:30 | 6409.3 | 5032.335 | 11441.635
14:00 | 6057.92 | 4733.56 | 10791.48
14:30 | 6106.955 | 4761.575 | 10868.53
15:00 | 6155.99 | 4789.59 | 10945.58
15:30 | 6091.5 | 4766.81 | 10858.31
16:00 | 6027.01 | 4744.03 | 10771.04
16:30 | 6113.62 | 4801.11 | 10914.73
17:00 | 6200.23 | 4858.19 | 11058.42
17:30 | 6303.135 | 4908.845 | 11211.98
18:00 | 6406.04 | 4959.5 | 11365.54
18:30 | 6522.02 | 5016.5 | 11538.52
19:00 | 6638 | 5073.5 | 11711.5
19:30 | 6580 | 5039.5 | 11619.5
20:00 | 6744 | 4972.5 | 11716.5
20:30 | 6769 | 5063.58 | 11832.58 |  | Executive Engineer
21:00 | 6794 | 5154.66 | 11948.66 |  | Network Operation Division
21:30 | 6820 | 5155.79 | 11975.79
22:00 | 6846 | 5156.92 | 12002.92
22:30 | 6819 | 5101.67 | 11920.67
23:00 | 6792 | 5046.42 | 11838.42

## En-Curve
QF-LDC-12
Date | 21-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3794 | 2309 | 888 | 0 | 78 | 1265.64 | 46 | 3438 | 0 | 462 | 813 | 0 | 0 | 0 | 36 | DAILY ENERGY CURVE
00:30 | 3769 | 2230.75 | 888.5 | 0 | 78 | 1215.795 | 46 | 3360 | 0 | 462 | 760 | 0 | 0 | 0.5 | 41.5 | 21-03-2025
01:00 | 3744 | 2152.5 | 889 | 0 | 78 | 1165.95 | 46 | 3282 | 0 | 462 | 707 | 0 | 0 | 1 | 47
01:30 | 3713.5 | 2086 | 893 | 0 | 77 | 1166.345 | 46 | 3242 | 0 | 462 | 701.5 | 0 | 0 | 1 | 36.5 | Energy Generated | 279.4046 |  | MKWHr
02:00 | 3683 | 2019.5 | 897 | 0 | 76 | 1166.74 | 46 | 3202 | 0 | 462 | 696 | 0 | 0 | 1 | 26 | Energy not Served | 0.263 |  | MKWHr
02:30 | 3636 | 2062.85 | 896 | 0 | 74 | 1140.625 | 46 | 3308 | 0 | 461.5 | 690.5 | 0 | 0 | 1 | 33.5 | Total Energy Requirement | 279.6676 |  | MKWHr
03:00 | 3589 | 2106.2 | 895 | 0 | 72 | 1114.51 | 46 | 3414 | 0 | 461 | 685 | 0 | 0 | 1 | 41
03:30 | 3606.5 | 2149.2 | 895 | 0 | 71 | 1091.06 | 46 | 3471 | 0 | 428.5 | 686 | 0 | 0 | 0.5 | 35.5
04:00 | 3624 | 2192.2 | 895 | 0 | 70 | 1067.61 | 46 | 3528 | 0 | 396 | 687 | 0 | 0 | 0 | 30
04:30 | 3568 | 2124.7 | 895 | 0 | 69 | 990.165 | 46 | 3385 | 0 | 268 | 617 | 0 | 0 | 0 | 28
05:00 | 3512 | 2057.2 | 895 | 0 | 68 | 912.72 | 46 | 3242 | 0 | 140 | 547 | 0 | 0 | 0 | 26
05:30 | 3511.5 | 2006.6 | 895.5 | 0 | 63 | 870.92 | 46 | 3054.5 | 0 | 123.5 | 506.5 | 0 | 0 | 0 | 22.5
06:00 | 3511 | 1956 | 896 | 0 | 58 | 829.12 | 46 | 2867 | 0 | 107 | 466 | 0 | 0 | 0 | 19
06:30 | 3499.5 | 1941.25 | 895.5 | 0 | 58 | 828.935 | 46 | 2810 | 13.75 | 107 | 414.5 | 0 | 0 | 0 | 16.5
07:00 | 3488 | 1926.5 | 895 | 0 | 58 | 828.75 | 46 | 2753 | 27.5 | 107 | 363 | 0 | 0 | 0 | 14
07:30 | 3468.5 | 1933 | 877 | 0 | 57 | 827.475 | 46 | 2751.5 | 65.19 | 114 | 358.5 | 0 | 0 | 0 | 19
08:00 | 3449 | 1939.5 | 859 | 0 | 56 | 826.2 | 46 | 2750 | 102.88 | 121 | 354 | 0 | 0 | 0 | 24
08:30 | 3514.5 | 1947.5 | 859.5 | 0 | 56 | 828.79 | 46 | 2779 | 140.84 | 150 | 354 | 0 | 0 | 0 | 12
09:00 | 3580 | 1955.5 | 860 | 0 | 56 | 831.38 | 46 | 2808 | 178.8 | 179 | 354 | 0 | 0 | 0 | 0
09:30 | 3569 | 1941 | 883 | 0 | 57 | 827.705 | 46 | 2805 | 257.765 | 179.5 | 354 | 0 | 0 | 0 | 0
10:00 | 3558 | 1926.5 | 906 | 0 | 58 | 824.03 | 46 | 2802 | 336.73 | 180 | 354 | 0 | 0 | 0 | 0
10:30 | 3598 | 1928.5 | 906.5 | 0 | 56 | 825.8 | 46 | 2798 | 317.005 | 200 | 354 | 0 | 0 | 0 | 0
11:00 | 3638 | 1930.5 | 907 | 0 | 54 | 827.57 | 46 | 2794 | 297.28 | 220 | 354 | 0 | 0 | 0 | 0
11:30 | 3723.5 | 2030.5 | 907 | 0 | 59 | 845.09 | 46 | 2824 | 292.47 | 216.5 | 362 | 0 | 0 | 0 | 0
12:00 | 3809 | 2130.5 | 907 | 0 | 64 | 862.61 | 46 | 2854 | 287.66 | 213 | 370 | 0 | 0 | 0 | 0
12:30 | 3824.5 | 2147.25 | 907 | 0 | 65 | 892.185 | 46 | 2953 | 312.345 | 226 | 439 | 0 | 0 | 5.5 | 0
13:00 | 3840 | 2164 | 907 | 0 | 66 | 921.76 | 46 | 3052 | 337.03 | 239 | 508 | 0 | 0 | 11 | 0
13:30 | 3697.5 | 2036.5 | 906.5 | 0 | 64 | 875.88 | 46 | 2890.5 | 279.755 | 181 | 450.5 | 0 | 0 | 13.5 | 0
14:00 | 3555 | 1909 | 906 | 0 | 62 | 830 | 46 | 2729 | 222.48 | 123 | 393 | 0 | 0 | 16 | 0
14:30 | 3578.5 | 1988.5 | 906.5 | 0 | 62 | 825.5 | 46 | 2712.4 | 212.13 | 123 | 390 | 0 | 0 | 24 | 0
15:00 | 3602 | 2068 | 907 | 0 | 62 | 821 | 46 | 2695.8 | 201.78 | 123 | 387 | 0 | 0 | 32 | 0
15:30 | 3628 | 2059.75 | 907 | 0 | 62 | 820.5 | 46 | 2696.15 | 156.91 | 107.5 | 340 | 0 | 0 | 34.5 | 0
16:00 | 3654 | 2051.5 | 907 | 0 | 62 | 820 | 46 | 2696.5 | 112.04 | 92 | 293 | 0 | 0 | 37 | 0
16:30 | 3690 | 2113.25 | 907 | 0 | 59 | 820.5 | 46 | 2730.75 | 80.23 | 92 | 337 | 0 | 0 | 39 | 0
17:00 | 3726 | 2175 | 907 | 0 | 56 | 821 | 46 | 2765 | 48.42 | 92 | 381 | 0 | 0 | 41 | 0
17:30 | 3603.5 | 2015.75 | 907.5 | 0 | 58 | 846.5 | 46 | 2951 | 25.23 | 193 | 522 | 0 | 0 | 43.5 | 0
18:00 | 3481 | 1856.5 | 908 | 0 | 60 | 872 | 46 | 3137 | 2.04 | 294 | 663 | 0 | 0 | 46 | 0
18:30 | 3576.5 | 2009 | 884 | 0 | 58 | 868.5 | 46 | 3173 | 1.02 | 249 | 629 | 0 | 0 | 44.5 | 0
19:00 | 3672 | 2161.5 | 860 | 0 | 56 | 865 | 46 | 3209 | 0 | 204 | 595 | 0 | 0 | 43 | 0
19:30 | 3721 | 2215.5 | 861 | 0 | 56 | 865 | 46 | 3187 | 0 | 194 | 440 | 0 | 0 | 34 | 0
20:00 | 3750 | 2313.5 | 861 | 0 | 64 | 865 | 46 | 3143 | 0 | 194 | 440 | 0 | 0 | 40 | 0
20:30 | 3774 | 2316.5 | 882 | 0 | 63 | 865.08 | 46 | 3229.5 | 0 | 167.5 | 443 | 0 | 0 | 46 | 0
21:00 | 3798 | 2319.5 | 903 | 0 | 62 | 865.16 | 46 | 3316 | 0 | 141 | 446 | 0 | 0 | 52 | 0
21:30 | 3783.5 | 2343.5 | 902.5 | 0 | 67 | 863.79 | 46 | 3314.5 | 0 | 141 | 461 | 0 | 0 | 53 | 0
22:00 | 3769 | 2367.5 | 902 | 0 | 72 | 862.42 | 46 | 3313 | 0 | 141 | 476 | 0 | 0 | 54 | 0
22:30 | 3742.5 | 2307 | 902.5 | 0 | 71 | 863.17 | 46 | 3319.5 | 0 | 141 | 474.5 | 0 | 0 | 53.5 | 0
23:00 | 3716 | 2246.5 | 903 | 0 | 70 | 863.92 | 46 | 3326 | 0 | 141 | 473 | 0 | 0 | 53 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 06:00 | 387 | 22:00 | Payra | 419 | 06:00 | 412 | 21:00
Ashuganj | 412 | 18:00 | 396 | 23:00 | Rahanpur | 400 | 05:00 | 392 | 00:00
Bhulta | 408 | 18:00 | 393 | 00:00 | Rampal | 410 | 06:00 | 400 | 21:00
Bibiana | 397 | 04:00 | 388 | 00:00
BIPTC | 399 | 03:00 | 390 | 12:00
Bogura | 387 | 06:00 | 377 | 00:00
Gopalganj | 408 | 07:00 | 398 | 00:00
Kaliakoir | 379 | 18:00 | 365 | 00:00
Madunaghat | 398 | 07:00 | 393 | 21:00
Meghnaghat | 401 | 06:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 06:00 | 227 | 00:00 | Keranigonj | 231 | 18:00 | 225 | 00:00
AKSML | 233 | 07:00 | 227 | 22:00 | Khulna(S) | 238 | 06:00 | 229 | 12:00
Aminbazar | 233 | 18:30 | 228 | 00:00 | Madunaghat | 234 | 07:00 | 230 | 11:00
Ashuganj | 235 | 18:30 | 228 | 00:00 | Madunaghat-400 | 234 | 07:00 | 230 | 22:00
Ashuganj-400 | 235 | 18:30 | 228 | 00:00 | Maniknagar | 231 | 18:00 | 223 | 00:00
Baghabari | 236 | 04:00 | 228 | 12:00 | Meghnaghat | 237 | 18:30 | 230 | 00:00
Barapukuria | 226 | 18:30 | 217 | 10:00 | Meghnaghat-400 | 232 | 18:30 | 226 | 00:00
Barapukuria-230 | 226 | 18:30 | 217 | 10:00 | Mirsorai | 231 | 07:00 | 224 | 13:00
Barishal | 239 | 06:00 | 234 | 00:00 | Rajshahi | 236 | 05:00 | 222 | 12:00
Bheramara | 235 | 05:00 | 224 | 12:00 | Rampal | 236 | 06:00 | 228 | 12:00
Bhulta | 232 | 18:00 | 223 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 04:00 | 223 | 00:00 | Rampura | 228 | 06:00 | 223 | 00:00
BIPTC | 237 | 05:00 | 223 | 12:00 | Shikalbaha | 231 | 07:00 | 226 | 20:00
Bogura | 237 | 06:00 | 230 | 12:00 | Shyampur | 231 | 18:30 | 225 | 00:00
Bogura-400 | 237 | 18:30 | 230 | 11:00 | Siddhirganj | 230 | 19:00 | 224 | 00:00
Borhanuddin | 243 | 07:00 | 238 | 00:00 | Sirajgonj | 241 | 18:00 | 236 | 11:00
BSRM | 229 | 06:00 | 224 | 12:00 | Sreepur | 234 | 18:30 | 228 | 10:00
Cumilla(N) | 228 | 18:30 | 221 | 00:00 | Tongi | 232 | 13:00 | 222 | 00:00
Faridpur | 235 | 05:00 | 230 | 00:00
Fenchuganj | 233 | 13:00 | 229 | 00:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 230 | 18:30 | 223 | 00:00
Gopalganj | 235 | 06:00 | 229 | 00:00
GPH | 231 | 06:00 | 226 | 22:00
Haripur | 230 | 18:00 | 224 | 00:00
Hasnabad | 230 | 18:30 | 226 | 00:00
Hathazari | 235 | 09:00 | 230 | 23:00
Ishurdi | 237 | 05:00 | 225 | 12:00
Jhenaidah | 234 | 05:00 | 222 | 12:00
Kaliakoir | 235 | 18:00 | 226 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 06:00 | 133 | 00:00 | Madunaghat | 134 | 06:00 | 131 | 11:00
Agargaon | 139 | 06:00 | 130 | 19:30 | Magura | 136 | 04:00 | 129 | 12:00
Agrabad | 132 | 06:00 | 128 | 11:00 | Mahasthangarh | 133 | 18:30 | 126 | 11:00
AKS | 132 | 18:00 | 127 | 03:00 | Manikganj | 134 | 18:00 | 125 | 07:00
Aminbazar | 136 | 18:30 | 132 | 12:00 | Maniknagar | 135 | 06:00 | 131 | 00:00
Amnura | 136 | 05:00 | 130 | 00:00 | Matarbari | 120 | 07:00 | 113 | 00:00
Ashuganj | 138 | 18:30 | 135 | 00:00 | Matuail | 134 | 18:30 | 128.8 | 00:00
Bagerhat | 135 | 10:00 | 126 | 21:00 | Millgate | 139 | 18:00 | 132 | 00:00
Bajitpur | 133 | 18:30 | 129 | 00:00 | Mirpur | 136 | 18:00 | 130 | 12:00
Bakulia | 133 | 05:00 | 129 | 21:00 | Mirzapur | 132 | 13:00 | 125 | 08:00
Banani | 139 | 06:00 | 134 | 00:00 | Mithapukur | 133 | 18:30 | 123 | 11:00
Bangabhaban | 135 | 18:00 | 131 | 00:00 | MI_Cement | 135 | 18:30 | 129 | 00:00
Barapukuria | 140 | 18:30 | 130 | 10:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 136 | 06:00 | 132 | 00:00 | Mogbazar | 138 | 06:00 | 135 | 00:00
Barishal | 133 | 08:00 | 128 | 00:00 | Mongla | 135 | 06:00 | 128 | 00:00
Barishal-230 | 134 | 06:00 | 129 | 00:00 | Motijheel | 135 | 18:00 | 131 | 00:00
Baroaulia | 133 | 16:00 | 130 | 02:00 | Muktagacha | 136 | 18:00 | 120 | 00:00
Baroirhat | 125 | 18:30 | 119 | 15:00 | Munshiganj | 133 | 18:00 | 129 | 00:00
Bashundhara | 138 | 06:00 | 132 | 00:00 | Muradnagar | 130 | 18:30 | 122 | 00:00
BashundharaCement | 131 | 04:00 | 128 | 00:00 | Mymensingh | 135 | 18:00 | 117 | 00:00
Beanibazar | 132 | 05:00 | 130 | 00:00 | Naogaon | 131 | 18:30 | 126 | 04:00
Benapole | 134 | 06:00 | 124 | 18:30 | Narail | 137 | 05:00 | 129 | 12:00
Bhaluka | 129 | 03:00 | 123 | 11:00 | Narinda | 135 | 18:30 | 131 | 12:00
Bhandaria | 130 | 09:00 | 120 | 00:00 | Narshingdi | 131 | 13:00 | 123 | 00:00
Bhangura | 135 | 05:00 | 130 | 11:00 | Natore | 134 | 05:00 | 128 | 12:00
Bheramara | 135 | 05:00 | 129 | 12:00 | Nawabganj | 139 | 06:00 | 134 | 00:00
Bheramara(GK) | 135 | 05:00 | 129 | 12:00 | Netrakona | 125 | 05:00 | 118 | 00:00
Bhulta | 128 | 14:00 | 123 | 00:00 | New | 139 | 18:00 | 133 | 00:00
Bog-Sherpur | 134 | 18:30 | 129 | 08:00 | Niamatpur | 137 | 19:00 | 131 | 00:00
Bogura | 135 | 18:30 | 130 | 00:00 | Noapara | 135 | 05:00 | 130 | 00:00
Bogura-230 | 135 | 18:30 | 130 | 09:00 | Pabna | 136 | 05:00 | 129 | 12:00
Brahmanbaria | 133 | 13:00 | 126 | 00:00 | Palashbari | 130 | 18:30 | 121 | 08:00
Cantonment | 139 | 06:00 | 135 | 00:00 | Panchagarh | 136 | 18:30 | 116 | 08:00
Chandpur | 125 | 18:00 | 115 | 01:00 | Patuakhali | 135 | 05:00 | 132 | 00:00
Chandraghona | 133 | 06:00 | 130 | 19:30 | Payra | 138 | 08:00 | 135 | 00:00
Chapai | 135 | 13:00 | 131 | 00:00 | PHP | 123 | 18:30 | 117 | 12:00
Charsaidpur | 133 | 18:00 | 129 | 00:00 | Postogola | 136 | 18:00 | 131 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 18:00 | 118 | 15:00 | Purbachal | 139 | 18:00 | 133 | 12:00
Chhatak | 132 | 06:00 | 129 | 00:00 | Purbasadipur | 133 | 18:30 | 116 | 10:00
Chowmuhani | 116 | 03:00 | 110 | 00:00 | Rahanpur | 138 | 06:00 | 134 | 00:00
Chuadanga | 135 | 05:00 | 127 | 12:00 | Rahanpur-400 | 138 | 06:00 | 134 | 00:00
Coxsbazar | 119 | 07:00 | 113 | 21:00 | Rahim | 133 | 14:00 | 130 | 00:00
Cumilla(N) | 130 | 18:00 | 125 | 00:00 | Rajbari | 132 | 06:00 | 128 | 00:00
Cumilla(S) | 130 | 05:00 | 122 | 00:00 | Rajendrapur | 135 | 18:30 | 121 | 08:00
Daudkandi | 127 | 07:00 | 120 | 00:00 | Rajshahi | 135 | 05:00 | 128 | 12:00
Dhaka | 138 | 13:00 | 133 | 06:00 | Rajshahi-230 | 136 | 05:00 | 128 | 00:00
Dhamrai | 134 | 18:00 | 127 | 12:00 | Ramganj | 120 | 18:00 | 110 | 00:00
Dhanmondi | 138 | 04:00 | 134 | 00:00 | Rampur | 132 | 08:00 | 129 | 11:00
Dohazari | 129 | 04:00 | 123 | 12:00 | Rampura | 138 | 06:00 | 134 | 00:00
Faridpur | 132 | 05:00 | 130 | 00:00 | Rangamati | 132 | 02:00 | 129 | 21:00
Fatullah | 137 | 18:00 | 131 | 00:00 | Rangpur | 130 | 01:00 | 121 | 10:00
Fenchuganj | 136 | 13:00 | 132 | 00:00 | Ruppur | 137 | 04:00 | 132 | 12:00
Feni | 124 | 07:00 | 118 | 00:00 | Saidpur | 133 | 18:30 | 121 | 11:00
Ghatail | 132 | 13:00 | 119 | 00:00 | Satkhira | 135 | 06:00 | 127 | 18:30
Ghorashal | 140 | 07:00 | 134 | 00:00 | Satmasjid | 140 | 18:30 | 134 | 12:00
Goalpara | 137 | 06:00 | 130 | 00:00 | Savar | 136 | 18:00 | 130 | 11:00
Gollamari | 137 | 05:00 | 132 | 00:00 | SevenRings | 139 | 18:00 | 133 | 00:00
Gopalganj | 137 | 06:00 | 132 | 00:00 | ShahCement | 133 | 18:00 | 130 | 16:00
Gopalganj-400 | 139 | 06:00 | 135 | 00:00 | Shahjadpur | 139 | 19:30 | 134 | 12:00
Gulshan | 137 | 05:00 | 134 | 00:00 | Shahjibazar | 133 | 06:00 | 128 | 00:00
Halishahar | 132 | 02:00 | 129 | 12:00 | Shahmirpur | 134 | 18:00 | 130 | 11:00
Haripur | 134 | 18:00 | 130 | 00:00 | Shariatpur | 137 | 06:00 | 132 | 00:00
HaripurSBU | 134 | 18:00 | 129 | 00:00 | Sherpur | 134 | 13:00 | 117 | 00:00
Hasnabad | 137 | 18:00 | 132 | 00:00 | Shikalbaha | 124 | 02:00 | 118 | 22:00
Hathazari | 135 | 09:00 | 132 | 10:00 | Shikalbaha-230 | 134 | 00:00 | 131 | 21:00
Ishurdi | 138 | 05:00 | 131 | 12:00 | Shitalakhya | 135 | 18:30 | 129 | 00:00
Jaldhaka | 132 | 18:30 | 118 | 11:00 | Sholosohor | 133 | 06:00 | 130 | 12:00
Jamalpur | 137 | 13:00 | 120 | 00:00 | Shyampur | 133 | 14:00 | 129 | 00:00
Jashore | 135 | 05:00 | 128 | 13:00 | Shyampur-230 | 135 | 06:00 | 130 | 00:00
Jhenaidah | 137 | 05:00 | 129 | 12:00 | Siddhirganj | 134 | 18:00 | 130 | 00:00
Jhenaidah-230 | 139 | 12:00 | 130 | 13:00 | Sirajganj | 133 | 15:00 | 127 | 11:00
Joydebpur | 136 | 18:30 | 127 | 04:00 | Sonargaon | 132 | 18:30 | 126 | 00:00
Joypurhat | 129 | 18:30 | 123 | 09:00 | Sreemongol | 133 | 13:00 | 129 | 01:00
Juldah | 134 | 01:00 | 130 | 12:00 | Sreepur | 132 | 18:30 | 127 | 10:00
Kabirpur | 138 | 18:00 | 126 | 08:00 | Srinagar | 140 | 18:30 | 135 | 00:00
Kachua | 123 | 03:00 | 118 | 00:00 | SSM | 138 | 07:00 | 131 | 15:00
Kaliakoir | 138 | 18:00 | 129 | 08:00 | Sunamganj | 131 | 05:00 | 128 | 00:00
Kallyanpur | 136 | 04:00 | 132 | 12:00 | Sylhet | 133 | 07:00 | 130 | 00:00
Kalurghat | 133 | 02:00 | 131 | 11:00 | Sylhet-132 | 133 | 05:00 | 131 | 00:00
Kamrangirchar | 141 | 18:00 | 134 | 00:00 | Tangail | 134 | 18:00 | 122 | 00:00
Kaptai | 135 | 1:00 | 132 | 22:00 | Thakurgaon | 134 | 18:30 | 114 | 11:00
Kasba | 128 | 10:00 | 121 | 00:00 | TK | 135 | 18:00 | 131 | 22:00
Kazla | 135 | 19:00 | 130 | 00:00 | Tongi | 140 | 13:00 | 135 | 00:00
Keranigonj | 139 | 06:00 | 135 | 00:00 | Ullahpara | 135 | 18:30 | 130 | 03:00
Khagrachori | 132 | 06:00 | 129 | 11:00 | Ullon | 138 | 06:00 | 132 | 14:00
Khulna | 135 | 05:00 | 130 | 00:00 | Uttara | 139 | 18:30 | 129 | 12:00
Khulna(S) | 138 | 06:00 | 132 | 00:00 | UttaraNew | 138 | 00:00 | 133 | 15:00
Khulshi | 131 | 18:00 | 128 | 12:00 | Zigatola | 140 | 18:30 | 135 | 00:00
Kishoreganj | 132 | 18:30 | 126 | 00:00
Kodda | 136 | 18:00 | 124 | 07:00
KSRM | 134 | 18:00 | 130 | 00:00
Kulaura | 134 | 07:00 | 132 | 00:00
Kurigram | 133 | 18:00 | 120 | 09:00
Kushtia | 134 | 03:00 | 128 | 12:00
Lalbag | 140 | 18:30 | 134 | 00:00
Lalmonirhat | 130 | 18:30 | 120 | 10:00
Madanganj | 131 | 04:00 | 128 | 00:00
Madaripur | 138 | 08:00 | 132 | 00:00
Madartek | 137 | 06:00 | 132 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division