## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-03-2025 | during | 23-03-2025 | during | 23-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 22 | 97.3 | 97.3 | 22 | 22 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 369 | 232 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 310 | 251 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 39 | 100 | 208.13 | 208.13 | 105 | 105 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 227 | 220 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.5 | 17.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 20 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 1 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 34 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 15 | 0 | 15 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2137.5 | 2061.5 | 5255.5 | 5240.5 | 3795.31 | 3780.31
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 163 | 162 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 17 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 48 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 29 | 2 | 32 | 2 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.79 | 0 | 3.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 305 | 612 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 22 | 3 | 45 | 3 | 45 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 770 | 770 | 770 | 770 | 770 | 770 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1329 | 1714 | 3608.51 | 3658.72 | 3608.51 | 3658.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 193 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 360 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 15 | 83 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 27 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 58 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 48 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 94 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 78 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1121 | 1290 | 2410.99 | 2345.99 | 2216.55 | 2151.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-03-2025 | during | 23-03-2025 | during | 23-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 6 | 11 | 210 | 210 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 176 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 99 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 6.58 | 0 | 40 | 0 | 40 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 113.58 | 298 | 642.7 | 601.5 | 452.7 | 411.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 41 | 38 | 39 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 43 | 43 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 137 | 132 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 5 | 5 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 20 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 164 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 275 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 335 | 360 | 360 | 332 | 332 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1452 | 1426 | 1636 | 1637 | 1527 | 1527
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 910 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 57.91 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 380 | 620 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1340.91 | 1530 | 3579.2 | 3514.2 | 1987.02 | 1922.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 308 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 9 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 108 | 108 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 745 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.43 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1526.43 | 1778 | 2062.12 | 2061.12 | 2050.12 | 2049.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 167 | 157 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 155 | 185 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 197 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 390 | 351 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.84 | 0 | 3.5 | 0 | 3.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 824.45 | 1363 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 26 | 0 | 75 | 0 | 75 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1724.99 | 2255.5 | 3075.03 | 2935.53 | 3033.24 | 2893.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 62 | 62 | 62 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 128 | 120 | 130 | 130 | 130 | 130 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 47 | 0 | 63 | 0 | 63 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 253 | 216 | 543.4 | 454 | 507.42 | 418.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 10998.41 | 12569 | 22813.45 | 22448.56 | 19177.87 | 18811.98
Forecast Scenario (23-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12630 |  | 0 |  | 12630
|  |  |  | 1:00 | 12200 |  | 0 |  | 12200
|  |  |  | 2:00 | 11610 |  | 0 |  | 11610
|  |  |  | 3:00 | 11870 |  | 0 |  | 11870
|  |  |  | 4:00 | 12030 |  | 0 |  | 12030
|  |  |  | 5:00 | 10990 |  | 0 |  | 10990
|  |  |  | 6:00 | 10130 |  | 0 |  | 10130
|  |  |  | 7:00 | 10350 |  | 0 |  | 10350
|  |  |  | 8:00 | 10970 |  | 0 |  | 10970
|  |  |  | 9:00 | 11730 |  | 0 |  | 11730
|  |  |  | 10:00 | 11860 |  | 0 |  | 11860
|  |  |  | 11:00 | 11770 |  | 0 |  | 11770
|  |  |  | 12:00 | 12020 |  | 0 |  | 12020
|  |  |  | 13:00 | 12300 |  | 0 |  | 12300
|  |  |  | 14:00 | 12370 |  | 0 |  | 12370
|  |  |  | 15:00 | 11960 |  | 0 |  | 11960
|  |  |  | 16:00 | 12090 |  | 0 |  | 12090
|  |  |  | 17:00 | 12240 |  | 0 |  | 12240
|  |  |  | 18:00 | 12280 |  | 0 |  | 12280
|  |  |  | 18:30 | 12350 |  | 0 |  | 12350
|  |  |  | 19:00 | 12530 |  | 0 |  | 12530
|  |  |  | 19:30 | 12810 |  | 0 |  | 12810
|  |  |  | 20:00 | 13020 |  | 0 |  | 13020
|  |  |  | 21:00 | 13140 |  | 0 |  | 13140
|  |  |  | 22:00 | 13220 |  | 0 |  | 13220
|  |  |  | 23:00 | 12900 |  | 0 |  | 12900
Probable Maximum Temperature: |  |  | 29.40°C
Probable Maximum Demand at Day Peak: |  |  | 12020.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13140.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13140.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 288.21 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:27 hrs on 23-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-03-2025 | [28 empty] | Date: | 22-03-2025 | [28 empty] | Date: | 22-03-2025 | [28 empty] | Date: | 22-03-2025 | [28 empty] | Date: | 22-03-2025 | [18 empty] | Date: | 22-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 51 | 43 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 45 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 281 | 583 | 0 | 0 | 14 | 238 | 100 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 565 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 455 | 0 | 51 | 0 | 8 | 0 | 359 | 285 | 54 | 182 | 33 | 68 | 0 | 63 | 38 | 20 | 52 | 70 | 25 | 0 | 0 | 295 | 320 | 349 | 5 | 43 | 0 | 5 | 152 | 21 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 45 | 105 | 0 | 0 | 0 | 12 | 6555 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 860.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 170 | 0 | 160 | 0 | 414 | 0 | 0 | 2.5 | 122 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 108 | 110 | 0 | 623 | 836 | 0 | 4972.1 | 11527.1 | 86.24
01:00 | 0 | 51 | 43 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 283 | 550 | 0 | 0 | 14 | 235 | 102 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 453 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 402 | 0 | 51 | 0 | 8 | 0 | 359 | 285 | 54 | 181 | 36 | 27 | 0 | 68 | 29 | 20 | 70 | 72 | 25 | 0 | 0 | 275 | 320 | 310 | 5 | 43 | 0 | 5 | 152 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 85 | 20 | 0 | 0 | 12 | 6224 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 823.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 170 | 0 | 167 | 0 | 350 | 0 | 0 | 0 | 121 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 108 | 110 | 0 | 624 | 782 | 0 | 4780.52 | 11004.52 | 86.23
02:00 | 0 | 34 | 43 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 313 | 500 | 0 | 0 | 14 | 232 | 102 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 421 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 351 | 0 | 51 | 0 | 8 | 0 | 359 | 285 | 54 | 194 | 36 | 17 | 0 | 68 | 29 | 20 | 70 | 60 | 25 | 0 | 0 | 300 | 320 | 311 | 5 | 43 | 0 | 5 | 152 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 45 | 85 | 18 | 0 | 0 | 12 | 5981 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 823.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 122 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 114 | 110 | 0 | 624 | 700 | 0 | 4622.31 | 10603.31 | 86.23
03:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 314 | 550 | 0 | 0 | 14 | 232 | 101 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 358 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 8 | 0 | 320 | 285 | 54 | 219 | 36 | 17 | 0 | 68 | 29 | 20 | 70 | 64 | 25 | 0 | 0 | 320 | 320 | 365 | 5 | 43 | 0 | 5 | 161 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 55 | 92 | 18 | 0 | 0 | 12 | 6132 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 863.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 168 | 0 | 161 | 0 | 320 | 0 | 0 | 0 | 124 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 130 | 110 | 0 | 624 | 746 | 0 | 4742.31 | 10874.31 | 86.22
04:00 | 0 | 34 | 43 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 252 | 550 | 0 | 0 | 16 | 231 | 96 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 359 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 8 | 0 | 360 | 285 | 53 | 181 | 36 | 44 | 0 | 68 | 29 | 20 | 34 | 68 | 8 | 0 | 0 | 305 | 320 | 349 | 5 | 41 | 0 | 5 | 152 | 21 | 0 | 41 | 30 | 0 | 18 | 164 | 0 | 45 | 135 | 18 | 0 | 0 | 12 | 6132 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 912.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 178 | 0 | 166 | 0 | 414 | 0 | 0 | 0 | 126 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 9 | 108 | 110 | 0 | 624 | 800 | 0 | 5019.33 | 11151.33 | 86.22
05:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 16 | 0 | 350 | 249 | 400 | 0 | 0 | 16 | 230 | 36 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 359 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 0 | 10 | 0 | 8 | 0 | 300 | 285 | 27 | 181 | 10 | 51 | 0 | 34 | 29 | 20 | 17 | 64 | 8 | 0 | 0 | 280 | 304 | 349 | 5 | 41 | 0 | 5 | 132 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 45 | 105 | 18 | 0 | 0 | 12 | 5381 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 822.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 2.5 | 126 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 108 | 110 | 0 | 625 | 712 | 0 | 4781.15 | 10162.15 | 86.21
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 278 | 300 | 0 | 0 | 16 | 230 | 37 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 360 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 303 | 0 | 10 | 0 | 8 | 0 | 280 | 240 | 11 | 181 | 10 | 34 | 0 | 17 | 29 | 20 | 0 | 62 | 8 | 0 | 0 | 265 | 320 | 349 | 5 | 41 | 0 | 5 | 132 | 21 | 0 | 11 | 20 | 0 | 18 | 164 | 0 | 35 | 45 | 18 | 0 | 0 | 12 | 4866 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 823.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 250 | 0 | 0 | 2.5 | 126 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 108 | 110 | 0 | 624 | 532 | 0 | 4495.55 | 9361.55 | 86.21
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 314 | 300 | 0 | 0 | 16 | 231 | 38 | 0 | 1 | 0 | 18.7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 18 | 420 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 303 | 3 | 10 | 0 | 8 | 0 | 280 | 240 | 10 | 203 | 10 | 34 | 0 | 17 | 0 | 20 | 0 | 56 | 8 | 3 | 0 | 300 | 320 | 378 | 5 | 41 | 0 | 2 | 136 | 21 | 0 | 11 | 20 | 0 | 18 | 164 | 0 | 35 | 45 | 18 | 0 | 3.42 | 12 | 5005.12 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.56 | 380 | 0 | 825.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 4.36 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 0.4 | 2.5 | 126 | 60 | 0 | 1 | 0 | 0 | 0 | 0 | 7 | 0.03 | 0 | 150 | 6 | 108 | 110 | 0 | 625 | 520 | 0 | 4557.8 | 9562.92 | 86.2
08:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 10 | 0 | 4 | 32 | 0 | 0 | 0 | 0 | 16 | 0 | 350 | 293 | 450 | 0 | 0 | 16 | 231 | 38 | 0 | 1 | 0 | 22 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 46 | 0 | 8 | 570 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 303 | 8 | 10 | 0 | 8 | 0 | 360 | 240 | 10 | 189 | 10 | 34 | 0 | 25 | 0 | 20 | 17 | 54 | 8 | 10 | 0 | 310 | 320 | 356 | 5 | 41 | 0 | 2 | 136 | 21 | 0 | 50 | 20 | 0 | 18 | 164 | 0 | 65 | 75 | 16 | 0 | 21.9 | 12 | 5605.9 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.96 | 380 | 0 | 821.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 11.59 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 1.08 | 2.5 | 125 | 59 | 0 | 6 | 0 | 0 | 0 | 1.5 | 30 | 0.03 | 0 | 150 | 6 | 120 | 110 | 0 | 623 | 542 | 0 | 4613.82 | 10219.72 | 86.2
09:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 35 | 0 | 29 | 32 | 0 | 0 | 0 | 0 | 16 | 0 | 420 | 272 | 583 | 0 | 0 | 16 | 225 | 39 | 0 | 4 | 0 | 22 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 46 | 0 | 5 | 750 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 303 | 13 | 10 | 0 | 8 | 0 | 335 | 285 | 10 | 182 | 10 | 24 | 0 | 34 | 0 | 20 | 0 | 36 | 0 | 29 | 0 | 300 | 320 | 355 | 5 | 41 | 0 | 2 | 137 | 21 | 0 | 50 | 20 | 0 | 18 | 164 | 0 | 65 | 75 | 11 | 0 | 7.95 | 12 | 5994.95 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.75 | 380 | 0 | 825.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 6.11 | 155 | 0 | 140 | 0 | 140 | 0 | 381 | 0 | 0.54 | 2.5 | 129 | 59 | 0 | 7 | 0 | 0 | 0 | 1.5 | 34 | 0.38 | 0 | 250 | 5 | 108 | 110 | 0 | 455 | 623 | 0 | 4744.77 | 10739.72 | 86.19
10:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 35 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 16 | 0 | 420 | 287 | 583 | 0 | 0 | 16 | 226 | 39 | 0 | 1 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 0 | 3 | 46 | 0 | 5 | 772 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 305 | 17 | 10 | 0 | 8 | 0 | 300 | 285 | 10 | 182 | 10 | 17 | 0 | 17 | 0 | 20 | 0 | 56 | 0 | 36 | 0 | 285 | 320 | 350 | 5 | 41 | 0 | 2 | 132 | 21 | 0 | 50 | 20 | 0 | 18 | 164 | 0 | 45 | 55 | 9 | 0 | 17.01 | 12 | 5902.51 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.02 | 380 | 0 | 827.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 5.34 | 167 | 0 | 140 | 0 | 140 | 0 | 314 | 0 | 0.43 | 2.5 | 127 | 61 | 0 | 21 | 0 | 0 | 0 | 0 | 53 | 0.05 | 0 | 250 | 5 | 110 | 111 | 0 | 304 | 740 | 0 | 4753.75 | 10656.26 | 86.19
11:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 16 | 0 | 420 | 300 | 583 | 0 | 0 | 16 | 226 | 39 | 0 | 5 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 6 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 307 | 18 | 10 | 0 | 8 | 0 | 300 | 285 | 10 | 198 | 10 | 17 | 0 | 17 | 0 | 20 | 0 | 54 | 0 | 42 | 0 | 300 | 320 | 375 | 5 | 40 | 0 | 2 | 133 | 21 | 0 | 50 | 20 | 0 | 18 | 164 | 0 | 45 | 55 | 5 | 0 | 7.85 | 12 | 5933.35 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.36 | 380 | 0 | 825.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 9.42 | 167 | 0 | 140 | 0 | 140 | 0 | 337 | 0 | 0.83 | 2.5 | 128 | 60 | 0 | 13 | 0 | 0 | 0 | 0 | 54 | 0.74 | 0 | 250 | 5 | 114 | 110 | 0 | 310 | 755 | 0 | 4817.18 | 10750.53 | 86.18
12:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 17 | 0 | 1 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 420 | 310 | 583 | 0 | 0 | 16 | 227 | 39 | 0 | 4 | 0 | 22.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 5 | 770 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 305 | 20 | 10 | 0 | 15 | 0 | 360 | 285 | 10 | 193 | 33 | 17 | 0 | 27 | 0 | 20 | 17 | 56 | 0 | 78 | 0 | 310 | 320 | 365 | 5 | 40 | 0 | 2 | 137 | 21 | 0 | 50 | 20 | 0 | 18 | 164 | 0 | 45 | 55 | 6 | 1 | 6.58 | 0 | 6153.08 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.91 | 380 | 0 | 824.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 18.2 | 167 | 0 | 155 | 0 | 140 | 0 | 390 | 0 | 1.84 | 2.5 | 128 | 61 | 0 | 9 | 0 | 0 | 0 | 8 | 47 | 0.43 | 0 | 250 | 5 | 108 | 110 | 0 | 308 | 745 | 0 | 4845.33 | 10998.41 | 86.18
13:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 22 | 376 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 420 | 285 | 583 | 0 | 0 | 16 | 226 | 103 | 0 | 4 | 0 | 22.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 7 | 770 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 300 | 19 | 29 | 0 | 55 | 0 | 360 | 285 | 22 | 182 | 36 | 17 | 0 | 48 | 0 | 20 | 40 | 66 | 0 | 69 | 0 | 300 | 320 | 350 | 5 | 41 | 0 | 2 | 160 | 21 | 0 | 82 | 30 | 0 | 18 | 164 | 0 | 45 | 55 | 5 | 1 | 14.42 | 0 | 6372.92 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.25 | 381 | 0 | 820.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13.27 | 168 | 0 | 197 | 0 | 140 | 0 | 381 | 0 | 1.18 | 2.5 | 129 | 60 | 0 | 12 | 0 | 0 | 0 | 5.9 | 88 | 0.7 | 0 | 250 | 5 | 108 | 110 | 0 | 310 | 750 | 0 | 4908.22 | 11281.14 | 86.17
14:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 22 | 376 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 30 | 14 | 450 | 280 | 583 | 0 | 0 | 15 | 226 | 102 | 0 | 7 | 0 | 22.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 24 | 0 | 3 | 46 | 0 | 5 | 770 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 350 | 17 | 43 | 0 | 83 | 0 | 360 | 285 | 34 | 183 | 36 | 20 | 0 | 67 | 0 | 20 | 52 | 56 | 0 | 63 | 0 | 300 | 320 | 350 | 5 | 42 | 0 | 2 | 158 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 24 | 62 | 5 | 1 | 10.17 | 0 | 6535.67 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.17 | 421 | 0 | 882.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 11.28 | 168 | 0 | 211 | 0 | 211 | 0 | 325 | 0 | 1.01 | 2.5 | 128 | 61 | 0 | 21 | 0 | 0 | 0 | 6.8 | 97 | 0.62 | 0 | 250 | 5 | 108 | 110 | 0 | 308 | 680 | 0 | 4999.83 | 11535.5 | 86.17
15:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 22 | 373 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 350 | 305 | 583 | 0 | 0 | 14 | 224 | 102 | 0 | 15 | 0 | 22.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 48 | 0 | 2 | 46 | 0 | 3 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 350 | 13 | 43 | 0 | 83 | 0 | 360 | 285 | 48 | 194 | 36 | 34 | 0 | 68 | 0 | 20 | 34 | 58 | 0 | 22 | 0 | 285 | 320 | 362 | 5 | 42 | 0 | 2 | 151 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 28 | 75 | 5 | 1 | 5.56 | 0 | 6452.06 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.7 | 375 | 0 | 864.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 37.75 | 169 | 0 | 212 | 0 | 214 | 0 | 322 | 0 | 3.38 | 2.5 | 125 | 61 | 0 | 11 | 0 | 0 | 0 | 4.8 | 103 | 0.2 | 0 | 150 | 6 | 108 | 110 | 0 | 310 | 680 | 0 | 4866.66 | 11318.72 | 86.16
16:00 | 0 | 40 | 17 | 0 | 0 | 0 | 0 | 22 | 372 | 0 | 0 | 0 | 17 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 30 | 0 | 420 | 306 | 583 | 0 | 0 | 14 | 224 | 100 | 0 | 11 | 17 | 22.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 48 | 0 | 1 | 46 | 0 | 3 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 350 | 8 | 43 | 0 | 26 | 0 | 360 | 285 | 49 | 201 | 36 | 34 | 0 | 68 | 10 | 20 | 34 | 58 | 0 | 10 | 0 | 310 | 320 | 381 | 5 | 43 | 0 | 2 | 156 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 60 | 105 | 5 | 1 | 22.64 | 0 | 6658.14 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.94 | 379 | 0 | 863.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 27.55 | 177 | 0 | 181 | 0 | 198 | 0 | 414 | 0 | 2.71 | 2.5 | 119 | 61 | 0 | 15 | 0 | 0 | 0 | 1.7 | 59 | 0.16 | 0 | 150 | 5 | 124 | 110 | 0 | 231 | 700 | 0 | 4769.49 | 11427.63 | 86.16
17:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 22 | 379 | 0 | 0 | 1 | 52 | 0 | 30 | 64 | 15 | 0 | 3 | 15 | 30 | 0 | 420 | 300 | 583 | 0 | 0 | 14 | 224 | 100 | 0 | 4 | 17 | 22 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 39 | 7 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 19 | 780 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 400 | 2 | 43 | 0 | 26 | 0 | 360 | 285 | 50 | 190 | 36 | 34 | 0 | 68 | 28 | 20 | 34 | 54 | 0 | 6 | 0 | 315 | 320 | 351 | 5 | 43 | 0 | 2 | 159 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 65 | 115 | 5 | 0 | 9.18 | 1 | 6827.18 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.37 | 435 | 0 | 953.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9.33 | 178 | 0 | 174 | 0 | 197 | 0 | 403 | 0 | 0.76 | 2.5 | 121 | 63 | 22 | 5 | 26 | 0 | 0 | 1.2 | 30 | 0.11 | 0 | 250 | 6 | 110 | 110 | 0 | 24 | 809 | 0 | 4868.29 | 11695.47 | 86.15
18:00 | 0 | 73 | 25 | 0 | 0 | 0 | 0 | 22 | 376 | 0 | 0 | 20 | 54 | 0 | 56 | 64 | 15 | 0 | 30 | 17 | 30 | 10 | 420 | 266 | 583 | 0 | 0 | 15 | 224 | 101 | 0 | 0 | 35 | 15 | 12 | 0 | 0 | 2 | 15 | 0 | 0 | 22 | 17 | 0 | 0 | 48 | 0 | 0 | 46 | 3 | 19 | 769 | 0 | 0 | 0 | 0 | 12 | 162 | 0 | 0 | 0 | 468 | 0 | 43 | 10 | 26 | 0 | 360 | 285 | 50 | 182 | 36 | 68 | 0 | 68 | 30 | 20 | 34 | 60 | 0 | 0 | 0 | 300 | 320 | 300 | 5 | 41 | 0 | 2 | 149 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 97 | 172 | 5 | 0 | 0.83 | 12 | 7037.83 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 432 | 0 | 1072.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.48 | 160 | 0 | 163 | 0 | 158 | 0 | 354 | 0 | 0.04 | 2.5 | 119 | 63 | 41 | 0 | 70 | 0 | 8 | 0.1 | 2 | 0 | 0 | 250 | 7 | 90 | 110 | 0 | 0 | 962 | 0 | 4973.36 | 12011.19 | 86.15
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 22 | 361 | 0 | 0 | 25 | 52 | 0 | 72 | 32 | 0 | 0 | 17 | 17 | 22 | 16 | 420 | 300 | 583 | 0 | 0 | 15 | 224 | 101 | 0 | 0 | 35 | 19 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 31 | 0 | 0 | 48 | 0 | 0 | 46 | 10 | 23 | 771 | 0 | 0 | 0 | 1 | 33 | 162 | 0 | 0 | 0 | 523 | 0 | 43 | 20 | 55 | 0 | 360 | 285 | 15 | 200 | 36 | 94 | 0 | 68 | 48 | 20 | 0 | 54 | 0 | 0 | 0 | 295 | 320 | 330 | 5 | 41 | 0 | 2 | 135 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 99 | 172 | 11 | 0 | 0 | 12 | 7177 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 0 | 1183.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 166 | 0 | 166 | 0 | 333 | 0 | 0 | 2.5 | 120 | 63 | 71 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 8 | 120 | 110 | 0 | 0 | 995 | 0 | 5158.05 | 12335.05 | 86.14
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 22 | 359 | 0 | 0 | 17 | 54 | 0 | 17 | 16 | 0 | 0 | 17 | 17 | 22 | 10 | 420 | 277 | 583 | 0 | 0 | 21 | 224 | 102 | 0 | 0 | 35 | 17.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 23 | 770 | 0 | 0 | 0 | 8 | 31 | 162 | 0 | 0 | 0 | 580 | 0 | 43 | 15 | 55 | 0 | 360 | 285 | 40 | 182 | 36 | 94 | 0 | 34 | 48 | 20 | 0 | 58 | 0 | 0 | 0 | 300 | 320 | 303 | 5 | 41 | 0 | 2 | 135 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 99 | 172 | 11 | 0 | 0 | 12 | 7048.5 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481 | 0 | 1239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 165 | 0 | 157 | 0 | 308 | 0 | 0 | 2.5 | 120 | 62 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 120 | 110 | 0 | 0 | 1200 | 0 | 5403.5 | 12452
20:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 22 | 360 | 0 | 0 | 0 | 54 | 0 | 27 | 16 | 0 | 0 | 17 | 17 | 22 | 0 | 420 | 257 | 583 | 0 | 0 | 20 | 224 | 101 | 0 | 0 | 35 | 17.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 17 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 29 | 740 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 43 | 0 | 55 | 0 | 360 | 285 | 45 | 181 | 33 | 93 | 0 | 34 | 48 | 20 | 0 | 62 | 0 | 0 | 0 | 290 | 320 | 303 | 5 | 41 | 0 | 2 | 133 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 99 | 176 | 11 | 0 | 0 | 12 | 6934.5 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524 | 0 | 1368.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 161 | 0 | 156 | 0 | 309 | 0 | 0 | 2.5 | 117 | 62 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 110 | 0 | 0 | 1205 | 0 | 5557.89 | 12492.39 | 86.14
21:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 22 | 232 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 251 | 583 | 0 | 0 | 20 | 220 | 100 | 0 | 0 | 17 | 17.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 29 | 770 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 612 | 0 | 43 | 0 | 83 | 0 | 360 | 285 | 50 | 182 | 33 | 94 | 0 | 34 | 48 | 20 | 0 | 58 | 0 | 0 | 0 | 275 | 320 | 335 | 5 | 41 | 0 | 2 | 132 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 99 | 176 | 11 | 0 | 0 | 12 | 6789.5 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 185 | 0 | 197 | 0 | 351 | 0 | 0 | 2.5 | 120 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 110 | 0 | 0 | 1244 | 0 | 5779.5 | 12569 | 86.13
22:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 30 | 166 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 288 | 583 | 0 | 0 | 20 | 220 | 98 | 0 | 0 | 17 | 17.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 88 | 0 | 0 | 46 | 0 | 29 | 770 | 0 | 0 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 571 | 0 | 43 | 0 | 83 | 0 | 360 | 285 | 50 | 181 | 36 | 80 | 0 | 50 | 49 | 20 | 17 | 58 | 0 | 0 | 0 | 280 | 320 | 348 | 5 | 41 | 0 | 5 | 147 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 99 | 166 | 11 | 0 | 0 | 12 | 6786.5 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 0 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 197 | 0 | 198 | 0 | 375 | 0 | 0 | 2.5 | 127 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 110 | 0 | 0 | 1112 | 0 | 5697.5 | 12484 | 86.13
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 32 | 72 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 293 | 583 | 0 | 0 | 20 | 220 | 100 | 0 | 0 | 17 | 17.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 24 | 700 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 545 | 0 | 43 | 0 | 83 | 0 | 360 | 285 | 51 | 182 | 36 | 46 | 0 | 78 | 49 | 14 | 17 | 64 | 0 | 0 | 0 | 285 | 320 | 348 | 5 | 43 | 0 | 5 | 152 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 55 | 166 | 12 | 0 | 0 | 9 | 6493.5 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 0 | 1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 198 | 0 | 198 | 0 | 376 | 0 | 0 | 2.5 | 125 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 110 | 0 | 0 | 1100 | 0 | 5388.5 | 11882 | 86.12
Total KWH | 0 | 1005120 | 573600 | 0 | 0 | 0 | 0 | 267636.36 | 7999200 | 0 | 0 | 59760 | 748440 | 0 | 317520 | 689760 | 33873 | 0 | 115626 | 74880 | 524160 | 42240 | 9471000 | 6987316 | 12875455 | 0 | 0 | 387600 | 5464593 | 2004000 | 0 | 68637 | 192000 | 471000 | 243000 | 0 | 0 | 15055 | 35127 | 0 | 0 | 544320 | 112330 | 0 | 0 | 700800 | 0 | 25082 | 1102260 | 23400 | 544800 | 15360000 | 0 | 0 | 0 | 28177.2 | 71091 | 3840956 | 0 | 0 | 0 | 9659999 | 138240 | 827528 | 53527 | 786182 | 0 | 8568100 | 6770000 | 831840 | 4619000 | 701352 | 977280 | 19500 | 1299840 | 527520 | 463670 | 614460 | 1407360 | 135677 | 360473 | 0 | 7202500 | 7670300 | 8665000 | 200088 | 985000 | 0 | 76992 | 3487009 | 506469 | 0 | 1580160 | 644352 | 0 | 433000 | 3390200 | 0 | 1459200 | 2536800 | 241920 | 6450 | 146530 | 226080 | 151239412.56 | 21738181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483120 | 10174550 | 0 | 22831663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299250 | 0 | 150752 | 3937182 | 0 | 4234145 | 0 | 4173973 | 0 | 8375345.5 | 0 | 13500 | 55944 | 3070000 | 1435199 | 188570 | 121766 | 343603 | 0 | 0 | 29605.68 | 588240 | 3753 | 0 | 4735000 | 171633 | 2674000 | 2646350 | 0 | 8133090 | 20170181.82 | 0 | 120778597 | 272018009.56

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10998.41 | MW | 12:00 Hr. | Energy Generated |  |  | 272.018 |  | MKWHr.
| Day Peak Demand |  |  | 11024.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.132 |  | MKWHr.
| Evening Peak Generation |  |  | 12569 | MW | 21:00 Hr. | Energy Demand |  |  | 272.15 |  | MKWHr.
| Evening Peak Demand |  |  | 12569 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.1 |  | °C
| Minimum Generation of the Day |  |  | 9361.55 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 962.72 |  | MMCFD
| Maximum Generation of the Day |  |  | 12569 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.2436 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 46.695 | 0 | 3.8528 | 0 | 0 | 0.068637 | 0 | 0 | 50.6164 | Gas | 136.0195 | Gas | 445499514.466
| Chattogram Zone |  |  | 4.3858 | 25.02 | 0.98598 | 0 | 1.1023 | 0.16332 | 0 | 0.54432 | 32.2016 | Coal | 72.738 | Coal | 460010685.4966
| Cumilla Zone |  |  | 23.5872 | 0 | 3.6083 | 0 | 0 | 0.36047 | 1.4074 | 0 | 28.9633 | HFO | 13.2014 | HFO | 243591653.014
| Mymensingh Zone |  |  | 0.24192 | 0 | 4.2221 | 0 | 0 | 0.15298 | 0 | 0 | 4.617 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8411 | Hydro | 1.1023 | Hydro | 110226
| Khulna Zone |  |  | 0 | 10.1745 | 0 | 0 | 0 | 0.48312 | 21.7382 | 0 | 32.3959 | Solar | 2.4354 | Solar | 39153520.3748
| Barishal Zone |  |  | 5.492 | 33.0383 | 0 | 0 | 0 | 0.003753 | 0 | 0 | 38.534 | Import | 45.9772 | Import | 230030468.99
| Rajshahi Zone |  |  | 20.7766 | 0 | 0 | 0 | 0 | 0.4635 | 22.8317 | 0 | 44.0718 | Wind | 0.54432 | Wind | 7968844.8
| Rangpur Zone |  |  | 0 | 4.5052 | 0.53217 | 0 | 0 | 0.73961 | 0 | 0 | 5.777
| Total |  |  | 136.0195 | 72.738 | 13.2014 | 0 | 1.1023 | 2.4354 | 45.9772 | 0.54432 | 272.018
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 445499514.466 |  | Hydro | 110226
|  |  |  | Coal | 460010685.4966 |  | Solar | 39153520.3748
|  |  |  | HFO | 243591653.014 |  | Import | 230030468.99
|  |  |  | HSD | 0 |  | Wind | 7968844.8
[5 empty] | Total: | 142,63,64,913 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7382 | Peak Hr Flow | 910.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35510690.98 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.8317 | Peak Hr Flow | 1363.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 637 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4074 | Peak Hr Flow | 58.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 930 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.9772 | Peak Hr Flow | 2331.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4525
|  |  |  | Chattogram |  | 0 |  | 1317
|  |  |  | Cumilla |  | 0 |  | 1168
|  |  |  | Mymensingh |  | 0 |  | 983
|  |  |  | Sylhet |  | 0 |  | 402
|  |  |  | Khulna |  | 0 |  | 1340
|  |  |  | Barishal |  | 0 |  | 377
|  |  |  | Rajshahi |  | 0 |  | 1179
|  |  |  | Rangpur |  | 0 |  | 729
|  |  |  | Total |  | 0 |  | 12020
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 990 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1425.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 | 10:21 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D | [7 empty] | 4.0MW load
interrup.
| 08:07 | 10:21 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D | [7 empty] | 4.0MW load
interrup.
| 08:28 | 12:10 | Chandpur 132/33kV S/S 402T LT Scheduled S/D Due to 33kv Bus section high temperature | [7 empty] | 12.0MW load
|  |  | remove work | [7 empty] | interrup.
| 08:28 | 12:10 | Chandpur 132/33kV S/S 402T HT Scheduled S/D Due to 33kv bus section high temperature | [7 empty] | 12.0MW load
|  |  | remove work | [7 empty] | interrup.
| 08:28 | 10:50 | Chandpur 132/33kV S/S 412T HT Scheduled S/D Due to 33kv bus section high temperature
remove work
| 08:30 | 16:40 | Chowmuhani 132/33kV S/S TR3-435T HT Scheduled S/D Due to TR-3 33kv side CT loop red hot
maintenance.
| 08:30 | 16:41 | Chowmuhani 132/33kV S/S TR3-435T LT Scheduled S/D Due to TR-3 33kv side CT loop red hot
maintenance.
| 08:41 | 13:52 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to Disc
change work
| 08:52 | 17:28 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Bay Extension Work
| 09:02 | 12:44 | Ghorashal 230kV S/S TARFO-2 HT Project Work S/D Due to Shutdown requisition from | [7 empty] | 40.0MW load
|  |  | Project-1 for repair control cable and insulator bussing. | [7 empty] | interrup.
| 09:05 | 12:49 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to 33 kv Bus Maintenance by PDB | [7 empty] | 18.0MW load
interrup.
| 09:06 | 12:48 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to 33 kv Bus Maintenance by PDB
| 09:07 | 13:10 | Pabna 132/33kV S/S T-3 HT Forced S/D
| 09:07 | 13:11 | Pabna 132/33kV S/S T-3 LT Forced S/D
| 09:10 |  | Kallyanpur 132/33kV S/S GT-2 (132kV) LT Scheduled S/D Due to Oil Centrifuging
| 09:11 |  | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to Oil Centrifuging
| 09:12 | 16:56 | Rahanpur 400/132kV S/S AT-02 LT Project Work S/D Due to Due to project work.
| 09:13 | 16:55 | Rahanpur 400/132kV S/S AT-02 HT Project Work S/D Due to Due to project work.
| 09:13 | 12:53 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Scheduled S/D Due to 33 kv Bus Maintenance by PDB | [7 empty] | 18.0MW load
interrup.
| 09:13 | 12:52 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to 33 kv Bus Maintenance by PDB
| 09:13 | 16:23 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast Wall Construction
Work.
| 09:13 | 16:23 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast Wall Construction
Work.
| 09:14 | 14:28 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Blast Wall Construction
Work.
| 09:14 | 14:28 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Blast Wall Construction
Work.
| 09:18 | 10:39 | Rajbari 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Punch & Commission point
rectification work of 75MVA Transformer-2(LV Bushing oil leakage check & Rectification
work)
| 09:18 | 10:38 | Rajbari 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Punch & Commission point
rectification work of 75MVA Transformer-2(LV Bushing oil leakage check & Rectification
work)
| 09:40 | 17:40 | Cumilla(S) 132/33kV S/S 53.2MW Lakthanavi Scheduled S/D Due to Lakhdhanvi PP will work
for their Transformer Bus maintenance.
| 10:20 | 19:48 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Tripped showing MICOM P-127 relays Due to Due
to underground cable blast in 33kV R-Phase.
| 10:20 | 19:48 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Tripped showing MICOM P-122 relays Due to Due
to underground cable blast in 33kV R-Phase.
| 10:24 | 16:30 | Hasnabad 132/33kV S/S 33kv Reserve Bus Scheduled S/D Due to Red hot maintenance.
| 10:26 | 12:33 | Daudkandi-Sonargaon 132 kV Ckt-1 Forced S/D from Daudkandi 132/33kV end Due to
Maintenance Work for Sonergaon SS
| 10:30 | 11:52 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to Red hot maintenance.
| 10:31 | 10:43 | Goalpara 132/33kV S/S T-5 LT Tripped showing O/C Relay N0- 50/51 relays Due to ৩৩ কেভি | [7 empty] | 11.0MW load
|  |  | পিবিএস ফিডার সেনেরবাজার ও তেরোখাদায় ফল্ট হওয়ার কারনে উক্ত ট্রিপিং সংঘঠিত হয়। | [7 empty] | interrup.
| 10:31 | 10:44 | Goalpara 132/33kV S/S T-6 LT Tripped showing O/C Relay No- 50/51 relays Due to ৩৩ কেভি | [7 empty] | 11.0MW load
|  |  | পিবিএস ফিডার সেনেরবাজার ও তেরোখাদায় ফল্ট হওয়ার কারনে উক্ত ট্রিপিং সংঘঠিত হয়। | [7 empty] | interrup.
| 10:44 |  | Daudkandi-Sonargaon 132 kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to Corrective
maintenance due to high temperature.
|  | 10:52 | Chandpur 132/33kV S/S 412T LT is restored.
| 10:52 | 13:29 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Oil Leakage Maintenance in
main tank valve of Transformer-1
| 10:53 | 13:28 | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Oil Leakage Maintenance in
main tank valve of Transformer-1
|  | 11:11 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 11:16 | Barishal 230/132kV S/S T-4 LT is restored.
| 11:17 | 11:42 | Tangail 132/33kV S/S Tr-1 LT Tripped showing ABB REF 615 relays Due to Due to 33kv New | [7 empty] | 36.0MW load
|  |  | REB, Porabari, Ghatail REB Feeder Fault. | [7 empty] | interrup.
| 11:17 | 15:48 | Tangail 132/33kV S/S Tr-2 LT Tripped showing ABB REF 615 relays Due to Due to 33kv New | [7 empty] | 36.0MW load
|  |  | REB, Porabari, Ghatail REB Feeder Fault. | [7 empty] | interrup.
| 11:21 | 12:20 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to
Temperature Rising.
| 11:21 | 12:02 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to
Temperature Rising.
| 11:22 | 12:11 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to
Temperature Rising.
| 11:56 | 15:56 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Scheduled S/D Due to Red hot maintenance
| 12:00 |  | Day peak Generation is 10994 MW
| 12:01 | 16:00 | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to 33kv shakhipur feeder RED HOT.
| 12:01 | 15:58 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to 33kv shakhipur feeder RED HOT.
| 12:10 | 15:47 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33Kv T-2 BUS Fault
|  | 12:31 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 12:32 | Barishal 230/132kV S/S T-5 LT is restored.
| 13:27 | 17:08 | Ishurdi-Pabna 132kV ckt Forced S/D from Pabna 132/33kV end. | [7 empty] | 15.0MW load
interrup. Pabna
132/33kV end
| 13:56 | 20:47 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Insulator disc cleaning work
| 14:32 | 16:28 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to BLAST WALL CONSTRUCTION
| 14:32 | 16:29 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to BLAST WALL CONSTRUCTION
|  | 14:52 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
| 14:53 | 16:40 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Khulna PBS taken 33 KV bus shutdown
| 14:54 | 16:38 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Khulna PBS taken 33 KV bus shutdown
| 14:59 | 16:28 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Khulna PBS taken 33 KV bus shutdown
| 15:00 | 16:34 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Khulna PBS taken 33 KV bus shutdown
| 15:03 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO minimum @15:01 hrs [ Mr.
Fahad Mahmud, XEN]
|  | 15:25 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
| 15:26 | 19:07 | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing siemens
siprotec relays. and from Ghorashal 230kV end showing Distance protection relay relays
Due to Unknown
|  | 16:19 | Kulaura 132/33kV S/S TR-1 LT is restored.
|  | 16:19 | Kulaura 132/33kV S/S TR-1 HT is restored.
| 16:55 | 17:09 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Narshingdi 132/33kV end showing
Distance relays Due to N/A
| 17:01 |  | Patuakhali 1320 MW (RNPL) unit-1 was shutdown.
| 19:37 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:- FGMO Minimum @17:47 hrs.
| 20:16 |  | Haripur EGCB 412 MW CCPP ST tripped.
| 21:00 |  | Evening Peak Generation: 12568 MW.
| 21:07 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:- FGMO OFF @20:31 hrs.
| 22:00 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- FGMO OFF @20:31 [ Mr. Rayhan, AE]
| 22:54 |  | Haripur EGCB 412 MW CCPP ST synchronized.
| 22:54 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 23:22 |  | SS Power unit-2 was synchronized.
| 23:33 |  | Chandpur CCPP GT was synch.
| 06:00 |  | Min. Gen. 9315 MW
| 07:24 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to Project works.
| 07:36 |  | Bashundhara-Rampura 132 kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance
Protection (21/1): Z1 A B relays Due to Unknown.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 22 | 267636.36 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 232 | 7999200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9471000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 251 | 6987316 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 2004000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 220 | 5464593 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 59760 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 689760 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 115626 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 471000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 243000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 524160 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 387600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 573600 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 33873 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 317520 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 1005120 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 42240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 74880 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 68637 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 748440 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 12875455 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 17 | 192000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6085.764 | 2061.5 | 50616416.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 28177.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138240 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1102260 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 162 | 3840956 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 71091 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 112330 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 48 | 700800 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 544800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25082 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 35127 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 23400 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 15055 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 9659999 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 22 | 544320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 770 | 15360000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 1714 | 32201637.2
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4619000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8568100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6770000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 701352 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 831840 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 83 | 786182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 827528 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 53527 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 19500 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 1299840 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1407360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 135677 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 463670 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 614460 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 48 | 527520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 977280 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 360473 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1290 | 28963309
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 241920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 176 | 2536800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1459200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 146530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 226080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 298 | 4616980
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 985000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 132 | 3487009 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 5 | 200088 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 76992 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 644352 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1580160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 3390200 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 506469 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7202500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8665000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7670300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1426 | 34841070
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 910 | 21738181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Power evacuation problem in PGCB switchyard
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 483120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 620 | 10174550 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1530 | 32395851
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 8133090 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 9 | 171633 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 108 | 2674000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 20170181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2646350 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4735000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3753 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1778 | 38534007.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 157 | 3937182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4234145 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4173973 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 351 | 8375345.5 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 55944 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 13500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1363 | 22831663 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 150752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 299250 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2255.5 | 44071754.5
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1435199 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 120 | 3070000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 343603 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29605.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 188570 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 121766 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 588240 | -
Rangpur Area Total |  |  |  |  | 950 | 216 | 5776983.68
Eastern Grid Total |  |  |  |  | 16921.242 | 6789.5 | 151239412.56
Western Grid Total |  |  |  |  | 11614.5 | 5779.5 | 120778597
National Grid Total |  |  |  |  | 28535.742 | 12569 | 272018009.56
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8395.08 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3624.6 | MW
i) Dhaka area |  |  | 4525.08 |  | MW | i) Khulna area |  |  |  | 1340 | MW
ii) Chattogram area |  |  | 1317 |  | MW | ii) Barishal area |  |  |  | 377 | MW
iii) Cumilla area |  |  | 1168 |  | MW | iii) Rajshahi area |  |  |  | 1178.6 | MW
iv) Mymensingh area |  |  | 983 |  | MW | iv) Rangpur area |  |  |  | 729 | MW
v) Sylhet area |  |  | 402 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12019.68 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 68 | 18:00 | 133 | Payra | 24 | 00:00
2 | AKSML | 28 | 19:00 | 68 | Jamalpur | 110 | 18:00 | 134 | Postogola | 45 | 15:00
3 | Aftabnagar | 28 | 00:00 | 69 | Jashore | 109 | 19:00 | 135 | Purbachal | 15 | 00:00
4 | Agargaon | 83 | 20:00 | 70 | Jhenaidah | 96 | 19:00 | 136 | Purbasadipur | 118 | 13:00
5 | Agrabad | 90 | 20:00 | 71 | Joydebpur | 142 | 12:00 | 137 | Rahanpur | 23 | 09:00
6 | Amnura | 40 | 13:00 | 72 | Joypurhat | 62 | 13:00 | 138 | Rahim | 39 | 00:00
7 | Ashuganj | 78 | 00:00 | 73 | Juldah | 15 | 01:00 | 139 | Rajbari | 54 | 03:00
8 | BSRM | 201 | 23:00 | 74 | KSRM | 42 | 11:00 | 140 | Rajendrapur | 110 | 13:00
9 | Bagerhat | 71 | 19:00 | 75 | Kabirpur | 242 | 10:00 | 141 | Rajshahi | 123 | 13:00
10 | Bajitpur | 36 | 18:00 | 76 | Kachua | 69 | 00:00 | 142 | Rajshahi-230 | 54 | 04:00
11 | Bakulia | 90 | 13:00 | 77 | Kallyanpur | 87 | 00:00 | 143 | Ramganj | 110 | 00:00
12 | Banani | 27 | 23:00 | 78 | Kalurghat | 36 | 17:00 | 144 | Rampur | 38 | 23:00
13 | Bangabhaban | 5 | 10:00 | 79 | Kamrangirchar | 64.6 | 13:00 | 145 | Rangamati | 15 | 18:30
14 | Barapukuria | 63 | 10:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 135 | 18:00
15 | Barguna | 16 | 00:00 | 81 | Kasba | 27 | 01:00 | 147 | Ruppur | 3.8 | 15:00
16 | Barishal | 94 | 11:00 | 82 | Kazla | 90 | 16:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 76 | 19:00 | 83 | Keranigonj | 66 | 19:30 | 149 | Saidpur | 109 | 15:00
18 | Baroaulia | 54 | 11:00 | 84 | Khagrachori | 28 | 18:00 | 150 | Satkhira | 102 | 18:30
19 | Baroirhat | 52 | 20:00 | 85 | Khulna | 70 | 19:00 | 151 | Satmasjid | 84 | 20:00
20 | Bashundhara | 144 | 21:00 | 86 | Khulshi | 144 | 14:00 | 152 | Savar | 196 | 14:00
21 | BashundharaCement | 8 | 19:30 | 87 | Kishoreganj | 114 | 18:00 | 153 | SevenRings | 19.82 | 21:00
22 | Beanibazar | 44 | 04:00 | 88 | Kodda | 281 | 09:00 | 154 | ShahCement | 38 | 00:00
23 | Benapole | 50 | 09:00 | 89 | Kulaura | 26 | 00:00 | 155 | Shahjadpur | 69 | 09:00
24 | Bhaluka | 127 | 13:00 | 90 | Kurigram | 60 | 18:00 | 156 | Shahjibazar | 92 | 21:00
25 | Bhandaria | 41 | 00:00 | 91 | Kushtia | 106 | 13:00 | 157 | Shahmirpur | 51.5 | 00:00
26 | Bhangura | 28 | 03:00 | 92 | Lalbag | 61 | 17:00 | 158 | Shariatpur | 63 | 00:00
27 | Bheramara(GK) | 42 | 19:00 | 93 | Lalmonirhat | 56 | 18:00 | 159 | Sherpur | 144 | 18:00
28 | Bhulta | 253 | 17:00 | 94 | MI_Cement | 18 | 11:00 | 160 | Shikalbaha | 25 | 23:00
29 | Bog-Sherpur | 56 | 09:00 | 95 | Madanganj | 42 | 00:00 | 161 | Shitalakhya | 68.6 | 13:00
30 | Bogura | 130 | 16:00 | 96 | Madaripur | 80 | 21:00 | 162 | Sholosohor | 40 | 14:00
31 | Borhanuddin | 70 | 21:00 | 97 | Madartek | 70.15 | 22:00 | 163 | Shyampur | 174 | 10:00
32 | Brahmanbaria | 99 | 00:00 | 98 | Madunaghat | 45 | 18:30 | 164 | Siddhirganj | 114 | 11:00
33 | Cantonment | 102 | 00:00 | 99 | Magura | 48 | 19:00 | 165 | Sirajganj | 84 | 20:00
34 | Chandpur | 56 | 01:00 | 100 | Mahasthangarh | 64 | 09:00 | 166 | Sonargaon | 112 | 08:00
35 | Chandraghona | 32 | 20:00 | 101 | Manikganj | 99 | 19:00 | 167 | Sreemongol | 52 | 21:00
36 | Chapai | 56 | 13:00 | 102 | Maniknagar | 52 | 13:00 | 168 | Sreepur | 83 | 08:00
37 | Charsaidpur | 46 | 07:00 | 103 | Matarbari | 47 | 20:00 | 169 | Srinagar | 34.2 | 21:00
38 | Chauddagram | 66 | 00:00 | 104 | Matuail | 65 | 11:00 | 170 | Sunamganj | 38 | 20:00
39 | Chhatak | 23 | 13:00 | 105 | Millgate | 71 | 12:00 | 171 | Sylhet | 31 | 16:00
40 | Chowmuhani | 189 | 00:00 | 106 | Mirpur | 113 | 14:00 | 172 | Sylhet-132 | 81 | 13:00
41 | Chuadanga | 76 | 19:00 | 107 | Mirsorai | 9 | 00:00 | 173 | TK | 21 | 21:00
42 | Coxsbazar | 125 | 19:00 | 108 | Mirzapur | 38 | 09:00 | 174 | Tangail | 150 | 22:00
43 | Cumilla(N) | 129 | 20:00 | 109 | Mithapukur | 52 | 04:00 | 175 | Thakurgaon | 84 | 14:00
44 | Cumilla(S) | 150 | 00:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 126 | 11:00
45 | Daudkandi | 121 | 21:00 | 111 | Mogbazar | 110.1 | 14:00 | 177 | Ullahpara | 26 | 09:00
46 | Dhaka | 36 | 11:00 | 112 | Mongla | 30 | 19:00 | 178 | Ullon | 39 | 18:30
47 | Dhamrai | 114 | 09:00 | 113 | Motijheel | 29 | 12:00 | 179 | Uttara | 67 | 12:00
48 | Dhanmondi | 107 | 12:00 | 114 | Muktagacha | 33 | 14:00 | 180 | UttaraNew | 36 | 21:00
49 | Dohazari | 111 | 19:30 | 115 | Munshiganj | 105 | 00:00 | 181 | Zigatola | 56 | 00:00
50 | Faridpur | 139 | 21:00 | 116 | Muradnagar | 22 | 00:00
51 | Fatullah | 89 | 10:00 | 117 | Mymensingh | 174 | 18:00
52 | Fenchuganj | 26 | 04:00 | 118 | Naogaon | 97 | 22:00
53 | Feni | 99 | 00:00 | 119 | Narail | 44 | 19:00
54 | GPH | 93 | 02:00 | 120 | Narinda | 68 | 14:00
55 | Ghatail | 74 | 17:00 | 121 | Narshingdi | 167 | 00:00
56 | Ghorashal | 14 | 11:00 | 122 | Natore | 117 | 21:00
57 | Ghorashal-230 | 75 | 21:00 | 123 | Nawabganj | 40 | 21:00
58 | Goalpara | 28 | 00:00 | 124 | Netrakona | 137 | 18:00
59 | Gollamari | 72 | 00:00 | 125 | New | 77.5 | 14:00
60 | Gopalganj | 84 | 21:00 | 126 | Niamatpur | 86 | 14:00
61 | Gulshan | 78 | 13:00 | 127 | Noapara | 38 | 19:00
62 | Halishahar | 66 | 15:00 | 128 | PHP | 8 | 19:00
63 | HaripurSBU | 160 | 10:00 | 129 | Pabna | 88 | 18:00
64 | Hasnabad | 68 | 21:00 | 130 | Palashbari | 99 | 18:00
65 | Hathazari | 73 | 22:00 | 131 | Panchagarh | 48 | 18:00
66 | Ishurdi | 54 | 13:00 | 132 | Patuakhali | 61 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11527.1 | 0 |  | 11527.1
1:00 | 11004.52 | 0 |  | 11004.52
2:00 | 10603.31 | 0 |  | 10603.31
3:00 | 10874.31 | 0 |  | 10874.31
4:00 | 11151.33 | 0 |  | 11151.33
5:00 | 10162.15 | 0 |  | 10162.15
6:00 | 9361.55 | 0 |  | 9361.55
7:00 | 9562.92 | 0 |  | 9562.92
8:00 | 10219.72 | 0 |  | 10219.72
9:00 | 10739.72 | 0 |  | 10739.72
10:00 | 10656.26 | 0 |  | 10656.26
11:00 | 10750.53 | 0 |  | 10750.53
12:00 | 10998.41 | 25 |  | 11024.41
13:00 | 11281.14 | 22 |  | 11304.14
14:00 | 11535.5 | 30 |  | 11566.5
15:00 | 11318.72 | 30 |  | 11349.72
16:00 | 11427.63 | 25 |  | 11453.63
17:00 | 11695.47 | 0 |  | 11695.47
18:00 | 12011.19 | 0 |  | 12011.19
19:00 | 12335.05 | 0 |  | 12335.05
19:30 | 12452 | 0 |  | 12452
20:00 | 12492.39 | 0 |  | 12492.39
21:00 | 12569 | 0 |  | 12569
22:00 | 12484 | 0 |  | 12484
23:00 | 11882 | 0 |  | 11882
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6555 | 4972.1 | 11527.1 | DAILY GENERATION CURVE
00:30 | 6389.5 | 4876.31 | 11265.81
01:00 | 6224 | 4780.52 | 11004.52 | 22-03-2025
01:30 | 6102.5 | 4701.415 | 10803.915
02:00 | 5981 | 4622.31 | 10603.31
02:30 | 6056.5 | 4682.31 | 10738.81
03:00 | 6132 | 4742.31 | 10874.31
03:30 | 6132 | 4880.82 | 11012.82
04:00 | 6132 | 5019.33 | 11151.33
04:30 | 5756.5 | 4900.24 | 10656.74
05:00 | 5381 | 4781.15 | 10162.15
05:30 | 5123.5 | 4638.35 | 9761.85
06:00 | 4866 | 4495.55 | 9361.55
06:30 | 4935.56 | 4526.675 | 9462.235
07:00 | 5005.12 | 4557.8 | 9562.92
07:30 | 5305.51 | 4585.81 | 9891.32
08:00 | 5605.9 | 4613.82 | 10219.72
08:30 | 5800.425 | 4679.295 | 10479.72
09:00 | 5994.95 | 4744.77 | 10739.72
09:30 | 5948.73 | 4749.26 | 10697.99
10:00 | 5902.51 | 4753.75 | 10656.26
10:30 | 5917.93 | 4785.465 | 10703.395
11:00 | 5933.35 | 4817.18 | 10750.53
11:30 | 6043.215 | 4831.255 | 10874.47
12:00 | 6153.08 | 4845.33 | 10998.41
12:30 | 6263 | 4876.775 | 11139.775
13:00 | 6372.92 | 4908.22 | 11281.14
13:30 | 6454.295 | 4954.025 | 11408.32
14:00 | 6535.67 | 4999.83 | 11535.5
14:30 | 6493.865 | 4933.245 | 11427.11
15:00 | 6452.06 | 4866.66 | 11318.72
15:30 | 6555.1 | 4818.075 | 11373.175
16:00 | 6658.14 | 4769.49 | 11427.63
16:30 | 6742.66 | 4818.89 | 11561.55
17:00 | 6827.18 | 4868.29 | 11695.47
17:30 | 6932.505 | 4920.825 | 11853.33
18:00 | 7037.83 | 4973.36 | 12011.19
18:30 | 7107.415 | 5065.705 | 12173.12
19:00 | 7177 | 5158.05 | 12335.05
19:30 | 7048.5 | 5403.5 | 12452
20:00 | 6934.5 | 5557.89 | 12492.39
20:30 | 6862 | 5668.695 | 12530.695 |  | Executive Engineer
21:00 | 6789.5 | 5779.5 | 12569 |  | Network Operation Division
21:30 | 6788 | 5738.5 | 12526.5
22:00 | 6786.5 | 5697.5 | 12484
22:30 | 6640 | 5543 | 12183
23:00 | 6493.5 | 5388.5 | 11882

## En-Curve
QF-LDC-12
Date | 22-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3673 | 2231.5 | 903 | 0 | 70 | 860.6 | 46 | 3088 | 0 | 142 | 465 | 0 | 0 | 48 | 0 | DAILY ENERGY CURVE
00:30 | 3634 | 2179.25 | 903.5 | 0 | 71 | 842.06 | 46 | 2958 | 0 | 134 | 446 | 0 | 0 | 52 | 0 | 22-03-2025
01:00 | 3595 | 2127 | 904 | 0 | 72 | 823.52 | 46 | 2828 | 0 | 126 | 427 | 0 | 0 | 56 | 0
01:30 | 3549.5 | 2104.5 | 904 | 0 | 66 | 823.415 | 46 | 2746 | 0 | 109.5 | 403.5 | 0 | 0 | 51.5 | 0 | Energy Generated | 272.018 |  | MKWHr
02:00 | 3504 | 2082 | 904 | 0 | 60 | 823.31 | 46 | 2664 | 0 | 93 | 380 | 0 | 0 | 47 | 0 | Energy not Served | 0.132 |  | MKWHr
02:30 | 3541 | 2122 | 904 | 0 | 62 | 843.31 | 46 | 2679.5 | 0 | 110 | 388.5 | 0 | 0 | 42.5 | 0 | Total Energy Requirement | 272.15 |  | MKWHr
03:00 | 3578 | 2162 | 904 | 0 | 64 | 863.31 | 46 | 2695 | 0 | 127 | 397 | 0 | 0 | 38 | 0
03:30 | 3632.5 | 2132.5 | 904 | 0 | 66 | 887.82 | 46 | 2781 | 0 | 126 | 400.5 | 0 | 0 | 36.5 | 0
04:00 | 3687 | 2103 | 904 | 0 | 68 | 912.33 | 46 | 2867 | 0 | 125 | 404 | 0 | 0 | 35 | 0
04:30 | 3520.5 | 1920.75 | 904.5 | 0 | 66 | 867.49 | 46 | 2840.5 | 0 | 108 | 358.5 | 0 | 0 | 24.5 | 0
05:00 | 3354 | 1738.5 | 905 | 0 | 64 | 822.65 | 46 | 2814 | 0 | 91 | 313 | 0 | 0 | 14 | 0
05:30 | 3263 | 1662 | 904.5 | 0 | 63 | 822.85 | 46 | 2674.5 | 0 | 66 | 252.5 | 0 | 0 | 7.5 | 0
06:00 | 3172 | 1585.5 | 904 | 0 | 62 | 823.05 | 46 | 2535 | 0 | 41 | 192 | 0 | 0 | 1 | 0
06:30 | 3224 | 1610.85 | 901.5 | 0 | 59 | 824.5 | 46 | 2559.5 | 17.885 | 41 | 177.5 | 0 | 0 | 0.5 | 0
07:00 | 3276 | 1636.2 | 899 | 0 | 56 | 825.95 | 46 | 2584 | 35.77 | 41 | 163 | 0 | 0 | 0 | 0
07:30 | 3318 | 1744.35 | 884.5 | 0 | 55 | 823.555 | 46 | 2668 | 81.415 | 58 | 212.5 | 0 | 0 | 0 | 0
08:00 | 3360 | 1852.5 | 870 | 0 | 54 | 821.16 | 46 | 2752 | 127.06 | 75 | 262 | 0 | 0 | 0 | 0
08:30 | 3407.5 | 1937 | 870 | 0 | 45 | 823.575 | 46 | 2850.5 | 146.645 | 79.5 | 274 | 0 | 0 | 0 | 0
09:00 | 3455 | 2021.5 | 870 | 0 | 36 | 825.99 | 46 | 2949 | 166.23 | 84 | 286 | 0 | 0 | 0 | 0
09:30 | 3386 | 2019.25 | 886.5 | 0 | 46 | 826.7 | 46 | 2944 | 206.04 | 88 | 248 | 0 | 0 | 1.5 | 0
10:00 | 3317 | 2017 | 903 | 0 | 56 | 827.41 | 46 | 2939 | 245.85 | 92 | 210 | 0 | 0 | 3 | 0
10:30 | 3348.5 | 2031.5 | 902.5 | 0 | 55 | 826.37 | 46 | 2949.5 | 257.025 | 92 | 192.5 | 0 | 0 | 2.5 | 0
11:00 | 3380 | 2046 | 902 | 0 | 54 | 825.33 | 46 | 2960 | 268.2 | 92 | 175 | 0 | 0 | 2 | 0
11:30 | 3471 | 2068.5 | 902.5 | 0 | 55 | 824.89 | 46 | 2953.5 | 275.08 | 92 | 183 | 0 | 0 | 3 | 12.5
12:00 | 3562 | 2091 | 903 | 0 | 56 | 824.45 | 46 | 2947 | 281.96 | 92 | 191 | 0 | 0 | 4 | 25
12:30 | 3607.5 | 2148.5 | 905 | 0 | 61 | 822.435 | 46 | 2948.5 | 291.34 | 75 | 221 | 0 | 0 | 13.5 | 23.5
13:00 | 3653 | 2206 | 907 | 0 | 66 | 820.42 | 46 | 2950 | 300.72 | 58 | 251 | 0 | 0 | 23 | 22
13:30 | 3668 | 2243.5 | 907 | 0 | 61 | 851.435 | 46 | 2959 | 311.885 | 57 | 274 | 0 | 0 | 29.5 | 26
14:00 | 3683 | 2281 | 907 | 0 | 56 | 882.45 | 46 | 2968 | 323.05 | 56 | 297 | 0 | 0 | 36 | 30
14:30 | 3692.5 | 2238.5 | 906.5 | 0 | 57 | 873.39 | 46 | 2894.5 | 316.72 | 53 | 300.5 | 0 | 0 | 48.5 | 30
15:00 | 3702 | 2196 | 906 | 0 | 58 | 864.33 | 46 | 2821 | 310.39 | 50 | 304 | 0 | 0 | 61 | 30
15:30 | 3748.5 | 2219.5 | 906 | 0 | 58 | 864.13 | 46 | 2790.5 | 256.045 | 84 | 340 | 0 | 0 | 60.5 | 27.5
16:00 | 3795 | 2243 | 906 | 0 | 58 | 863.93 | 46 | 2760 | 201.7 | 118 | 376 | 0 | 0 | 60 | 25
16:30 | 3762 | 2251.25 | 906 | 0 | 56 | 908.475 | 46 | 2821 | 150.825 | 136.5 | 474 | 0 | 0 | 49.5 | 12.5
17:00 | 3729 | 2259.5 | 906 | 0 | 54 | 953.02 | 46 | 2882 | 99.95 | 155 | 572 | 0 | 0 | 39 | 0
17:30 | 3629 | 2230 | 906 | 0 | 57 | 1012.58 | 46 | 2972.5 | 53.25 | 184.5 | 728 | 4 | 0 | 30.5 | 0
18:00 | 3529 | 2200.5 | 906 | 0 | 60 | 1072.14 | 46 | 3063 | 6.55 | 214 | 884 | 8 | 0 | 22 | 0
18:30 | 3557 | 2205.5 | 884.5 | 0 | 57 | 1127.845 | 46 | 3119 | 3.275 | 221 | 928 | 4 | 0 | 20 | 0
19:00 | 3585 | 2210.5 | 863 | 0 | 54 | 1183.55 | 46 | 3175 | 0 | 228 | 972 | 0 | 0 | 18 | 0
19:30 | 3503 | 2222 | 863 | 0 | 58 | 1239 | 46 | 3520 | 0 | 180 | 798 | 0 | 0 | 23 | 0
20:00 | 3480 | 2202 | 862 | 0 | 62 | 1368.39 | 46 | 3567 | 0 | 143 | 738 | 0 | 0 | 24 | 0
20:30 | 3485.5 | 2223 | 886 | 0 | 60 | 1365.695 | 46 | 3651 | 0 | 118 | 672.5 | 0 | 0 | 23 | 0
21:00 | 3491 | 2244 | 910 | 0 | 58 | 1363 | 46 | 3735 | 0 | 93 | 607 | 0 | 0 | 22 | 0
21:30 | 3491 | 2274.5 | 910 | 0 | 58 | 1359.5 | 46 | 3650.5 | 0 | 93 | 632 | 0 | 0 | 12 | 0
22:00 | 3491 | 2305 | 910 | 0 | 58 | 1356 | 46 | 3566 | 0 | 93 | 657 | 0 | 0 | 2 | 0
22:30 | 3445 | 2308.5 | 910 | 0 | 61 | 1284.5 | 46 | 3454 | 0 | 80.5 | 589.5 | 0 | 0 | 4 | 0
23:00 | 3399 | 2312 | 910 | 0 | 64 | 1213 | 46 | 3342 | 0 | 68 | 522 | 0 | 0 | 6 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 402 | 04:00 | 390 | 00:00 | Payra | 418 | 14:00 | 413 | 00:00
Ashuganj | 409 | 6:00 | 389 | 12:00 | Rahanpur | 401 | 02:00 | 385 | 21:00
Bhulta | 408 | 05:00 | 392 | 11:00 | Rampal | 410 | 05:00 | 398 | 21:00
Bibiana | 398 | 00:00 | 389 | 11:00
BIPTC | 400 | 04:00 | 393 | 10:00
Bogura | 389 | 06:00 | 370 | 21:00
Gopalganj | 409 | 05:00 | 399 | 21:00
Kaliakoir | 377 | 18:00 | 361 | 15:00
Madunaghat | 400 | 06:00 | 392 | 22:00
Meghnaghat | 404 | 04:00 | 394 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 18:30 | 226 | 11:00 | Keranigonj | 233 | 04:00 | 225 | 11:00
AKSML | 236 | 05:00 | 227 | 22:00 | Khulna(S) | 239 | 05:00 | 228 | 20:00
Aminbazar | 235 | 05:00 | 228 | 13:00 | Madunaghat | 237 | 18:00 | 134 | 09:00
Ashuganj | 235 | 01:00 | 228 | 11:00 | Madunaghat-400 | 236 | 06:00 | 230 | 22:00
Ashuganj-400 | 236 | 6:00 | 222 | 12:00 | Maniknagar | 231 | 05:00 | 222 | 11:00
Baghabari | 237 | 05:00 | 228 | 16:00 | Meghnaghat | 240 | 18:00 | 231 | 11:00
Barapukuria | 225 | 05:00 | 218 | 09:00 | Meghnaghat-400 | 234 | 18:30 | 226 | 11:00
Barapukuria-230 | 225 | 6:00 | 220 | 10:00 | Mirsorai | 232 | 09:00 | 224 | 23:00
Barishal | 239 | 06:00 | 234 | 22:00 | Rajshahi | 235 | 05:00 | 222 | 13:00
Bheramara | 236 | 05:00 | 223 | 17:00 | Rampal | 237 | 05:00 | 227 | 22:00
Bhulta | 232 | 05:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 05:00 | 225 | 11:00 | Rampura | 238 | 18:30 | 222 | 11:00
BIPTC | 238 | 05:00 | 223 | 18:00 | Shikalbaha | 231 | 04:00 | 225 | 23:00
Bogura | 239 | 05:00 | 228 | 21:00 | Shyampur | 232 | 04:00 | 225 | 11:00
Bogura-400 | 238 | 05:00 | 228 | 17:00 | Siddhirganj | 233 | 04:00 | 225 | 11:00
Borhanuddin | 242 | 06:00 | 238 | 17:00 | Sirajgonj | 243 | 05:00 | 237 | 21:00
BSRM | 232 | 09:00 | 224 | 23:00 | Sreepur | 235 | 05:00 | 228 | 12:00
Cumilla(N) | 229 | 05:00 | 222 | 12:00 | Tongi | 230 | 04:00 | 220 | 15:00
Faridpur | 238 | 05:00 | 232 | 19:30
Fenchuganj | 236 | 03:00 | 230 | 11:00
Ghorashal | 236 | 01:00 | 230 | 00:00
Ghorashal-230 | 232 | 04:00 | 223 | 11:00
Gopalganj | 236 | 05:00 | 230 | 21:00
GPH | 234 | 18:30 | 226 | 23:00
Haripur | 233 | 18:30 | 222 | 11:00
Hasnabad | 233 | 05:00 | 222 | 17:00
Hathazari | 235 | 07:00 | 229 | 21:00
Ishurdi | 238 | 05:00 | 226 | 17:00
Jhenaidah | 235 | 05:00 | 222 | 17:00
Kaliakoir | 235 | 18:00 | 225 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 01:00 | 132 | 11:00 | Madunaghat | 136 | 18:00 | 130 | 21:00
Agargaon | 140 | 03:00 | 135 | 11:00 | Magura | 137 | 04:00 | 126 | 17:00
Agrabad | 132 | 03:00 | 128 | 21:00 | Mahasthangarh | 133 | 02:00 | 126 | 12:00
AKS | 132 | 02:00 | 127 | 21:00 | Manikganj | 131 | 02:00 | 122 | 12:00
Aminbazar | 137 | 18:00 | 131 | 13:00 | Maniknagar | 136 | 04:00 | 130 | 11:00
Amnura | 138 | 05:00 | 128 | 10:00 | Matarbari | 122 | 09:00 | 110 | 23:00
Ashuganj | 139 | 01:00 | 135 | 11:00 | Matuail | 135 | 06:00 | 129 | 11:00
Bagerhat | 137 | 05:00 | 126 | 18:00 | Millgate | 140 | 03:00 | 130 | 15:00
Bajitpur | 134 | 03:00 | 130 | 14:00 | Mirpur | 137 | 02:00 | 130 | 11:00
Bakulia | 135 | 05:00 | 129 | 21:00 | Mirzapur | 132 | 03:00 | 124 | 14:00
Banani | 138 | 01:00 | 132 | 11:00 | Mithapukur | 133 | 05:00 | 124 | 09:00
Bangabhaban | 136 | 05:00 | 130 | 11:00 | MI_Cement | 135 | 05:00 | 129 | 11:00
Barapukuria | 139 | 05:00 | 131 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 136 | 05:00 | 133 | 19:30 | Mogbazar | 140 | 04:00 | 134 | 12:00
Barishal | 134 | 05:00 | 130 | 00:00 | Mongla | 137 | 05:00 | 127 | 19:00
Barishal-230 | 135 | 09:00 | 131 | 12:00 | Motijheel | 136 | 06:00 | 130 | 11:00
Baroaulia | 133 | 05:00 | 130 | 00:00 | Muktagacha | 134 | 05:00 | 122 | 17:00
Baroirhat | 126 | 05:00 | 120 | 15:00 | Munshiganj | 136 | 18:00 | 128 | 11:00
Bashundhara | 140 | 05:00 | 131 | 11:00 | Muradnagar | 130 | 18:30 | 123 | 11:00
BashundharaCement | 132 | 03:00 | 126 | 12:00 | Mymensingh | 135 | 05:00 | 118 | 18:00
Beanibazar | 133 | 05:00 | 130 | 11:00 | Naogaon | 132 | 04:00 | 123 | 12:00
Benapole | 134 | 04:00 | 128 | 14:00 | Narail | 139 | 05:00 | 126 | 21:00
Bhaluka | 128 | 00:00 | 123 | 13:00 | Narinda | 136 | 4:00 | 130 | 23:00
Bhandaria | 130 | 06:00 | 125 | 00:00 | Narshingdi | 134 | 18:00 | 124 | 12:00
Bhangura | 137 | 06:00 | 129 | 16:00 | Natore | 135 | 05:00 | 127 | 13:00
Bheramara | 136 | 05:00 | 129 | 12:00 | Nawabganj | 141 | 05:00 | 134 | 12:00
Bheramara(GK) | 136 | 05:00 | 128 | 17:00 | Netrakona | 126 | 00:00 | 116 | 18:00
Bhulta | 130 | 18:30 | 124 | 11:00 | New | 140 | 06:00 | 132 | 11:00
Bog-Sherpur | 135 | 05:00 | 127 | 09:00 | Niamatpur | 137 | 00:00 | 130 | 21:00
Bogura | 136 | 05:00 | 129 | 09:00 | Noapara | 136 | 05:00 | 128 | 21:00
Bogura-230 | 136 | 05:00 | 129 | 09:00 | Pabna | 137 | 05:00 | 125 | 16:00
Brahmanbaria | 139 | 21:00 | 127 | 12:00 | Palashbari | 131 | 05:00 | 121 | 17:00
Cantonment | 141 | 05:00 | 135 | 11:00 | Panchagarh | 136 | 18:30 | 116 | 12:00
Chandpur | 127 | 18:00 | 115 | 11:00 | Patuakhali | 135 | 05:00 | 133 | 15:00
Chandraghona | 135 | 05:00 | 130 | 21:00 | Payra | 137 | 05:00 | 135 | 00:00
Chapai | 135 | 02:00 | 129 | 11:00 | PHP | 125 | 18:30 | 118 | 11:00
Charsaidpur | 135 | 18:30 | 128 | 11:00 | Postogola | 137 | 04:00 | 132 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 127 | 18:00 | 119 | 12:00 | Purbachal | 140 | 05:00 | 132 | 11:00
Chhatak | 134 | 05:00 | 130 | 10:00 | Purbasadipur | 132 | 18:30 | 119 | 09:00
Chowmuhani | 123 | 18:00 | 112 | 00:00 | Rahanpur | 138 | 01:00 | 132 | 10:00
Chuadanga | 138 | 05:00 | 126 | 22:00 | Rahanpur-400 | 138 | 01:00 | 132 | 10:00
Coxsbazar | 123 | 09:00 | 112 | 21:00 | Rahim | 134 | 01:00 | 129 | 11:00
Cumilla(N) | 131 | 05:00 | 125 | 11:00 | Rajbari | 133 | 05:00 | 129 | 17:00
Cumilla(S) | 130 | 03:00 | 123 | 21:00 | Rajendrapur | 135 | 18:30 | 122 | 16:00
Daudkandi | 129 | 18:30 | 121 | 11:00 | Rajshahi | 137 | 05:00 | 128 | 13:00
Dhaka | 138 | 01:00 | 132 | 11:00 | Rajshahi-230 | 136 | 01:00 | 124 | 10:00
Dhamrai | 135 | 05:00 | 128 | 11:00 | Ramganj | 122 | 18:30 | 113 | 02:00
Dhanmondi | 140 | 05:00 | 132 | 12:00 | Rampur | 133 | 04:00 | 129 | 13:00
Dohazari | 129 | 07:00 | 123 | 21:00 | Rampura | 139 | 04:00 | 132 | 11:00
Faridpur | 134 | 06:00 | 130 | 21:00 | Rangamati | 134 | 06:00 | 129 | 21:00
Fatullah | 136 | 04:00 | 130 | 11:00 | Rangpur | 130 | 04:00 | 119 | 17:00
Fenchuganj | 136 | 00:00 | 133 | 11:00 | Ruppur | 138 | 05:00 | 130 | 21:00
Feni | 124 | 09:00 | 116 | 15:00 | Saidpur | 134 | 18:30 | 120 | 09:00
Ghatail | 132 | 05:00 | 122 | 15:00 | Satkhira | 137 | 05:00 | 126 | 19:00
Ghorashal | 140 | 01:00 | 134 | 11:00 | Satmasjid | 140 | 02:00 | 135 | 11:00
Goalpara | 139 | 05:00 | 131 | 18:00 | Savar | 138 | 18:00 | 128 | 11:00
Gollamari | 139 | 05:00 | 131 | 18:30 | SevenRings | 140 | 04:00 | 132 | 12:00
Gopalganj | 139 | 05:00 | 132 | 19:00 | ShahCement | 135 | 18:30 | 128 | 11:00
Gopalganj-400 | 139 | 04:00 | 136 | 15:00 | Shahjadpur | 141 | 02:00 | 132 | 16:00
Gulshan | 139 | 05:00 | 130 | 00:00 | Shahjibazar | 133 | 02:00 | 129 | 11:00
Halishahar | 134 | 05:00 | 130 | 18:00 | Shahmirpur | 134 | 10:00 | 130 | 21:00
Haripur | 136 | 18:30 | 130 | 11:00 | Shariatpur | 138 | 07:00 | 133 | 21:00
HaripurSBU | 136 | 18:30 | 130 | 11:00 | Sherpur | 137 | 22:00 | 121 | 17:00
Hasnabad | 135 | 01:00 | 131 | 12:00 | Shikalbaha | 124 | 06:00 | 119 | 00:00
Hathazari | 136 | 03:00 | 131 | 11:00 | Shikalbaha-230 | 135 | 05:00 | 130 | 23:00
Ishurdi | 139 | 05:00 | 131 | 17:00 | Shitalakhya | 135 | 05:00 | 129 | 11:00
Jaldhaka | 131 | 06:00 | 119 | 09:00 | Sholosohor | 134 | 05:00 | 131 | 00:00
Jamalpur | 140 | 21:00 | 125 | 17:00 | Shyampur | 133 | 00:00 | 130 | 13:00
Jashore | 137 | 05:00 | 126 | 18:00 | Shyampur-230 | 135 | 04:00 | 130 | 11:00
Jhenaidah | 137 | 04:00 | 128 | 17:00 | Siddhirganj | 135 | 04:00 | 130 | 11:00
Jhenaidah-230 | 138 | 05:00 | 128 | 17:00 | Sirajganj | 134 | 00:00 | 126 | 09:00
Joydebpur | 137 | 03:00 | 126 | 10:00 | Sonargaon | 133 | 05:00 | 125 | 13:00
Joypurhat | 130 | 06:00 | 120 | 12:00 | Sreemongol | 134 | 18:00 | 129 | 11:00
Juldah | 134 | 05:00 | 130 | 00:00 | Sreepur | 132 | 05:00 | 127 | 11:00
Kabirpur | 138 | 03:00 | 126 | 15:00 | Srinagar | 141 | 18:30 | 134 | 11:00
Kachua | 126 | 18:00 | 118 | 15:00 | SSM | 139 | 05:00 | 130 | 00:00
Kaliakoir | 137 | 18:30 | 128 | 11:00 | Sunamganj | 132 | 05:00 | 129 | 11:00
Kallyanpur | 137 | 03:00 | 131 | 11:00 | Sylhet | 134 | 01:00 | 131 | 11:00
Kalurghat | 134 | 03:00 | 131 | 10:00 | Sylhet-132 | 134 | 05:00 | 132 | 14:00
Kamrangirchar | 141 | 18:30 | 134 | 11:00 | Tangail | 132 | 05:00 | 122 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 18:30 | 116 | 12:00
Kasba | 129 | 18:30 | 122 | 11:00 | TK | 135 | 04:00 | 131 | 21:00
Kazla | 136 | 04:00 | 130 | 12:00 | Tongi | 141 | 04:00 | 134 | 11:00
Keranigonj | 141 | 04:00 | 135 | 11:00 | Ullahpara | 136 | 00:00 | 127 | 17:00
Khagrachori | 133 | 05:00 | 129 | 20:00 | Ullon | 139 | 05:00 | 132 | 11:00
Khulna | 137 | 05:00 | 128 | 19:00 | Uttara | 137 | 04:00 | 129 | 11:00
Khulna(S) | 139 | 05:00 | 131 | 19:00 | UttaraNew | 140 | 05:00 | 130 | 11:00
Khulshi | 133 | 05:00 | 128 | 14:00 | Zigatola | 141 | 06:00 | 140 | 18:30
Kishoreganj | 132 | 00:00 | 125 | 18:00
Kodda | 136 | 18:00 | 122 | 15:00
KSRM | 135 | 06:00 | 129 | 19:30
Kulaura | 135 | 04:00 | 132 | 11:00
Kurigram | 131 | 06:00 | 120 | 08:00
Kushtia | 137 | 05:00 | 128 | 17:00
Lalbag | 141 | 05:00 | 133 | 11:00
Lalmonirhat | 130 | 05:00 | 122 | 09:00
Madanganj | 132 | 03:00 | 130 | 19:00
Madaripur | 137 | 09:00 | 135 | 17:00
Madartek | 138 | 04:00 | 131 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division