## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-03-2025 | during | 24-03-2025 | during | 24-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 32 | 22 | 97.3 | 97.3 | 97.3 | 97.3 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 383 | 371 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 290 | 304 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 100 | 100 | 208.13 | 208.13 | 105 | 105 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 220 | 220 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 24 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 13 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 24 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 20 | 20 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 79 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 70 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 17 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 52 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2372 | 2432 | 4832.7 | 4805.7 | 3846.42 | 3819.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 162 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 72 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 28 | 4 | 30 | 4 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 50 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.8 | 0 | 3.8 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 701 | 1051 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 2 | 15 | 26 | 15 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 750 | 759 | 770 | 770 | 770 | 770 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1724 | 2190 | 3635.52 | 3650.72 | 3577.52 | 3592.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 360 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 33 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 14 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 83 | 138 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 35 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 16 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 0 | 0 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 23 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 60 | 64 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 29 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 50 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 75 | 0 | 75 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1313 | 1379 | 2420.99 | 2345.99 | 2227.55 | 2152.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-03-2025 | during | 24-03-2025 | during | 24-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 17 | 210 | 210 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 89 | 175 | 200 | 200 | 165 | 165 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 65 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.53 | 0 | 48.5 | 0 | 48.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 230.53 | 269 | 652.1 | 601.5 | 427.1 | 376.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 41 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 154 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 5 | 5 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 164 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 382 | 372 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 385 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1599 | 1525 | 1616 | 1616 | 1547 | 1547
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 907 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 69.62 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 383 | 457 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1367.62 | 1364 | 3587.2 | 3512.2 | 1890.02 | 1815.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 8 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 108 | 116 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 685 | 1015 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.22 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1158.22 | 1556 | 2172.12 | 2171.12 | 2160.12 | 2159.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 180 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 214 | 197 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 220 | 200 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 392 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 2.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.98 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 967 | 1064.48 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.19 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 116 | 0 | 75 | 0 | 75 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2143.67 | 2057.98 | 3077.15 | 2935.53 | 3035.36 | 2893.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 63 | 63 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 124 | 127 | 170 | 170 | 170 | 170 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 188 | 0 | 183 | 0 | 183 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 395.7 | 190 | 687.4 | 478 | 667.42 | 458.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12303.74 | 12962.98 | 22681.18 | 22116.76 | 19378.51 | 18814.09
Forecast Scenario (24-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11720 |  | 0 |  | 11720
|  |  |  | 1:00 | 11210 |  | 0 |  | 11210
|  |  |  | 2:00 | 10860 |  | 0 |  | 10860
|  |  |  | 3:00 | 11030 |  | 0 |  | 11030
|  |  |  | 4:00 | 11320 |  | 0 |  | 11320
|  |  |  | 5:00 | 10210 |  | 0 |  | 10210
|  |  |  | 6:00 | 9410 |  | 0 |  | 9410
|  |  |  | 7:00 | 9570 |  | 0 |  | 9570
|  |  |  | 8:00 | 10050 |  | 0 |  | 10050
|  |  |  | 9:00 | 10850 |  | 0 |  | 10850
|  |  |  | 10:00 | 11600 |  | 0 |  | 11600
|  |  |  | 11:00 | 11850 |  | 0 |  | 11850
|  |  |  | 12:00 | 12400 |  | 0 |  | 12400
|  |  |  | 13:00 | 12600 |  | 0 |  | 12600
|  |  |  | 14:00 | 12760 |  | 0 |  | 12760
|  |  |  | 15:00 | 12680 |  | 0 |  | 12680
|  |  |  | 16:00 | 12570 |  | 0 |  | 12570
|  |  |  | 17:00 | 12600 |  | 0 |  | 12600
|  |  |  | 18:00 | 12620 |  | 0 |  | 12620
|  |  |  | 18:30 | 12700 |  | 0 |  | 12700
|  |  |  | 19:00 | 12800 |  | 0 |  | 12800
|  |  |  | 19:30 | 13000 |  | 0 |  | 13000
|  |  |  | 20:00 | 13000 |  | 0 |  | 13000
|  |  |  | 21:00 | 12700 |  | 0 |  | 12700
|  |  |  | 22:00 | 12600 |  | 0 |  | 12600
|  |  |  | 23:00 | 12400 |  | 0 |  | 12400
Probable Maximum Temperature: |  |  | 31°C
Probable Maximum Demand at Day Peak: |  |  | 12400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 281.41 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:15 hrs on 24-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-03-2025 | [28 empty] | Date: | 23-03-2025 | [28 empty] | Date: | 23-03-2025 | [28 empty] | Date: | 23-03-2025 | [28 empty] | Date: | 23-03-2025 | [18 empty] | Date: | 23-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 30 | 269 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 295 | 583 | 0 | 0 | 20 | 220 | 98 | 0 | 0 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 24 | 701 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 577 | 0 | 43 | 0 | 45 | 0 | 360 | 285 | 52 | 182 | 36 | 17 | 30 | 100 | 32 | 20 | 17 | 64 | 0 | 0 | 0 | 295 | 320 | 348 | 5 | 43 | 0 | 5 | 152 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 45 | 125 | 12 | 0 | 0 | 12 | 6623.5 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 198 | 0 | 193 | 0 | 383 | 0 | 0 | 2.5 | 124 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 110 | 0 | 0 | 1000 | 0 | 4998.5 | 11622 | 86.12
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 232 | 0 | 0 | 0 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 272 | 583 | 0 | 0 | 20 | 220 | 98 | 0 | 0 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 6 | 700 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 653 | 0 | 43 | 0 | 45 | 0 | 360 | 285 | 52 | 181 | 37 | 17 | 50 | 100 | 29 | 12 | 17 | 64 | 0 | 0 | 0 | 295 | 320 | 350 | 5 | 43 | 0 | 5 | 152 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 49 | 57 | 12 | 0 | 0 | 12 | 6595.5 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 185 | 0 | 168 | 0 | 309 | 0 | 0 | 2.5 | 123 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 8 | 108 | 110 | 0 | 0 | 855 | 0 | 4516.5 | 11112 | 86.11
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 358 | 0 | 0 | 0 | 35 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 266 | 583 | 0 | 0 | 20 | 220 | 39 | 0 | 0 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 2 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 11 | 700 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 704 | 0 | 10 | 0 | 45 | 0 | 300 | 285 | 52 | 182 | 37 | 17 | 50 | 68 | 29 | 20 | 17 | 62 | 0 | 0 | 0 | 295 | 320 | 291 | 5 | 42 | 0 | 5 | 132 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 49 | 58 | 16 | 0 | 0 | 12 | 6506.5 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 178 | 0 | 155 | 0 | 309 | 0 | 0 | 2.5 | 120 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 108 | 110 | 0 | 0 | 700 | 0 | 4259.5 | 10766 | 86.11
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 343 | 0 | 0 | 0 | 35 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 298 | 450 | 0 | 0 | 20 | 220 | 39 | 0 | 0 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 17 | 707 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 710 | 0 | 21 | 0 | 45 | 0 | 300 | 285 | 51 | 204 | 37 | 17 | 50 | 68 | 29 | 20 | 17 | 54 | 0 | 0 | 0 | 310 | 320 | 342 | 5 | 42 | 0 | 5 | 141 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 49 | 94 | 18 | 0 | 0 | 12 | 6551.5 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 171 | 0 | 150 | 0 | 414 | 0 | 0 | 2.5 | 119 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 128 | 110 | 0 | 0 | 712 | 0 | 4378.5 | 10930 | 86.1
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 32 | 370 | 0 | 0 | 0 | 35 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 285 | 550 | 0 | 0 | 20 | 218 | 101 | 0 | 0 | 0 | 21.5 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 14 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 29 | 708 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 688 | 0 | 43 | 0 | 45 | 0 | 360 | 285 | 52 | 184 | 34 | 44 | 50 | 17 | 29 | 20 | 17 | 62 | 0 | 0 | 0 | 305 | 320 | 346 | 5 | 42 | 0 | 5 | 158 | 21 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 68 | 115 | 16 | 0 | 0 | 12 | 6836.5 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 170 | 0 | 167 | 0 | 380 | 0 | 0 | 2.5 | 112 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 7 | 108 | 110 | 0 | 0 | 805 | 0 | 4387.5 | 11224 | 86.1
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 32 | 365 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 257 | 500 | 0 | 0 | 21 | 218 | 39 | 0 | 0 | 0 | 20.5 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 610 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 602 | 0 | 10 | 0 | 8 | 0 | 340 | 285 | 48 | 182 | 34 | 16 | 50 | 17 | 29 | 20 | 0 | 50 | 0 | 0 | 0 | 300 | 320 | 360 | 5 | 42 | 0 | 5 | 132 | 21 | 0 | 11 | 30 | 0 | 18 | 163 | 0 | 45 | 75 | 16 | 0 | 0 | 12 | 6007.5 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 140 | 0 | 375 | 0 | 0 | 2.5 | 118 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 114 | 110 | 0 | 0 | 659 | 0 | 4109.5 | 10117 | 86.09
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 32 | 305 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 297 | 250 | 0 | 0 | 21 | 218 | 39 | 0 | 0 | 0 | 22.5 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 608 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 607 | 0 | 10 | 0 | 8 | 0 | 280 | 285 | 11 | 150 | 30 | 0 | 50 | 0 | 9 | 20 | 0 | 46 | 0 | 0 | 0 | 300 | 320 | 306 | 5 | 42 | 0 | 5 | 134 | 21 | 0 | 11 | 30 | 0 | 18 | 163 | 0 | 45 | 65 | 19 | 0 | 0 | 0 | 5413.5 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 140 | 0 | 250 | 0 | 0 | 2.5 | 120 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 120 | 110 | 0 | 0 | 566 | 0 | 3901.5 | 9315 | 86.09
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 302 | 0 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 302 | 400 | 0 | 0 | 22 | 219 | 39 | 0 | 4 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 14 | 609 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 606 | 3 | 10 | 0 | 8 | 0 | 280 | 285 | 10 | 150 | 30 | 0 | 50 | 0 | 0 | 20 | 0 | 44 | 0 | 8 | 0 | 315 | 320 | 356 | 5 | 43 | 0 | 5 | 141 | 16 | 0 | 11 | 30 | 0 | 18 | 163 | 0 | 45 | 65 | 19 | 0 | 5.61 | 0 | 5581.61 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 383 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 5.15 | 130 | 0 | 130 | 0 | 140 | 0 | 250 | 0 | 0.47 | 2.5 | 120 | 61 | 0 | 4 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0 | 150 | 5 | 126 | 110 | 0 | 0 | 500 | 0 | 3896.15 | 9477.76 | 86.08
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 345 | 0 | 0 | 0 | 17 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 300 | 500 | 0 | 0 | 22 | 218 | 38 | 0 | 13 | 0 | 23.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 6 | 611 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 606 | 8 | 10 | 0 | 8 | 0 | 360 | 285 | 21 | 202 | 30 | 0 | 50 | 0 | 0 | 14 | 0 | 46 | 0 | 15 | 0 | 305 | 320 | 368 | 5 | 41 | 0 | 5 | 142 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 53 | 77 | 20 | 1 | 13.26 | 0 | 5962.76 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 383 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 21.06 | 139 | 0 | 130 | 0 | 140 | 0 | 300 | 0 | 1.75 | 2.5 | 120 | 61 | 0 | 1 | 0 | 0 | 0 | 0.4 | 54 | 0.26 | 0 | 150 | 5 | 136 | 110 | 0 | 0 | 500 | 0 | 3994.97 | 9957.73 | 86.08
09:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 32 | 394 | 0 | 0 | 0 | 17 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 310 | 550 | 0 | 0 | 21 | 220 | 99 | 0 | 22 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 7 | 612 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 606 | 14 | 10 | 0 | 16 | 0 | 360 | 285 | 46 | 213 | 37 | 0 | 50 | 0 | 0 | 20 | 0 | 48 | 0 | 50 | 0 | 320 | 320 | 347 | 5 | 42 | 0 | 5 | 157 | 21 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 65 | 85 | 19 | 2 | 34.98 | 5 | 6390.98 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.16 | 385 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 36.92 | 178 | 0 | 210 | 0 | 202 | 0 | 414 | 0 | 3.37 | 2.5 | 124 | 61 | 0 | 8 | 0 | 0 | 0 | 2 | 59 | 0.24 | 0 | 150 | 4 | 128 | 110 | 0 | 0 | 500 | 0 | 4367.19 | 10758.17 | 86.07
10:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 32 | 369 | 0 | 0 | 0 | 17 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 307 | 583 | 0 | 0 | 21 | 220 | 100 | 0 | 27 | 0 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 46 | 0 | 4 | 650 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 604 | 17 | 29 | 0 | 55 | 0 | 360 | 285 | 47 | 199 | 37 | 2 | 50 | 4 | 0 | 20 | 0 | 50 | 0 | 48 | 0 | 310 | 320 | 363 | 5 | 40 | 0 | 5 | 155 | 21 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 65 | 85 | 17 | 2 | 47.18 | 12 | 6718.18 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.76 | 384 | 0 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 49.21 | 188 | 0 | 217 | 0 | 220 | 0 | 414 | 0 | 4.41 | 2.5 | 125 | 62 | 0 | 8 | 0 | 0 | 0 | 0 | 152 | 0.23 | 0 | 200 | 5 | 120 | 110 | 0 | 0 | 582 | 0 | 4786.11 | 11504.29 | 86.07
11:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 32 | 369 | 0 | 0 | 0 | 24 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 300 | 583 | 0 | 0 | 20 | 220 | 98 | 0 | 27 | 35 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 3 | 46 | 0 | 4 | 670 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 605 | 19 | 43 | 0 | 55 | 0 | 355 | 285 | 47 | 204 | 36 | 18 | 50 | 17 | 0 | 18 | 0 | 50 | 0 | 42 | 0 | 315 | 320 | 396 | 5 | 40 | 0 | 5 | 156 | 21 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 65 | 85 | 11 | 2 | 50.87 | 12 | 6887.87 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3 | 384 | 0 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 61.28 | 189 | 0 | 215 | 0 | 220 | 0 | 414 | 0 | 5.18 | 5.5 | 110 | 64 | 0 | 22 | 0 | 0 | 0 | 6.4 | 197 | 0.28 | 0 | 200 | 5 | 124 | 110 | 0 | 0 | 610 | 0 | 4868.94 | 11756.81 | 86.06
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 32 | 383 | 0 | 0 | 0 | 35 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 290 | 583 | 0 | 0 | 20 | 220 | 100 | 0 | 33 | 35 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 36 | 0 | 4 | 46 | 0 | 5 | 750 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 701 | 19 | 43 | 0 | 83 | 0 | 360 | 285 | 49 | 183 | 36 | 34 | 50 | 23 | 0 | 20 | 17 | 60 | 0 | 70 | 0 | 315 | 385 | 382 | 5 | 40 | 0 | 5 | 156 | 13 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 65 | 89 | 11 | 2 | 51.53 | 12 | 7238.53 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.62 | 383 | 0 | 967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 36.19 | 189 | 0 | 214 | 0 | 220 | 0 | 392 | 0 | 3.98 | 5.5 | 124 | 63 | 0 | 13 | 0 | 0 | 0 | 7.7 | 188 | 0.22 | 0 | 250 | 5 | 108 | 110 | 0 | 0 | 685 | 0 | 5065.21 | 12303.74 | 86.06
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 32 | 401 | 0 | 0 | 0 | 35 | 0 | 79 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 310 | 583 | 0 | 0 | 20 | 219 | 98 | 0 | 31 | 35 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 4 | 46 | 0 | 14 | 760 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 800 | 18 | 43 | 0 | 120 | 0 | 360 | 285 | 49 | 184 | 36 | 36 | 50 | 35 | 0 | 20 | 34 | 66 | 0 | 60 | 0 | 310 | 320 | 349 | 5 | 40 | 0 | 5 | 155 | 13 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 65 | 110 | 11 | 2 | 33.94 | 12 | 7370.94 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.11 | 407 | 0 | 964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 45.99 | 186 | 0 | 213 | 0 | 216 | 0 | 397 | 0 | 4.93 | 5.5 | 120 | 62 | 0 | 19 | 0 | 0 | 0 | 7.7 | 106 | 0.41 | 0 | 307 | 6 | 112 | 110 | 0 | 0 | 754 | 0 | 5131.64 | 12502.58 | 86.05
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 379 | 0 | 0 | 0 | 17 | 0 | 79 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 300 | 583 | 0 | 0 | 20 | 220 | 97 | 0 | 28 | 44 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 48 | 0 | 3 | 46 | 0 | 4 | 760 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 882 | 17 | 43 | 0 | 120 | 0 | 360 | 285 | 45 | 198 | 33 | 50 | 50 | 48 | 0 | 20 | 34 | 68 | 0 | 37 | 0 | 310 | 320 | 369 | 5 | 40 | 0 | 5 | 154 | 21 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 65 | 125 | 11 | 1 | 42.66 | 12 | 7471.16 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.14 | 463 | 0 | 960.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 23.12 | 186 | 0 | 209 | 0 | 216 | 0 | 387 | 0 | 2.69 | 5.5 | 118 | 63 | 0 | 30 | 0 | 0 | 0 | 7.4 | 166 | 0.37 | 0 | 260 | 6 | 116 | 110 | 0 | 0 | 832 | 0 | 5198.18 | 12669.34 | 86.05
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 372 | 0 | 0 | 0 | 18 | 0 | 79 | 31 | 0 | 0 | 0 | 35 | 24 | 0 | 450 | 295 | 583 | 0 | 0 | 19 | 220 | 97 | 0 | 15 | 84 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 70 | 0 | 2 | 46 | 0 | 4 | 760 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 908 | 12 | 43 | 0 | 92 | 0 | 354 | 285 | 16 | 192 | 33 | 50 | 50 | 51 | 0 | 17 | 34 | 62 | 0 | 19 | 0 | 310 | 320 | 337 | 5 | 40 | 0 | 5 | 147 | 21 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 65 | 135 | 7 | 2 | 35.51 | 12 | 7429.31 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.98 | 462 | 0 | 962.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40.5 | 185 | 0 | 207 | 0 | 215 | 0 | 366 | 0 | 3.7 | 5.5 | 118 | 63 | 0 | 25 | 0 | 0 | 0 | 5.4 | 126 | 0.19 | 0 | 260 | 6 | 116 | 110 | 0 | 0 | 892 | 0 | 5153.69 | 12583 | 86.04
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 372 | 0 | 0 | 0 | 19 | 0 | 79 | 40 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 301 | 583 | 0 | 0 | 19 | 220 | 98 | 0 | 6 | 90 | 22.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 73 | 0 | 0 | 46 | 0 | 8 | 757 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 902 | 9 | 43 | 0 | 73 | 0 | 360 | 285 | 10 | 206 | 33 | 50 | 50 | 51 | 0 | 12 | 34 | 68 | 0 | 14 | 0 | 315 | 320 | 349 | 5 | 40 | 0 | 5 | 140 | 21 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 73 | 135 | 7 | 1 | 14.46 | 12 | 7412.96 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.77 | 460 | 0 | 959.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 13.02 | 185 | 0 | 203 | 0 | 210 | 0 | 394 | 0 | 1.12 | 2.5 | 125 | 63 | 0 | 15 | 0 | 0 | 0 | 3.6 | 79 | 0.13 | 0 | 260 | 6 | 108 | 110 | 0 | 0 | 892 | 0 | 5062.13 | 12475.09 | 86.04
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 371 | 0 | 0 | 1 | 36 | 0 | 81 | 64 | 15 | 0 | 6 | 35 | 12 | 3 | 450 | 285 | 583 | 0 | 0 | 19 | 220 | 99 | 0 | 2 | 90 | 22.5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 100 | 12 | 0 | 46 | 0 | 19 | 712 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 950 | 3 | 43 | 0 | 73 | 0 | 360 | 285 | 10 | 206 | 33 | 50 | 50 | 51 | 0 | 20 | 34 | 60 | 0 | 3 | 15 | 300 | 320 | 349 | 5 | 40 | 0 | 5 | 153 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 145 | 5 | 0 | 10.76 | 12 | 7554.26 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.35 | 407 | 0 | 919.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 10.55 | 185 | 0 | 202 | 0 | 204 | 0 | 387 | 0 | 0.94 | 2.5 | 127 | 63 | 20 | 6 | 50 | 0 | 0 | 1.5 | 30 | 0.12 | 0 | 250 | 6 | 108 | 110 | 0 | 0 | 932 | 0 | 4969.14 | 12523.4 | 86.03
18:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 22 | 366 | 0 | 0 | 18 | 23 | 0 | 96 | 64 | 25 | 0 | 17 | 72 | 24 | 18 | 450 | 292 | 583 | 0 | 0 | 19 | 220 | 100 | 0 | 1 | 90 | 22 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 72 | 36 | 0 | 46 | 0 | 22 | 754 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 902 | 0 | 43 | 10 | 73 | 0 | 360 | 285 | 10 | 206 | 35 | 54 | 50 | 52 | 24 | 20 | 34 | 64 | 8 | 0 | 48 | 305 | 320 | 352 | 5 | 40 | 0 | 5 | 156 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 164 | 5 | 0 | 0.53 | 12 | 7802.53 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 393 | 0 | 916.41 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.39 | 181 | 0 | 198 | 0 | 200 | 0 | 401 | 0 | 0.07 | 2.5 | 125 | 63 | 35 | 1 | 70 | 0 | 0 | 0.1 | 3 | 0.01 | 0 | 200 | 7 | 108 | 110 | 0 | 0 | 954 | 0 | 4884.99 | 12687.52 | 86.03
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 22 | 366 | 0 | 0 | 35 | 33 | 0 | 92 | 32 | 0 | 0 | 17 | 72 | 24 | 28 | 420 | 301 | 500 | 0 | 0 | 21 | 220 | 101 | 0 | 0 | 90 | 24.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 72 | 36 | 0 | 46 | 0 | 22 | 755 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1000 | 0 | 43 | 55 | 73 | 0 | 345 | 285 | 10 | 189 | 35 | 92 | 50 | 68 | 27 | 20 | 34 | 68 | 25 | 0 | 32 | 290 | 320 | 342 | 5 | 42 | 0 | 5 | 143 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 108 | 173 | 11 | 0 | 0 | 12 | 7850.2 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 2 | 993.24 | 0 | 0 | 0 | 26 | 0 | 51 | 0 | 0 | 0 | 0 | 22 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 403 | 0 | 0 | 2.5 | 125 | 63 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 7 | 108 | 110 | 0 | 0 | 956 | 0 | 5022.74 | 12872.94 | 86.02
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 22 | 367 | 0 | 0 | 54 | 35 | 0 | 79 | 32 | 0 | 0 | 0 | 72 | 24 | 50 | 420 | 300 | 583 | 0 | 0 | 21 | 220 | 100 | 0 | 0 | 70 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 72 | 36 | 0 | 46 | 0 | 22 | 758 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1000 | 0 | 43 | 30 | 73 | 0 | 360 | 285 | 10 | 188 | 35 | 68 | 50 | 51 | 27 | 20 | 34 | 70 | 0 | 0 | 42 | 310 | 320 | 365 | 5 | 42 | 0 | 5 | 151 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 85 | 174 | 11 | 0 | 0 | 12 | 7888 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454 | 17 | 1000.98 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 172 | 0 | 170 | 0 | 398 | 0 | 0 | 2.5 | 125 | 63 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 114 | 110 | 0 | 0 | 922 | 0 | 4972.48 | 12860.48
20:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 22 | 367 | 0 | 0 | 54 | 35 | 0 | 79 | 32 | 0 | 0 | 0 | 54 | 24 | 50 | 450 | 300 | 583 | 0 | 0 | 20 | 220 | 100 | 0 | 0 | 70 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 72 | 36 | 0 | 46 | 0 | 28 | 756 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 73 | 0 | 360 | 285 | 10 | 188 | 36 | 50 | 50 | 51 | 29 | 20 | 34 | 70 | 0 | 0 | 48 | 300 | 320 | 357 | 5 | 41 | 0 | 5 | 152 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 65 | 174 | 11 | 0 | 0 | 12 | 7824 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 15 | 1026.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 197 | 0 | 200 | 0 | 399 | 0 | 0 | 2.5 | 126 | 63 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 112 | 110 | 0 | 0 | 982 | 0 | 5099.42 | 12923.42 | 86.02
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 22 | 371 | 0 | 0 | 0 | 35 | 0 | 79 | 32 | 0 | 0 | 0 | 0 | 24 | 17 | 450 | 304 | 583 | 0 | 0 | 20 | 220 | 100 | 0 | 0 | 52 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 72 | 36 | 0 | 46 | 0 | 28 | 759 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1051 | 0 | 35 | 0 | 138 | 0 | 360 | 285 | 14 | 200 | 33 | 50 | 50 | 51 | 29 | 20 | 34 | 64 | 0 | 0 | 16 | 310 | 320 | 372 | 5 | 41 | 0 | 5 | 154 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 65 | 175 | 17 | 0 | 0 | 12 | 7795 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 1064.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 197 | 0 | 200 | 0 | 414 | 0 | 0 | 2.5 | 127 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 116 | 110 | 0 | 0 | 1015 | 0 | 5167.98 | 12962.98 | 86.01
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 22 | 371 | 0 | 0 | 0 | 35 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 284 | 583 | 0 | 0 | 20 | 220 | 103 | 0 | 0 | 52 | 23.5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 34 | 0 | 0 | 72 | 24 | 0 | 46 | 0 | 28 | 758 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1050 | 0 | 35 | 0 | 138 | 0 | 360 | 285 | 25 | 182 | 36 | 50 | 50 | 51 | 28 | 20 | 34 | 66 | 0 | 0 | 0 | 305 | 320 | 347 | 5 | 43 | 10 | 5 | 153 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 65 | 165 | 15 | 0 | 0 | 12 | 7675.5 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 1069.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 196 | 0 | 200 | 0 | 394 | 0 | 0 | 2.5 | 130 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 108 | 110 | 0 | 0 | 1039 | 0 | 5170.16 | 12845.66 | 86.01
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 22 | 375 | 0 | 0 | 0 | 35 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 270 | 583 | 0 | 0 | 20 | 220 | 100 | 0 | 0 | 35 | 23.5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 72 | 24 | 0 | 46 | 0 | 22 | 756 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1051 | 0 | 35 | 0 | 83 | 0 | 360 | 285 | 25 | 188 | 36 | 50 | 50 | 51 | 29 | 20 | 17 | 68 | 0 | 0 | 0 | 280 | 320 | 300 | 5 | 43 | 0 | 5 | 139 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 65 | 165 | 11 | 0 | 0 | 12 | 7440.5 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 1063.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 198 | 0 | 199 | 0 | 315 | 0 | 0 | 2.5 | 179 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 220 | 0 | 0 | 1042 | 0 | 5177.13 | 12617.63 | 86
Total KWH | 0 | 840000 | 306240 | 0 | 0 | 0 | 0 | 673272.73 | 8704800 | 0 | 0 | 146160 | 675360 | 0 | 1224144 | 753120 | 63731 | 0 | 47810 | 315360 | 445680 | 136320 | 9704000 | 7088349 | 12998182 | 0 | 0 | 486900 | 5282266 | 2134000 | 0 | 189241 | 812400 | 513000 | 209520 | 0 | 0 | 0 | 0 | 137280 | 0 | 147840 | 222715 | 0 | 0 | 1151040 | 214080 | 23340 | 1097280 | 0 | 403680 | 17112727.27 | 0 | 0 | 0 | 0 | 0 | 3879578 | 0 | 0 | 0 | 19030908 | 138240 | 787708 | 105381 | 1522182 | 0 | 8608700 | 6928000 | 730080 | 4680000 | 827352 | 860160 | 1095510 | 996480 | 330960 | 439000 | 466260 | 1397760 | 26261 | 417764 | 172640 | 7410500 | 7697800 | 8848000 | 189864 | 978000 | 27840 | 116448 | 3545345 | 484272 | 0 | 1660800 | 710592 | 0 | 434000 | 4419000 | 0 | 1622400 | 2798400 | 297600 | 14700 | 360560 | 256800 | 169573683 | 22129454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452160 | 10036360 | 32160 | 22077946 | 0 | 0 | 0 | 45984 | 0 | 57968 | 0 | 0 | 0 | 600730 | 23397 | 333744 | 4125364 | 0 | 4639773 | 0 | 4677691 | 0 | 8898909.1 | 0 | 29820 | 77256 | 3069000 | 1435199 | 136620 | 163971 | 235526 | 0 | 0 | 38724.72 | 1171440 | 2931 | 0 | 5541000 | 161680 | 2750000 | 2802820 | 0 | 0 | 19597090.91 | 0 | 115344718.73 | 284918401.73

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12303.74 | MW | 12:00 Hr. | Energy Generated |  |  | 284.9184 |  | MKWHr.
| Day Peak Demand |  |  | 12303.74 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12962.98 | MW | 21:00 Hr. | Energy Demand |  |  | 284.9184 |  | MKWHr.
| Evening Peak Demand |  |  | 12962.98 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 9315 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1023.74 |  | MMCFD
| Maximum Generation of the Day |  |  | 12962.98 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.5 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 48.24 | 0 | 5.3206 | 0 | 0 | 0.18924 | 0 | 0 | 53.7499 | Gas | 143.0953 | Gas | 469189291.9655
| Chattogram Zone |  |  | 4.2833 | 36.1436 | 1.7251 | 0 | 1.0973 | 0.16158 | 0 | 0.14784 | 43.5587 | Coal | 75.8223 | Coal | 537198544.8299
| Cumilla Zone |  |  | 25.6185 | 0 | 2.9581 | 0 | 0 | 0.41776 | 1.3978 | 0 | 30.3922 | HFO | 15.2132 | HFO | 269188377.3
| Mymensingh Zone |  |  | 0.2976 | 0 | 4.6776 | 0 | 0 | 0.37526 | 0 | 0 | 5.3505 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.5225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5225 | Hydro | 1.0973 | Hydro | 109728
| Khulna Zone |  |  | 0 | 10.0364 | 0.03216 | 0 | 0 | 0.45216 | 22.1295 | 0 | 32.6501 | Solar | 3.9374 | Solar | 64451153.8892
| Barishal Zone |  |  | 5.7145 | 25.1381 | 0 | 0 | 0 | 0.002931 | 0 | 0 | 30.8555 | Import | 45.6052 | Import | 224762959.06
| Rajshahi Zone |  |  | 22.419 | 0 | 0.12735 | 0 | 0 | 0.96429 | 22.0779 | 0 | 45.5886 | Wind | 0.14784 | Wind | 2164377.6
| Rangpur Zone |  |  | 0 | 4.5042 | 0.37215 | 0 | 0 | 1.3741 | 0 | 0 | 6.2505
| Total |  |  | 143.0953 | 75.8223 | 15.2132 | 0 | 1.0973 | 3.9374 | 45.6052 | 0.14784 | 284.9184
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 469189291.9655 |  | Hydro | 109728
|  |  |  | Coal | 537198544.8299 |  | Solar | 64451153.8892
|  |  |  | HFO | 269188377.3 |  | Import | 224762959.06
|  |  |  | HSD | 0 |  | Wind | 2164377.6
[5 empty] | Total: | 156,70,64,432 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1295 | Peak Hr Flow | 907.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26071881.53 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.0779 | Peak Hr Flow | 1064.48 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 588 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3978 | Peak Hr Flow | 64.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 850 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.6052 | Peak Hr Flow | 2035.48 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4740
|  |  |  | Chattogram |  | 0 |  | 1415
|  |  |  | Cumilla |  | 0 |  | 1202
|  |  |  | Mymensingh |  | 0 |  | 1055
|  |  |  | Sylhet |  | 0 |  | 445
|  |  |  | Khulna |  | 0 |  | 1404
|  |  |  | Barishal |  | 0 |  | 366
|  |  |  | Rajshahi |  | 0 |  | 1225
|  |  |  | Rangpur |  | 0 |  | 722
|  |  |  | Total |  | 0 |  | 12574
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:16 | 17:03 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D
| 08:17 | 17:00 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D
| 08:23 | 16:58 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D
| 08:24 | 16:58 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D
| 08:37 |  | Shikalbaha 230/132kV S/S Interconnection-2 Scheduled S/D
| 08:37 |  | Shikalbaha 230/132kV S/S Interconnection-2 Scheduled S/D
| 08:37 |  | Shikalbaha 230/132kV S/S Interconnection-2 Scheduled S/D
| 08:37 |  | Shikalbaha 230/132kV S/S Interconnection-2 Scheduled S/D
| 09:52 | 15:17 | BSRM-GPH 230 kV Ckt-1 Forced S/D from BSRM 230/33kV end Due to Disk Cleaning
| 09:54 | 15:16 | BSRM-GPH 230 kV Ckt-2 Scheduled S/D from GPH 230/33kV end Due to disk maintenance
|  | 10:31 | Bashundhara-Rampura 132 kV Ckt-2 is restored.
| 10:35 | 12:35 | Pabna 132/33kV S/S T-1 LT Forced S/D Due to Redhot Maintenance
| 10:36 | 12:35 | Pabna 132/33kV S/S T-1 HT Forced S/D Due to Redhot Maintenance
| 10:57 | 13:03 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ishurdi 132/33kV end.
| 11:40 | 12:39 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D Due to 33KV SF6 Gas
Filling.
| 11:41 | 12:34 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to 33KV SF6 Gas
Filling.
| 13:05 | 16:17 | Ishwardi-Rooppur 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end.
|  | 15:15 | Baghabari-Shahjadpur 132 kV Ckt-2 is restored.
|  | 16:00 | Ishurdi 132/33kV S/S 132 kV Baghabari Line is restored.
| 16:15 |  | Chandpur 132/33kV S/S 402T LT Scheduled S/D Due to For the permission of higher
authorities.
|  | 16:57 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
|  | 16:58 | Sherpur 132/33kV S/S Transformer- 04 HT is restored.
|  | 17:34 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 is restored.
| 21:00 |  | Evening peak Generation is 12962 MW
| 05:09 | 05:45 | Bhangura 132/33kV S/S Tr-1(403T) HT Tripped showing 51 relays Due to Due to pbs 33 kv | [7 empty] | 24.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 05:09 | 05:49 | Bhangura 132/33kV S/S Tr-2(413T) LT Tripped showing 51 relays Due to Due to pbs 33 kv | [7 empty] | 24.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 05:09 | 05:49 | Bhangura 132/33kV S/S Tr-2(413T) HT Tripped showing 51 relays Due to Pbs33 kv feeder | [7 empty] | 24.0MW load
|  |  | fault | [7 empty] | interrup.
| 05:09 | 05:45 | Bhangura 132/33kV S/S Tr-1(403T) LT Tripped showing 51 relays Due to Pbs 33kv feeder | [7 empty] | 24.0MW load
|  |  | fault | [7 empty] | interrup.
| 05:33 |  | Siddhirganj CCPP 335 MW was shutdown to change air-intake filter.
| 05:52 | 06:43 | Rampura 230/132kV S/S Auto Transformer - 03 LT Scheduled S/D Due to Relay change Siemens
7UT61
| 05:52 | 06:43 | Rampura 230/132kV S/S Auto Transformer - 03 HT Scheduled S/D Due to Relay change Siemens
7UT61
| 06:00 |  | Minimum Generation: 9454 MW.
| 07:06 |  | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to Emergency maintenance work
| 07:27 | 07:46 | Chattak-Sylhet 132 kV Ckt-1 Tripped from Sylhet 132/33kV end showing Distance C -phase
,Z-1 relays.
| 07:32 |  | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Rope removing
| 07:54 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Maintenance work | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 22 | 673272.73 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 371 | 8704800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9704000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7088349 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 2134000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 220 | 5282266 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 146160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 753120 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 47810 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 513000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 13 | 209520 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 445680 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 486900 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 306240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 63731 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 79 | 1224144 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 840000 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 17 | 136320 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 315360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 189241 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 675360 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 12998182 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 52 | 812400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2432 | 53749855.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138240 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1097280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 162 | 3879578 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 222715 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 72 | 1151040 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 403680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 137280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23340 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 214080 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1051 | 19030908 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 147840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 759 | 17112727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 2190 | 43558708.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 200 | 4680000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8608700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6928000 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 827352 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 14 | 730080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 138 | 1522182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 35 | 787708 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 105381 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 16 | 172640 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1095510 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 996480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 64 | 1397760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 26261 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 439000 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 466260 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 330960 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 860160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 417764 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1379 | 30392198
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 17 | 297600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 175 | 2798400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 65 | 1622400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 360560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 256800 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 269 | 5350460
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 978000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 27840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3545345 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 5 | 189864 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 116448 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 710592 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1660800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 164 | 4419000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 434000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 484272 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7410500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 372 | 8848000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7697800 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1525 | 36522461
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 907 | 22129454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 32160 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 452160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 457 | 10036360 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1364 | 32650134
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 161680 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 116 | 2750000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1015 | 19597090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2802820 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5541000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2931 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1556 | 30855521.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4125364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4639773 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 200 | 4677691 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8898909.1 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 23397 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 77256 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 57968 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 45984 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1064.48 | 22077946 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 333744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 600730 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2057.98 | 45588582.1
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 63 | 1435199 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 127 | 3069000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 235526 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38724.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 136620 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 163971 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1171440 | -
Rangpur Area Total |  |  |  |  | 950 | 190 | 6250480.72
Eastern Grid Total |  |  |  |  | 16921.242 | 7795 | 169573683
Western Grid Total |  |  |  |  | 11614.5 | 5167.98 | 115344718.73
National Grid Total |  |  |  |  | 28535.742 | 12962.98 | 284918401.73
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8857.41 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3716.9 | MW
i) Dhaka area |  |  | 4740.31 |  | MW | i) Khulna area |  |  |  | 1403.5 | MW
ii) Chattogram area |  |  | 1415.1 |  | MW | ii) Barishal area |  |  |  | 366 | MW
iii) Cumilla area |  |  | 1202 |  | MW | iii) Rajshahi area |  |  |  | 1225.4 | MW
iv) Mymensingh area |  |  | 1055 |  | MW | iv) Rangpur area |  |  |  | 722 | MW
v) Sylhet area |  |  | 445 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12574.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 67 | 18:00 | 133 | Payra | 26 | 21:00
2 | AKSML | 23.5 | 10:00 | 68 | Jamalpur | 116 | 18:00 | 134 | Postogola | 45 | 14:00
3 | Aftabnagar | 30 | 14:00 | 69 | Jashore | 120 | 19:00 | 135 | Purbachal | 15 | 18:00
4 | Agargaon | 90 | 14:00 | 70 | Jhenaidah | 103 | 18:00 | 136 | Purbasadipur | 115 | 13:00
5 | Agrabad | 90 | 19:00 | 71 | Joydebpur | 144 | 14:00 | 137 | Rahanpur | 25 | 04:00
6 | Amnura | 41 | 17:00 | 72 | Joypurhat | 57 | 22:00 | 138 | Rahim | 45 | 16:00
7 | Ashuganj | 80 | 22:00 | 73 | Juldah | 13 | 10:00 | 139 | Rajbari | 56 | 03:00
8 | BSRM | 195 | 02:00 | 74 | KSRM | 29 | 19:00 | 140 | Rajendrapur | 109 | 15:00
9 | Bagerhat | 71 | 19:00 | 75 | Kabirpur | 250 | 16:00 | 141 | Rajshahi | 101 | 00:00
10 | Bajitpur | 43 | 18:30 | 76 | Kachua | 68 | 18:30 | 142 | Rajshahi-230 | 55 | 18:00
11 | Bakulia | 89 | 00:00 | 77 | Kallyanpur | 88 | 21:00 | 143 | Ramganj | 100 | 18:30
12 | Banani | 42 | 13:00 | 78 | Kalurghat | 40 | 14:00 | 144 | Rampur | 38 | 00:00
13 | Bangabhaban | 13 | 10:00 | 79 | Kamrangirchar | 66.2 | 16:00 | 145 | Rangamati | 17 | 18:30
14 | Barapukuria | 63 | 18:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 138 | 18:00
15 | Barguna | 16 | 20:00 | 81 | Kasba | 30 | 22:00 | 147 | Ruppur | 5.8 | 11:00
16 | Barishal | 90 | 13:00 | 82 | Kazla | 91 | 21:00 | 148 | SSM | 9 | 00:00
17 | Barishal-230 | 74 | 19:00 | 83 | Keranigonj | 69 | 19:30 | 149 | Saidpur | 108 | 17:00
18 | Baroaulia | 60 | 09:00 | 84 | Khagrachori | 26 | 18:00 | 150 | Satkhira | 114 | 18:30
19 | Baroirhat | 53 | 19:00 | 85 | Khulna | 83 | 19:00 | 151 | Satmasjid | 84 | 14:00
20 | Bashundhara | 150 | 19:30 | 86 | Khulshi | 149 | 14:00 | 152 | Savar | 196 | 14:00
21 | BashundharaCement | 8 | 00:00 | 87 | Kishoreganj | 118 | 18:00 | 153 | SevenRings | 19.46 | 08:00
22 | Beanibazar | 50 | 18:30 | 88 | Kodda | 287 | 15:00 | 154 | ShahCement | 38 | 07:00
23 | Benapole | 56 | 19:00 | 89 | Kulaura | 36 | 18:30 | 155 | Shahjadpur | 72 | 12:00
24 | Bhaluka | 142 | 15:00 | 90 | Kurigram | 62 | 17:00 | 156 | Shahjibazar | 109 | 19:00
25 | Bhandaria | 40 | 21:00 | 91 | Kushtia | 108 | 12:00 | 157 | Shahmirpur | 52 | 23:00
26 | Bhangura | 32 | 08:00 | 92 | Lalbag | 62 | 19:30 | 158 | Shariatpur | 63 | 22:00
27 | Bheramara(GK) | 45 | 19:00 | 93 | Lalmonirhat | 54 | 18:30 | 159 | Sherpur | 158 | 18:00
28 | Bhulta | 248 | 13:00 | 94 | MI_Cement | 18 | 15:00 | 160 | Shikalbaha | 28 | 00:00
29 | Bog-Sherpur | 58 | 11:00 | 95 | Madanganj | 40 | 21:00 | 161 | Shitalakhya | 72.4 | 14:00
30 | Bogura | 137 | 03:00 | 96 | Madaripur | 81 | 21:00 | 162 | Sholosohor | 44 | 14:00
31 | Borhanuddin | 67 | 21:00 | 97 | Madartek | 72.81 | 22:00 | 163 | Shyampur | 170 | 15:00
32 | Brahmanbaria | 108 | 22:00 | 98 | Madunaghat | 46 | 19:00 | 164 | Siddhirganj | 109 | 23:00
33 | Cantonment | 88 | 13:00 | 99 | Magura | 52 | 19:00 | 165 | Sirajganj | 96 | 19:30
34 | Chandpur | 54 | 20:00 | 100 | Mahasthangarh | 60 | 21:00 | 166 | Sonargaon | 97 | 12:00
35 | Chandraghona | 33 | 19:00 | 101 | Manikganj | 106 | 19:00 | 167 | Sreemongol | 51 | 21:00
36 | Chapai | 58 | 03:00 | 102 | Maniknagar | 60 | 14:00 | 168 | Sreepur | 70 | 15:00
37 | Charsaidpur | 46 | 12:00 | 103 | Matarbari | 46 | 19:00 | 169 | Srinagar | 36.35 | 19:00
38 | Chauddagram | 63 | 00:00 | 104 | Matuail | 64 | 11:00 | 170 | Sunamganj | 42 | 18:30
39 | Chhatak | 25 | 21:00 | 105 | Millgate | 72 | 12:00 | 171 | Sylhet | 32 | 14:00
40 | Chowmuhani | 183 | 19:00 | 106 | Mirpur | 118 | 20:00 | 172 | Sylhet-132 | 91 | 21:00
41 | Chuadanga | 80 | 19:00 | 107 | Mirsorai | 10 | 15:00 | 173 | TK | 20.5 | 00:00
42 | Coxsbazar | 126 | 21:00 | 108 | Mirzapur | 41 | 18:00 | 174 | Tangail | 164 | 03:00
43 | Cumilla(N) | 132 | 20:00 | 109 | Mithapukur | 56 | 18:00 | 175 | Thakurgaon | 81 | 19:00
44 | Cumilla(S) | 159 | 14:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 113 | 11:00
45 | Daudkandi | 135 | 21:00 | 111 | Mogbazar | 121.8 | 14:00 | 177 | Ullahpara | 30 | 10:00
46 | Dhaka | 44 | 14:00 | 112 | Mongla | 33 | 19:00 | 178 | Ullon | 41 | 19:30
47 | Dhamrai | 124 | 15:00 | 113 | Motijheel | 31 | 12:00 | 179 | Uttara | 72 | 15:00
48 | Dhanmondi | 122 | 13:00 | 114 | Muktagacha | 34 | 17:00 | 180 | UttaraNew | 40 | 21:00
49 | Dohazari | 107 | 18:30 | 115 | Munshiganj | 96 | 14:00 | 181 | Zigatola | 58 | 15:00
50 | Faridpur | 129 | 19:30 | 116 | Muradnagar | 21 | 18:30
51 | Fatullah | 90 | 12:00 | 117 | Mymensingh | 198 | 18:00
52 | Fenchuganj | 25 | 04:00 | 118 | Naogaon | 107 | 08:00
53 | Feni | 98 | 19:00 | 119 | Narail | 50 | 19:00
54 | GPH | 84 | 09:00 | 120 | Narinda | 73 | 13:00
55 | Ghatail | 78 | 18:00 | 121 | Narshingdi | 159 | 22:00
56 | Ghorashal | 16 | 11:00 | 122 | Natore | 120 | 20:00
57 | Ghorashal-230 | 86 | 16:00 | 123 | Nawabganj | 44.2 | 21:00
58 | Goalpara | 24 | 23:00 | 124 | Netrakona | 136 | 18:00
59 | Gollamari | 64 | 13:00 | 125 | New | 76.6 | 14:00
60 | Gopalganj | 88 | 21:00 | 126 | Niamatpur | 92 | 18:00
61 | Gulshan | 96 | 13:00 | 127 | Noapara | 40 | 19:00
62 | Halishahar | 72 | 10:00 | 128 | PHP | 9 | 19:30
63 | HaripurSBU | 147 | 14:00 | 129 | Pabna | 89 | 18:00
64 | Hasnabad | 72 | 19:00 | 130 | Palashbari | 104 | 13:00
65 | Hathazari | 73 | 21:00 | 131 | Panchagarh | 45 | 19:00
66 | Ishurdi | 57 | 19:00 | 132 | Patuakhali | 59 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11622 | 0 |  | 11622
1:00 | 11112 | 0 |  | 11112
2:00 | 10766 | 0 |  | 10766
3:00 | 10930 | 0 |  | 10930
4:00 | 11224 | 0 |  | 11224
5:00 | 10117 | 0 |  | 10117
6:00 | 9315 | 0 |  | 9315
7:00 | 9477.76 | 0 |  | 9477.76
8:00 | 9957.73 | 0 |  | 9957.73
9:00 | 10758.17 | 0 |  | 10758.17
10:00 | 11504.29 | 0 |  | 11504.29
11:00 | 11756.81 | 0 |  | 11756.81
12:00 | 12303.74 | 0 |  | 12303.74
13:00 | 12502.58 | 0 |  | 12502.58
14:00 | 12669.34 | 0 |  | 12669.34
15:00 | 12583 | 0 |  | 12583
16:00 | 12475.09 | 0 |  | 12475.09
17:00 | 12523.4 | 0 |  | 12523.4
18:00 | 12687.52 | 0 |  | 12687.52
19:00 | 12872.94 | 0 |  | 12872.94
19:30 | 12860.48 | 0 |  | 12860.48
20:00 | 12923.42 | 0 |  | 12923.42
21:00 | 12962.98 | 0 |  | 12962.98
22:00 | 12845.66 | 0 |  | 12845.66
23:00 | 12617.63 | 0 |  | 12617.63
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6623.5 | 4998.5 | 11622 | DAILY GENERATION CURVE
00:30 | 6609.5 | 4757.5 | 11367
01:00 | 6595.5 | 4516.5 | 11112 | 23-03-2025
01:30 | 6551 | 4388 | 10939
02:00 | 6506.5 | 4259.5 | 10766
02:30 | 6529 | 4319 | 10848
03:00 | 6551.5 | 4378.5 | 10930
03:30 | 6694 | 4383 | 11077
04:00 | 6836.5 | 4387.5 | 11224
04:30 | 6422 | 4248.5 | 10670.5
05:00 | 6007.5 | 4109.5 | 10117
05:30 | 5710.5 | 4005.5 | 9716
06:00 | 5413.5 | 3901.5 | 9315
06:30 | 5497.555 | 3898.825 | 9396.38
07:00 | 5581.61 | 3896.15 | 9477.76
07:30 | 5772.185 | 3945.56 | 9717.745
08:00 | 5962.76 | 3994.97 | 9957.73
08:30 | 6176.87 | 4181.08 | 10357.95
09:00 | 6390.98 | 4367.19 | 10758.17
09:30 | 6554.58 | 4576.65 | 11131.23
10:00 | 6718.18 | 4786.11 | 11504.29
10:30 | 6803.025 | 4827.525 | 11630.55
11:00 | 6887.87 | 4868.94 | 11756.81
11:30 | 7063.2 | 4967.075 | 12030.275
12:00 | 7238.53 | 5065.21 | 12303.74
12:30 | 7304.735 | 5098.425 | 12403.16
13:00 | 7370.94 | 5131.64 | 12502.58
13:30 | 7421.05 | 5164.91 | 12585.96
14:00 | 7471.16 | 5198.18 | 12669.34
14:30 | 7450.235 | 5175.935 | 12626.17
15:00 | 7429.31 | 5153.69 | 12583
15:30 | 7421.135 | 5107.91 | 12529.045
16:00 | 7412.96 | 5062.13 | 12475.09
16:30 | 7483.61 | 5015.635 | 12499.245
17:00 | 7554.26 | 4969.14 | 12523.4
17:30 | 7678.395 | 4927.065 | 12605.46
18:00 | 7802.53 | 4884.99 | 12687.52
18:30 | 7826.365 | 4953.865 | 12780.23
19:00 | 7850.2 | 5022.74 | 12872.94
19:30 | 7888 | 4972.48 | 12860.48
20:00 | 7824 | 5099.42 | 12923.42
20:30 | 7809.5 | 5133.7 | 12943.2 |  | Executive Engineer
21:00 | 7795 | 5167.98 | 12962.98 |  | Network Operation Division
21:30 | 7735.25 | 5169.07 | 12904.32
22:00 | 7675.5 | 5170.16 | 12845.66
22:30 | 7558 | 5173.645 | 12731.645
23:00 | 7440.5 | 5177.13 | 12617.63

## En-Curve
QF-LDC-12
Date | 23-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3618 | 2295 | 910 | 0 | 64 | 1022 | 46 | 3182 | 0 | 42 | 443 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3554.5 | 2271 | 911 | 0 | 64 | 947.5 | 46 | 3108.5 | 0 | 58.5 | 406 | 0 | 0 | 0 | 0 | 23-03-2025
01:00 | 3491 | 2247 | 912 | 0 | 64 | 873 | 46 | 3035 | 0 | 75 | 369 | 0 | 0 | 0 | 0
01:30 | 3456.5 | 2186.5 | 911.5 | 0 | 63 | 851 | 46 | 2964.5 | 0 | 90 | 369 | 0 | 0 | 1 | 0 | Energy Generated | 284.9184 |  | MKWHr
02:00 | 3422 | 2126 | 911 | 0 | 62 | 829 | 46 | 2894 | 0 | 105 | 369 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3508.5 | 2095 | 911 | 0 | 58 | 827 | 46 | 2906 | 0 | 105 | 387 | 0 | 0 | 4.5 | 0 | Total Energy Requirement | 284.9184 |  | MKWHr
03:00 | 3595 | 2064 | 911 | 0 | 54 | 825 | 46 | 2918 | 0 | 105 | 405 | 0 | 0 | 7 | 0
03:30 | 3639.5 | 2151 | 911 | 0 | 58 | 823.5 | 46 | 2932.5 | 0 | 97.5 | 407.5 | 0 | 0 | 10.5 | 0
04:00 | 3684 | 2238 | 911 | 0 | 62 | 822 | 46 | 2947 | 0 | 90 | 410 | 0 | 0 | 14 | 0
04:30 | 3598.5 | 2077 | 911 | 0 | 56 | 820 | 46 | 2765.5 | 0 | 61.5 | 322.5 | 0 | 0 | 12.5 | 0
05:00 | 3513 | 1916 | 911 | 0 | 50 | 818 | 46 | 2584 | 0 | 33 | 235 | 0 | 0 | 11 | 0
05:30 | 3350 | 1770 | 913 | 0 | 48 | 819 | 46 | 2538.5 | 0 | 25 | 197.5 | 0 | 0 | 9 | 0
06:00 | 3187 | 1624 | 915 | 0 | 46 | 820 | 46 | 2493 | 0 | 17 | 160 | 0 | 0 | 7 | 0
06:30 | 3214.5 | 1688.25 | 915 | 0 | 45 | 821 | 46 | 2461 | 36.13 | 21 | 144 | 0 | 0 | 4.5 | 0
07:00 | 3242 | 1752.5 | 915 | 0 | 44 | 822 | 46 | 2429 | 72.26 | 25 | 128 | 0 | 0 | 2 | 0
07:30 | 3369 | 1809.75 | 891.5 | 0 | 45 | 822 | 46 | 2430 | 125.995 | 25 | 152.5 | 0 | 0 | 1 | 0
08:00 | 3496 | 1867 | 868 | 0 | 46 | 822 | 46 | 2431 | 179.73 | 25 | 177 | 0 | 0 | 0 | 0
08:30 | 3694 | 1944.25 | 868 | 0 | 47 | 820 | 46 | 2434.5 | 258.7 | 46 | 199.5 | 0 | 0 | 0 | 0
09:00 | 3892 | 2021.5 | 868 | 0 | 48 | 818 | 46 | 2438 | 337.67 | 67 | 222 | 0 | 0 | 0 | 0
09:30 | 3893 | 2156 | 891.5 | 0 | 49 | 855 | 46 | 2522.5 | 415.23 | 67 | 236 | 0 | 0 | 0 | 0
10:00 | 3894 | 2290.5 | 915 | 0 | 50 | 892 | 46 | 2607 | 492.79 | 67 | 250 | 0 | 0 | 0 | 0
10:30 | 3907.5 | 2301 | 915 | 0 | 50 | 890 | 46 | 2625 | 526.05 | 84.5 | 285.5 | 0 | 0 | 0 | 0
11:00 | 3921 | 2311.5 | 915 | 0 | 50 | 888 | 46 | 2643 | 559.31 | 102 | 321 | 0 | 0 | 0 | 0
11:30 | 3927 | 2320 | 915 | 0 | 55 | 927.5 | 46 | 2799.5 | 586.775 | 102 | 351 | 0 | 0 | 0.5 | 0
12:00 | 3933 | 2328.5 | 915 | 0 | 60 | 967 | 46 | 2956 | 614.24 | 102 | 381 | 0 | 0 | 1 | 0
12:30 | 3892.5 | 2358 | 915 | 0 | 63 | 965.5 | 46 | 3083 | 560.16 | 102 | 417.5 | 0 | 0 | 0.5 | 0
13:00 | 3852 | 2387.5 | 915 | 0 | 66 | 964 | 46 | 3210 | 506.08 | 102 | 454 | 0 | 0 | 0 | 0
13:30 | 3851.5 | 2371.25 | 915 | 0 | 67 | 962.48 | 46 | 3294 | 492.73 | 106.5 | 466 | 0 | 0 | 13.5 | 0
14:00 | 3851 | 2355 | 915 | 0 | 68 | 960.96 | 46 | 3378 | 479.38 | 111 | 478 | 0 | 0 | 27 | 0
14:30 | 3811 | 2318.65 | 914 | 0 | 65 | 961.69 | 46 | 3420.5 | 418.83 | 138.5 | 513.5 | 0 | 0 | 18.5 | 0
15:00 | 3771 | 2282.3 | 913 | 0 | 62 | 962.42 | 46 | 3463 | 358.28 | 166 | 549 | 0 | 0 | 10 | 0
15:30 | 3793 | 2261.15 | 912.5 | 0 | 65 | 961.205 | 46 | 3461 | 287.19 | 173.5 | 555 | 0 | 0 | 13.5 | 0
16:00 | 3815 | 2240 | 912 | 0 | 68 | 959.99 | 46 | 3459 | 216.1 | 181 | 561 | 0 | 0 | 17 | 0
16:30 | 3806.5 | 2248.5 | 912.5 | 0 | 64 | 939.585 | 46 | 3450 | 159.16 | 200.5 | 660 | 0 | 0 | 12.5 | 0
17:00 | 3798 | 2257 | 913 | 0 | 60 | 919.18 | 46 | 3441 | 102.22 | 220 | 759 | 0 | 0 | 8 | 0
17:30 | 3799.5 | 2272.75 | 913 | 0 | 62 | 917.795 | 46 | 3416 | 55.415 | 262 | 854 | 0 | 0 | 7 | 0
18:00 | 3801 | 2288.5 | 913 | 0 | 64 | 916.41 | 46 | 3391 | 8.61 | 304 | 949 | 0 | 0 | 6 | 0
18:30 | 3721 | 2225.1 | 886.5 | 0 | 66 | 954.825 | 46 | 3514.5 | 4.305 | 325.5 | 1030.5 | 0 | 0 | 6 | 0
19:00 | 3641 | 2161.7 | 860 | 0 | 68 | 993.24 | 46 | 3638 | 0 | 347 | 1112 | 0 | 0 | 6 | 0
19:30 | 3732 | 2271.5 | 860 | 0 | 70 | 1000.98 | 46 | 3629 | 0 | 284 | 965 | 0 | 0 | 2 | 0
20:00 | 3787 | 2298.5 | 860 | 0 | 70 | 1026.92 | 46 | 3686 | 0 | 270 | 879 | 0 | 0 | 0 | 0
20:30 | 3818.5 | 2337 | 883.5 | 0 | 67 | 1045.7 | 46 | 3732.5 | 0 | 245 | 767 | 0 | 0 | 1 | 0
21:00 | 3850 | 2375.5 | 907 | 0 | 64 | 1064.48 | 46 | 3779 | 0 | 220 | 655 | 0 | 0 | 2 | 0
21:30 | 3822 | 2367.75 | 910.5 | 0 | 65 | 1067.07 | 46 | 3788 | 0 | 203 | 630.5 | 0 | 0 | 4.5 | 0
22:00 | 3794 | 2360 | 914 | 0 | 66 | 1069.66 | 46 | 3797 | 0 | 186 | 606 | 0 | 0 | 7 | 0
22:30 | 3726.5 | 2358.5 | 914 | 0 | 67 | 1066.645 | 46 | 3788 | 0 | 160.5 | 598 | 0 | 0 | 6.5 | 0
23:00 | 3659 | 2357 | 914 | 0 | 68 | 1063.63 | 46 | 3779 | 0 | 135 | 590 | 0 | 0 | 6 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 407 | 05:00 | 387 | 14:00 | Payra | 422 | 06:00 | 413 | 14:00
Ashuganj | 415 | 18:00 | 392 | 11:00 | Rahanpur | 400 | 02:00 | 391 | 13:00
Bhulta | 409 | 04:00 | 385 | 15:00 | Rampal | 413 | 05:00 | 397 | 14:00
Bibiana | 396 | 04:00 | 388 | 15:00
BIPTC | 399 | 03:00 | 393 | 21:00
Bogura | 388 | 05:00 | 375 | 13:00
Gopalganj | 414 | 05:00 | 396 | 15:00
Kaliakoir | 376 | 04:00 | 357 | 14:00
Madunaghat | 401 | 06:00 | 392 | 15:00
Meghnaghat | 407 | 05:00 | 389 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 222 | 14:00 | Keranigonj | 235 | 05:00 | 220 | 15:00
AKSML | 235 | 18:00 | 223 | 05:00 | Khulna(S) | 239 | 01:00 | 226 | 14:00
Aminbazar | 236 | 04:00 | 224 | 14:00 | Madunaghat | 236 | 06:00 | 229 | 14:00
Ashuganj | 237 | 05:00 | 226 | 15:00 | Madunaghat-400 | 236 | 06:00 | 229 | 15:00
Ashuganj-400 | 237 | 05:00 | 226 | 15:00 | Maniknagar | 232 | 18:30 | 218 | 15:00
Baghabari | 238 | 05:00 | 228 | 11:00 | Meghnaghat | 240 | 04:00 | 228 | 14:00
Barapukuria | 225 | 05:00 | 219 | 13:00 | Meghnaghat-400 | 235 | 05:00 | 221 | 14:00
Barapukuria-230 | 225 | 05:00 | 219 | 13:00 | Mirsorai | 234 | 05:00 | 221 | 15:00
Barishal | 241 | 06:00 | 233 | 14:00 | Rajshahi | 235 | 05:00 | 23 | 06:00
Bheramara | 235 | 05:00 | 222 | 11:00 | Rampal | 237 | 01:00 | 226 | 14:00
Bhulta | 232 | 04:00 | 218 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 04:00 | 223 | 14:00 | Rampura | 231 | 05:00 | 216 | 15:00
BIPTC | 238 | 05:00 | 222 | 11:00 | Shikalbaha | 233 | 07:00 | 225 | 13:00
Bogura | 238 | 02:00 | 230 | 10:00 | Shyampur | 234 | 05:00 | 220 | 15:00
Bogura-400 | 237 | 02:00 | 229 | 13:00 | Siddhirganj | 233 | 04:00 | 221 | 15:00
Borhanuddin | 243 | 05:00 | 238 | 13:00 | Sirajgonj | 243 | 01:00 | 237 | 10:00
BSRM | 234 | 05:00 | 220 | 15:00 | Sreepur | 237 | 18:30 | 226 | 14:00
Cumilla(N) | 228 | 01:00 | 218 | 15:00 | Tongi | 232 | 04:00 | 215 | 13:00
Faridpur | 240 | 04:00 | 230 | 14:00
Fenchuganj | 236 | 01:00 | 224 | 23:00
Ghorashal | 238 | 01:00 | 225 | 11:00
Ghorashal-230 | 234 | 18:30 | 219 | 14:00
Gopalganj | 239 | 05:00 | 229 | 14:00
GPH | 235 | 05:00 | 225 | 15:00
Haripur | 233 | 05:00 | 220 | 15:00
Hasnabad | 235 | 05:00 | 220 | 14:00
Hathazari | 236 | 08:00 | 228 | 15:00
Ishurdi | 238 | 05:00 | 225 | 10:00
Jhenaidah | 235 | 06:00 | 221 | 11:00
Kaliakoir | 235 | 04:00 | 221 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 04:00 | 127 | 15:00 | Madunaghat | 135 | 06:00 | 131 | 12:00
Agargaon | 142 | 05:00 | 133 | 14:00 | Magura | 134 | 01:00 | 125 | 10:00
Agrabad | 133 | 04:00 | 127 | 14:00 | Mahasthangarh | 134 | 05:00 | 126 | 12:00
AKS | 132 | 04:00 | 126 | 14:00 | Manikganj | 135 | 18:30 | 122 | 14:00
Aminbazar | 138 | 04:00 | 129 | 14:00 | Maniknagar | 137 | 05:00 | 127 | 15:00
Amnura | 138 | 18:00 | 128 | 10:00 | Matarbari | 121 | 06:00 | 112 | 00:00
Ashuganj | 140 | 18:30 | 135 | 11:00 | Matuail | 135 | 04:00 | 127 | 14:00
Bagerhat | 136 | 05:00 | 125 | 14:00 | Millgate | 139 | 05:00 | 127 | 14:00
Bajitpur | 135 | 04:00 | 127 | 16:00 | Mirpur | 138 | 18:00 | 127 | 14:00
Bakulia | 134 | 06:00 | 130 | 00:00 | Mirzapur | 131 | 02:00 | 123 | 14:00
Banani | 138 | 01:00 | 126 | 15:00 | Mithapukur | 133 | 05:00 | 124 | 12:00
Bangabhaban | 136 | 01:00 | 127 | 15:00 | MI_Cement | 135 | 05:00 | 126.2 | 15:00
Barapukuria | 139 | 05:00 | 133 | 13:00 | Modern | 0 | 00:00 | 0 | 00:00
Barguna | 138 | 06:00 | 134 | 14:00 | Mogbazar | 140 | 04:00 | 128 | 15:00
Barishal | 136 | 06:00 | 130 | 13:00 | Mongla | 136 | 05:00 | 126 | 15:00
Barishal-230 | 136 | 05:00 | 129 | 14:00 | Motijheel | 136 | 01:00 | 127 | 15:00
Baroaulia | 132 | 02:00 | 128 | 14:00 | Muktagacha | 133 | 23:00 | 12 | 06:00
Baroirhat | 126 | 06:00 | 118 | 14:00 | Munshiganj | 134 | 03:00 | 126 | 14:00
Bashundhara | 140 | 04:00 | 126 | 11:00 | Muradnagar | 131 | 18:30 | 121 | 15:00
BashundharaCement | 134 | 04:00 | 123 | 14:00 | Mymensingh | 134 | 23:00 | 117 | 14:00
Beanibazar | 132 | 01:00 | 127 | 15:00 | Naogaon | 130 | 05:00 | 123 | 10:00
Benapole | 134 | 06:00 | 122 | 13:00 | Narail | 135 | 02:00 | 123 | 14:00
Bhaluka | 130 | 05:00 | 121 | 14:00 | Narinda | 137 | 05:00 | 127 | 15:00
Bhandaria | 132 | 06:00 | 125 | 17:00 | Narshingdi | 132 | 18:30 | 120 | 17:00
Bhangura | 136 | 01:00 | 128 | 10:00 | Natore | 134 | 02:00 | 127 | 10:00
Bheramara | 136 | 05:00 | 127 | 11:00 | Nawabganj | 141 | 04:00 | 128 | 14:00
Bheramara(GK) | 136 | 05:00 | 127 | 11:00 | Netrakona | 127 | 06:00 | 115 | 14:00
Bhulta | 131 | 18:30 | 121 | 15:00 | New | 141 | 18:30 | 127 | 14:00
Bog-Sherpur | 134 | 02:00 | 127 | 10:00 | Niamatpur | 136 | 05:00 | 131 | 00:00
Bogura | 135 | 05:00 | 129 | 10:00 | Noapara | 137 | 02:00 | 126 | 14:00
Bogura-230 | 136 | 05:00 | 129 | 10:00 | Pabna | 137 | 05:00 | 128 | 10:00
Brahmanbaria | 134 | 18:00 | 125 | 14:00 | Palashbari | 130 | 05:00 | 122 | 15:00
Cantonment | 142 | 06:00 | 129 | 05:00 | Panchagarh | 136 | 08:00 | 120 | 13:00
Chandpur | 127 | 18:30 | 117 | 15:00 | Patuakhali | 136 | 05:00 | 133 | 23:00
Chandraghona | 136 | 05:00 | 130 | 13:00 | Payra | 138 | 02:00 | 135 | 14:00
Chapai | 135 | 05:00 | 130 | 00:00 | PHP | 127 | 18:30 | 116 | 15:00
Charsaidpur | 136 | 18:30 | 126 | 15:00 | Postogola | 137 | 01:00 | 129 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 125 | 05:00 | 118 | 14:00 | Purbachal | 138 | 01:00 | 126 | 15:00
Chhatak | 132 | 00:00 | 128 | 13:00 | Purbasadipur | 134 | 08:00 | 121 | 13:00
Chowmuhani | 123 | 18:30 | 113 | 14:00 | Rahanpur | 143 | 22:00 | 134 | 09:00
Chuadanga | 136 | 05:00 | 123 | 11:00 | Rahanpur-400 | 138 | 02:00 | 134 | 09:00
Coxsbazar | 119 | 08:00 | 114 | 00:00 | Rahim | 135 | 06:00 | 127 | 14:00
Cumilla(N) | 131 | 01:00 | 124 | 15:00 | Rajbari | 134 | 02:00 | 127 | 14:00
Cumilla(S) | 132 | 03:00 | 121 | 15:00 | Rajendrapur | 136 | 18:30 | 123 | 16:00
Daudkandi | 129 | 05:00 | 119 | 15:00 | Rajshahi | 135 | 05:00 | 128 | 10:00
Dhaka | 139 | 04:00 | 127 | 15:00 | Rajshahi-230 | 135 | 03:00 | 126 | 12:00
Dhamrai | 134 | 05:00 | 124 | 15:00 | Ramganj | 121 | 18:30 | 113 | 12:00
Dhanmondi | 138.5 | 05:00 | 127.4 | 15:00 | Rampur | 134 | 07:00 | 128 | 14:00
Dohazari | 129 | 07:00 | 124 | 00:00 | Rampura | 139 | 01:00 | 127 | 15:00
Faridpur | 135 | 06:00 | 129 | 14:00 | Rangamati | 134 | 05:00 | 129 | 14:00
Fatullah | 138 | 18:30 | 127 | 15:00 | Rangpur | 131 | 05:00 | 123 | 17:00
Fenchuganj | 136 | 01:00 | 134 | 04:00 | Ruppur | 137 | 02:00 | 130 | 11:00
Feni | 126 | 18:30 | 115 | 14:00 | Saidpur | 133 | 08:00 | 125 | 17:00
Ghatail | 130 | 04:00 | 122 | 08:00 | Satkhira | 137 | 05:00 | 126 | 14:00
Ghorashal | 138 | 01:00 | 132 | 11:00 | Satmasjid | 142 | 05:00 | 132 | 14:00
Goalpara | 140 | 05:00 | 129 | 15:00 | Savar | 137 | 18:30 | 126 | 14:00
Gollamari | 140 | 05:00 | 130 | 14:00 | SevenRings | 139 | 02:00 | 131 | 14:00
Gopalganj | 139 | 05:00 | 131 | 14:00 | ShahCement | 136 | 18:30 | 126 | 15:00
Gopalganj-400 | 141 | 05:00 | 135 | 14:00 | Shahjadpur | 136 | 00:00 | 132 | 13:00
Gulshan | 138 | 04:00 | 127 | 15:00 | Shahjibazar | 135 | 04:00 | 128 | 08:00
Halishahar | 132 | 03:00 | 128 | 19:30 | Shahmirpur | 135 | 18:00 | 130 | 15:00
Haripur | 136 | 18:30 | 127 | 15:00 | Shariatpur | 139 | 05:00 | 132 | 14:00
HaripurSBU | 135 | 04:00 | 127 | 15:00 | Sherpur | 136 | 23:00 | 124 | 03:00
Hasnabad | 136 | 05:00 | 129 | 13:00 | Shikalbaha | 125 | 06:00 | 119 | 14:00
Hathazari | 135 | 06:00 | 131 | 03:00 | Shikalbaha-230 | 136 | 07:00 | 131 | 00:00
Ishurdi | 138 | 01:00 | 130 | 11:00 | Shitalakhya | 135 | 05:00 | 126.2 | 15:00
Jaldhaka | 131 | 00:00 | 123 | 13:00 | Sholosohor | 135 | 05:00 | 130 | 14:00
Jamalpur | 139 | 17:00 | 128 | 02:00 | Shyampur | 135 | 18:00 | 128 | 15:00
Jashore | 134 | 01:00 | 123 | 14:00 | Shyampur-230 | 137 | 07:00 | 127 | 15:00
Jhenaidah | 135 | 05:00 | 126 | 12:00 | Siddhirganj | 136 | 18:00 | 128 | 14:00
Jhenaidah-230 | 138 | 05:00 | 127 | 12:00 | Sirajganj | 133 | 06:00 | 125 | 16:00
Joydebpur | 137 | 19:00 | 124 | 15:00 | Sonargaon | 130 | 03:00 | 125 | 13:00
Joypurhat | 130 | 05:00 | 120 | 10:00 | Sreemongol | 134 | 01:00 | 128 | 14:00
Juldah | 133 | 19:00 | 131 | 00:00 | Sreepur | 132 | 01:00 | 125 | 14:00
Kabirpur | 137 | 04:00 | 124 | 14:00 | Srinagar | 141 | 03:00 | 128 | 14:00
Kachua | 128 | 18:30 | 118 | 14:00 | SSM | 136 | 00:00 | 132 | 13:00
Kaliakoir | 136 | 04:00 | 126 | 14:00 | Sunamganj | 132 | 06:00 | 127 | 13:00
Kallyanpur | 137 | 01:00 | 128 | 14:00 | Sylhet | 133 | 01:00 | 128 | 14:00
Kalurghat | 135 | 06:00 | 130 | 14:00 | Sylhet-132 | 133 | 01:00 | 130 | 12:00
Kamrangirchar | 142 | 05:00 | 127 | 14:00 | Tangail | 128 | 03:00 | 120 | 14:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 135 | 08:00 | 120 | 13:00
Kasba | 131 | 18:30 | 121 | 15:00 | TK | 135 | 04:00 | 131 | 14:00
Kazla | 137 | 05:00 | 127 | 15:00 | Tongi | 142 | 04:00 | 130 | 13:00
Keranigonj | 142 | 05:00 | 128 | 15:00 | Ullahpara | 135 | 05:00 | 127 | 12:00
Khagrachori | 134 | 06:00 | 128 | 15:00 | Ullon | 138 | 01:00 | 127 | 15:00
Khulna | 138 | 06:00 | 128 | 14:00 | Uttara | 137 | 05:00 | 127 | 14:00
Khulna(S) | 140 | 05:00 | 130 | 14:00 | UttaraNew | 139 | 04:00 | 127 | 15:00
Khulshi | 133 | 07:00 | 127 | 00:00 | Zigatola | 141 | 05:00 | 128 | 15:00
Kishoreganj | 134 | 05:00 | 124 | 14:00
Kodda | 135 | 18:30 | 123 | 12:00
KSRM | 135 | 06:00 | 129 | 14:00
Kulaura | 135 | 01:00 | 130 | 15:00
Kurigram | 132 | 05:00 | 122 | 13:00
Kushtia | 136 | 05:00 | 127 | 12:00
Lalbag | 140 | 01:00 | 128 | 14:00
Lalmonirhat | 132 | 19:30 | 122 | 13:00
Madanganj | 134 | 04:00 | 123 | 14:00
Madaripur | 140 | 04:00 | 133 | 14:00
Madartek | 139 | 01:00 | 127 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division