## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: February 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-02-02 |  | 2025-01-01 |  | 2024-02-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12659.87 | 2025-02-25 | 11385.54 | 2025-01-31 | 11433 | 2024-02-20 | 16477 | 2024-04-30
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 6902.27 | 2025-02-08 | 6331.7 | 2025-01-04 | 6491 | 2024-02-26 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11385.54 | 2025-01-31 | 11385.54 | 2025-01-31 | 11433 | 2024-02-20 | 16477 | 2024-04-30
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11609.39 | 2025-02-18 | 10755.81 | 2025-01-28 | 11433 | 2024-02-20 | 14488 | 2024-05-16
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 19:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12119 | 2025-02-25 | 11385.54 | 2025-01-31 | 11600 | 2024-02-29 | 17200 | 2024-04-29
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11482.7239 |  | 10693.0548 |  | 10621.7586 |  | - | -
7 | Average Generation (MW) at Day Peak | 10803.4786 |  | 10062.5852 |  | 9975.931 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 936 | 2025-02-24 | 933 | 2025-01-26 | 927 | 2024-02-29 | 970 | 2024-07-06
|  |  | 23:30 |  | 22:30 |  | 22:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 157 | 2025-02-27 | 135 | 2025-01-06 | 134 | 2024-02-14 | 194 | 12/06/19
|  |  | 14:00 |  | 14:00 |  | 14:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 198 | 2025-02-24 | 138 | 2025-01-23 | 166 | 2024-02-19 | 4395 | 04/10/2022
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 11673 | 2025-02-24 | 10747 | 2025-01-23 | 11426 | 45341 | 14965 | 2024-05-16
|  |  | 19:00 |  | 19:00 | - | 0.79167 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-02-02 | 0 | 2025-01-01 | 0 | 45343 | - | -
|  |  | 19:00 |  | 18:00 |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 10784 | 2025-02-02 | 10336.5 | 2025-01-01 | 9940 | 2024-02-21 | - | -
|  |  | 19:00 |  | 18:00 |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 153 | 2025-02-25 | 90 | 2025-01-29 | 448 | 45328 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11072 | 2025-02-25 | 10341 | 2025-01-29 | 9431 | 45328 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-02-02 | 0 | 2025-01-01 | 0 | 45343 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10451 | 2025-02-02 | 9365 | 2025-01-01 | 9810 | 45343 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 21 |  | 12 |  | 19 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 24 |  | 10 |  | 20 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1181.7677 |  | 1538.3298 |  | 1547.5883 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 92.8264 |  | 40.8794 |  | 26.3507 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1088.9413 |  | 1497.4503 |  | 1521.2375 |  | - | -
23 | Net Generation of IPP (MKWH) | 2334.8935 |  | 2109.9074 |  | 2281.563 |  | - | -
23b | Net Generation by Generation Companies | 1804.9675 |  | 1968.7062 |  | 1785.399
24 | Net Generation of REB (MKWH) | 67.3293 |  | 63.5555 |  | 89.9855 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 257.6077 |  | 208.7373 |  | 118.5854 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 5553.7393 |  | 5848.3567 |  | 5796.7704 |  | - | -
26 | Energy Generation by Gas (MKWH) | 2920.098 |  | 3127.6858 |  | 3054.7436 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 259.6658 |  | 469.3291 |  | 16.4698 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 888.4431 |  | 426.0344 |  | 508.5277 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 0.60499 |  | 3.6257 |  | 28.5971 |  | - | -
30 | Energy Generation by Solar (MKWH) | 124.2522 |  | 93.1478 |  | 65.9163 |  | - | -
30b | Energy Generation by Wind (MKWH) | 0 |  | 0.64176 |  | 5.5733 |  | - | -
31 | Energy Generation by Coal (MKWH) | 1453.5016 |  | 1768.7717 |  | 2143.2933 |  | - | -
32 | Enegry Import from India (MKWH) | 1050.6819 |  | 1029.682 |  | 586.2757 |  | - | -
33 | Monthly Load Factor (%) | 78.7223 |  | 81.6792 |  | 70.7431 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: February 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12659.87 | 2025-02-25 | 19:00 Hr.
Generation Period
| Dhaka | MW | 4692.39
| Chattogram | MW | 1317
| Cumilla | MW | 1026.5
| Mymensingh | MW | 1029
| Sylhet | MW | 393
a) | Total supply in East zone | MW | 8457.89
| Khulna | MW | 1338
| Barisal | MW | 315.2
| Rajshahi | MW | 1227
| Rangpur | MW | 782
b) | Total supply in West zone | MW | 3662.2
c) | Total supply in both zone ( a+b) | MW | 12120.09
Ref: | 27.21.0000.603.16.087.20.920 | Date: 16/03/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:February 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 354 | 2025-02-26 | 19:30
| b) Ishurdi end | MW | 328 | 2025-02-22 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 840 | 2025-02-14 | 11:00
| b) Ishurdi end | MW | 120 | 2025-02-26 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.44664
| b) Ishurdi end | MKWH | 119.6736
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 116.0834
| b) Ishurdi end | MKWH | 0.43363
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 400 | 2025-02-26 | 19:30
| b)Serajganj end | MW | 634 | 2025-02-08 | 12:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2025-02-06 | 17:00
| b)Sirajganj end | MW | 90 | 2025-02-26 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 231.2369
| b)Sirajganj end | MKWH | 0.224
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 2e-08
| b)Sirajganj end | MKWH | 281.858
30 | Transmission loss of EWI /NO-2 | % | 2.75'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2338 | 2025-02-11 | 12:00
|  | MW | 1578
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2325 | 2025-02-11 | 12:00
|  | MW | 1577
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 30183 | 2025-02-11 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 30150 | 2025-02-11
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 485.624
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 488.829
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | -0.66
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirzapur 132/33kV | Transformer-02(E07) | 2025-02-03 04:03 | 2025-02-03 04:03 | 0 | T | 33 KV Pbs Outgoing feeder fault. 87.1 Trip T phase. | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-02-12 07:59 | 2025-02-12 08:29 | 0.020833 | T | 33 Kv Jamurki PBS feeder fult OC,EF | 25 | 12.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-02-01 05:14 | 2025-02-01 05:23 | 0.00625 | T | Under Frequency BCPU | 8 | 1.2 | Power interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2025-02-02 09:50 | 2025-02-02 10:25 | 0.024306 | T | Diff. Pickup Diff. relay | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 | 2025-02-24 13:15 | 2025-02-24 19:50 | 0.27431 | T | Earth Fault Alstom MVAJM15JA0754A and Micom P122 | 0 | 0 | No interruption
Tongi 230/132/33kV | T-2 | 2025-02-08 11:29 | 2025-02-08 12:40 | 0.049306 | T | None SPS triping | 14 | 16.5667 | Power interruption
Tongi 230/132/33kV | T-1 | 2025-02-08 12:29 | 2025-02-08 12:40 | 0.0076389 | T | None SPS tripping | 28 | 5.1333 | Power interruption
Tongi 230/132/33kV | T-3 | 2025-02-08 12:29 | 2025-02-08 12:40 | 0.0076389 | T | None SPS tripping. | 24 | 4.4 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-02-06 14:56 | 2025-02-06 16:40 | 0.072222 | E/O | Shutdown is taken by Tangail PBS due to high temperature maintenance work of 33 KV gorai feeder. | 100 | 173.3333 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-02-03 06:58 | 2025-02-03 09:07 | 0.089583 | E/O | Emergency maint.work | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 | 2025-02-24 16:16 | 2025-02-24 19:50 | 0.14861 | E/O | 33kv Shakhipur Feeder under ground cable fault. | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2025-02-07 08:47 | 2025-02-11 22:05 | 1900-01-03 13:18 | E/O | Oil Down FOR maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 06:07 |  | Unserved Energy: |  | 213.1333
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2025-02-09 03:20 | 2025-02-10 00:55 | 0.89931 | E/O | WT-01 and WT-02 Meter burn, Diff. realy ( siemens siprotec 7UT85) burn due to PBS 33 kv fault. | 0 | 0 | No interruption
Bhulta 132/33kV | GT1 | 2025-02-12 09:26 | 2025-02-12 16:02 | 0.275 | E/O | GT-1 winding temperature meter change. | 15 | 99 | Power interruption
Haripur 230/132kV | 132KV Bhult | 2025-02-15 10:14 | 2025-02-15 11:38 | 0.058333 | T | Trip Siprotec: General Trip, Zone-2, R-phase Trip, Y-phase Trip, A/R Off/BLK. | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-02-15 10:18 | 2025-02-15 10:41 | 0.015972 | T | Overload. Siprotec: General Trip, OC/EF/EFCOM, A/R Off/BLK. | 150 | 57.5 | Power interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-02-15 15:41 | 2025-02-15 17:30 | 0.075694 | E/O | RED HOT at other end. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2025-02-23 00:31 | 2025-02-25 18:24 | 1900-01-01 17:53 | E/O | To prevent further damage to the Transformer & the System from fire which has been lit inside the cable trench in front of 230/132 KV Auto TR-1. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-02-25 13:05 | 2025-02-25 15:12 | 0.088194 | E/O | 33KV CT connection recheck | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 | 2025-02-22 18:32 | 2025-02-22 19:25 | 0.036806 | T | Phase instantaneous fault | 4 | 3.5333 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2025-02-06 10:05 | 2025-02-07 14:43 | 1899-12-31 04:38 | E/O | Transformer -02 Bushing maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-2 | 2025-02-27 02:15 | 2025-02-27 02:23 | 0.0055556 | T | Due to 33 KV N-1 Feeder ( Palli Biddhut) by O/C & E/F ABB REF 630 | 48 | 6.4 | Power interruption
Nawabganj 132/33kV | TR-1 | 2025-02-12 08:01 | 2025-02-12 08:11 | 0.0069444 | T | Due to 33kV outgoing feeder(Kushumhati-8) breaker insulation failure. Overcurrent protection relay. | 9.5 | 1.5833 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-02-12 08:01 | 2025-02-12 08:12 | 0.0076389 | T | Due to 33kV outgoing feeder(Kusumhati-8) breaker insulation failure. Overcurrent protection relay. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-02-19 11:30 | 2025-02-19 13:06 | 0.066667 | E/O | PBS 33 kv barpa feeder ds red hot maintenance near 33 kv bus | 45 | 72 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2025-02-22 18:30 | 2025-02-22 19:30 | 0.041667 | T | Due to PBS 33kv Astha feed feeder earth fault. DIR E/F & O/C Relay. | 18 | 18 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-02-22 19:00 | 2025-02-22 20:35 | 0.065972 | T | Due to PBS Langolbond feeder 3 phase earth fault and at the same time auxiliary T2 fuse barrel burst. Directional O/C & E/C Relay. | 15 | 23.75 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-02-27 09:08 | 2025-02-27 10:28 | 0.055556 | E/O | Auxiliary Transformer-2 corrective maintenance work. Shutdown taken by PBS. | 30 | 40 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2025-02-27 10:48 | 2025-02-27 12:14 | 0.059722 | E/O | PBS 33kv MIEZ feeder corrective maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 16:44 |  | Unserved Energy: |  | 321.7667
Chattogram Grid Circle :
Coxsbazar 132/33kV | 405T-T1 | 2025-02-02 06:21 | 2025-02-02 07:42 | 0.05625 | T | Ukhiya 33kv feeder tripped No signal | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-02-11 12:20 | 2025-02-11 12:58 | 0.026389 | E/O | Pt checking by pdb | 0 | 0 | No interruption
Madunaghat 400/230kV | ATR-2 7106T | 2025-02-18 10:23 | 2025-02-18 13:02 | 0.11042 | T | CB pole discrepancy Trip, R phase CP pole discrepancy | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 | 2025-02-04 11:47 | 2025-02-04 13:42 | 0.079861 | E/O | Shutdown needed to clear out crow nests from 33KV gantry and to clean 132KV bushing. | 0 | 0 | No interruption
|  |  | Total : | 0.27292 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-02-26 21:01 | 2025-02-26 22:27 | 0.059722 | T | Palm cibat entered 33 kV bus that's why incomer 1 tripped and tr-1 tripped Rec650 | 0 | 0 | No interruption
Chandpur 132/33kV | 422T | 2025-02-05 17:16 | 2025-02-05 19:15 | 0.082639 | E/O | Pbs ReD hotaintainence | 19 | 37.6833 | Power interruption
Chowmuhani 132/33kV | TR1-415T | 2025-02-13 08:14 | 2025-02-13 12:16 | 0.16806 | T | Chow (33/11kv) T-4 trans Breaker trip Chow (33/11kv) T-3 Trans Y-Phase Incoming Loop Cut-off. And Verious feeder under ground cable Flashing and firing. Lockout RY Trip TR. PRD. | 30 | 121 | Power interruption
Chowmuhani 132/33kV | TR12 415T | 2025-02-13 08:14 | 2025-02-13 08:52 | 0.026389 | T | Chow (33/11kv) T-4 trans Breaker trip Chow (33/11kv) T-3 Trans Y-Phase Incoming Loop Cut-off. And Verious feeder under ground cable Flashing and firing. Over Current | 40 | 25.3333 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2025-02-04 01:42 | 2025-02-04 14:26 | 0.53056 | E/O | 132/33 KV Transformer-3 shutdown of under ground cable change( Y-Phase)for over temperature | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-02-04 18:33 | 2025-02-04 18:55 | 0.015278 | T | 33kv PDB Auxilary Transformer bushing loop burn O/C & E/F: Inst fault | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-02-04 18:33 | 2025-02-04 20:58 | 0.10069 | T | 33kv PDB Auxilary Transformer bushing loop burn N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-02-04 18:33 | 2025-02-04 18:55 | 0.015278 | T | 33kv PDB Auxilary Transformer bushing loop burn O/C & E/F: A & B-phase fault | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2025-02-22 04:02 | 2025-02-22 04:20 | 0.0125 | T | Fault Over Current | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-02-22 04:02 | 2025-02-22 04:20 | 0.0125 | T | Fault Over Current | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 00:34 |  | Unserved Energy: |  | 184.0167
Khulna Grid Circle :
Barguna 132/33kV | Transformer-1 | 2025-02-21 14:28 | 2025-02-21 14:43 | 0.010417 | T | Over Current & Earth Fault for WZPDCL-2 Bus side D/S Flashing. Over Current & Earth Fault Relay. | 5 | 1.25 | Power interruption
Barguna 132/33kV | Transformer-2 | 2025-02-21 14:28 | 2025-02-21 14:43 | 0.010417 | T | Over Current & Earth Fault for WZPDCL-2 Bus side D/S Flashing. Over Current & Earth Fault Relay | 0 | 0 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-02-27 06:42 | 2025-02-27 07:03 | 0.014583 | T | 33kv dopdopia feeder 2 fault Ins O/C,deff O/C,Ins E/F | 35 | 12.25 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-02-27 06:42 | 2025-02-27 07:00 | 0.0125 | T | 33 kv dopdopia feeder fault Ins O/C,Def O/C,Ins E/F | 23 | 6.9 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2025-02-17 19:54 | 2025-02-18 13:15 | 0.72292 | T | 33 KV Bamna PBS Feeder Fault. 50-OC DMT trip(A,B,C Phase) | 0 | 0 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2025-02-17 19:54 | 2025-02-17 21:15 | 0.05625 | T | 33 KV Bamna PBS feeder Fault 50 OC DMT trip. | 35 | 47.25 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2025-02-18 00:40 | 2025-02-18 01:14 | 0.023611 | E/O | Auxilary Transformer Fuse connection. | 30 | 17 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2025-02-18 00:40 | 2025-02-18 13:15 | 0.52431 | E/O | Aux -Tx fuse cut | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-02-02 20:48 | 2025-02-05 12:54 | 1900-01-01 16:06 | E/O | Underground cable problem | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-02-13 14:35 | 2025-02-13 14:46 | 0.0076389 | T | Trip due to 33KV therokhada Feeder Fault E/F | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2025-02-13 14:35 | 2025-02-13 14:46 | 0.0076389 | T | Trip due to 33KV therokhada Feeder Fault E/F | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-02-16 05:59 | 2025-02-16 06:26 | 0.01875 | T | Tripped due to REB 33KV feeder fault Dir OC, EF | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-02-08 08:52 | 2025-02-08 14:35 | 0.23819 | E/O | Due to WZPDCL | 0 | 0 | No interruption
Madaripur 132/33kV | T3-426T | 2025-02-22 17:57 | 2025-02-22 20:52 | 0.12153 | T | Earth Fault Siemens | 12 | 35 | Power interruption
|  |  | Total : | 1900-01-03 10:33 |  | Unserved Energy: |  | 119.65
HVDC Grid Circle :
Bheramara(GK) 132/33kV | TR-2 | 2025-02-01 16:28 | 2025-02-01 18:47 | 0.096528 | E/O | 33 kV BUS PT change | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-02-05 16:11 | 2025-02-05 16:22 | 0.0076389 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Jashore 132/33kV | T-1 | 2025-02-27 09:16 | 2025-02-28 19:17 | 1899-12-31 10:01 | E/O | Oil centrifuse | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 12:31 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2025-02-12 10:14 | 2025-02-12 10:59 | 0.03125 | E/O | Emergency redhot maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2025-02-12 11:26 | 2025-02-12 12:52 | 0.059722 | E/O | 33 KV CT emergency maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-02-12 13:10 | 2025-02-12 14:33 | 0.057639 | E/O | Emergency maintenance work at 33KV CT R phase | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2025-02-01 16:30 | 2025-02-01 18:15 | 0.072917 | E/O | Red hot maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2025-02-01 18:36 | 2025-02-01 19:39 | 0.04375 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-4 | 2025-02-27 07:52 | 2025-02-27 09:57 | 0.086806 | E/O | T-4 Transformer 132 CT Connector Redhot | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2025-02-19 11:48 | 2025-02-19 12:19 | 0.021528 | T | Due over current 50/51 OC Relay | 0 | 0 | Power interruption
Jaldhaka 132/33kV | 416T-2 | 2025-02-19 11:48 | 2025-02-19 12:19 | 0.021528 | T | Due over current 50/51 OC relay | 27 | 13.95 | Power interruption
Joypurhat 132/33kV | Transformer T-2 (417 T) | 2025-02-01 11:57 | 2025-02-01 12:26 | 0.020139 | E/O | Core Bushing Oil leakage | 0 | 0 | No interruption
Rahanpur 132/33kV | TR-2 (414T) | 2025-02-17 12:12 | 2025-02-17 13:50 | 0.068056 | E/O | 33kV side tariff meter change | 0 | 0 | No interruption
Rahanpur 132/33kV | TR-1 404T | 2025-02-17 13:58 | 2025-02-17 14:37 | 0.027083 | E/O | 33kV side tariff meter change. | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-02-09 14:50 | 2025-02-09 15:11 | 0.014583 | T | Dut to Bus Fault Siprotec 7SJ 82 | 26 | 9.1 | Power interruption
Rajshahi 132/33kV | Main | 2025-02-09 14:50 | 2025-02-09 15:07 | 0.011806 | T | Bus Fault Siprotec 7SJ82 | 75 | 21.25 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-02-22 14:45 | 2025-02-22 15:57 | 0.05 | T | BUS Fault RYB 3 Phase O/C | 27 | 32.4 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2025-02-22 14:46 | 2025-02-22 18:29 | 0.15486 | T | 50 Trip , 51 Trip | 0 | 0 | Power interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2025-02-22 14:48 | 2025-02-22 15:24 | 0.025 | T | BUS Fault Instant E/F | 35 | 21 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2025-02-22 16:37 | 2025-02-22 18:28 | 0.077083 | E/O | Cleaning og bird droppings. | 0 | 0 | No interruption
|  |  | Total : | 0.84375 |  | Unserved Energy: |  | 97.7
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-18 01:17 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Aminbazar Ckt-1 | 2025-02-04 09:35 | 2025-02-04 09:38 | 0.0020833 | T | Disc failure. | 184 | 9.2 | Power interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2025-02-03 06:53 | 2025-02-03 08:02 | 0.047917 | E/O | Emergency maint.work | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2025-02-03 06:54 | 2025-02-03 08:02 | 0.047222 | E/O | Emergency maint.work | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Kaliakair-ckt-2A(E08) | 2025-02-03 06:56 | 2025-02-03 08:43 | 0.074306 | E/O | Emergency maint.work | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Kaliakoir ckt-2B(E-09) | 2025-02-03 06:56 | 2025-02-03 08:43 | 0.074306 | E/O | Emergency maint.work | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2025-02-02 09:50 | 2025-02-02 10:26 | 0.025 | T | Z1 trip at 34.9 km. | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2025-02-22 08:38 | 2025-02-22 12:53 | 0.17708 | E/O | NLDC instruction. (working for bhaluka End) | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2025-02-27 15:08 | 2025-02-27 16:23 | 0.052083 | E/O | removal a kite | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-02-06 09:11 | 2025-02-06 09:38 | 0.01875 | T | Tripped | 150 | 67.5 | Power interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-02-25 08:55 | 2025-02-25 08:57 | 0.0013889 | T | Tripped | 70 | 2.3333 | Power interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-02-25 08:55 | 2025-02-25 08:57 | 0.0013889 | T | Tripped | 70 | 2.3333 | Power interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-02-25 09:00 | 2025-02-25 09:00 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-02-25 09:00 | 2025-02-25 09:00 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2025-02-28 11:40 | 2025-02-28 12:14 | 0.023611 | T | Tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-02-01 05:14 | 2025-02-01 09:15 | 0.16736 | T | Line tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Agargaon-01 | 2025-02-04 09:35 | 2025-02-04 19:04 | 0.39514 | T | Line tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2025-02-11 05:47 | 2025-02-11 20:08 | 0.59792 | T | Line tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-02-12 01:38 | 2025-02-12 15:22 | 0.57222 | T | General trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2025-02-12 02:29 | 2025-02-17 18:44 | 1900-01-04 16:15 | T | Dist.Relay | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-02-12 02:40 | 2025-02-12 20:33 | 0.74514 | T | Dist zoon -1 | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Mirpur-01 | 2025-02-22 18:02 | 2025-02-22 19:26 | 0.058333 | T | Rainy weather | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Mirpur-02 | 2025-02-22 18:05 | 2025-02-22 19:19 | 0.051389 | T | Rainy weather | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tangail-2 | 2025-02-03 06:45 | 2025-02-03 07:06 | 0.014583 | T | Zone -01 Trip | 141 | 49.35 | Power interruption
Kaliakoir 400/230/132kV | Tangail-1 | 2025-02-03 06:45 | 2025-02-03 07:07 | 0.015278 | T | Dir.Over Current | 147 | 53.9 | Power interruption
Muktagacha 132/33kV | RPCL-1 | 2025-02-23 11:02 | 2025-02-23 11:10 | 0.0055556 | T | Line tripped | 3 | 0.4 | Power interruption
Muktagacha 132/33kV | RPCL-2 | 2025-02-23 11:02 | 2025-02-23 11:11 | 0.00625 | T | Line tripped | 3 | 0.45 | Power interruption
Tangail 132/33kV | RPCL-2 | 2025-02-11 07:48 | 2025-02-11 07:52 | 0.0027778 | T | Distance OPTD | 0 | 0 | No interruption
|  |  | Total : | 1900-01-07 20:30 |  | Unserved Energy: |  | 185.4667
Dhaka (South) Grid Circle :
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2025-02-05 11:34 | 2025-02-05 14:53 | 0.13819 | E/O | Emergency maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2025-02-26 16:04 | 2025-02-26 19:53 | 0.15903 | T | Insulator disc crack. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-02-12 08:51 | 2025-02-17 18:45 | 1900-01-04 09:54 | E/O | Shutdown for maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-02-12 08:52 | 2025-02-12 20:34 | 0.4875 | E/O | Shutdown for maintenance work. | 100 | 1170 | Power interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-02-13 16:11 | 2025-02-13 20:30 | 0.17986 | E/O | Shutdown requested by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-02-19 08:53 | 2025-02-19 19:15 | 0.43194 | E/O | Aminbazar ckt-2 shutdown by NLDC | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2025-02-05 11:42 | 2025-02-05 14:56 | 0.13472 | E/O | SF6 Gas pressure return valve leakage maintenance on R- Phase | 0 | 0 | No interruption
Mogbazar 132/33kV | Rampura 1 | 2025-02-02 12:57 | 2025-02-02 15:33 | 0.10833 | E/O | Line Isolator Redhot | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2025-02-19 12:43 | 2025-02-19 13:21 | 0.026389 | T | distance 21/z1 PI 1 (dist/def) | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2025-02-22 15:03 | 2025-02-22 15:12 | 0.00625 | T | Unknown | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Fatullah-1(E06) | 2025-02-22 18:34 | 2025-02-22 23:20 | 0.19861 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2025-02-22 18:14 | 2025-02-22 21:27 | 0.13403 | T | Bad weather | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-2 | 2025-02-17 10:20 | 2025-02-17 13:14 | 0.12083 | E/O | Emergency maintenance at CB Point. | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2025-02-17 12:09 | 2025-02-17 13:17 | 0.047222 | T | Line distance protection | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2025-02-22 18:14 | 2025-02-22 19:11 | 0.039583 | T | Bad weather | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 15:00 |  | Unserved Energy: |  | 1170
Chattogram Grid Circle :
Khulshi 132/33kV | Khulshi-AKSPL Line | 2025-02-05 13:40 | 2025-02-05 15:14 | 0.065278 | E/O | Baloon Removing from tower no-28 | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Madunaghat Ckt-1 | 2025-02-15 11:58 | 2025-02-15 12:58 | 0.041667 | T | Tripped | 0 | 0 | No interruption
AKS 132/33kV | Khulshi | 2025-02-05 13:37 | 2025-02-05 15:14 | 0.067361 | E/O | Emergency shutdown from Khulshi to AKSPL 132 kv line Circuit-1 because a balloon shown in tower no. 28 & remove it from tower. | 0 | 0 | No interruption
AKS 132/33kV | Bar Aulia | 2025-02-25 08:38 | 2025-02-25 15:30 | 0.28611 | E/O | AKSPL- Baraulia 132 KV line S/D due to Tower No. 57 maintenance. | 0 | 0 | No interruption
GPH 230/33kV | ABUL KHAIR | 2025-02-02 09:56 | 2025-02-02 14:33 | 0.19236 | E/O | Maintenance work in B phase Isolator. | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2025-02-19 09:22 | 2025-02-19 13:13 | 0.16042 | E/O | finding red hot, in hathajari line. R and Y phase | 0 | 0 | No interruption
Hathazari 230/132/33kV | GPH-01 | 2025-02-19 09:20 | 2025-02-19 13:13 | 0.16181 | E/O | Red hot maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Baraulia Feeder | 2025-02-19 00:24 | 2025-02-19 01:40 | 0.052778 | E/O | Regarding Shut Down Baraulia 132 KV Line Feeder For SF6 Gas refill. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-1 | 2025-02-15 11:58 | 2025-02-15 12:57 | 0.040972 | T | General Trip, Zone1, 67N Trip, R-Phase fault | 0 | 0 | No interruption
Rampur 230/132/33 | Halishahar-2 | 2025-02-13 17:19 | 2025-02-13 17:42 | 0.015972 | T | Distance | 0 | 0 | No interruption
Rampur 230/132/33 | Halishahar-1 | 2025-02-27 07:12 | 2025-02-27 12:44 | 0.23056 | E/O | Red Hot Maintenance at Monopoll Shagorika | 0 | 0 | No interruption
Rampur 230/132/33 | Halishahar-2 | 2025-02-27 07:14 | 2025-02-27 12:44 | 0.22917 | E/O | Only energize line S/D for Hali-1 saftey. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 13:04 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 230/132/33kV | Cumilla(N) 230 kV Ckt-2 | 2025-02-01 07:10 | 2025-02-01 07:28 | 0.0125 | T | Distance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2025-02-18 16:55 | 2025-02-18 17:17 | 0.015278 | T | Distance | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-02 | 2025-02-06 09:09 | 2025-02-06 14:35 | 0.22639 | E/O | For Ramgonj S/S | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2025-02-09 13:36 | 2025-02-09 13:47 | 0.0076389 | T | Fault | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2025-02-08 06:40 | 2025-02-08 06:57 | 0.011806 | T | N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2025-02-18 16:55 | 2025-02-18 17:17 | 0.015278 | T | Stormy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2025-02-25 08:25 | 2025-02-25 15:59 | 0.31528 | E/O | S/D taken by ashuganj end | 0 | 0 | No interruption
Bibiana 400/230kV | Bibiyana-III GTG | 2025-02-10 10:15 | 2025-02-10 16:37 | 0.26528 | E/O | Oil leckage | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2025-02-02 06:13 | 2025-02-02 06:33 | 0.013889 | T | unknown | 0 | 0 | No interruption
|  |  | Total : | 0.88333 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2025-02-02 12:46 | 2025-02-02 17:12 | 0.18472 | E/O | Emergency maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2025-02-14 07:46 | 2025-02-15 16:32 | 1899-12-31 08:46 | E/O | Maintenance at Aminbazar Substation | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2025-02-22 09:58 | 2025-02-23 12:17 | 1899-12-31 02:19 | E/O | Emergency maintenance | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2025-02-13 11:59 | 2025-02-14 23:37 | 1899-12-31 11:38 | E/O | Due to low voltage. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2025-02-18 12:50 | 2025-02-18 12:50 | 0 | E/O | Due to low voltage | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 03:09 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara 230/132kV | GTG (NW) | 2025-02-07 06:49 | 2025-02-10 11:21 | 1900-01-02 04:32 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF22 | 2025-02-03 11:44 | 2025-02-03 16:39 | 0.20486 | T | Tripeed by capacitor unbalance 60/61 instant L2 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-02-23 10:53 | 2025-02-23 11:03 | 0.0069444 | T | Tripped | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 09:37 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura 230/132kV | Bogra 132KV Line-2 | 2025-02-08 09:41 | 2025-02-08 12:28 | 0.11597 | E/O | Emergency maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2025-02-12 04:55 | 2025-02-12 05:14 | 0.013194 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2025-02-20 11:51 | 2025-02-20 13:12 | 0.05625 | E/O | 98 No Tower Insulator maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-2 | 2025-02-20 13:16 | 2025-02-20 15:08 | 0.077778 | E/O | 98 No Tower Insulator maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-02-23 08:36 | 2025-02-23 12:37 | 0.16736 | T | Tripped | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-02-10 16:59 | 2025-02-10 19:07 | 0.088889 | E/O | Energy Meter Accuracy Test | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-02-10 16:59 | 2025-02-10 19:08 | 0.089583 | E/O | Energy Meter Accuracy Test | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-2 | 2025-02-23 08:36 | 2025-02-23 12:40 | 0.16944 | T | Trip | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132 kV Rajshahi ckt-01 | 2025-02-09 14:50 | 2025-02-09 15:05 | 0.010417 | T | E/F IDMT START | 46 | 11.5 | Power interruption
Rajshahi 230/132/33kV | 132 kV Rajshahi ckt-02 | 2025-02-09 14:50 | 2025-02-09 15:09 | 0.013194 | T | E/F IDMT START | 46 | 14.5667 | Power interruption
Natore 132/33kV | Rajshahi-1 | 2025-02-09 14:50 | 2025-02-09 15:25 | 0.024306 | T | Tripped | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-2 | 2025-02-09 14:50 | 2025-02-09 15:26 | 0.025 | T | Tripped | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-02-23 10:54 | 2025-02-23 11:03 | 0.00625 | T | Ishurdi 132/33 kv side fault | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2025-02-21 07:17 | 2025-02-21 07:28 | 0.0076389 | T | Tripped | 55 | 10.0833 | Power interruption
Sirajganj 132/33kV | Solar Park 1 | 2025-02-05 15:27 | 2025-02-05 16:16 | 0.034028 | E/O | BCRECL has taken Shutdown due to CB mechanical problem at 68MW Sirajgonj Solar park End. | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-1 | 2025-02-22 18:55 | 2025-02-23 07:25 | 0.52083 | E/O | As per the Instruction of ALDC bogura, Sherpur Ckt -1 CB Open .Due to Shajadpur -Ullapara Line Over Load, | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-2 | 2025-02-22 18:55 | 2025-02-23 07:27 | 0.52222 | E/O | As per the Instruction of ALDC bogura ,Sherpur Ckt -2 CB Open .Due to Shajadpur -Ullapara Line Over Load, | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 22:37 |  | Unserved Energy: |  | 36.15
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-27 09:09 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 230kV Transformer-1 ( 705T1) | 2025-02-06 08:24 | 2025-02-06 17:03 | 8:39 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV | Auxiliary Tr-1 | 2025-02-06 08:24 | 2025-02-06 17:03 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 132kV Transformer-2 (415T2) | 2025-02-08 08:16 | 2025-02-08 14:43 | 6:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 230kV Transformer-2 ( 715T2) | 2025-02-08 08:16 | 2025-02-08 14:48 | 6:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 132kV Transformer-1 (405T1) | 2025-02-13 08:09 | 2025-02-13 14:03 | 5:54 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-02-02 13:55 | 2025-02-02 15:13 | 1:18 | S/O | Relay tripping test by SPMD | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-02 | 2025-02-05 10:18 | 2025-02-09 15:11 | 100:53 | S/O | 230/132KV TR-2 B-PH Oil Senrifusing | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-02-12 11:42 | 2025-02-22 17:05 | 245:23 | S/O | Oil sentrifusing & protection test by SPMD | 0 | 0 | No interruption
Bhaluka 132/33kV | Bu | 2025-02-11 09:53 | 2025-02-11 10:24 | 0:31 | S/O | TR-3 project work jumpering. | 0 | 0 | No interruption
Bhaluka 132/33kV | Bu | 2025-02-11 10:38 | 2025-02-11 15:31 | 4:53 | S/O | TR-3 project work jumpering | 0 | 0 | No interruption
Bhaluka 132/33kV | Bu | 2025-02-22 08:53 | 2025-02-22 12:57 | 4:04 | S/O | T3 jumper connection | 55 | 223.6667 | Power interruption
Bhaluka 132/33kV | Bus Section- | 2025-02-23 07:50 | 2025-02-23 13:18 | 5:28 | S/O | Development work | 15 | 82 | Power interruption
Jamalpur 132/33kV | T-1 | 2025-02-01 10:17 | 2025-02-01 11:37 | 1:20 | S/O | Project work bus D/S change | 0 | 0 | No interruption
Jamalpur 132/33kV | Bu | 2025-02-01 10:30 | 2025-02-03 16:56 | 54:26 | S/O | Project work bus D/S change | 0 | 0 | No interruption
Jamalpur 132/33kV | T-1 | 2025-02-03 15:12 | 2025-02-03 16:50 | 1:38 | S/O | Project work | 0 | 0 | No interruption
Jamalpur 132/33kV | Bu | 2025-02-03 17:03 | 2025-02-03 21:23 | 4:20 | S/O | Project work | 0 | 0 | No interruption
Jamalpur 132/33kV | Bu | 2025-02-06 09:08 | 2025-02-06 10:10 | 1:02 | S/O | Mym ckt-1 bus d/s change Work | 0 | 0 | No interruption
Jamalpur 132/33kV | Bu | 2025-02-06 10:16 | 2025-02-08 13:35 | 51:19 | S/O | Mym ckt-1 bus d/s change Work | 0 | 0 | No interruption
Jamalpur 132/33kV | Bu | 2025-02-08 13:45 | 2025-02-08 16:50 | 3:05 | S/O | Mymensingh ckt-1 Bus D.S. replacement. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-1 | 2025-02-26 08:42 | 2025-02-26 17:41 | 8:59 | S/O | Loop & connector replace of 33kv Nnadina feeder incomming DS. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 | 2025-02-27 08:20 | 2025-02-27 16:59 | 8:39 | S/O | Tr-03 &Tr-04 Section Isolator Maintenance Work. | 12 | 103.8 | Power interruption
Joydebpur 132/33kV | GT-2 | 2025-02-26 12:33 | 2025-02-26 15:33 | 3:00 | S/O | Rajendrapur-2 33 kV Feeder CT Test. | 40 | 120 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-02-22 07:26 | 2025-02-25 12:34 | 77:08 | S/O | Oil centrifusing work. | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-02-26 07:26 | 2025-03-01 11:01 | 75:35 | S/O | a) 33kv CB and DS instsllation by dhaka PBS-1 b) Oil centifusing work of T-3 | 50 | 3779.1667 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bu | 2025-02-12 08:53 | 2025-02-12 17:45 | 8:52 | S/O | Project work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bu | 2025-02-13 08:12 | 2025-02-13 16:41 | 8:29 | S/O | Project Work IDRNPP | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bu | 2025-02-15 08:47 | 2025-02-15 17:00 | 8:13 | S/O | Project work. | 0 | 0 | No interruption
Kallyanpur 132/33kV | Reserve | 2025-02-09 08:55 | 2025-02-09 17:18 | 8:23 | S/O |  | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-1 (132kV) | 2025-02-27 11:09 | 2025-03-03 11:58 | 96:49 | S/O | Oil Centrifuging Work. | 0 | 0 | No interruption
Kodda 132/33kV | Tr-4 (436T) | 2025-02-16 11:44 | 2025-02-16 16:46 | 5:02 | S/O | Colour work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-02-17 11:37 | 2025-02-17 16:32 | 4:55 | S/O | Colour work. | 0 | 0 | No interruption
Mirpur 132/33kV | T1 | 2025-02-02 11:28 | 2025-02-02 12:29 | 1:01 | S/O | Anuual Maintenance on 132 KV, Relay test by spmd PGCB. | 0 | 0 | No interruption
Mirpur 132/33kV | T2 | 2025-02-03 10:48 | 2025-02-03 11:21 | 0:33 | S/O | Annual Maintenance Relay test | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve | 2025-02-11 08:20 | 2025-02-11 16:57 | 8:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Main | 2025-02-12 08:26 | 2025-02-12 15:51 | 7:25 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV | Main | 2025-02-13 07:58 | 2025-02-13 16:19 | 8:21 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-02-15 11:12 | 2025-02-15 13:10 | 1:58 | S/O | oil temperature meter maintenance | 20 | 39.3333 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-02-24 10:26 | 2025-02-24 14:50 | 4:24 | S/O | OLTC oil Change. | 0 | 0 | No interruption
Netrakona 132/33kV | Transformer-1 (415T) | 2025-02-08 08:12 | 2025-02-08 08:12 | 0:00 | S/O | X-former Replacement works. | 0 | 0 | No interruption
Satmasjid 132/33kV | 132/33 KV Transformer-1 | 2025-02-11 10:01 | 2025-02-11 15:26 | 5:25 | S/O | 132kv & 33kv energy meter testing. 33 kv TR-1 MFM change. | 0 | 0 | No interruption
Satmasjid 132/33kV | 132/33 KV Transformer-2 | 2025-02-11 15:58 | 2025-02-11 16:50 | 0:52 | S/O | 132 kv & 33kv energy meter testing. 33kv TR-1 & TR-2 side magnetic contact change in PT CKT. | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-02-12 09:54 | 2025-02-12 17:58 | 8:04 | S/O | Interlock update work | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-02-13 08:49 | 2025-02-13 18:45 | 9:56 | S/O | Inter lock implemantation work | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-02-15 10:37 | 2025-02-15 18:03 | 7:26 | S/O | Interlock work | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-02-16 09:38 | 2025-02-16 19:52 | 10:14 | S/O | Interlock update work. | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-02-17 10:58 | 2025-02-17 12:55 | 1:57 | S/O | Interlock installation work. | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-02-18 09:03 | 2025-02-18 19:48 | 10:45 | S/O | Interlock work | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2025-02-19 10:23 | 2025-02-19 13:56 | 3:33 | S/O | Interlock checkup | 0 | 0 | No interruption
Savar 132/33kV | Main Bu | 2025-02-22 10:29 | 2025-02-22 15:33 | 5:04 | S/O | For hotspot maintenance work. | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-02-27 11:34 | 2025-02-27 17:08 | 5:34 | S/O | Interlock work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2025-02-01 08:48 | 2025-02-01 14:44 | 5:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Tr-1 | 2025-02-16 10:29 | 2025-02-16 11:09 | 0:40 | S/O | Realy Setting (SPMD) | 25 | 16.6667 | Power interruption
Tangail 132/33kV | Tr-2 | 2025-02-16 11:11 | 2025-02-16 11:52 | 0:41 | S/O | Realy Setting (SPMD) | 0 | 0 | Power interruption
Tangail 132/33kV | Tr-4 | 2025-02-16 12:20 | 2025-02-16 13:27 | 1:07 | S/O | Realy Setting (SPMD) | 0 | 0 | Power interruption
Tongi 230/132/33kV | T-1 | 2025-02-12 14:14 | 2025-02-12 15:34 | 1:20 | S/O | Shutdown taken by DESCO. | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bu | 2025-02-17 11:01 | 2025-02-17 16:42 | 5:41 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus | 2025-02-25 12:20 | 2025-03-04 15:00 | 170:40 | S/O | Bus conductor replacement work. | 0 | 0 | No interruption
Tongi 230/132/33kV | T-02 | 2025-02-28 06:41 | 2025-02-28 07:45 | 1:04 | S/O | Bus-1 conductor replacement work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2025-02-28 08:17 | 2025-02-28 10:06 | 1:49 | S/O | 230kv Bus conductor replacement work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2025-02-28 15:38 | 2025-02-28 17:39 | 2:01 | S/O | 230 kV Busbar-1 replacement work. | 0 | 0 | No interruption
Tongi 230/132/33kV | T-02 | 2025-02-28 17:44 | 2025-02-28 18:31 | 0:47 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 1900-02-14 18:50 |  | Unserved Energy: |  | 4364.6333
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2025-02-10 10:20 | 2025-02-10 13:07 | 2:47 | S/O | Shutdown requsition by BPDB for commissioning of Fertilizer (33kV outgiong-3) feeder. | 58 | 161.4333 | Power interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-02-17 13:35 | 2025-02-17 15:16 | 1:41 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Se | 2025-02-28 09:48 | 2025-02-28 23:43 | 13:55 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-02-10 09:45 | 2025-02-10 17:37 | 7:52 | S/O | hydrolic pipe change | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main | 2025-02-23 13:05 | 2025-02-23 17:10 | 4:05 | S/O | Zinzira-2 ckt. Faulty Bus riser change. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-02-24 07:26 | 2025-02-25 12:47 | 29:21 | S/O | CT CHANGE | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2025-02-05 07:37 | 2025-02-05 13:04 | 5:27 | S/O | oil Leakage Maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-2 | 2025-02-05 13:01 | 2025-02-05 13:40 | 0:39 | S/O | 33KV Kalatiya feeder problem | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2025-02-10 07:14 | 2025-02-12 14:17 | 55:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-2 | 2025-02-13 07:38 | 2025-02-15 16:23 | 56:45 | S/O | Annual maintence and renovation work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2025-02-15 07:09 | 2025-02-15 10:04 | 2:55 | S/O | Annual maintenance and renovation work . | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 | 2025-02-14 08:20 | 2025-02-14 16:30 | 8:10 | S/O | Yearly maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 | 2025-02-22 09:25 | 2025-02-22 15:21 | 5:56 | S/O | Maint.work | 0 | 0 | No interruption
Madartek 132/33kV | GT-02 | 2025-02-05 09:36 | 2025-02-05 09:36 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madartek 132/33kV | GT-02 | 2025-02-05 17:17 | 2025-02-05 17:50 | 0:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 | 2025-02-22 10:27 | 2025-02-22 14:01 | 3:34 | S/O | Oil Leakage Maintenance by DPDC. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 | 2025-02-19 15:10 | 2025-02-19 16:05 | 0:55 | S/O | Tr-3 Transformer Oil Leakage Maintenance Work. | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2025-02-22 08:22 | 2025-02-22 13:50 | 5:28 | S/O | Due to DS clamp Maintenance of Kusumhati feeder. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-02-05 07:15 | 2025-02-05 18:00 | 10:45 | S/O | Dead line checking | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-02-09 07:38 | 2025-02-09 20:26 | 12:48 | S/O | Dead line check | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-02-10 07:27 | 2025-02-10 19:18 | 11:51 | S/O | Bhulta 03(230kV) shut down for annual maintenance (Deadline). | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-02-12 06:59 | 2025-02-12 16:10 | 9:11 | S/O | Dead line check | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-02-13 07:27 | 2025-02-13 15:04 | 7:37 | S/O | Dead line check | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busba | 2025-02-22 08:21 | 2025-02-22 19:39 | 11:18 | S/O | G2G Project work | 0 | 0 | No interruption
Rampura 230/132kV | NLDC Trafo | 2025-02-22 10:27 | 2025-02-22 13:27 | 3:00 | S/O | Annual Maintenance on NLDC side | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busba | 2025-02-23 08:28 | 2025-02-23 18:55 | 10:27 | S/O | Maint.work | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busba | 2025-02-25 10:44 | 2025-02-25 15:38 | 4:54 | S/O | CT test by SPMD-1 | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 04 | 2025-02-28 06:42 | 2025-02-28 08:54 | 2:12 | S/O | G2G Project work | 0 | 0 | No interruption
Rampura 230/132kV | NLDC Trafo | 2025-02-28 06:44 | 2025-02-28 09:20 | 2:36 | S/O | G2G Project work | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2025-02-28 08:23 | 2025-02-28 14:38 | 6:15 | S/O | Ten delta Test | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 1 | 2025-02-08 08:10 | 2025-02-08 23:26 | 15:16 | S/O | Relay changing work | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2025-02-27 13:50 | 2025-02-27 15:00 | 1:10 | S/O | 33 kv Bus -2 (Feeder-6) Red hot Maintenance. | 12 | 14 | Power interruption
|  |  | Total : | 1900-01-12 02:26 |  | Unserved Energy: |  | 175.4333
Chattogram Grid Circle :
Agrabad 132/33kV | MTR-01 (406T) | 2025-02-16 09:00 | 2025-02-16 13:27 | 4:27 | S/O | Relay Test by SPMD,Ctg | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-1, 406T | 2025-02-22 08:26 | 2025-02-22 11:08 | 2:42 | S/O | Maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-2, 416T | 2025-02-22 11:14 | 2025-02-22 14:20 | 3:06 | S/O | 33 kv Bus-02 Annual maintenance work | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-2 (125/140 MVA) | 2025-02-01 10:21 | 2025-02-05 12:09 | 97:48 | S/O | For Annual Maintenance, S/D taken by BSRM SS. | 0 | 0 | No interruption
Coxsbazar 132/33kV | Main | 2025-02-08 05:30 | 2025-02-08 08:35 | 3:05 | S/O | Circuit Breaker(402B) Commission. | 77 | 237.4167 | Power interruption
Coxsbazar 132/33kV | Main | 2025-02-15 06:02 | 2025-02-15 09:25 | 3:23 | S/O | CB commissioning & replacement | 90 | 304.5 | Power interruption
Coxsbazar 132/33kV | Main | 2025-02-22 06:48 | 2025-02-22 09:20 | 2:32 | S/O | CB replacement & new CB commissioning | 88 | 222.9333 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-02-12 09:09 | 2025-02-12 13:41 | 4:32 | S/O | maintenance work for gph | 0 | 0 | No interruption
GPH 230/33kV | Transformer -2 (D07) | 2025-02-13 09:03 | 2025-02-14 11:35 | 26:32 | S/O | general maintenanace | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-02 | 2025-02-01 09:20 | 2025-02-01 17:45 | 8:25 | S/O | Annual Maintenace | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-01 | 2025-02-01 09:20 | 2025-02-01 17:45 | 8:25 | S/O | Annual Maintenace | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-01 | 2025-02-03 12:25 | 2025-02-03 16:11 | 3:46 | S/O | Maint.work | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-04 | 2025-02-04 09:45 | 2025-02-04 16:15 | 6:30 | S/O | Maint.work | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2025-02-05 09:25 | 2025-02-05 17:37 | 8:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2025-02-18 09:27 | 2025-02-18 19:51 | 10:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-04 | 2025-02-19 09:44 | 2025-02-20 17:51 | 32:07 | S/O | oil leakage maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-02 | 2025-02-21 08:30 | 2025-02-27 16:37 | 152:07 | S/O | Maint.work | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 | 2025-02-27 09:54 | 2025-02-27 13:13 | 3:19 | S/O | Protection Relay test. | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-2 | 2025-02-27 13:16 | 2025-02-27 16:07 | 2:51 | S/O | Protection relay test. | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2025-02-22 07:20 | 2025-02-22 09:51 | 2:31 | S/O | 33kV outdoor bus maintenance wok by BPDB | 10 | 25.1667 | Power interruption
Khulshi 132/33kV | 415T (T2) | 2025-02-22 07:20 | 2025-02-22 13:23 | 6:03 | S/O | 33kV outdoor bus maintenance wok by BPDB. | 0 | 0 | No interruption
Khulshi 132/33kV | 425T(BSRM) | 2025-02-22 08:51 | 2025-02-22 17:46 | 8:55 | S/O | Annual maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2025-02-03 09:25 | 2025-02-03 17:40 | 8:15 | S/O | 33KV Bus Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2025-02-12 12:54 | 2025-02-17 21:39 | 128:45 | S/O | Oil leakage maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | ATR-2 7106T | 2025-02-19 09:20 | 2025-02-19 17:28 | 8:08 | S/O | Project Work | 0 | 0 | No interruption
Madunaghat 400/230kV | ATR-3 7206T | 2025-02-20 08:45 | 2025-03-02 19:32 | 250:47 | S/O | Hydro Fire fighting install work | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 01 | 2025-02-06 10:33 | 2025-02-06 16:57 | 6:24 | S/O | Maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 02 | 2025-02-07 08:53 | 2025-02-07 16:58 | 8:05 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-02-01 20:06 |  |  |  | 790.0167
Cumilla Grid Circle :
Chandpur 132/33kV | Bu | 2025-02-01 09:05 | 2025-02-01 14:35 | 5:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Bu | 2025-02-02 08:20 | 2025-02-02 13:06 | 4:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 422T | 2025-02-20 09:30 | 2025-02-20 12:13 | 2:43 | S/O | Maint.work | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR3-435T | 2025-02-14 10:08 | 2025-02-14 10:58 | 0:50 | S/O | Station Auxiliary TR fuse replacement. | 15 | 12.5 | Power interruption
Chowmuhani 132/33kV | TR1-415T | 2025-02-15 08:15 | 2025-02-15 14:38 | 6:23 | S/O | 33 kv Tr-01 Bus and Loop Maintenance Work | 25 | 159.5833 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-04 | 2025-02-12 07:35 | 2025-02-12 11:40 | 4:05 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 | 2025-02-06 07:24 | 2025-02-06 11:31 | 4:07 | S/O | Red Hot Works to 33kv bus ds | 20 | 82.3333 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2025-02-12 09:58 | 2025-02-12 10:10 | 0:12 | S/O | Maint.work | 22 | 4.4 | Power interruption
Cumilla(S) 132/33kV | TR-1 | 2025-02-12 10:19 | 2025-02-17 11:13 | 120:54 | S/O | None | 30 | 3627 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-02-12 10:19 | 2025-02-12 10:25 | 0:06 | S/O | Maint.work | 30 | 3 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-02-17 11:20 | 2025-02-22 10:11 | 118:51 | S/O | Painting work | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-4 | 2025-02-26 07:44 | 2025-02-26 09:35 | 1:51 | S/O | 33KV Bus maintenance By PDB. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-3 | 2025-02-26 09:00 | 2025-02-26 10:19 | 1:19 | S/O | 33KV Bus maintenance by PDB. | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-3 | 2025-02-09 11:32 | 2025-02-09 11:52 | 0:20 | S/O | SCADA Intergration Work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-02-05 07:16 | 2025-02-05 08:34 | 1:18 | S/O | For BPDB maintenance work. | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-02-07 08:35 | 2025-02-07 10:02 | 1:27 | S/O | 33kV Bus-1 Maintenance work | 15 | 21.75 | Power interruption
Kachua 132/33kV | Main Bu | 2025-02-01 08:29 | 2025-02-01 16:07 | 7:38 | S/O | For project work | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 | 2025-02-06 07:20 | 2025-02-06 09:58 | 2:38 | S/O | Station Aux-1 transformer fuse set replace and jumper wire connection | 12 | 31.6 | Power interruption
Ramganj 132/33kV | 132 Kv Bu | 2025-02-18 08:20 | 2025-02-18 09:30 | 1:10 | S/O | 132kV Main Bus-2 DS maintenance of 132kV Desh Energy Ckt-1 | 0 | 0 | No interruption
Ramganj 132/33kV | 132 Kv Bus | 2025-02-18 09:32 | 2025-02-18 10:25 | 0:53 | S/O | 132kV Main Bus-1 DS maintenance of 132kV Desh Energy Ckt-1 | 0 | 0 | No interruption
Ramganj 132/33kV | 132 Kv Bus | 2025-02-19 08:36 | 2025-02-19 09:10 | 0:34 | S/O | 132kV Main Bus-1 DS maintenance of 132kV Desh Energy Ckt-2 | 0 | 0 | No interruption
Ramganj 132/33kV | 132 Kv Bu | 2025-02-19 09:12 | 2025-02-19 09:35 | 0:23 | S/O | 132kV Main Bus-2 DS maintenance of 132kV Desh Energy Ckt-2 | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-02-03 07:10 | 2025-02-03 08:58 | 1:48 | S/O | CB=152, B Phase Bus loop joint redhot maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-02-18 07:17 | 2025-02-18 09:17 | 2:00 | S/O | S/D Taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-02-18 07:17 | 2025-02-18 09:16 | 1:59 | S/O | S/D Taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-02-23 10:35 | 2025-02-23 12:26 | 1:51 | S/O | shutdown taken by PBS for new feeder commissioning | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-02-23 10:35 | 2025-02-23 12:26 | 1:51 | S/O | shutdown taken by PBS for new feeder commissioning | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2025-02-22 08:11 | 2025-02-22 14:51 | 6:40 | S/O | 132Kv Transformer -1 Shutdown due to BPDB, Sunamganj Feeder Bay Extension workk | 8 | 53.3333 | Power interruption
Sunamganj 132/33kV | Tr-1 | 2025-02-23 10:19 | 2025-02-23 18:33 | 8:14 | S/O | Tr - 1` R Phase Oil Centrifusing | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-02-03 08:44 | 2025-02-04 18:26 | 33:42 | S/O | 132 Bus Section 3-4 Shutdown | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-02-05 08:23 | 2025-02-05 08:27 | 0:04 | S/O | Load Shift to T4 X-former Informed to NLDC 299724 | 10 | 0.66667 | Power interruption
|  |  | Total : | 1900-01-13 10:07 |  |  |  | 3996.1667
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-2 (413 T) | 2025-02-01 12:28 | 2025-02-01 13:10 | 0:42 | S/O | 33 kv bus PT rearrange | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2025-02-01 13:24 | 2025-02-01 14:49 | 1:25 | S/O | 33 kv bus PT rearrange | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-1 | 2025-02-22 11:34 | 2025-02-22 12:48 | 1:14 | S/O | WZPDCL-2 33Kv Bus Side D/S Maintenance | 2.5 | 3.0833 | Power interruption
Barishal 230/132kV | ATR-2 | 2025-02-22 09:19 | 2025-02-22 13:28 | 4:09 | S/O | Oil likeage repair | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2025-02-22 14:39 | 2025-02-22 17:27 | 2:48 | S/O | Oil leakage repair | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-02-28 07:11 | 2025-02-28 10:25 | 3:14 | S/O | Red hot repair | 5 | 16.1667 | Power interruption
Barishal 230/132kV | T-5 | 2025-02-28 07:11 | 2025-02-28 10:27 | 3:16 | S/O | Red hot repair | 20.5 | 66.9667 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2025-02-11 11:01 | 2025-02-11 12:46 | 1:45 | S/O | Maint.work | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2025-02-19 06:14 | 2025-02-19 14:17 | 8:03 | S/O | Maint.work | 12.5 | 100.625 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2025-02-19 06:14 | 2025-02-19 14:10 | 7:56 | S/O | None | 12.5 | 99.1667 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2025-02-20 07:47 | 2025-02-20 17:52 | 10:05 | S/O | Copper ber change | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-1 | 2025-02-05 09:59 | 2025-02-05 12:45 | 2:46 | S/O | Maint.work | 20 | 55.3333 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-02-07 07:33 | 2025-02-08 12:10 | 28:37 | S/O | Centrifuge | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-02-13 11:45 | 2025-02-13 12:37 | 0:52 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2025-02-14 08:05 | 2025-02-15 11:36 | 27:31 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | Bu | 2025-02-15 09:58 | 2025-02-15 10:34 | 0:36 | S/O | Red hot | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2025-02-08 07:31 | 2025-02-08 10:22 | 2:51 | S/O | Wzpdcl 33 kv loop connection work. | 14 | 39.9 | Power interruption
Gopalganj 400/132kV | ATR-04 | 2025-02-05 10:06 | 2025-02-05 19:54 | 9:48 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-05 | 2025-02-06 10:31 | 2025-02-06 21:12 | 10:41 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-05 | 2025-02-08 10:36 | 2025-02-08 19:41 | 9:05 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-05 | 2025-02-09 09:16 | 2025-02-09 18:00 | 8:44 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-04 | 2025-02-09 18:14 | 2025-02-09 22:06 | 3:52 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-05 | 2025-02-22 11:05 | 2025-02-22 12:51 | 1:46 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2025-02-22 10:07 | 2025-02-22 10:07 | 0:00 | S/O | Maintenance Work NWPGCL 800MW Project | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-2 | 2025-02-22 10:08 | 2025-02-22 17:05 | 6:57 | S/O | Maintenance Work at NWPGCL Project | 0 | 0 | No interruption
Khulna(S) 230/132kV | 230 KV Main Bus | 2025-02-22 10:43 | 2025-02-22 16:36 | 5:53 | S/O | Maintenance Work at NWPGCL Project | 0 | 0 | No interruption
Mongla 132/33kV | Main | 2025-02-22 05:19 | 2025-02-22 10:33 | 5:14 | S/O | Bus conduct change | 13 | 68.0333 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2025-02-08 12:07 | 2025-03-09 17:23 | 701:16 | S/O | Power Station end silicon coating work | 0 | 0 | No interruption
Payra 400/132/33kV | 132/33 kV Transformer-04 | 2025-02-21 08:32 | 2025-02-21 15:06 | 6:34 | S/O | Relay replacement work | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2025-02-25 11:50 | 2025-02-25 15:17 | 3:27 | S/O | Faculty Bay Unit Relay Replace Work. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2025-02-26 10:30 | 2025-02-26 16:47 | 6:17 | S/O | Faulty relay change. | 0 | 0 | No interruption
Rajbari 132/33kV | 132 kV Bu | 2025-02-26 11:45 | 2025-02-26 16:39 | 4:54 | S/O | Transformer-1 faulty relay and Busbar protection relay testing | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-02-26 08:27 | 2025-02-26 12:32 | 4:05 | S/O | 33 kv bus conductor maintenance | 50 | 204.1667 | Power interruption
Shariatpur 132/33kV | T1-406T | 2025-02-15 08:43 | 2025-02-15 14:03 | 5:20 | S/O | Maintenance by PBS. | 10 | 53.3333 | Power interruption
Shariatpur 132/33kV | T2-416T | 2025-02-22 08:42 | 2025-02-22 13:18 | 4:36 | S/O | Maintenance by PBS. | 8 | 36.8 | Power interruption
|  |  | Total : | 1900-02-05 18:19 |  | Unserved Energy : |  | 743.575
HVDC Grid Circle
Baghabari 230/132kV | T-2 Bank | 2025-02-19 09:27 | 2025-02-19 15:17 | 5:50 | S/O | Relay replace | 0 | 0 | No interruption
BIPTC | 21T01 | 2025-02-28 06:01 | 2025-02-28 12:20 | 6:19 | S/O | Emergency replacement of failed oil cooling pump of L-2 phase converter transformer of block-01 | 0 | 0 | No interruption
BIPTC | 11T01 | 2025-02-28 06:01 | 2025-02-28 12:20 | 6:19 | S/O | Emergency replacement of failed oil cooling pump of L-2 phase converter transformer of block-01 | 0 | 0 | No interruption
BIPTC | 22T01 | 2025-02-28 15:04 | 2025-02-28 18:05 | 3:01 | S/O | For replacement of burnt main MCB & magnetic contactor of one cooler group for converter transformer | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2025-02-28 06:58 | 2025-02-28 09:35 | 2:37 | S/O | 33kV bus maintenance | 35 | 91.5833 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-02-28 06:59 | 2025-02-28 09:36 | 2:37 | S/O | 33kV bus maintenance | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2025-02-01 08:21 | 2025-02-01 10:10 | 1:49 | S/O | 33 kv busbar maintenance work and 33 kv all feeder annual maintenance work will be done by WZPDCL | 10 | 18.1667 | Power interruption
Kushtia 132/33kV | T2 | 2025-02-01 08:22 | 2025-02-01 11:23 | 3:01 | S/O | 33 kv busbar maintenance work and 33 kv all feeder annual maintenance work will be done by WZPDCL | 30 | 90.5 | Power interruption
Kushtia 132/33kV | T-3 | 2025-02-22 08:13 | 2025-02-22 11:34 | 3:21 | S/O | T-3A 33 kV Bus Extension | 25 | 83.75 | Power interruption
Ullahpara 132/33kV | Power Transformer -1 | 2025-02-27 11:56 | 2025-02-27 12:41 | 0:45 | S/O | Replacing Energy Meter of TR-1 | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer -1 | 2025-02-27 11:57 | 2025-02-27 12:39 | 0:42 | S/O | Replacing Energy Meter of TR-1 | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer-2 | 2025-02-27 13:03 | 2025-02-27 13:33 | 0:30 | S/O | Replacing Energy Meter of TR-2 | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer-2 | 2025-02-27 13:04 | 2025-02-27 13:31 | 0:27 | S/O | Replacing Energy Meter of TR-2 | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 13:18 |  | Unserved Energy : |  | 284
Bogura Grid Circle:
Bogura 132/33kV | Transformer-3 | 2025-02-16 06:50 | 2025-02-16 18:03 | 11:13 | S/O | 33 kV Busbar up-gradation work. | 0 | 0 | Power interruption
Bogura 132/33kV | Transformer-4 | 2025-02-16 06:50 | 2025-02-16 08:20 | 1:30 | S/O | 33 kV Busbar up-gradation work. | 25 | 37.5 | Power interruption
Bogura 132/33kV | Transformer-4 | 2025-02-17 07:14 | 2025-02-17 15:46 | 8:32 | S/O | 33 KV Bus Upgrading Work. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-02-18 07:17 | 2025-02-18 19:29 | 12:12 | S/O | 33kV Bus bar up gradation work. | 0 | 0 | No interruption
Bogura 132/33kV | 132KV Bu | 2025-02-18 08:40 | 2025-02-18 11:40 | 3:00 | S/O | For T-1, 132kV Transformer 132kV Bus-B to DS Loop conductor up-gradation work. | 0 | 0 | No interruption
Bogura 132/33kV | 132KV Bu | 2025-02-18 12:10 | 2025-02-18 15:14 | 3:04 | S/O | T-1 132kV Bus-A to DS loop Conductor up gradation work. | 0 | 0 | No interruption
Bogura 132/33kV | 132KV Bu | 2025-02-19 10:35 | 2025-02-19 13:12 | 2:37 | S/O | Due to T-1 132kv Bus A loop Connection. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-02-20 08:35 | 2025-02-20 17:43 | 9:08 | S/O | T-3 & T-4 Transformer 33 kv bus coupler Isolator change | 0 | 0 | Power interruption
Bogura 132/33kV | Transformer-4 | 2025-02-20 08:35 | 2025-02-20 17:42 | 9:07 | S/O | T-3 & T-4 Transformer 33 kv bus coupler Isolator change | 15 | 136.75 | Power interruption
Bogura 132/33kV | Transformer-2 | 2025-02-22 07:05 | 2025-02-22 09:16 | 2:11 | S/O | 33kv Bus Upgrading Work. | 30 | 65.5 | Power interruption
Bogura 132/33kV | Transformer-2 | 2025-02-22 18:44 | 2025-02-22 19:49 | 1:05 | S/O | t-1&T-2 33kv BUS work | 25 | 27.0833 | Power interruption
Bogura 132/33kV | Transformer-1 | 2025-02-24 13:28 | 2025-02-24 14:34 | 1:06 | S/O | Project work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 | 2025-02-24 15:38 | 2025-02-24 16:18 | 0:40 | S/O | Metering CT polarity change Work. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-2 | 2025-02-24 17:16 | 2025-02-24 17:16 | 0:00 | S/O | For T-1 Full load Test | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-2 | 2025-02-25 07:18 | 2025-02-25 07:18 | 0:00 | S/O | 33kv Bus Upgrading Work. | 0 | 0 | Power interruption
Bogura 132/33kV | Transformer-1 | 2025-02-25 07:19 | 2025-02-25 09:12 | 1:53 | S/O | 33kv Bus Upgrading Work. | 25 | 47.0833 | Power interruption
Bogura 132/33kV | Transformer-1 | 2025-02-25 16:29 | 2025-02-25 17:58 | 1:29 | S/O | 33 KV bus coupler loop change. | 30 | 44.5 | Power interruption
Bogura 132/33kV | 132KV Bu | 2025-02-27 08:56 | 2025-03-02 13:19 | 76:23 | S/O | Shutdown taken for T-2 transformer B-bus isolator change. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV BUS | 2025-02-24 14:48 | 2025-02-24 15:10 | 0:22 | S/O | Bus LA Grounding Rearrangement. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV BUS | 2025-02-24 15:21 | 2025-02-24 16:22 | 1:01 | S/O | Bus LA Grounding Rearrangement. | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2025-02-11 08:27 | 2025-02-11 14:32 | 6:05 | S/O | T 2 maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2025-02-28 07:35 | 2025-02-28 10:03 | 2:28 | S/O | 33 Bus Maintenace | 27 | 66.6 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-02-28 07:46 | 2025-02-28 11:45 | 3:59 | S/O | 33 Bus Maintenace | 0 | 0 | Power interruption
Naogaon 132/33kV | T-3 | 2025-02-01 07:43 | 2025-02-01 14:28 | 6:45 | S/O | Annual Maintenance by NESCO Naogaon | 36 | 243 | Power interruption
Naogaon 132/33kV | T-2 | 2025-02-01 07:46 | 2025-02-01 14:26 | 6:40 | S/O | Annual Maintenance by NESCO Naogaon | 20 | 133.3333 | Power interruption
Naogaon 132/33kV | T-1 | 2025-02-01 07:46 | 2025-02-01 14:26 | 6:40 | S/O | Annual Maintenance by NESCO Naogaon | 0 | 0 | Power interruption
Naogaon 132/33kV | T-2 | 2025-02-04 12:37 | 2025-02-04 16:33 | 3:56 | S/O | T-2,33 KV CB Trip coil maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-02-19 10:10 | 2025-02-23 13:15 | 99:05 | S/O | T-2, 132 kv CSE installation & XLPE cable Termination. With T-2 33KV CB Change. | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-02-23 16:09 | 2025-02-27 17:44 | 97:35 | S/O | 132 KV CSE installation & XLPE cable Termination. | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 | 2025-02-28 10:23 | 2025-03-03 16:52 | 78:29 | S/O | Project work. | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2025-02-15 08:46 | 2025-02-15 09:46 | 1:00 | S/O | 33kV Bus maintenance | 30 | 30 | Power interruption
Purbasadipur 132/33kV | Single | 2025-02-08 07:15 | 2025-02-08 08:55 | 1:40 | S/O | maintenance | 180 | 300 | Power interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2025-02-17 09:25 | 2025-02-17 10:19 | 0:54 | S/O | maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-2 Transformer (413T) | 2025-02-17 09:30 | 2025-02-17 09:30 | 0:00 | S/O | maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-4 Transformer | 2025-02-23 07:16 | 2025-02-23 11:12 | 3:56 | S/O | maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-02-26 09:31 | 2025-02-26 17:10 | 7:39 | S/O | Fire fighting project | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-02-27 10:01 | 2025-02-27 16:29 | 6:28 | S/O | maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2025-02-09 08:19 | 2025-02-09 17:23 | 9:04 | S/O | maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-02-13 08:19 | 2025-02-13 09:38 | 1:19 | S/O | MFT / IED Changing Work | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2025-02-13 08:14 | 2025-02-13 19:03 | 10:49 | S/O | T-3 Punch list rectification work. | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2025-02-14 08:24 | 2025-02-14 16:50 | 8:26 | S/O | PGNS(G2G) project, has taken shutdown for 33kV T3 & T4 Section DS Clamps Replacement Work. | 0 | 0 | No interruption
Sirajganj 132/33kV | T4-(445) | 2025-02-14 08:24 | 2025-02-14 16:50 | 8:26 | S/O | PGNS(G2G) project, has taken shutdown for 33kV T3 & T4 Section DS Clamps Replacement Work. | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2025-02-23 14:17 | 2025-02-23 14:59 | 0:42 | S/O | For Energy Meter Change | 0 | 0 | No interruption
Sirajganj 132/33kV | T4-(445) | 2025-02-23 15:02 | 2025-02-23 15:40 | 0:38 | S/O | For Energy Meter Change. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-20 15:16 |  | Unserved Energy : |  | 1131.35
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 4058:22 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:February 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-02-03 08:31 | 2025-02-03 18:08 | 9:37 | S/O | Shutdown due to Deep Cleaning. | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-02-04 08:19 | 2025-02-04 10:37 | 2:18 | S/O | Annual Maintenance ( Deep Cleaning of Insulator Disc) | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-02-05 08:24 | 2025-02-05 20:13 | 11:49 | S/O | Shutdown due to Annual Maintenance( Deep Cleaning). | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2025-02-09 07:50 | 2025-02-09 09:28 | 1:38 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-02-11 07:24 | 2025-02-11 10:01 | 2:37 | S/O | Annual Maintenance ( Removing Bird's nest from 6No Tower) | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2025-02-11 10:02 | 2025-02-11 19:01 | 8:59 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2025-02-12 08:23 | 2025-02-12 19:04 | 10:41 | S/O | Annual Maintenance.(Deep Cleaning) | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2025-02-23 10:17 | 2025-03-05 15:00 | 244:43 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2025-02-22 08:28 | 2025-02-22 12:54 | 4:26 | S/O | T3 jumper connection | 55 | 243.8333 | Power interruption
Jamalpur 132/33kV | 132KV UMPL Ckt-02 | 2025-02-01 09:25 | 2025-02-03 21:20 | 59:55 | S/O | Project work bus D/S change. | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-02-06 08:52 | 2025-02-08 17:07 | 56:15 | S/O | Bus d/s change Work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2025-02-08 09:42 | 2025-02-08 17:25 | 7:43 | S/O | Deadline checking. | 10 | 77.1667 | Power interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2025-02-10 11:02 | 2025-02-10 12:24 | 1:22 | S/O | Realy Test | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-02-10 12:26 | 2025-02-10 13:22 | 0:56 | S/O | Relay Test | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-02-11 08:57 | 2025-02-11 17:54 | 8:57 | S/O | Dead Line Checking | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2025-02-05 07:56 | 2025-02-05 18:37 | 10:41 | S/O | due to relay Changing work by SPMD-2 | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-01 | 2025-02-08 08:54 | 2025-02-08 17:49 | 8:55 | S/O | DS Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2025-02-09 08:27 | 2025-02-09 17:33 | 9:06 | S/O | annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-01 | 2025-02-11 11:59 | 2025-02-11 12:00 | 0:01 | S/O | Relay Testing Work by SPMD | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-02-11 12:49 | 2025-02-11 19:47 | 6:58 | S/O | Maint.work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2025-02-12 10:18 | 2025-02-12 21:05 | 10:47 | S/O | Maint.work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2025-02-13 12:46 | 2025-02-13 21:55 | 9:09 | S/O | SPMD WORK | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-02-18 08:37 | 2025-02-18 17:27 | 8:50 | S/O | RELAY TESTING | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-02-20 08:34 | 2025-02-20 14:01 | 5:27 | S/O | Protection Checking by SPMD | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2025-02-04 10:13 | 2025-02-04 16:50 | 6:37 | S/O | Maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2025-02-11 09:40 | 2025-02-20 14:32 | 220:52 | S/O | Shifting to New Control Room | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2025-02-20 14:50 | 2025-02-20 16:44 | 1:54 | S/O | G to G Project worek | 0 | 0 | No interruption
Kishoreganj 132/33kV | Ashuganj Ckt-2 | 2025-02-23 10:15 | 2025-03-05 14:58 | 244:43 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2025-02-04 10:10 | 2025-02-04 16:52 | 6:42 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-02-06 08:50 | 2025-02-08 17:15 | 56:25 | S/O | NLDC AE. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2025-02-11 09:41 | 2025-02-20 14:33 | 220:52 | S/O | NLDC reporting desk -2 | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-02-01 08:27 | 2025-02-01 17:19 | 8:52 | S/O | Annual maintenance ( Dead line cheaking) | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-02-02 08:21 | 2025-02-02 17:00 | 8:39 | S/O | Annual maintenance. | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-1 | 2025-02-15 13:07 | 2025-02-15 18:10 | 5:03 | S/O | Interlocking work | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-02-22 09:45 | 2025-02-22 12:09 | 2:24 | S/O | For hotspot maintenance. | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-1 | 2025-02-27 10:04 | 2025-02-27 12:32 | 2:28 | S/O | Interlock work | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2025-02-27 10:12 | 2025-02-27 14:23 | 4:11 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-02-02 12:48 | 2025-02-02 21:50 | 9:02 | S/O | Bay Extension Work. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-02-03 08:26 | 2025-02-03 19:53 | 11:27 | S/O | Line bypass by the contractor | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2025-02-10 08:58 | 2025-02-10 10:09 | 1:11 | S/O | Relay Testing. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2025-02-10 10:13 | 2025-02-10 10:38 | 0:25 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2025-02-10 10:38 | 2025-02-10 17:45 | 7:07 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-New Tongi Ckt-2 | 2025-02-12 11:09 | 2025-02-12 15:41 | 4:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-02-14 07:13 | 2025-02-14 12:22 | 5:09 | S/O | S/D taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-02-17 08:24 | 2025-02-22 09:32 | 121:08 | S/O | Shutdown taken by Manikganj Grid via NLDC for ERS Tower installation. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2025-02-17 09:36 | 2025-02-17 16:04 | 6:28 | S/O | For relay testing work. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-02-19 07:40 | 2025-02-19 14:28 | 6:48 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-02-23 07:37 | 2025-02-27 17:40 | 106:03 | S/O | Shutdown taken by Manikganj Grid ss via NLDC. | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2025-02-14 07:14 | 2025-02-15 16:30 | 33:16 | S/O | Dead line checking and disk cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-02-18 08:56 | 2025-02-18 21:47 | 12:51 | S/O | Disk cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-02-19 08:52 | 2025-02-19 19:16 | 10:24 | S/O | Annual dead line checking & disx cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-02-20 08:54 | 2025-02-20 18:05 | 9:11 | S/O | Paininting work and insulator disk cleaning tower no-1/2 | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2025-02-20 10:11 | 2025-02-20 19:26 | 9:15 | S/O | Disc cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2025-02-22 09:58 | 2025-02-23 12:16 | 26:18 | S/O | Disc cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-02-23 08:46 | 2025-02-23 18:04 | 9:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-02-24 08:33 | 2025-02-24 17:20 | 8:47 | S/O | Tower painting work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2025-02-25 10:51 | 2025-02-25 17:55 | 7:04 | S/O | Dick cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2025-02-26 09:46 | 2025-02-26 15:57 | 6:11 | S/O | Disc cleaning works | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-01 | 2025-02-27 08:39 | 2025-02-27 18:11 | 9:32 | S/O | Tower painting work, Mirpur grid works on that line | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2025-02-12 07:48 | 2025-02-12 16:28 | 8:40 | S/O | Development work | 30 | 260 | Power interruption
Kabirpur 132/33kV | Tongi-2 | 2025-02-14 07:11 | 2025-02-14 12:21 | 5:10 | S/O | River crossing tower work. | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2025-02-19 07:38 | 2025-02-19 14:29 | 6:51 | S/O | Dead line checking. | 30 | 205.5 | Power interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2025-02-22 07:50 | 2025-02-22 15:21 | 7:31 | S/O | Disc Cleaning | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2025-02-23 09:09 | 2025-02-23 12:46 | 3:37 | S/O | Line Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2025-02-24 08:27 | 2025-02-24 15:24 | 6:57 | S/O | Deep Disk Cleaning in bricks field area | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2025-02-25 09:21 | 2025-02-25 09:21 | 0:00 | S/O | Disc cleaning work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-02-26 08:50 | 2025-02-26 12:45 | 3:55 | S/O | Disk deep cleaning. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2025-02-03 09:06 | 2025-02-03 10:19 | 1:13 | S/O | Relay Testing work by SMPD2 | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-02-14 08:25 | 2025-03-01 14:53 | 366:28 | S/O | Conductor stringing to Tower no 4&5 Amin bazar CKT-1. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2025-02-13 13:16 | 2025-02-13 14:58 | 1:42 | S/O | Maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2025-02-24 09:21 | 2025-02-24 17:16 | 7:55 | S/O | Tower Insulator Disc Change | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-02-25 09:07 | 2025-02-25 16:26 | 7:19 | S/O | Tower Insulator Disc Change | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2025-02-16 10:50 | 2025-02-16 11:29 | 0:39 | S/O | Realy Setting (SPMD) | 25 | 16.25 | Power interruption
Tangail 132/33kV | Kaliakair-2 | 2025-02-16 11:31 | 2025-02-16 12:16 | 0:45 | S/O | Realy Setting (SPMD) | 25 | 18.75 | Power interruption
Tangail 132/33kV | RPCL-1 | 2025-02-16 12:25 | 2025-02-16 13:24 | 0:59 | S/O | Realy Setting (SPMD) | 25 | 24.5833 | Power interruption
Tangail 132/33kV | RPCL-2 | 2025-02-16 13:41 | 2025-02-16 14:04 | 0:23 | S/O | Realy Setting (SPMD) | 25 | 9.5833 | Power interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2025-02-11 10:42 | 2025-02-11 13:45 | 3:03 | S/O | Relay Testing Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-02 | 2025-02-16 11:15 | 2025-02-16 16:03 | 4:48 | S/O | Relay test | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-02-16 16:14 | 2025-02-16 17:24 | 1:10 | S/O | SPMD work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Summit/Kodda PS | 2025-02-26 08:49 | 2025-02-26 12:44 | 3:55 | S/O | Disk deep cleaning. | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2025-02-26 06:42 | 2025-02-26 09:08 | 2:26 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-03-29 22:25 |  | Unserved Energy: |  | 855.6667
Dhaka (South) Grid Circle :
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-02-08 08:50 | 2025-02-08 14:59 | 6:09 | S/O | Cradle guard installation for Ruppur to Dhaka line | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-02-08 08:50 | 2025-02-08 14:59 | 6:09 | S/O | Cradle guard installation for Ruppur to Dhaka line | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-02-16 08:24 | 2025-02-16 16:51 | 8:27 | S/O | Insulator disk cleaning work requsition by Dhamrai 132/33kV S/S. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-02-17 07:49 | 2025-02-17 17:08 | 9:19 | S/O | Insulator Disc cleaning | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-02-18 08:27 | 2025-02-18 16:47 | 8:20 | S/O | Insuletor Disc cleaning by Dhamrai Grid Substation | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-02-19 08:29 | 2025-02-19 15:24 | 6:55 | S/O | Requisition form Dhamrai Grid for Disc cleaning work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-02-28 07:30 | 2025-02-28 16:36 | 9:06 | S/O | 400kV Stringing purpose work Ghorashal to purbachal. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-02-28 07:30 | 2025-02-28 16:39 | 9:09 | S/O | 400kV Stringing purpose work Ghorashal to purbachal. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2025-02-01 09:19 | 2025-02-01 17:35 | 8:16 | S/O | Dead line checking at Nawabganj end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2025-02-02 08:52 | 2025-02-02 15:01 | 6:09 | S/O | Dead line cheking and yearly maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2025-02-05 09:02 | 2025-02-05 17:29 | 8:27 | S/O | Dead line checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2025-02-06 08:26 | 2025-02-06 14:02 | 5:36 | S/O | Dead line check. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2025-02-25 10:50 | 2025-02-25 17:55 | 7:05 | S/O | Work at AminBazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2025-02-26 09:45 | 2025-02-26 16:58 | 7:13 | S/O | Maientenance work at AminBazar end. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-1 | 2025-02-03 08:45 | 2025-02-03 12:46 | 4:01 | S/O | As per request of Backup NLDC. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2025-02-03 12:51 | 2025-02-03 17:12 | 4:21 | S/O | As per order of Backup NLDC. | 0 | 0 | No interruption
Maniknagar 132/33kV | Kazla Ckt -1 | 2025-02-23 10:20 | 2025-02-23 14:42 | 4:22 | S/O | Red phase LA change | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2025-02-25 08:12 | 2025-02-25 11:15 | 3:03 | S/O | Reserve Bus & Line Bus DS Maintenance work. | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-1 | 2025-02-05 08:26 | 2025-02-08 18:09 | 81:43 | S/O | Aircraft obstruction Light installation between Tower no 30 and 31. | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-2 | 2025-02-09 07:21 | 2025-02-10 14:34 | 31:13 | S/O | Aircraft obstruction Light installation . | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-02-11 10:46 | 2025-02-11 20:08 | 9:22 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Reliance PP 400KV Ckt-1 | 2025-02-11 11:37 | 2025-02-11 12:12 | 0:35 | S/O | Testing for SAS operation | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Reliance PP 400KV Ckt-2 | 2025-02-11 12:26 | 2025-02-11 13:35 | 1:09 | S/O | Testing of SAS operation | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-02-18 09:15 | 2025-02-18 21:46 | 12:31 | S/O | Maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2025-02-20 07:47 | 2025-02-20 12:50 | 5:03 | S/O | Shutdown instructed by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-02-20 13:03 | 2025-02-20 15:19 | 2:16 | S/O | Maintenance work | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj Ckt-1 | 2025-02-03 08:46 | 2025-02-03 12:49 | 4:03 | S/O | Deadline Checking | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2025-02-03 12:49 | 2025-02-03 17:14 | 4:25 | S/O | Dead Line Check | 0 | 0 | No interruption
Postogola 132/33kV | Hasnabad Circuit-2 | 2025-02-20 11:13 | 2025-02-20 11:13 | 0:00 | S/O | Yearly maintenance | 0 | 0 | No interruption
Postogola 132/33kV | Hasnabad Circuit-1 | 2025-02-20 12:38 | 2025-02-20 12:38 | 0:00 | S/O | Yearly maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt-02 | 2025-02-05 07:15 | 2025-02-05 18:00 | 10:45 | S/O | Dead line checking | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt-03 | 2025-02-09 07:38 | 2025-02-09 20:26 | 12:48 | S/O | Dead line check | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt-03 | 2025-02-10 07:27 | 2025-02-10 19:18 | 11:51 | S/O | Bhulta 03(230kV) shut down for annual maintenance (Deadline). | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt-04 | 2025-02-12 06:59 | 2025-02-12 16:10 | 9:11 | S/O | Dead line check | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt-04 | 2025-02-13 07:27 | 2025-02-13 15:04 | 7:37 | S/O | Dead line check | 0 | 0 | No interruption
Sonargaon 132/33kV | Bashundhara Line | 2025-02-02 11:03 | 2025-02-02 13:20 | 2:17 | S/O | multi-meter change purpose. | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2025-02-04 07:23 | 2025-02-06 16:02 | 56:39 | S/O | Shutdown Taken by Ghorasal power station for Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-02 | 2025-02-05 07:16 | 2025-02-05 17:59 | 10:43 | S/O | Annual Maintenance work by Rampura Grid Substation. | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-03 | 2025-02-09 07:40 | 2025-02-09 20:24 | 12:44 | S/O | Shutdown taken by Rampura 230/132 kV grid susstation | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-03 | 2025-02-10 07:29 | 2025-02-10 19:15 | 11:46 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-04 | 2025-02-12 07:00 | 2025-02-12 16:06 | 9:06 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-04 | 2025-02-13 07:27 | 2025-02-13 15:02 | 7:35 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Sonargaon 2 | 2025-02-17 10:19 | 2025-02-17 13:15 | 2:56 | S/O | From other end. | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2025-02-28 09:13 | 2025-02-28 18:04 | 8:51 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-2 | 2025-02-28 09:13 | 2025-02-28 18:04 | 8:51 | S/O | Maint.work | 0 | 0 | No interruption
Mogbazar 132/33kV | Rampura 2 | 2025-02-02 09:14 | 2025-02-02 12:56 | 3:42 | S/O | Maint.work | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-02 | 2025-02-19 08:39 | 2025-02-19 17:18 | 8:39 | S/O | Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-02 | 2025-02-20 08:56 | 2025-02-20 14:58 | 6:02 | S/O | Shut down was taken from B.baria grid ss. | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-1 | 2025-02-01 09:17 | 2025-02-01 17:35 | 8:18 | S/O | Deadline checking. | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-1 | 2025-02-02 08:51 | 2025-02-02 15:03 | 6:12 | S/O | Deadline checking | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-2 | 2025-02-05 09:01 | 2025-02-05 17:16 | 8:15 | S/O | Dead line Checking | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-2 | 2025-02-06 08:25 | 2025-02-06 13:55 | 5:30 | S/O | Deadline checking for yearly maintenance. | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2025-02-02 09:15 | 2025-02-02 12:55 | 3:40 | S/O | Work@ Mogbazar End for Annual Maintenance. | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2025-02-02 12:58 | 2025-02-02 15:32 | 2:34 | S/O | Maintetance. Mogbazar 1 End. | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2025-02-18 08:46 | 2025-02-18 20:04 | 11:18 | S/O | Maint.work | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 1 | 2025-02-08 08:08 | 2025-02-08 23:27 | 15:19 | S/O | Realy change of 230kV end | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 1 | 2025-02-28 09:11 | 2025-02-28 18:03 | 8:52 | S/O | Maintenance work Haripur SS ends | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 2 | 2025-02-28 09:11 | 2025-02-28 18:03 | 8:52 | S/O | Maintenance work Haripur SS ends | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 1 | 2025-02-05 08:28 | 2025-02-08 18:09 | 81:41 | S/O | Internal work of Maniknagar end | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-1 | 2025-02-26 10:28 | 2025-02-26 12:56 | 2:28 | S/O | Haripur - Sonargaon Ckt- 01, Tower No. 30 Suspension Disk Nut Bolt replacement | 0 | 0 | No interruption
|  |  | Total : | 1900-01-25 15:29 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
BSRM 230/33kV | AKSML Ckt | 2025-02-15 08:48 | 2025-02-15 16:03 | 7:15 | S/O | For Deadline Checking, S/D taken by Baraulia SS. | 0 | 0 | No interruption
BSRM 230/33kV | AKSML Ckt | 2025-02-16 09:36 | 2025-02-16 16:48 | 7:12 | S/O | Annual Line Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2025-02-22 06:51 | 2025-02-22 07:31 | 0:40 | S/O | SD taken by Cox'sBazar | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-02-22 06:51 | 2025-02-22 09:20 | 2:29 | S/O | SD taken by Cox'sBazar | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-02-22 16:10 | 2025-02-22 16:19 | 0:09 | S/O | Instructed by NLDC for bus coupler operation at Cox's GSS. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2025-02-24 08:19 | 2025-02-24 17:22 | 9:03 | S/O | Disc Change and Cleaning at Brick Field Area. | 30 | 271.5 | Power interruption
GPH 230/33kV | BSRM CKT-1 | 2025-02-15 08:59 | 2025-02-15 16:01 | 7:02 | S/O | annual maintenance | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2025-02-16 09:27 | 2025-02-16 16:01 | 6:34 | S/O | annual maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Rampur Ckt-1 | 2025-02-27 07:15 | 2025-02-27 12:58 | 5:43 | S/O | Red hot R phase at monopole sagorika end | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Julda Ckt. line | 2025-02-28 08:23 | 2025-02-28 08:23 | 0:00 | S/O | Due to terminal tower jumper loop connection work of Khulsi ckt -3 by ESPNER project. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Baraulia Circuit-2 | 2025-02-05 08:30 | 2025-02-05 13:09 | 4:39 | S/O | Annual maintenance dead line checking | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Baraulia Circuit-2 | 2025-02-08 08:23 | 2025-02-08 16:02 | 7:39 | S/O | Annual maintenance (dead line checking) | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-02-28 08:27 | 2025-02-28 08:27 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Shikalbaha 230kV Ckt.-1 | 2025-02-16 09:01 | 2025-02-16 15:08 | 6:07 | S/O | Project work | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Hathazari 230kV Ckt.-2 | 2025-02-17 09:09 | 2025-02-17 16:05 | 6:56 | S/O | Project work by CCCE | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Old Madunaghat 230kV Ckt.-1 | 2025-02-20 08:50 | 2025-02-20 16:58 | 8:08 | S/O | Maintenance | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Old Madunaghat 230kV Ckt.-2 | 2025-02-22 10:27 | 2025-02-22 16:39 | 6:12 | S/O | Project Work | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Madunaghat Ckt-1 | 2025-02-24 08:45 | 2025-02-24 12:51 | 4:06 | S/O | Disc Changing work by Khulshi Grid | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Khulshi Ckt-1 | 2025-02-24 13:15 | 2025-02-24 14:43 | 1:28 | S/O | Disc Changing Work by Khulshi Grid | 0 | 0 | No interruption
Agrabad 132/33kV | Rampur-01 | 2025-02-09 11:40 | 2025-02-09 16:25 | 4:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agrabad 132/33kV | Rampur-02 | 2025-02-10 09:35 | 2025-02-10 14:31 | 4:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
AKS 132/33kV | Bar Aulia | 2025-02-01 08:34 | 2025-02-01 14:51 | 6:17 | S/O | Annual maintenance dead line checking (Khulshi Demand) | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2025-02-05 07:00 | 2025-02-05 08:31 | 1:31 | S/O | Annual Deadline checking by Khulsi ss | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2025-02-05 08:31 | 2025-02-05 08:31 | 0:00 | S/O | Annual Deadline checking by Khulsi ss | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2025-02-23 08:50 | 2025-02-23 14:40 | 5:50 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-01 | 2025-02-19 09:20 | 2025-02-19 12:10 | 2:50 | S/O | annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-02 | 2025-02-19 12:15 | 2025-02-19 13:54 | 1:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-02 | 2025-02-25 10:08 | 2025-02-25 16:37 | 6:29 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-02 | 2025-02-26 09:26 | 2025-02-26 15:17 | 5:51 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2025-02-03 13:47 | 2025-02-03 13:47 | 0:00 | S/O | H-Pole Installation work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-02-28 08:22 | 2025-02-28 16:59 | 8:37 | S/O | Halishahar project work | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-1 | 2025-02-24 08:46 | 2025-02-24 12:51 | 4:05 | S/O | Maintenance Work ( Insulator disk change) | 0 | 0 | No interruption
Mirsorai 230/33kV | EGCB 75MW Solar Power Station | 2025-02-15 14:34 | 2025-02-15 17:40 | 3:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV | EGCB 75MW Solar Power Station | 2025-02-16 14:15 | 2025-02-16 18:25 | 4:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 | Agrabad-1 | 2025-02-09 11:49 | 2025-02-09 16:28 | 4:39 | S/O | annual maintenance at agrabad end | 0 | 0 | No interruption
Rampur 230/132/33 | Agrabad-2 | 2025-02-10 09:37 | 2025-02-10 14:30 | 4:53 | S/O | Anual maintenance in Agrabad grid substation. | 0 | 0 | No interruption
Rampur 230/132/33 | Halishahar-2 | 2025-02-28 11:19 | 2025-02-28 18:02 | 6:43 | S/O | GIS Bay commission in Halishahar Grid ss | 0 | 0 | No interruption
Shikalbaha 230/132kV | Julda | 2025-02-03 13:48 | 2025-02-03 13:48 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV | Anowara-1 | 2025-02-11 08:56 | 2025-02-11 15:25 | 6:29 | S/O | Maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV | Anwara-2 | 2025-02-12 09:04 | 2025-02-12 16:11 | 7:07 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 181:19 |  | Unserved Energy: |  | 271.5
Cumilla Grid Circle :
Bibiana 400/230kV | Bibi-Shahzi Ckt-I | 2025-02-16 08:16 | 2025-02-16 16:37 | 8:21 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Fen Ckt-I | 2025-02-16 09:07 | 2025-02-16 17:16 | 8:09 | S/O | For AM | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-I | 2025-02-17 08:13 | 2025-02-17 17:03 | 8:50 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-I | 2025-02-18 08:47 | 2025-02-18 18:18 | 9:31 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-II | 2025-02-22 08:46 | 2025-02-22 17:30 | 8:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-II | 2025-02-23 08:58 | 2025-02-24 16:46 | 31:48 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-02-13 08:37 | 2025-02-13 16:50 | 8:13 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-02-18 08:26 | 2025-02-18 17:21 | 8:55 | S/O | 0 | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-02-19 08:38 | 2025-02-19 17:17 | 8:39 | S/O | 0 | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-02-20 08:45 | 2025-02-20 14:56 | 6:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-02-22 09:19 | 2025-02-22 12:51 | 3:32 | S/O | 0 | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-02-10 08:09 | 2025-02-10 16:32 | 8:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-02-11 08:34 | 2025-02-11 16:33 | 7:59 | S/O | Annual maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-02-12 09:25 | 2025-02-12 16:33 | 7:08 | S/O | Schedule Shutdown | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-02-09 08:25 | 2025-02-09 19:05 | 10:40 | S/O | For Maint workBall-I) Change program in 132KV Feni-Chow Ckt-01. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2025-02-01 08:46 | 2025-02-02 18:49 | 34:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2025-02-03 08:50 | 2025-02-03 16:08 | 7:18 | S/O | Annual Maintenance works | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2025-02-04 08:53 | 2025-02-04 16:54 | 8:01 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2025-02-05 08:31 | 2025-02-08 15:38 | 79:07 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-02-11 08:30 | 2025-02-11 17:23 | 8:53 | S/O | Annual Maintenance B-Baria SS end | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2025-02-12 08:32 | 2025-02-12 16:20 | 7:48 | S/O | Dead line checking. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2025-02-12 08:41 | 2025-02-12 16:37 | 7:56 | S/O | 0 | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-02-09 08:22 | 2025-02-09 19:05 | 10:43 | S/O | For multiple Disk Nutt Bolt Change by Chawmuhani grid. | 0 | 0 | No interruption
Kachua 132/33kV | Chandpur CKT-2 | 2025-02-10 07:55 | 2025-02-10 16:33 | 8:38 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Kachua 132/33kV | Chandpur CKT-2 | 2025-02-11 08:35 | 2025-02-11 16:31 | 7:56 | S/O | Annual maintenance work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-01 | 2025-02-12 08:31 | 2025-02-12 16:22 | 7:51 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-01 | 2025-02-12 09:01 | 2025-02-12 16:30 | 7:29 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-02 | 2025-02-15 08:42 | 2025-02-15 15:44 | 7:02 | S/O | Yearly maintenance | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Daudkandi Ckt-02 | 2025-02-16 08:38 | 2025-02-16 15:39 | 7:01 | S/O | yearly maintenance. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-02 | 2025-02-16 09:55 | 2025-02-16 15:09 | 5:14 | S/O | yearly maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-02 | 2025-02-06 09:12 | 2025-02-06 14:35 | 5:23 | S/O | Loop clamp need to change | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj- Desh Energy Ckt-01 | 2025-02-18 07:50 | 2025-02-18 10:15 | 2:25 | S/O | DS maintenance | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Desh Energy Ckt-02 | 2025-02-19 08:18 | 2025-02-19 09:31 | 1:13 | S/O | DS maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2025-02-06 08:21 | 2025-02-06 17:04 | 8:43 | S/O | Dead line checking work from Fen SS. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2025-02-08 08:40 | 2025-02-08 17:18 | 8:38 | S/O | Working at the Fenchuganj end. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2025-02-09 08:46 | 2025-02-09 16:32 | 7:46 | S/O | Annual maintanance works by fenchugong ss | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2025-02-11 08:29 | 2025-02-11 16:58 | 8:29 | S/O | Works at Fenchuganj end. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2025-02-12 08:41 | 2025-02-12 17:50 | 9:09 | S/O | Works at Fenchuganj End | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2025-02-13 08:20 | 2025-02-13 16:32 | 8:12 | S/O | Annual maintenance works at Fenchuganj SS | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-02-02 09:22 | 2025-02-08 16:08 | 150:46 | S/O | dead line checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-02-03 08:57 | 2025-02-03 09:37 | 0:40 | S/O | 132 Bus Section 3-4 Shutdown | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-02-03 19:37 | 2025-02-03 19:58 | 0:21 | S/O | 132 kV bus section 3&4 close | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-02-16 11:19 | 2025-02-16 18:55 | 7:36 | S/O | dead line checking of chhatak end | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-02-17 08:24 | 2025-02-17 18:02 | 9:38 | S/O | 132 kV Sylhet-Chhatak ckt-1 Dead Line Checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-02-18 09:36 | 2025-02-18 15:43 | 6:07 | S/O | Deadline checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-02-19 10:04 | 2025-02-19 18:58 | 8:54 | S/O | Dead Line checking for Chhatak end | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-02-20 10:36 | 2025-02-20 18:07 | 7:31 | S/O | dead line checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-02-23 08:34 | 2025-02-23 18:28 | 9:54 | S/O | Maintenance Work | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-02-24 08:59 | 2025-02-24 14:44 | 5:45 | S/O | Dead Line checking | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-02-25 09:26 | 2025-02-25 16:45 | 7:19 | S/O | dead line checking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2025-02-02 08:45 | 2025-02-02 19:33 | 10:48 | S/O | Deed line checking of Sylhet-Chhatak Ckt-1 | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2025-02-16 11:15 | 2025-02-16 18:56 | 7:41 | S/O | for dead line checking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2025-02-17 08:23 | 2025-02-17 18:04 | 9:41 | S/O | Due to deadline check on the Sylhet Grid, the 132kv Sylhet-Chhatak Circuit-01 has been shutdown. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2025-02-18 09:35 | 2025-02-18 15:44 | 6:09 | S/O | For deadline checking | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2025-02-24 08:58 | 2025-02-25 16:47 | 31:49 | S/O | Dead line cheecking. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2025-02-26 08:47 | 2025-02-26 15:59 | 7:12 | S/O | Dead Line checking of Sylhet-Chhatak Ckt-2. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR1 | 2025-02-15 08:15 | 2025-02-15 14:38 | 6:23 | S/O | 33 kv Tr-01 Bus and Loop Maintenance Work | 15 | 95.75 | Power interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-02-10 08:19 | 2025-02-10 16:11 | 7:52 | S/O | Annual maintenance work of DEAD line check | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-02-11 08:52 | 2025-02-11 15:46 | 6:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-02-12 09:02 | 2025-02-12 16:31 | 7:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-2 | 2025-02-15 08:43 | 2025-02-15 15:45 | 7:02 | S/O | line shutdown for annual maintenance work | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-2 | 2025-02-16 08:33 | 2025-02-16 15:40 | 7:07 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2025-02-06 08:32 | 2025-02-06 17:02 | 8:30 | S/O | Deadline checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2025-02-08 08:45 | 2025-02-08 17:24 | 8:39 | S/O | Deadline checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2025-02-09 08:48 | 2025-02-09 16:29 | 7:41 | S/O | Dead line check | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2025-02-11 08:31 | 2025-02-11 16:56 | 8:25 | S/O | Deadline checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2025-02-12 08:42 | 2025-02-12 17:48 | 9:06 | S/O | Deadline checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2025-02-13 08:26 | 2025-02-13 16:35 | 8:09 | S/O | Deadline checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2025-02-16 09:06 | 2025-02-16 17:16 | 8:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2025-02-17 08:38 | 2025-02-17 16:30 | 7:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2025-02-19 09:37 | 2025-02-19 16:30 | 6:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2025-02-24 10:41 | 2025-02-24 14:20 | 3:39 | S/O | Relay testing (SPMD) | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2025-02-24 14:26 | 2025-02-24 17:09 | 2:43 | S/O | Realy testing (SPMD) | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-02-02 14:53 | 2025-02-02 19:53 | 5:00 | S/O | S/D For Chhatak-1 and 90 MW PS Looping Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | 20 MW PP | 2025-02-03 08:56 | 2025-02-03 22:21 | 13:25 | S/O | 132 KV Bus Section-3 Shutdown Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | 150MW GT PS | 2025-02-03 09:18 | 2025-02-03 09:40 | 0:22 | S/O | 132 Bus Section 3-4 Shutdown | 0 | 0 | No interruption
Sylhet 132/33kV | 75 MW ST PS | 2025-02-03 09:21 | 2025-02-03 10:01 | 0:40 | S/O | 132 Bus Section 3-4 Shutdown | 0 | 0 | No interruption
Sylhet 132/33kV | 150MW GT PS | 2025-02-03 19:35 | 2025-02-03 20:00 | 0:25 | S/O | 132 kV bus section 3&4 close | 0 | 0 | No interruption
Sylhet 132/33kV | 75 MW ST PS | 2025-02-03 19:35 | 2025-02-03 22:48 | 3:13 | S/O | 132 kV bus section 3&4 close | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-02-08 10:40 | 2025-02-08 15:58 | 5:18 | S/O | Due to by Pass ( Sylhet-90MW PS) loop open | 0 | 0 | No interruption
Sylhet 132/33kV | 75 MW ST PS | 2025-02-10 16:04 | 2025-02-11 11:17 | 19:13 |  | RTU maintenance | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-02-27 07:19 | 2025-02-27 14:58 | 7:39 | S/O | Dead Line checking | 0 | 0 | No interruption
|  |  | Total : | 1900-02-04 21:41 |  | Unserved Energy: |  | 95.75
Khulna Grid Circle :
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2025-02-01 07:42 | 2025-02-01 16:52 | 9:10 | S/O | Barishal - Patuakhali line Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Patuakhali ckt | 2025-02-01 07:47 | 2025-02-16 09:40 | 361:53 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Rajbari ckt-2 | 2025-02-01 10:34 | 2025-02-01 14:51 | 4:17 | S/O | Annual maintenance for rajbary end | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2025-02-02 08:40 | 2025-02-02 21:46 | 13:06 | S/O | CT Replace | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-2 | 2025-02-02 12:45 | 2025-02-02 17:11 | 4:26 | S/O | Relay test by SPMD, Khulna. | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2025-02-10 07:42 | 2025-02-10 16:42 | 9:00 | S/O | Dead Line check | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2025-02-11 08:19 | 2025-02-11 14:44 | 6:25 | S/O | 0 | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2025-02-12 08:34 | 2025-02-12 15:43 | 7:09 | S/O | 0 | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2025-02-13 08:47 | 2025-02-13 14:33 | 5:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2025-02-24 08:10 | 2025-02-24 09:53 | 1:43 | S/O | Bird Nest Remove | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2025-02-03 07:44 | 2025-02-03 16:10 | 8:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2025-02-04 08:28 | 2025-02-04 15:09 | 6:41 | S/O | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2025-02-05 07:36 | 2025-02-05 17:20 | 9:44 | S/O | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2025-02-06 07:47 | 2025-02-06 15:12 | 7:25 | S/O | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2025-02-08 07:58 | 2025-02-08 16:03 | 8:05 | S/O | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2025-02-09 07:52 | 2025-02-09 17:02 | 9:10 | S/O | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2025-02-10 07:58 | 2025-02-10 16:42 | 8:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2025-02-11 08:20 | 2025-02-11 14:44 | 6:24 | S/O | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2025-02-20 10:13 | 2025-02-20 19:25 | 9:12 | S/O | None | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-1 | 2025-02-07 08:28 | 2025-02-07 18:02 | 9:34 | S/O | Shutdown taken by Project | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-2 | 2025-02-07 08:29 | 2025-02-07 18:03 | 9:34 | S/O | Shutdown taken by Project | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-02-01 07:42 | 2025-02-01 16:50 | 9:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400kV | Line-1 (Amtoli) | 2025-02-14 08:37 | 2025-02-14 08:37 | 0:00 | S/O | Line-1 has been taken shutdown for insulator painting | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-02-22 05:49 | 2025-02-22 10:25 | 4:36 | S/O | Mongla 132 kv bus maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2025-02-22 05:49 | 2025-02-22 10:27 | 4:38 | S/O | Same as monngla-1 line | 0 | 0 | No interruption
Barishal 132/33kV | 132 kv Summit power | 2025-02-28 08:57 | 2025-02-28 10:49 | 1:52 | S/O | Line PT oil lekage | 0 | 0 | No interruption
Rajbari 132/33kV | Faridpur - 2 | 2025-02-01 10:33 | 2025-02-01 14:52 | 4:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV | Bheramara-1 | 2025-02-26 10:31 | 2025-02-26 16:46 | 6:15 | S/O | Ralay Check | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2025-02-11 08:25 | 2025-02-11 16:49 | 8:24 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2025-02-12 08:24 | 2025-02-12 16:46 | 8:22 | S/O | Yearly maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2025-02-13 08:34 | 2025-02-13 14:56 | 6:22 | S/O | Yearly maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-22 17:50 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-02-11 08:55 | 2025-02-11 16:09 | 7:14 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-02-17 10:19 | 2025-02-17 10:19 | 0:00 | S/O | project work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2025-02-07 08:29 | 2025-02-07 18:01 | 9:32 | S/O | Kaligonj to mahespur line strining | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-2 | 2025-02-07 08:29 | 2025-02-07 18:03 | 9:34 | S/O | Kaligonj to mahespur line strining work | 0 | 0 | No interruption
Ullahpara 132/33kV | Baghabari ckt | 2025-02-18 17:41 | 2025-02-23 18:34 | 120:53 | S/O | 132kV Ullapara-Baghabari ckt Development Work | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 2 | 2025-02-16 10:41 | 2025-02-16 12:12 | 1:31 | S/O | Project work | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2025-02-01 11:50 | 2025-02-01 20:42 | 8:52 | S/O | Maint.work | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-02-03 10:18 | 2025-02-03 20:18 | 10:00 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | 20DF22 | 2025-02-03 11:44 | 2025-02-03 16:39 | 4:55 | S/O | Trip by C1 unbalance 60/61 instant L2 | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-02-04 10:44 | 2025-02-04 19:57 | 9:13 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-1 | 2025-02-13 11:27 | 2025-02-13 13:18 | 1:51 | S/O | Due to CVT Oil leakage rectification | 0 | 0 | No interruption
BIPTC | Baharampur-1 | 2025-02-17 10:33 | 2025-02-17 19:46 | 9:13 | S/O | Maint.work | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2025-02-18 10:00 | 2025-02-18 19:20 | 9:20 | S/O | Maint.work | 0 | 0 | No interruption
BIPTC | Ishurdi-3 | 2025-02-24 10:35 | 2025-02-24 18:04 | 7:29 | S/O | Shutdown is taken from Ishwardi end | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-02-16 10:40 | 2025-02-16 12:13 | 1:33 | S/O | G to G project work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-02-08 08:51 | 2025-02-08 15:01 | 6:10 | S/O | Cradel guard installation of rooppur-dhaka 400Kv line . Over ISD-GHO 230 Kv line | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-02-08 08:51 | 2025-02-08 15:02 | 6:11 | S/O | Cradel guard installation of rooppur-dhaka 400Kv line . Over ISD-GHO 230 Kv lin | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-02-16 08:25 | 2025-02-16 16:51 | 8:26 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-02-17 07:52 | 2025-02-17 17:07 | 9:15 | S/O | dhamrai disc cleaning work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-02-18 08:28 | 2025-02-18 16:47 | 8:19 | S/O | Dhamrai section insulator disk clearing | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-02-19 08:33 | 2025-02-19 15:25 | 6:52 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV HVDC 3 | 2025-02-24 09:54 | 2025-02-24 18:04 | 8:10 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-02-28 07:25 | 2025-02-28 16:37 | 9:12 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-02-28 07:25 | 2025-02-28 16:38 | 9:13 | S/O | Maint.work | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-2 | 2025-02-15 08:45 | 2025-02-18 15:10 | 78:25 | S/O | Piling work go on | 0 | 0 | No interruption
|  |  | Total : | 1900-01-14 01:23 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-1 | 2025-02-22 09:07 | 2025-02-22 14:49 | 5:42 | S/O | Maint.work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-2 | 2025-02-22 09:08 | 2025-02-22 14:50 | 5:42 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2025-02-04 08:50 | 2025-02-04 14:01 | 5:11 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-06 10:12 | 2025-02-06 17:25 | 7:13 | S/O | Tower painting | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-06 10:13 | 2025-02-06 17:26 | 7:13 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-07 09:04 | 2025-02-07 17:27 | 8:23 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-07 09:06 | 2025-02-07 17:28 | 8:22 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-08 09:31 | 2025-02-08 17:28 | 7:57 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-08 09:31 | 2025-02-08 17:29 | 7:58 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-09 09:17 | 2025-02-09 17:31 | 8:14 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-09 09:18 | 2025-02-09 17:31 | 8:13 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-10 08:23 | 2025-02-10 17:57 | 9:34 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-10 08:24 | 2025-02-10 17:57 | 9:33 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-11 08:12 | 2025-02-11 17:52 | 9:40 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-11 08:12 | 2025-02-11 17:52 | 9:40 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-12 09:13 | 2025-02-12 17:48 | 8:35 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-12 09:13 | 2025-02-12 17:48 | 8:35 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-02-13 09:01 | 2025-02-13 18:04 | 9:03 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-02-13 09:01 | 2025-02-13 18:04 | 9:03 | S/O | maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2025-02-19 12:56 | 2025-02-19 17:15 | 4:19 | S/O | Project work | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-2 | 2025-02-19 13:11 | 2025-02-19 17:16 | 4:05 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-06 10:04 | 2025-02-06 17:14 | 7:10 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-06 10:06 | 2025-02-06 17:15 | 7:09 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-06 10:12 | 2025-02-06 17:25 | 7:13 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-06 10:12 | 2025-02-06 17:26 | 7:14 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-02-06 12:53 | 2025-02-06 13:18 | 0:25 | S/O | Panel Discrepancy switch change. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-07 09:04 | 2025-02-07 17:27 | 8:23 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-07 09:06 | 2025-02-07 17:28 | 8:22 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-07 09:11 | 2025-02-07 17:24 | 8:13 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-07 09:12 | 2025-02-07 17:25 | 8:13 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-08 09:19 | 2025-02-08 17:26 | 8:07 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-08 09:20 | 2025-02-08 17:26 | 8:06 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-08 09:31 | 2025-02-08 17:27 | 7:56 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-08 09:31 | 2025-02-08 17:29 | 7:58 | S/O | Due to Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-09 09:15 | 2025-02-09 17:34 | 8:19 | S/O | Project Work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-09 09:15 | 2025-02-09 17:35 | 8:20 | S/O | Project Work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-09 09:17 | 2025-02-09 17:34 | 8:17 | S/O | Project Work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-09 09:17 | 2025-02-09 17:34 | 8:17 | S/O | Project Work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-10 08:28 | 2025-02-10 17:55 | 9:27 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-10 08:28 | 2025-02-10 17:56 | 9:28 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-10 08:28 | 2025-02-10 17:56 | 9:28 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-10 08:29 | 2025-02-10 17:55 | 9:26 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-11 08:13 | 2025-02-11 17:52 | 9:39 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-11 08:13 | 2025-02-11 17:52 | 9:39 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-11 08:16 | 2025-02-11 17:53 | 9:37 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-11 08:17 | 2025-02-11 17:53 | 9:36 | S/O | Tower Painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2025-02-11 15:20 | 2025-02-13 18:06 | 50:46 | S/O | Meter Testing Purpose | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-12 09:14 | 2025-02-12 17:48 | 8:34 | S/O | Project Work(Tower Painting) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-12 09:14 | 2025-02-12 17:48 | 8:34 | S/O | Project Work(Tower Painting) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-12 09:15 | 2025-02-12 17:44 | 8:29 | S/O | Project Work(Tower Painting) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-12 09:15 | 2025-02-12 17:45 | 8:30 | S/O | Project Work(Tower Painting) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-02-13 09:01 | 2025-02-13 18:03 | 9:02 | S/O | Tower painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-02-13 09:01 | 2025-02-13 18:03 | 9:02 | S/O | Tower painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-02-13 09:04 | 2025-02-13 18:05 | 9:01 | S/O | Tower painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-02-13 09:04 | 2025-02-13 18:05 | 9:01 | S/O | Tower painting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-02-19 10:11 | 2025-02-19 18:06 | 7:55 | S/O | Line check | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-02-19 10:13 | 2025-02-19 18:10 | 7:57 | S/O | Line check | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-02-20 09:41 | 2025-02-20 17:01 | 7:20 | S/O | Line Checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-02-20 09:41 | 2025-02-20 17:01 | 7:20 | S/O | Line Checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-02-23 11:15 | 2025-02-23 19:50 | 8:35 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-02-23 11:16 | 2025-02-23 19:50 | 8:34 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-02-24 09:23 | 2025-02-24 16:46 | 7:23 | S/O | Tower checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-02-24 09:23 | 2025-02-24 16:46 | 7:23 | S/O | None | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Rahanpur Ckt-2 | 2025-02-25 10:19 | 2025-02-25 12:01 | 1:42 | S/O | Energy Meter accuracy test Rahanpur 400 kV Grid substation End. | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-1 | 2025-02-01 10:58 | 2025-02-01 17:43 | 6:45 | S/O | Maintenance work from EPVTL End. | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-2 | 2025-02-02 10:59 | 2025-02-02 17:36 | 6:37 | S/O | maint.work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-01 | 2025-02-08 07:15 | 2025-02-08 08:55 | 1:40 | S/O | For bus shutdown at Purbasadipur grid SS | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2025-02-08 07:15 | 2025-02-08 08:55 | 1:40 | S/O | For bus shutdown at Purbasadipur grid SS. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-02-10 07:38 | 2025-02-10 16:00 | 8:22 | S/O | For Taragonj sub-station LILO work. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-02-11 08:08 | 2025-02-11 13:42 | 5:34 | S/O | maint.work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-02-12 09:54 | 2025-02-13 21:52 | 35:58 | S/O | As the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-1 | 2025-02-01 11:15 | 2025-02-01 17:48 | 6:33 | S/O | Tower painting for LILO Ckt | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-2 | 2025-02-02 11:10 | 2025-02-02 17:37 | 6:27 | S/O | Tower painting for LILo ckt | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2025-02-08 09:41 | 2025-02-08 12:31 | 2:50 | S/O | 132KV A Bus DS maintenance work. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2025-02-15 07:03 | 2025-02-15 13:19 | 6:16 | S/O | G2G project work on main bus | 32 | 200.5333 | Power interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 1 | 2025-02-10 11:04 | 2025-03-08 16:08 | 629:04 | S/O | Reconducting Purpose | 0 | 0 | No interruption
Palashbari 132/33kV | Mahasthangarh-01 | 2025-02-10 11:15 | 2025-03-08 16:11 | 628:56 | S/O | project work | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-02-22 10:06 | 2025-02-22 14:53 | 4:47 | S/O | Maintenance purpose | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-01 | 2025-02-22 10:07 | 2025-02-22 14:52 | 4:45 | S/O | Maintenance purpose | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-01 | 2025-02-23 11:48 | 2025-02-23 17:37 | 5:49 | S/O | maint.work | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-02-23 11:48 | 2025-02-23 17:38 | 5:50 | S/O | maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-02-10 07:40 | 2025-02-10 15:59 | 8:19 | S/O | maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-02-11 08:10 | 2025-02-11 13:43 | 5:33 | S/O | G to G Project | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-02-12 09:55 | 2025-02-13 21:50 | 35:55 | S/O | Breaker pole replace. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2025-02-15 07:04 | 2025-02-15 13:18 | 6:14 | S/O | maint.work | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 1 | 2025-02-11 09:34 | 2025-02-11 12:58 | 3:24 | S/O | RTU & SCADA Commissioning work. | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 2 | 2025-02-11 13:12 | 2025-02-11 17:25 | 4:13 | S/O | RTU & SCADA Commissioning work. | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-1 | 2025-02-22 09:08 | 2025-02-22 14:52 | 5:44 | S/O | Cradle Guard Removal Work | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-2 | 2025-02-22 09:09 | 2025-02-22 14:52 | 5:43 | S/O | Cradle Guard Removal Work | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -01 | 2025-02-04 08:51 | 2025-02-04 14:01 | 5:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -01 | 2025-02-19 13:12 | 2025-02-19 17:16 | 4:04 | S/O | Removing cradle guard at span | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -02 | 2025-02-19 13:12 | 2025-02-19 17:18 | 4:06 | S/O | Removing Cradle Guard at Span | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2025-02-01 12:10 | 2025-02-01 13:30 | 1:20 | S/O | Project work | 0 | 0 | No interruption
|  |  | Total : | 1900-03-23 17:03 |  | Unserved Energy: |  | 200.5333
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-10-09 13:10 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:February 2025
| Area | Previous Month (January' 2025) |  |  |  | Current Month (February '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 20 | 27 | 290 | 337 | 27 | 12 | 142 | 181
2 | Dhaka (South) Grid Circle. | 20 | 21 | 207 | 248 | 15 | 17 | 92 | 124
3 | Chattogram Grid Circle. | 2 | 1 | 107 | 110 | 5 | 11 | 68 | 84
4 | Cumilla Grid Circle. | 15 | 10 | 188 | 213 | 15 | 5 | 113 | 133
5 | Khulna Grid Circle. | 5 | 21 | 162 | 188 | 14 | 12 | 66 | 92
6 | HVDC Grid Circle | 8 | 9 | 126 | 143 | 3 | 3 | 38 | 44
7 | Bogura Grid Circle. | 4 | 10 | 154 | 168 | 16 | 18 | 137 | 171
8 | Others
9 | Total | 74 | 99 | 1234 | 1407 | 95 | 78 | 656 | 829
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:February 2025
| Area | Previous Month (January' 2025) |  |  |  | Current Month (February '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 482.55 | 876.92 | 2598.3 | 3957.77 | 225.27 | 173.33 | 5220.3 | 5618.9
2 | Dhaka (South) Grid Circle. | 448.6 | 135.75 | 1212.25 | 1796.6 | 110.77 | 1381 | 175.43 | 1667.2
3 | Chattogram Grid Circle. | 142.13 | - | 1250.12 | 1392.25 | - | - | 1061.52 | 1061.52
4 | Cumilla Grid Circle. | 71.83 | - | 758.98 | 830.81 | 146.33 | 37.68 | 4091.92 | 4275.93
5 | Khulna Grid Circle. | 47.64 | 479.07 | 1193.6 | 1720.31 | 102.65 | 17 | 743.57 | 863.22
6 | HVDC Grid Circle | 9 | 83.13 | 1610.05 | 1702 | - | - | 284 | 284
7 | Bogura Grid Circle. | 52.9 | 41.07 | 1970.97 | 2064.94 | 133.85 | - | 1131.25 | 1265.1
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1254.65 | 1615.94 | 10594.27 | 13464.68 | 718.87 | 1609.01 | 12707.99 | 15035.87
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:February 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 6 | 7 | 13 | 5 | 1 | 7 | 4577.76
2 | Dhaka (South) | 5031.6 | 9 | 2 | 11 | 3 | 2 | 6 | 497.2
3 | Chattogram | 2042 | - | 4 | 4 | - | - | 4 | 790.02
4 | Khulna | 2434 | 6 | 11 | 17 | 1 | 3 | 13 | 863.22
5 | HVDC | 5954.3 | - | 4 | 4 | - | - | 4 | 284
6 | Bogura | 3145.6 | 5 | 11 | 16 | 2 | 2 | 12 | 1229.05
7 | Cumilla | 2981 | 3 | 10 | 13 | 3 | 2 | 8 | 4180.19
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 12421.44
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 100%
4 | Khulna | 99.98%
5 | HVDC | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.98% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:February 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 8 | 8 | 16 | 9 | 3 | 4 | 1041.14
2 | Dhaka (South) | 990.29 | - | 1 | 1 | 2 | - | - | 1 | 1170
3 | Chattogram | 917 | - | - | 1 | 1 | - | - | 1 | 271.5
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 3 | - | 3 | 3 | - | - | 36.15
7 | Cumilla | 1648.16 | - | - | 1 | 1 | - | - | 1 | 95.75
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2614.54
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 100% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:February 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-02-01 | 9 | - | 2 | 07hr 10 min | 1 | 11hr 42 min | - | - |  |  | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:February 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Mirzapur 132/33kV | 1 | 0:30 | 12.5
Sreepur 230/132/33kV | 1 | 0:09 | 1.2
Tongi 230/132/33kV | 1 | 1:11 | 16.5667
Tongi 230/132/33kV | 1 | 0:11 | 5.1333
Tongi 230/132/33kV | 1 | 0:11 | 4.4
Kabirpur 132/33kV | 1 | 1:44 | 173.3333
Agargaon 230/132kV | 1 | 0:03 | 9.2
Tongi 230/132/33kV | 1 | 0:27 | 67.5
Tongi 230/132/33kV | 1 | 0:02 | 2.3333
Tongi 230/132/33kV | 1 | 0:02 | 2.3333
Kaliakoir 400/230/132kV | 1 | 0:21 | 49.35
Kaliakoir 400/230/132kV | 1 | 0:22 | 53.9
Bhaluka 132/33kV | 1 | 4:04 | 223.6667
Bhaluka 132/33kV | 1 | 5:28 | 82
Jamalpur 132/33kV | 1 | 8:39 | 103.8
Joydebpur 132/33kV | 1 | 3:00 | 120
Kabirpur 132/33kV | 1 | 75:35 | 3779.1667
Mirzapur 132/33kV | 1 | 1:58 | 39.3333
Tangail 132/33kV | 1 | 0:40 | 16.6667
Bhaluka 132/33kV | 1 | 4:26 | 243.8333
Joydebpur 132/33kV | 1 | 7:43 | 77.1667
Kabirpur 132/33kV | 1 | 8:40 | 260
Kabirpur 132/33kV | 1 | 6:51 | 205.5
Tangail 132/33kV | 1 | 0:39 | 16.25
Tangail 132/33kV | 1 | 0:45 | 18.75
Tangail 132/33kV | 1 | 0:59 | 24.5833
Tangail 132/33kV | 1 | 0:23 | 9.5833
Bhulta 132/33kV | 1 | 6:36 | 99
Haripur 230/132kV | 1 | 0:23 | 57.5
Madanganj 132/33kV | 1 | 0:53 | 3.5333
Narshingdi 132/33kV | 1 | 0:08 | 6.4
Nawabganj 132/33kV | 1 | 0:10 | 1.5833
Sonargaon 132/33kV | 1 | 1:36 | 72
Sonargaon 132/33kV | 1 | 1:00 | 18
Sonargaon 132/33kV | 1 | 1:35 | 23.75
Sonargaon 132/33kV | 1 | 1:20 | 40
Ghorashal 230kV |  | 2:47 | 161.4333
Srinagar 132/33kV | 1 | 1:10 | 14
Meghnaghat 400/230kV | 1 | 11:42 | 1170
Coxsbazar 132/33kV | 1 | 3:05 | 237.4167
Coxsbazar 132/33kV | 1 | 3:23 | 304.5
Coxsbazar 132/33kV | 1 | 2:32 | 222.9333
Khulshi 132/33kV | 1 | 2:31 | 25.1667
Dohazari 132/33kV | 1 | 9:03 | 271.5
Chandpur 132/33kV | 1 | 1:59 | 37.6833
Chowmuhani 132/33kV | 1 | 4:02 | 121
Chowmuhani 132/33kV | 1 | 0:38 | 25.3333
Chowmuhani 132/33kV | 1 | 0:50 | 12.5
Chowmuhani 132/33kV | 1 | 6:23 | 159.5833
Cumilla(S) 132/33kV | 1 | 4:07 | 82.3333
Cumilla(S) 132/33kV | 1 | 0:12 | 4.4
Cumilla(S) 132/33kV | 1 | 120:54 | 3627
Cumilla(S) 132/33kV | 1 | 0:06 | 3
Feni 132/33kV | 1 | 1:27 | 21.75
Kulaura 132/33kV | 1 | 2:38 | 31.6
Sunamganj 132/33kV | 1 | 6:40 | 53.3333
Sylhet 132/33kV | 1 | 0:04 | 0.66667
Chowmuhani 132/33kV | 1 | 6:23 | 95.75
Barguna 132/33kV | 1 | 0:15 | 1.25
Barishal 132/33kV | 1 | 0:21 | 12.25
Barishal 132/33kV | 1 | 0:18 | 6.9
Bhandaria 132/33kV | 1 | 1:21 | 47.25
Bhandaria 132/33kV | 1 | 0:34 | 17
Madaripur 132/33kV | 1 | 2:55 | 35
Barguna 132/33kV | 1 | 1:14 | 3.0833
Barishal 230/132kV | 1 | 3:14 | 16.1667
Barishal 230/132kV | 1 | 3:16 | 66.9667
Bhandaria 132/33kV | 1 | 8:03 | 100.625
Bhandaria 132/33kV | 1 | 7:56 | 99.1667
Faridpur 132/33kV | 1 | 2:46 | 55.3333
Gopalganj 132/33kV | 1 | 2:51 | 39.9
Mongla 132/33kV | 1 | 5:14 | 68.0333
Satkhira 132/33kV | 1 | 4:05 | 204.1667
Shariatpur 132/33kV | 1 | 5:20 | 53.3333
Shariatpur 132/33kV | 1 | 4:36 | 36.8
Chuadanga 132/33kV | 1 | 2:37 | 91.5833
Chuadanga 132/33kV | 1 | 2:37 | 0
Kushtia 132/33kV | 1 | 1:49 | 18.1667
Kushtia 132/33kV | 1 | 3:01 | 90.5
Kushtia 132/33kV | 1 | 3:21 | 83.75
Jaldhaka 132/33kV | 1 | 0:31 | 13.95
Rajshahi 132/33kV | 1 | 0:21 | 9.1
Rajshahi 132/33kV | 1 | 0:17 | 21.25
Rajshahi 132/33kV | 1 | 1:12 | 32.4
Rajshahi 132/33kV | 1 | 0:36 | 21
Rajshahi 230/132/33kV | 1 | 0:15 | 11.5
Rajshahi 230/132/33kV | 1 | 0:19 | 14.5667
Rangpur 132/33kV | 1 | 0:11 | 10.0833
Bogura 132/33kV | 1 | 1:30 | 37.5
Bogura 132/33kV | 1 | 9:07 | 136.75
Bogura 132/33kV | 1 | 2:11 | 65.5
Bogura 132/33kV | 1 | 1:05 | 27.0833
Bogura 132/33kV | 1 | 1:53 | 47.0833
Bogura 132/33kV | 1 | 1:29 | 44.5
Mahasthangarh 132/33kV | 1 | 2:28 | 66.6
Naogaon 132/33kV | 1 | 6:45 | 243
Naogaon 132/33kV | 1 | 6:40 | 133.3333
Palashbari 132/33kV | 1 | 1:00 | 30
Purbasadipur 132/33kV | 1 | 1:40 | 300
Total Unserved energy : | 62 | 448:34 | 15035.125

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: February 2025
Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 19 | 2025-02-04 23:00
2 | AKSML | 132 | 2025-02-08 14:00
3 | Aftabnagar | 30 | 2025-02-18 18:30
4 | Agargaon | 108 | 2025-02-25 19:30
5 | Agrabad | 106 | 2025-02-25 18:30
6 | Amnura | 63 | 2025-02-07 10:00
7 | Ashuganj | 104 | 2025-02-27 19:00
8 | BSRM | 204 | 2025-02-21 17:00
9 | Bagerhat | 77 | 2025-02-25 19:00
10 | Bajitpur | 42 | 2025-02-22 18:00
11 | Bakulia | 85 | 2025-02-22 13:00
12 | Banani | 51 | 2025-02-04 13:00
13 | Bangabhaban | 11 | 2025-02-18 10:00
14 | Barapukuria | 66 | 2025-02-02 12:00
15 | Barguna | 16 | 2025-02-01 18:00
16 | Barishal | 95 | 2025-02-22 12:00
17 | Barishal-230 | 80 | 2025-02-12 18:30
18 | Baroaulia | 75 | 2025-02-20 12:00
19 | Baroirhat | 60 | 2025-02-27 18:00
20 | Bashundhara | 155 | 2025-02-27 13:00
21 | BashundharaCement | 12 | 2025-02-01 10:00
22 | Beanibazar | 52 | 2025-02-01 18:00
23 | Benapole | 62 | 2025-02-27 13:00
24 | Bhaluka | 130 | 2025-02-24 09:00
25 | Bhandaria | 54 | 2025-02-20 21:00
26 | Bhangura | 36 | 2025-02-28 08:00
27 | Bheramara(GK) | 53 | 2025-02-22 12:00
28 | Bhulta | 274 | 2025-02-11 17:00
29 | Bog-Sherpur | 72 | 2025-02-19 08:00
30 | Bogura | 152 | 2025-02-17 15:00
31 | Borhanuddin | 59 | 2025-02-20 21:00
32 | Brahmanbaria | 118 | 2025-02-17 19:00
33 | Cantonment | 106 | 2025-02-13 13:00
34 | Chandpur | 50 | 2025-02-13 19:00
35 | Chandraghona | 29 | 2025-02-22 18:30
36 | Chapai | 76 | 2025-02-16 11:00
37 | Charsaidpur | 45 | 2025-02-02 15:00
38 | Chauddagram | 64 | 2025-02-25 13:00
39 | Chhatak | 33 | 2025-02-08 18:00
40 | Chowmuhani | 176 | 2025-02-22 18:30
41 | Chuadanga | 80 | 2025-02-28 13:00
42 | Coxsbazar | 133 | 2025-02-22 18:00
43 | Cumilla(N) | 158 | 2025-02-19 12:00
44 | Cumilla(S) | 157 | 2025-02-27 14:00
45 | Daudkandi | 115 | 2025-02-06 19:00
46 | Dhaka | 46 | 2025-02-27 12:00
47 | Dhamrai | 122 | 2025-02-22 16:00
48 | Dhanmondi | 118 | 2025-02-13 13:00
49 | Dohazari | 92 | 2025-02-14 13:00
50 | Faridpur | 115 | 2025-02-18 18:30
51 | Fatullah | 86 | 2025-02-06 12:00
52 | Fenchuganj | 31 | 2025-02-17 18:30
53 | Feni | 96 | 2025-02-22 18:30
54 | GPH | 101 | 2025-02-20 08:00
55 | Ghatail | 64 | 2025-02-25 18:00
56 | Ghorashal | 16 | 2025-02-06 14:00
57 | Ghorashal-230 | 98 | 2025-02-07 17:00
58 | Goalpara | 30 | 2025-02-03 13:00
59 | Gollamari | 88 | 2025-02-04 03:00
60 | Gopalganj | 83 | 2025-02-18 18:30
61 | Gulshan | 98 | 2025-02-18 13:00
62 | Halishahar | 74 | 2025-02-24 14:00
63 | HaripurSBU | 182 | 2025-02-23 11:00
64 | Hasnabad | 104 | 2025-02-11 18:00
65 | Hathazari | 66 | 2025-02-18 20:00
66 | Ishurdi | 66 | 2025-02-04 11:00
67 | Jaldhaka | 67 | 2025-02-28 18:30
68 | Jamalpur | 114 | 2025-02-28 08:00
69 | Jashore | 125 | 2025-02-25 13:00
70 | Jhenaidah | 104 | 2025-02-28 18:30
71 | Joydebpur | 165 | 2025-02-24 18:30
72 | Joypurhat | 74 | 2025-02-25 09:00
73 | Juldah | 17 | 2025-02-19 10:00
74 | KSRM | 41 | 2025-02-06 11:00
75 | Kabirpur | 272 | 2025-02-18 18:00
76 | Kachua | 61 | 2025-02-26 21:00
77 | Kallyanpur | 84 | 2025-02-28 13:00
78 | Kalurghat | 36 | 2025-02-22 18:00
79 | Kamrangirchar | 66 | 2025-02-04 12:00
80 | Kaptai | N/A | N/A
81 | Kazla | 103 | 2025-02-05 13:00
82 | Keranigonj | 79 | 2025-02-23 13:00
83 | Khagrachori | 28 | 2025-02-26 18:30
84 | Khosba | 30 | 2025-02-28 12:00
85 | Khulna | 85 | 2025-02-22 13:00
86 | Khulshi | 163 | 2025-02-19 12:00
87 | Kishoreganj | 130 | 2025-02-01 14:00
88 | Kodda | 295 | 2025-02-26 18:30
89 | Kulaura | 38 | 2025-02-22 18:00
90 | Kurigram | 70 | 2025-02-17 08:00
91 | Kushtia | 116 | 2025-02-23 18:30
92 | Lalbag | 76 | 2025-02-27 13:00
93 | Lalmonirhat | 52 | 2025-02-10 08:00
94 | MI_Cement | 18.3 | 2025-02-05 15:00
95 | Madanganj | 43 | 2025-02-27 13:00
96 | Madaripur | 77 | 2025-02-27 18:30
97 | Madartek | 70.41 | 2025-02-28 13:00
98 | Madunaghat | 43 | 2025-02-27 18:30
99 | Magura | 51 | 2025-02-09 18:30
100 | Mahasthangarh | 74 | 2025-02-18 18:30
101 | Manikganj | 117 | 2025-02-18 18:30
102 | Maniknagar | 76 | 2025-02-20 13:00
103 | Matarbari | 46 | 2025-02-24 18:30
104 | Matuail | 65 | 2025-02-13 12:00
105 | Millgate | 80 | 2025-02-20 12:00
106 | Mirpur | 116 | 2025-02-12 19:00
107 | Mirsorai | 13 | 2025-02-22 11:00
108 | Mirzapur | 42 | 2025-02-25 06:00
109 | Mithapukur | 74 | 2025-02-03 18:30
110 | Modern | 0 | 2025-02-01 00:00
111 | Mogbazar | 127.4 | 2025-02-23 12:00
112 | Mongla | 43 | 2025-02-27 19:00
113 | Motijheel | 36 | 2025-02-20 13:00
114 | Muktagacha | 33 | 2025-02-25 18:00
115 | Munshiganj | 76 | 2025-02-28 13:00
116 | Muradnagar | 11.01 | 2025-02-28 18:00
117 | Mymensingh | 183 | 2025-02-28 13:00
118 | Naogaon | 120 | 2025-02-17 09:00
119 | Narail | 46 | 2025-02-28 19:00
120 | Narinda | 72 | 2025-02-19 13:00
121 | Narshingdi | 168 | 2025-02-13 19:00
122 | Natore | 118 | 2025-02-26 19:30
123 | Nawabganj | 58.6 | 2025-02-06 14:00
124 | Netrakona | 147 | 2025-02-22 18:00
125 | New | 87 | 2025-02-12 15:00
126 | Niamatpur | 96 | 2025-02-19 08:00
127 | Noapara | 51 | 2025-02-27 19:00
128 | PHP | 10 | 2025-02-12 15:00
129 | Pabna | 91 | 2025-02-26 19:00
130 | Palashbari | 110 | 2025-02-09 08:00
131 | Panchagarh | 47 | 2025-02-04 18:30
132 | Patuakhali | 57.5 | 2025-02-15 19:00
133 | Payra | 24 | 2025-02-24 19:30
134 | Postogola | 45 | 2025-02-18 12:00
135 | Purbachal | 19 | 2025-02-21 13:00
136 | Purbasadipur | 130 | 2025-02-07 12:00
137 | Rahanpur | 12 | 2025-02-24 18:30
138 | Rahim | 49 | 2025-02-24 16:00
139 | Rajbari | 63 | 2025-02-12 18:30
140 | Rajendrapur | 124 | 2025-02-12 18:30
141 | Rajshahi | 114 | 2025-02-25 13:00
142 | Rajshahi-230 | 76 | 2025-02-11 13:00
143 | Ramganj | 106 | 2025-02-14 13:00
144 | Rampur | 39 | 2025-02-22 12:00
145 | Rangamati | 16 | 2025-02-22 18:30
146 | Rangpur | 129 | 2025-02-08 17:00
147 | Ruppur | 9 | 2025-02-03 16:00
148 | SSM | 22 | 2025-02-13 09:00
149 | Saidpur | 115 | 2025-02-20 09:00
150 | Satkhira | 103 | 2025-02-28 19:00
151 | Satmasjid | 88 | 2025-02-01 13:00
152 | Savar | 208 | 2025-02-20 15:00
153 | SevenRings | 21.3 | 2025-02-22 16:00
154 | ShahCement | 39 | 2025-02-27 12:00
155 | Shahjadpur | 73 | 2025-02-20 07:00
156 | Shahjibazar | 112 | 2025-02-11 18:30
157 | Shahmirpur | 48 | 2025-02-10 06:00
158 | Shariatpur | 58 | 2025-02-15 19:00
159 | Sherpur | 146 | 2025-02-21 18:30
160 | Shikalbaha | 28 | 2025-02-13 12:00
161 | Shitalakhya | 72.7 | 2025-02-13 12:00
162 | Sholosohor | 41 | 2025-02-22 15:00
163 | Shyampur | 182 | 2025-02-22 11:00
164 | Siddhirganj | 120 | 2025-02-19 12:00
165 | Sirajganj | 98 | 2025-02-18 19:30
166 | Sonargaon | 104 | 2025-02-18 12:00
167 | Sreemongol | 57 | 2025-02-28 18:30
168 | Sreepur | 104 | 2025-02-18 18:30
169 | Srinagar | 35.6 | 2025-02-28 12:00
170 | Sunamganj | 46 | 2025-02-22 18:00
171 | Sylhet | 34 | 2025-02-09 19:00
172 | Sylhet-132 | 101 | 2025-02-22 18:00
173 | TK | 25 | 2025-02-01 18:00
174 | Tangail | 175 | 2025-02-16 08:00
175 | Thakurgaon | 85 | 2025-02-10 08:00
176 | Tongi | 124 | 2025-02-13 11:00
177 | Ullahpara | 32 | 2025-02-25 07:00
178 | Ullon | 41 | 2025-02-18 21:00
179 | Uttara | 73 | 2025-02-13 13:00
180 | UttaraNew | 61 | 2025-02-10 15:00
181 | Zigatola | 68 | 2025-02-11 19:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: February 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 4692.39 | 2025-02-25 | 19:00
Chattogram | 1374.5 | 2025-02-25 | 18:30
Cumilla | 1083 | 2025-02-22 | 18:30
Mymensingh | 1044 | 2025-02-16 | 8:00
Sylhet | 433 | 2025-02-22 | 18:00
Khulna | 1339 | 2025-02-27 | 18:30
Barishal | 342.4 | 2025-02-20 | 21:00
Rajshahi | 1227 | 2025-02-25 | 19:00
Rangpur | 854 | 2025-02-17 | 8:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 416 | 2025-02-08 03:00 | 285 | 2025-02-27 15:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 417 | 2025-02-08 02:00 | 374 | 2025-02-13 12:00
4 | Bibiana | 400 | 417 | 2025-02-10 03:00 | 386 | 2025-02-23 17:00
5 | BIPTC | 400 | 409 | 2025-02-28 14:00 | 386 | 2025-02-01 13:00
6 | Bogura | 400 | 420 | 2025-02-03 04:00 | 388 | 2025-02-08 10:00
7 | Gopalganj | 400 | 422 | 2025-02-15 06:00 | 388 | 2025-02-25 12:00
8 | Kaliakoir | 400 | 406 | 2025-02-15 04:00 | 292 | 2025-02-19 03:00
9 | Madunaghat | 400 | 412 | 2025-02-01 05:00 | 393 | 2025-02-23 12:00
10 | Meghnaghat | 400 | 413 | 2025-02-08 03:00 | 381 | 2025-02-13 11:00
11 | Payra | 400 | 427 | 2025-02-15 06:00 | 406 | 2025-02-01 12:00
12 | Rahanpur | 400 | 420 | 2025-02-04 05:00 | 383 | 2025-02-26 13:00
13 | Rampal | 400 | 431 | 2025-02-04 02:00 | 239 | 2025-02-01 14:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 241 | 2025-02-15 06:00 | 217 | 2025-02-20 20:00
2 | AKSML | 230 | 240 | 2025-02-05 18:30 | 221 | 2025-02-23 12:00
3 | Aminbazar | 230 | 239 | 2025-02-08 01:00 | 218 | 2025-02-20 12:00
4 | Ashuganj | 230 | 246 | 2025-02-10 03:00 | 220 | 2025-02-20 11:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 243 | 2025-02-15 03:00 | 225 | 2025-02-13 12:00
7 | Barapukuria | 230 | 233 | 2025-02-16 15:00 | 204 | 2025-02-20 08:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 248 | 2025-02-08 05:00 | 233 | 2025-02-23 12:00
10 | Bheramara | 230 | 242 | 2025-02-15 05:00 | 222 | 2025-02-02 12:00
11 | Bhulta | 230 | 242 | 2025-02-08 04:00 | 216 | 2025-02-13 12:00
12 | Bibiana | 230 | 241 | 2025-02-08 03:00 | 223 | 2025-02-25 01:00
13 | BIPTC | 230 | 244 | 2025-02-08 05:00 | 223 | 2025-02-01 12:00
14 | Bogura | 230 | 243 | 2025-02-08 03:00 | 223 | 2025-02-26 13:00
15 | Bogura-400 | 230 | 248 | 2025-02-17 00:00 | 223 | 2025-02-26 13:00
16 | Borhanuddin | 230 | 250 | 2025-02-08 01:00 | 237 | 2025-02-23 12:00
17 | BSRM | 230 | 240 | 2025-02-06 19:30 | 220 | 2025-02-23 12:00
18 | Cumilla(N) | 230 | 240 | 2025-02-07 19:00 | 220 | 2025-02-23 12:00
19 | Faridpur | 230 | 248 | 2025-02-08 02:00 | 229 | 2025-02-23 12:00
20 | Fenchuganj | 230 | 244 | 2025-02-07 09:00 | 224 | 2025-02-25 18:00
21 | Ghorashal | 230 | 244 | 2025-02-08 01:00 | 225 | 2025-02-27
22 | Ghorashal-230 | 230 | 241 | 2025-02-22 18:30 | 216 | 2025-02-13 12:00
23 | Gopalganj | 230 | 248 | 2025-02-09 23:00 | 228 | 2025-02-25 12:00
24 | GPH | 230 | 239 | 2025-02-06 19:30 | 221 | 2025-02-23 12:00
25 | Haripur | 230 | 242 | 2025-02-08 03:00 | 216 | 2025-02-13 12:00
26 | Hasnabad | 230 | 241 | 2025-02-15 06:00 | 217 | 2025-02-13 12:00
27 | Hathazari | 230 | 240 | 2025-02-08 19:00 | 224 | 2025-02-23 12:00
28 | Ishurdi | 230 | 245 | 2025-02-15 05:00 | 225 | 2025-02-01 12:00
29 | Jhenaidah | 230 | 242 | 2025-02-15 05:00 | 218 | 2025-02-01 12:00
30 | Kaliakoir | 230 | 242 | 2025-02-22 18:00 | 211 | 2025-02-27 16:00
31 | Keranigonj | 230 | 240 | 2025-02-08 03:00 | 215 | 2025-02-20 12:00
32 | Khulna(S) | 230 | 244 | 2025-02-15 05:00 | 220 | 2025-02-25 12:00
33 | Madunaghat | 230 | 240 | 2025-02-06 20:00 | 223 | 2025-02-23 12:00
34 | Madunaghat-400 | 230 | 239 | 2025-02-06 20:00 | 224 | 2025-02-23 12:00
35 | Maniknagar | 230 | 243 | 2025-02-04 19:00 | 216 | 2025-02-13 12:00
36 | Meghnaghat | 230 | 245 | 2025-02-22 18:30 | 225 | 2025-02-13 12:00
37 | Meghnaghat-400 | 230 | 242 | 2025-02-08 03:00 | 220 | 2025-02-23 12:00
38 | Mirsorai | 230 | 242 | 2025-02-05 18:30 | 221 | 2025-02-23 15:00
39 | Rajshahi | 230 | 243 | 2025-02-08 04:00 | 222 | 2025-02-03 11:00
40 | Rampal | 230 | 270 | 2025-02-24 06:00 | 220 | 2025-02-03 12:00
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 242 | 2025-02-15 06:00 | 215 | 2025-02-13 12:00
43 | Shikalbaha | 230 | 239 | 2025-02-06 20:00 | 222 | 2025-02-23 12:00
44 | Shyampur | 230 | 240 | 2025-02-08 04:00 | 216 | 2025-02-20 12:00
45 | Siddhirganj | 230 | 260 | 2025-02-16 17:00 | 218 | 2025-02-13 12:00
46 | Sirajgonj | 230 | 247 | 2025-02-05 04:00 | 232 | 2025-02-13 12:00
47 | Sreepur | 230 | 244 | 2025-02-08 03:00 | 223 | 2025-02-13 12:00
48 | Tongi | 230 | 238 | 2025-02-22 18:00 | 212 | 2025-02-13 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 139 | 2025-02-22 18:00 | 120 | 2025-02-13 12:00
2 | Agargaon | 132 | 140 | 2025-02-08 03:00 | 124 | 2025-02-13 12:00
3 | Agrabad | 132 | 138 | 2025-02-06 20:00 | 125 | 2025-02-23 12:00
4 | AKS | 132 | 136 | 2025-02-19 08:00 | 125 | 2025-02-23 14:00
5 | Aminbazar | 132 | 145 | 2025-02-22 18:00 | 121 | 2025-02-20 12:00
6 | Amnura | 132 | 147 | 2025-02-14 16:00 | 123 | 2025-02-27 10:00
7 | Ashuganj | 132 | 145 | 2025-02-08 02:00 | 134 | 2025-02-27 14:00
8 | Bagerhat | 132 | 140 | 2025-02-15 05:00 | 122 | 2025-02-24 18:30
9 | Bajitpur | 132 | 139 | 2025-02-15 02:00 | 125 | 2025-02-27 15:00
10 | Bakulia | 132 | 164 | 2025-02-19 22:00 | 121 | 2025-02-23 13:00
11 | Banani | 132 | 139 | 2025-02-07 08:00 | 119 | 2025-02-13 12:00
12 | Bangabhaban | 132 | 138 | 2025-02-01 04:00 | 120 | 2025-02-13 12:00
13 | Barapukuria | 132 | 139 | 2025-02-23 10:00 | 120 | 2025-02-21 08:00
14 | Barguna | 132 | 142 | 2025-02-02 09:00 | 130 | 2025-02-02 21:00
15 | Barishal | 132 | 138 | 2025-02-06 19:30 | 128 | 2025-02-11 12:00
16 | Barishal-230 | 132 | 138 | 2025-02-04 05:00 | 128 | 2025-02-13 12:00
17 | Baroaulia | 132 | 139 | 2025-02-06 19:30 | 127 | 2025-02-23 12:00
18 | Baroirhat | 132 | 137 | 2025-02-06 04:00 | 121 | 2025-02-22 15:00
19 | Bashundhara | 132 | 141 | 2025-02-22 18:30 | 119 | 2025-02-13 12:00
20 | BashundharaCement | 132 | 139 | 2025-02-22 19:00 | 123 | 2025-02-06 01:00
21 | Beanibazar | 132 | 148 | 2025-02-05 06:00 | 124 | 2025-02-27 13:00
22 | Benapole | 132 | 139 | 2025-02-01 03:00 | 120 | 2025-02-11 13:00
23 | Bhaluka | 132 | 132 | 2025-02-05 13:00 | 115 | 2025-02-27 14:00
24 | Bhandaria | 132 | 136 | 2025-02-20 15:00 | 125 | 2025-02-01 14:00
25 | Bhangura | 132 | 140 | 2025-02-08 03:00 | 127 | 2025-02-13 12:00
26 | Bheramara | 132 | 140 | 2025-02-14 05:00 | 102 | 2025-02-17 23:00
27 | Bheramara(GK) | 132 | 140 | 2025-02-02 04:00 | 128 | 2025-02-01 12:00
28 | Bhulta | 132 | 134 | 2025-02-07 18:00 | 119 | 2025-02-13 12:00
29 | Bog-Sherpur | 132 | 138 | 2025-02-03 05:00 | 125 | 2025-02-26 13:00
30 | Bogura | 132 | 140 | 2025-02-18 23:00 | 126 | 2025-02-08 10:00
31 | Bogura-230 | 132 | 140 | 2025-02-17 20:00 | 127 | 2025-02-04 13:00
32 | Brahmanbaria | 132 | 140 | 2025-02-08 01:00 | 125 | 2025-02-13 12:00
33 | Cantonment | 132 | 144 | 2025-02-04 10:00 | 124 | 2025-02-13 12:00
34 | Chandpur | 132 | 142 | 2025-02-04 18:30 | 119 | 2025-02-22 17:00
35 | Chandraghona | 132 | 139 | 2025-02-06 20:00 | 129 | 2025-02-23 11:00
36 | Chapai | 132 | 140 | 2025-02-03 05:00 | 124 | 2025-02-27 11:00 |  | 27-02-2025 | 11:00 | 124
37 | Charsaidpur | 132 | 140 | 2025-02-15 03:00 | 124 | 2025-02-13 12:00
38 | Chauddagram | 132 | 138 | 2025-02-06 09:00 | 121 | 2025-02-22 15:00 |  | 22-02-2025 | 15:00 | 121
39 | Chhatak | 132 | 138 | 2025-02-02 05:00 | 120 | 2025-02-27 13:00
40 | Chowmuhani | 132 | 136 | 2025-02-06 09:00 | 114 | 2025-02-22 18:30
41 | Chuadanga | 132 | 141 | 2025-02-15 01:00 | 122 | 2025-02-03 12:00
42 | Coxsbazar | 132 | 129 | 2025-02-06 08:00 | 104 | 2025-02-15 11:00
43 | Cumilla(N) | 132 | 140 | 2025-02-07 19:00 | 127 | 2025-02-22 15:00
44 | Cumilla(S) | 132 | 140 | 2025-02-06 19:30 | 124 | 2025-02-12 12:00
45 | Daudkandi | 132 | 137 | 2025-02-15 05:00 | 120 | 2025-02-17 12:00
46 | Dhaka | 132 | 138 | 2025-02-01 04:00 | 121 | 2025-02-13 12:00
47 | Dhamrai | 132 | 142 | 2025-02-22 18:30 | 120 | 2025-02-13 12:00
48 | Dhanmondi | 132 | 139 | 2025-02-08 04:00 | 123.5 | 2025-02-13 12:00
49 | Dohazari | 132 | 139 | 2025-02-15 07:00 | 122 | 2025-02-23 12:00
50 | Faridpur | 132 | 145 | 2025-02-09 07:00 | 136 | 2025-02-18 09:00
51 | Fatullah | 132 | 141 | 2025-02-08 04:00 | 126 | 2025-02-20 12:00 |  | 20-02-2025 | 12:00 | 126
52 | Fenchuganj | 132 | 169 | 2025-02-17 21:00 | 130 | 2025-02-14 00:00
53 | Feni | 132 | 160 | 2025-02-11 18:00 | 120 | 2025-02-11 15:00
54 | Ghatail | 132 | 136 | 2025-02-16 04:00 | 115 | 2025-02-24 09:00
55 | Ghorashal | 132 | 145 | 2025-02-22 18:00 | 131 | 2025-02-25 14:00
56 | Goalpara | 132 | 142 | 2025-02-14 05:00 | 125 | 2025-02-25 12:00
57 | Gollamari | 132 | 142 | 2025-02-15 06:00 | 126 | 2025-02-25 12:00 |  | 25-02-2025 | 12:00 | 126
58 | Gopalganj | 132 | 140 | 2025-02-21 06:00 | 127 | 2025-02-11 12:00
59 | Gopalganj-400 | 132 | 141 | 2025-02-17 06:00 | 129 | 2025-02-11 12:00
60 | Gulshan | 132 | 137 | 2025-02-22 18:30 | 119 | 2025-02-13 12:00
61 | Halishahar | 132 | 138 | 2025-02-06 08:00 | 125 | 2025-02-23 12:00
62 | Haripur | 132 | 138 | 2025-02-08 03:00 | 124 | 2025-02-13 12:00
63 | HaripurSBU | 132 | 139 | 2025-02-13 03:00 | 123 | 2025-02-02 09:00 |  | 02-02-2025 | 09:00 | 123
64 | Hasnabad | 132 | 142 | 2025-02-22 18:00 | 110 | 2025-02-12 17:00
65 | Hathazari | 132 | 140 | 2025-02-06 19:00 | 130 | 2025-02-23 12:00 |  | 23-02-2025 | 12:00 | 130
66 | Ishurdi | 132 | 142 | 2025-02-08 03:00 | 130 | 2025-02-03 12:00
67 | Jaldhaka | 132 | 136 | 2025-02-23 10:00 | 105 | 2025-02-19 08:00
68 | Jamalpur | 132 | 135 | 2025-02-14 20:00 | 110 | 2025-02-28 03:00
69 | Jashore | 132 | 139 | 2025-02-04 03:00 | 122 | 2025-02-11 13:00 |  | 11-02-2025 | 13:00 | 122
70 | Jhenaidah | 132 | 141 | 2025-02-15 01:00 | 126 | 2025-02-06 13:00 |  | 06-02-2025 | 13:00 | 126
71 | Jhenaidah-230 | 132 | 142 | 2025-02-15 05:00 | 126 | 2025-02-01 12:00
72 | Joydebpur | 132 | 144 | 2025-02-22 18:00 | 139 | 2025-02-22 18:00 |  | 22-02-2025 | 18:00 | 139
73 | Joypurhat | 132 | 137 | 2025-02-04 04:00 | 116 | 2025-02-26 13:00
74 | Juldah | 132 | 140 | 2025-02-16 19:00 | 126 | 2025-02-23 12:00
75 | Kabirpur | 132 | 144 | 2025-02-22 18:00 | 126 | 2025-02-25 11.:00
76 | Kachua | 132 | 140 | 2025-02-04 18:30 | 120 | 2025-02-22 15:00
77 | Kaliakoir | 132 | 148 | 2025-02-03 07:00 | 129 | 2025-02-03 11:00
78 | Kallyanpur | 132 | 136 | 2025-02-01 02:00 | 123 | 2025-02-23 11:00
79 | Kalurghat | 132 | 138 | 2025-02-06 19:30 | 122 | 2025-02-07 10:00
80 | Kamrangirchar | 132 | 142 | 2025-02-14 19:30 | 119 | 2025-02-23 12:00
81 | Kaptai | 132 | N/A | N/A | N/A | N/A
82 | Kazla | 132 | 137 | 2025-02-01 03:00 | 120 | 2025-02-13 13:00
83 | Keranigonj | 132 | 142 | 2025-02-14 20:00 | 120 | 2025-02-13 13:00
84 | Khagrachori | 132 | 137 | 2025-02-06 19:30 | 127 | 2025-02-23 12:00
85 | Khosba | 132 | 134 | 2025-02-27 06:00 | 125 | 2025-02-27 11:00
86 | Khulna | 132 | 139 | 2025-02-02 05:00 | 125 | 2025-02-05 13:00
87 | Khulna(S) | 132 | 142 | 2025-02-15 06:00 | 126 | 2025-02-25 12:00
88 | Khulshi | 132 | 137 | 2025-02-06 20:00 | 124 | 2025-02-23 12:00
89 | Kishoreganj | 132 | 136 | 2025-02-12 03:00 | 113 | 2025-02-27 14:00
90 | Kodda | 132 | 147 | 2025-02-22 18:00 | 124 | 2025-02-23 15:00
91 | KSRM | 132 | 138 | 2025-02-04 19:00 | 128 | 2025-02-22 15:00
92 | Kulaura | 132 | 142 | 2025-02-03 05:00 | 129 | 2025-02-13 12:00
93 | Kurigram | 132 | 137 | 2025-02-23 10:00 | 112 | 2025-02-28 07:00
94 | Kushtia | 132 | 141 | 2025-02-15 01:00 | 126 | 2025-02-28 13:00
95 | Lalbag | 132 | 143 | 2025-02-14 20:00 | 124 | 2025-02-20 12:00
96 | Lalmonirhat | 132 | 159 | 2025-02-18 15:00 | 112 | 2025-02-16 07:00 |  | 09-01-2025 | 03:00 | 133
97 | Madanganj | 132 | 139 | 2025-02-22 19:00 | 124 | 2025-02-13 12:00
98 | Madaripur | 132 | 140 | 2025-02-22 06:00 | 131 | 2025-02-25 12:00 |  | 25-02-2025 | 12:00 | 131
99 | Madartek | 132 | 138 | 2025-02-15 06:00 | 119 | 2025-02-13 12:00
100 | Madunaghat | 132 | 138 | 2025-02-06 09:00 | 128 | 2025-02-23 15:00
101 | Magura | 132 | 141 | 2025-02-02 04:00 | 125 | 2025-02-11 12:00 |  | 11-02-2025 | 12:00 | 125
102 | Mahasthangarh | 132 | 138 | 2025-02-17 23:00 | 123 | 2025-02-08 10:00
103 | Manikganj | 132 | 141 | 2025-02-15 01:00 | 125 | 2025-02-23 16:00 |  | 23-02-2025 | 16:00 | 125 | 1119
104 | Maniknagar | 132 | 138 | 2025-02-15 04:00 | 121 | 2025-02-13 12:00
105 | Matarbari | 132 | 132 | 2025-02-12 21:00 | 109 | 2025-02-24 12:00
106 | Matuail | 132 | 139.5 | 2025-02-15 06:00 | 123.6 | 2025-02-13 12:00
107 | Millgate | 132 | 144 | 2025-02-22 18:30 | 120 | 2025-02-13 12:00
108 | Mirpur | 132 | 143 | 2025-02-22 06:00 | 122 | 2025-02-13 12:00
109 | Mirzapur | 132 | 140 | 2025-02-03 06:00 | 121 | 2025-02-24 10:00
110 | Mithapukur | 132 | 142 | 2025-02-23 10:00 | 118 | 2025-02-10 08:00
111 | MI_Cement | 132 | 140 | 2025-02-15 06:00 | 125 | 2025-02-13 12:00
112 | Modern | 132 | 0 | 2025-02-01 00:00 | N/A | N/A
113 | Mogbazar | 132 | 138 | 2025-02-01 04:00 | 120 | 2025-02-13 12:00
114 | Mongla | 132 | 140 | 2025-02-15 05:00 | 123 | 2025-02-05 12:00
115 | Motijheel | 132 | 163 | 2025-02-12 07:00 | 120 | 2025-02-13 12:00
116 | Muktagacha | 132 | 136 | 2025-02-16 03:00 | 114 | 2025-02-25 12:00
117 | Munshiganj | 132 | 139 | 2025-02-07 19:00 | 124 | 2025-02-13 12:00
118 | Muradnagar | 132 | 139 | 2025-02-15 06:00 | 125 | 2025-02-23 12:00
119 | Mymensingh | 132 | 135 | 2025-02-23 10:00 | 108 | 2025-02-27 13:00
120 | Naogaon | 132 | 137 | 2025-02-17 20:00 | 120 | 2025-02-26 13:00
121 | Narail | 132 | 140 | 2025-02-03 04:00 | 124 | 2025-02-02 13:00
122 | Narinda | 132 | 0 | 2025-02-01 00:00 | N/A | N/A
123 | Narshingdi | 132 | 138 | 2025-02-22 19:00 | 118 | 2025-02-13 13:00
124 | Natore | 132 | 139 | 2025-02-15 00:00 | 127 | 2025-02-08 10:00
125 | Nawabganj | 132 | 142 | 2025-02-14 20:00 | 130 | 2025-02-01 12:00
126 | Netrakona | 132 | 129 | 2025-02-23 12:00 | 108 | 2025-02-27 13:00
127 | New | 132 | 141 | 2025-02-08 03:00 | 121 | 2025-02-13 12:00
128 | Niamatpur | 132 | 141 | 2025-02-03 03:00 | 127 | 2025-02-26 13:00
129 | Noapara | 132 | 141 | 2025-02-15 05:00 | 124 | 2025-02-18 12:00
130 | Pabna | 132 | 139 | 2025-02-17 05:00 | 122 | 2025-02-13 12:00
131 | Palashbari | 132 | 136 | 2025-02-23 10:00 | 115 | 2025-02-27 08:00
132 | Panchagarh | 132 | 143 | 2025-02-15 19:30 | 114 | 2025-02-08 10:00
133 | Patuakhali | 132 | 140 | 2025-02-01 17:00 | 129 | 2025-02-17 15:00
134 | Payra | 132 | 141 | 2025-02-15 06:00 | 131 | 2025-02-17 13:00
135 | PHP | 132 | 137 | 2025-02-06 08:00 | 119 | 2025-02-22 15:00
136 | Postogola | 132 | 141 | 2025-02-07 19:00 | 127 | 2025-02-20 12:00
137 | Purbachal | 132 | 139 | 2025-02-22 18:30 | 120 | 2025-02-13 12:00
138 | Purbasadipur | 132 | 139 | 2025-02-23 10:00 | 111 | 2025-02-08 10:00
139 | Rahanpur | 132 | 142 | 2025-02-04 03:00 | 128 | 2025-02-26 13:00
140 | Rahanpur-400 | 132 | 142 | 2025-02-01 02:00 | 127 | 2025-02-26 13:00
141 | Rahim | 132 | 137 | 2025-02-01 03:00 | 123 | 2025-02-13 12:00
142 | Rajbari | 132 | 160 | 2025-02-16 11:00 | 127 | 2025-02-23 12:00
143 | Rajendrapur | 132 | 144 | 2025-02-22 18:00 | 122 | 2025-02-13 13:00
144 | Rajshahi | 132 | 141 | 2025-02-15 04:00 | 129 | 2025-02-01 13:00
145 | Rajshahi-230 | 132 | 141 | 2025-02-08 03:00 | 121 | 2025-02-27 10:00
146 | Ramganj | 132 | 138 | 2025-02-04 18:30 | 115 | 2025-02-22 15:00
147 | Rampur | 132 | 138 | 2025-02-12 18:30 | 124 | 2025-02-23 12:00
148 | Rampura | 132 | 138 | 2025-02-01 04:00 | 120 | 2025-02-13 12:00
149 | Rangamati | 132 | 138 | 2025-02-06 20:00 | 127 | 2025-02-23 12:00
150 | Rangpur | 132 | 140 | 2025-02-23 10:00 | 115 | 2025-02-21 08:00
151 | Ruppur | 132 | 142 | 2025-02-15 05:00 | 130 | 2025-02-02 12:00
152 | Saidpur | 132 | 140 | 2025-02-23 10:00 | 116 | 2025-02-20 07:00
153 | Satkhira | 132 | 140 | 2025-02-08 02:00 | 123 | 2025-02-11 13:00
154 | Satmasjid | 132 | 140 | 2025-02-08 02:00 | 123 | 2025-02-13 12:00
155 | Savar | 132 | 142 | 2025-02-22 07:00 | 122 | 2025-02-18 15:00
156 | SevenRings | 132 | 145 | 2025-02-15 00:00 | 131 | 2025-02-13 11:00
157 | ShahCement | 132 | 140 | 2025-02-15 03:00 | 124 | 2025-02-13 12:00
158 | Shahjadpur | 132 | 143 | 2025-02-17 03:00 | 131 | 2025-02-13 12:00
159 | Shahjibazar | 132 | 141 | 2025-02-05 06:00 | 127 | 2025-02-13 12:00
160 | Shahmirpur | 132 | 139 | 2025-02-05 18:30 | 126 | 2025-02-23 12:00
161 | Shariatpur | 132 | 139 | 2025-02-15 06:00 | 128 | 2025-02-01 13:00
162 | Sherpur | 132 | 134 | 2025-02-23 10:00 | 107 | 2025-02-14 01:00
163 | Shikalbaha | 132 | 128 | 2025-02-19 09:00 | 117 | 2025-02-23 12:00
164 | Shikalbaha-230 | 132 | 139 | 2025-02-05 19:00 | 117 | 2025-02-23 12:00
165 | Shitalakhya | 132 | 140 | 2025-02-15 06:00 | 125 | 2025-02-13 12:00
166 | Sholosohor | 132 | 137 | 2025-02-05 19:00 | 127 | 2025-02-23 12:00
167 | Shyampur | 132 | 140 | 2025-02-01 04:00 | 125 | 2025-02-13 12:00
168 | Shyampur-230 | 132 | 141 | 2025-02-15 06:00 | 125 | 2025-02-13 12:00
169 | Siddhirganj | 132 | 139 | 2025-02-08 04:00 | 124 | 2025-02-13 12:00
170 | Sirajganj | 132 | 140 | 2025-02-01 04:00 | 125 | 2025-02-20 08:00
171 | Sonargaon | 132 | 138 | 2025-02-15 04:00 | 112 | 2025-02-17 12:00
172 | Sreemongol | 132 | 141 | 2025-02-05 04:00 | 127 | 2025-02-13 12:00
173 | Sreepur | 132 | 132 | 2025-02-03 05:00 | 119 | 2025-02-27 13:00
174 | Srinagar | 132 | 142 | 2025-02-14 20:00 | 124 | 2025-02-20 11:00
175 | SSM | 132 | 141 | 2025-02-06 09:00 | 130 | 2025-02-10 22:00
176 | Sunamganj | 132 | 138 | 2025-02-03 05:00 | 120 | 2025-02-27 12:00
177 | Sylhet | 132 | 140 | 2025-02-02 05:00 | 124 | 2025-02-27 13:00
178 | Sylhet-132 | 132 | 140 | 2025-02-05 02:00 | 123 | 2025-02-27 14:00
179 | Tangail | 132 | 135 | 2025-02-15 03:00 | 117 | 2025-02-24 10:00
180 | Thakurgaon | 132 | 142 | 2025-02-19 21:00 | 112 | 2025-02-08 10:00
181 | TK | 132 | 139 | 2025-02-06 19:30 | 127 | 2025-02-23 12:00
182 | Tongi | 132 | 141 | 2025-02-01 04:00 | 124 | 2025-02-13 11:00
183 | Ullahpara | 132 | 141 | 2025-02-15 02:00 | 127 | 2025-02-20 08:00
184 | Ullon | 132 | 137 | 2025-02-01 06:00 | 121 | 2025-02-13 12:00
185 | Uttara | 132 | 142 | 2025-02-21 07:00 | 122 | 2025-02-13 12:00
186 | UttaraNew | 132 | 142 | 2025-02-22 18:30 | 122 | 2025-02-13 12:00
187 | Zigatola | 132 | 142 | 2025-02-14 19:00 | 123 | 2025-02-20 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: February 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 18-02-2025 | 14:00 | 399 | 67 | 77.805
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 11-02-2025 | 15:00 | 351 | 62 | 68.5449
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 28-02-2025 | 16:00 | 359 | 43 | 69.5319
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 20-02-2025 | 18:30 | 176 | 48 | 56.1317
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 04-02-2025 | 15:00 | -197 | 21 | 38.0993
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 04-02-2025 | 15:00 | -197 | 21 | 38.0993
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 04-02-2025 | 21:00 | -127 | 43 | 25.785
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 04-02-2025 | 21:00 | -122 | 45 | 25.0067
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 01-02-2025 | 18:30 | 267 | 35 | 35.9046
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 23-02-2025 | 07:00 | 198 | 34 | 26.7864
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 17-02-2025 | 10:00 | 262 | 27 | 35.1183
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 04-02-2025 | 19:00 | -105 | -17 | 32.7284
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 14-02-2025 | 17:00 | -480 | -20 | 147.8205
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 04-02-2025 | 19:00 | -105 | -17 | 32.7284
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 02-02-2025 | 03:00 | 238 | 34 | 32.0555
Gopalganj 400/230kV Grid Sub-Station | ATR-05 | 400/230 | 750 | 09-02-2025 | 18:30 | -96 | 53 | 14.6211
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 27-02-2025 | 14:00 | 141 | 82 | 31.3674
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 27-02-2025 | 14:00 | 141 | 82 | 31.3674
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 04-02-2025 | 18:30 | 306 | 73 | 96.796
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 04-02-2025 | 18:30 | 306 | 73 | 96.796
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 18-02-2025 | 11:00 | -514 | -204 | 73.7337
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 18-02-2025 | 11:00 | -515 | -202 | 73.7599
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 26-02-2025 | 19:30 | -285 | -8 | 54.8293
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 26-02-2025 | 19:30 | -281 | -9 | 54.0662
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 04-02-2025 | 12:00 | -49 | -26 | 17.0679
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 28-02-2025 | 23:00 | -178 | -23 | 55.2246
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 27-02-2025 | 12:00 | 268 | 60 | 52.8143
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 26-02-2025 | 13:00 | 263 | 69 | 52.2886
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 08-02-2025 | 13:00 | 223 | 58 | 76.8064
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 06-02-2025 | 13:00 | 242 | 73 | 84.2569
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 14-02-2025 | 16:00 | 212 | 24 | 94.8241
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 19-02-2025 | 09:00 | 176 | 23 | 78.8873
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 08-02-2025 | 10:00 | 158 | 19 | 70.7281
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 22-02-2025 | 18:30 | 205 | 105 | 76.7753
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 07-02-2025 | 14:00 | 194 | 38 | 65.8955
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 04-02-2025 | 07:00 | 149 | 50 | 52.3885
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 11-02-2025 | 09:00 | 113 | 42 | 53.5791
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 11-02-2025 | 08:00 | 212 | 34 | 95.4263
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 11-02-2025 | 08:00 | 178 | 45 | 81.6
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 11-02-2025 | 08:00 | 231 | 31 | 77.6903
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 22-02-2025 | 13:00 | 100 | 18 | 33.869
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 11-02-2025 | 18:30 | 97 | 18 | 32.8853
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 26-02-2025 | 19:30 | -86 | 41 | 42.3437
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 26-02-2025 | 19:30 | -86 | 41 | 42.3437
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 09-02-2025 | 08:00 | 118 | 36 | 54.8308
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 09-02-2025 | 08:00 | 118 | 36 | 54.8308
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 09-02-2025 | 08:00 | 158 | 52 | 55.4457
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 09-02-2025 | 08:00 | 158 | 52 | 55.4457
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 14-02-2025 | 22:00 | 137 | 54 | 65.4481
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 14-02-2025 | 22:00 | 136 | 52 | 64.7121
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 14-02-2025 | 22:00 | 147 | 60 | 70.566
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 06-02-2025 | 19:00 | 131 | 35 | 45.1983
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 22-02-2025 | 18:30 | 150 | 47 | 52.397
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 24-02-2025 | 18:00 | 99 | 0 | 79.2
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 24-02-2025 | 18:00 | 99 | 0 | 79.2
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 20-02-2025 | 15:00 | 78 | 14 | 35.2206
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 23-02-2025 | 10:00 | 118 | 5 | 52.4915
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 23-02-2025 | 10:00 | 107 | 9 | 47.7235
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 11-02-2025 | 12:00 | 74 | 45 | 38.4926
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 11-02-2025 | 12:00 | 74 | 45 | 38.4926
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 11-02-2025 | 12:00 | 74 | 45 | 38.4926
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 04-02-2025 | 13:00 | 78 | 42 | 59.0593
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 04-02-2025 | 13:00 | 78 | 42 | 59.0593
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 04-02-2025 | 13:00 | 78 | 42 | 59.0593
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 01-02-2025 | 12:00 | 75 | 45 | 58.3095
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 26-02-2025 | 19:30 | 99 | 54 | 50.1199
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 26-02-2025 | 19:30 | 99 | 54 | 50.1199
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 26-02-2025 | 19:30 | 99 | 54 | 50.1199
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 25-02-2025 | 19:00 | -158 | -40 | 54.3282
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 25-02-2025 | 19:00 | -158 | -40 | 54.3282
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 22-02-2025 | 16:00 | 122 | 56 | 44.7462
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 20-02-2025 | 13:00 | 156 | 64 | 56.206
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 20-02-2025 | 13:00 | 156 | 64 | 56.206
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-02-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 11-02-2025 | 19:00 | -122 | -31 | 55.9453
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 11-02-2025 | 19:00 | -122 | -31 | 55.9453
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 11-02-2025 | 19:00 | -157 | -35 | 53.618
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 20-02-2025 | 13:00 | 137 | 57 | 49.4615
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 20-02-2025 | 13:00 | 137 | 57 | 49.4615
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 26-02-2025 | 19:30 | -118 | 9 | 39.4476
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 26-02-2025 | 19:30 | -118 | 9 | 39.4476
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-02-2025 | 00:00 | 1 | 1 | 0.4714
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-02-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 01-02-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 11-02-2025 | 14:00 | 374 | 27 | 83.3274
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 11-02-2025 | 14:00 | 374 | 27 | 83.3274
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 22-02-2025 | 19:00 | 206 | 98 | 76.0409
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 22-02-2025 | 19:00 | 206 | 98 | 76.0409
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 28-02-2025 | 14:00 | 97 | 114 | 49.8943
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 05-02-2025 | 01:00 | 199 | 35 | 67.3515
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 23-02-2025 | 12:00 | 139 | 106 | 58.2685
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 23-02-2025 | 12:00 | 139 | 106 | 58.2685
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 19-02-2025 | 19:00 | 183 | 43 | 62.6613
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 01-02-2025 | 10:00 | 262 | 56 | 89.306
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 28-02-2025 | 09:00 | 210 | 28 | 94.1593
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 08-02-2025 | 11:00 | 205 | 36 | 92.5053
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 08-02-2025 | 11:00 | 205 | 36 | 92.5053
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: February 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: February 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-02-01 | 10784 | 10784 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-01 | 9914 | 9959 | 45 | 12:00 | 14 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | -
2025-02-02 | 10799 | 10799 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-02 | 10451 | 10451 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-02-03 | 10877 | 10908 | 31 | 19:00 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-03 | 10567 | 10608 | 41 | 12:00 | 20 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | -
2025-02-04 | 10914 | 10950 | 36 | 19:00 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-04 | 10425 | 10485 | 60 | 12:00 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | -
2025-02-05 | 11044 | 11134 | 90 | 19:00 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-05 | 10665 | 10700 | 35 | 12:00 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | -
2025-02-06 | 11118 | 11192 | 74 | 19:00 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-06 | 10874 | 10904 | 30 | 12:00 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | -
2025-02-07 | 9567 | 9597 | 30 | 19:00 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-07 | 9477 | 9527 | 50 | 12:00 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | -
2025-02-08 | 10778 | 10848 | 70 | 19:00 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-08 | 9823 | 9873 | 50 | 12:00 | 10 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | -
2025-02-09 | 10771 | 10861 | 90 | 19:00 | 40 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-09 | 10457 | 10524 | 67 | 12:00 | 47 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | -
2025-02-10 | 10867 | 10909 | 42 | 19:00 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-10 | 10396 | 10428 | 32 | 12:00 | 25 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-02-11 | 11012 | 11122 | 110 | 19:00 | 25 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-11 | 10615 | 10698 | 83 | 12:00 | 53 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | -
2025-02-12 | 11343 | 11403 | 60 | 19:00 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-12 | 10611 | 10671 | 60 | 12:00 | 10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | -
2025-02-13 | 11333 | 11455 | 122 | 19:00 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-13 | 11081 | 11131 | 50 | 12:00 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | -
2025-02-14 | 9501 | 9501 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-14 | 9900 | 9930 | 30 | 12:00 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | -
2025-02-15 | 9899 | 9899 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-15 | 8627 | 8627 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-02-16 | 11227 | 11227 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-16 | 10542 | 10598 | 56 | 12:00 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | -
2025-02-17 | 11479 | 11581 | 102 | 19:00 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-17 | 10946 | 10995 | 49 | 12:00 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | -
2025-02-18 | 11607 | 11697 | 90 | 19:00 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-18 | 11212 | 11227 | 15 | 12:00 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | -
2025-02-19 | 11741 | 11801 | 60 | 19:00 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-19 | 10982 | 11051 | 69 | 12:00 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | -
2025-02-20 | 11677 | 11769 | 92 | 19:00 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-20 | 11227 | 11305 | 78 | 12:00 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | -
2025-02-21 | 10333 | 10333 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-21 | 10008 | 10008 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-02-22 | 9874 | 9874 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-22 | 10193 | 10278 | 85 | 12:00 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 10 | -
2025-02-23 | 11348 | 11414 | 66 | 19:00 | 20 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-23 | 10016 | 10046 | 30 | 12:00 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-02-24 | 11673 | 11871 | 198 | 19:00 | 88 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-24 | 10919 | 11021 | 102 | 12:00 | 77 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | -
2025-02-25 | 12119 | 12119 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-25 | 11072 | 11225 | 153 | 12:00 | 30 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | -
2025-02-26 | 11752 | 11904 | 152 | 19:00 | 69 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-26 | 11130 | 11130 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-02-27 | 11808 | 11927 | 119 | 19:00 | 30 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-27 | 11073 | 11153 | 80 | 12:00 | 35 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 5 | -
2025-02-28 | 10995 | 11062 | 67 | 19:00 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | - | 2025-02-28 | 10581 | 10651 | 70 | 12:00 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | -
|  | - | - | - | [11 empty] | - | -
98
30
68

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: February 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12659.87 | 2025-02-25 | 19:00 Hr.
2 | Maximum Day Peak Genaration | MW | 11609.39 | 2025-02-18 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 12119 | 2025-02-25 | 19:00 Hr.
4 | Minimum Generation | MW | 6902.27 | 2025-02-08 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11482.7239 | - | -
6 | Average of the daily day peak Genaration | MW | 10803.4786 | - | -
7 | Maximum load shed (Evening Peak) | MW | 198 | 2025-02-24 | 19:00
8 | Minimum load shed | MW | 0 | 2025-02-02 | 19:00
9 | Total nos. of load shed days | Day | 21 | - | -
10 | Average load shed ( Avg. of the 28 days in the month) | MW/Day | 60.75 | - | -
11 | Total Generation | MkWh | 6697.2477 | - | -
12 | Total Generation by BPDB | MkWh | 1181.7677 | % of total Gen. | 17.65%
13 | Total Generation by IPP | MkWh | 2334.8935 | '' | 34.86%
14 | A) Total Generation by Generation Companies | MkWh | 1804.9675 | '' | 26.95%
| B) Total Generation by REB | MkWh | 67.3293 | " | 1.005%
| C) Total Generation by RENTAL | MkWh | 257.6077 | " | 3.846%
| D) Total Imported from India (BIPTC) | MkWh | 585.4144 | " | 8.741%
| E) Total Imported from Tripura, India (A.C) | MkWh | 3.9858 | " | 0.05951%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 461.2817 | " | 6.888%
15 | Fuel wise Generation.
| A) Gas | MkWh | 2920.098 | % of total Gen. | 43.6%
| B) Oil | MkWh | 1148.1089 | '' | 17.14%
| C) Hydro | MkWh | 0.60499 | '' | 0.009033%
| D) Solar | MkWh | 124.2522 | '' | 1.855%
| E) Coal | MkWh | 1453.5016 | '' | 21.7%
| F) BIPTC (Import from India) | MkWh | 585.4144 | '' | 8.741%
| G) A.C (Import from Tripura, India) | MkWh | 3.9858 | '' | 0.05951%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 461.2817 | '' | 6.888%
| J) Wind | MkWh | 0 | '' | 0%
16 | Maximun of the daily total Generation . | MkWh | 263.2651 | 2025-02-26
17 | Monthly Load factor | % | 78.7223 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 43673.0679 | - | -
| A) Gas | M.Taka | 10979.1819 | - | -
| B) Coal | M.Taka | 11695.7764 | - | -
| C) HFO | M.Taka | 13851.8883 | - | -
| D) HSD | M.Taka | 2.4416 | - | -
| E) Hydro | M.Taka | 2.6759 | - | -
| F) Solar | M.Taka | 1555.6217 | - | -
| G) Total Import | M.Taka | 5585.4821 | - | -
| H) Wind |  | 78.6667
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1908.5991 | 2025-02-19
| A) Gas | M.Taka | 429.9676 | 2025-02-16
| B) Coal | M.Taka | 500.0472 | 2025-02-01
| C) HFO | M.Taka | 903.4468 | 2025-02-19
| D) HSD | M.Taka | 2.2196 | 2025-02-20 | -
| E) Hydro | M.Taka | 0.10231 | 2025-02-23 | -
| F) Solar | M.Taka | 71.4963 | 2025-02-24 | -
| G) Total Import |  | 217.6185 | 2025-02-19
| H) Wind | M.Taka | 9.0862 | 2025-02-25
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.5328
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.6569
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93.15 | 28/02/2025 | 06:00
b) | Actual | FT (MSL) | 89.05 | 28/02/2025 | 06:00
22 | Peak Genaration of February 2024 | MW | 11433 | 2024-02-20 | 19:00
23 | Peak Demand of Februaru 2024 | MW | 11600 | 2024-02-29 | 19:00
24 | Maximum peak Generation recorded upto 28/02/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 28/02/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 28/02/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: February 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | BPDB | 383
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 |  |  | √ | √ | [13 empty] | √
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √
10 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | [15 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
36 | Shajibazar 100 MW PP | BPDB | 100
37 | Payra 1320 MW Unit-1 | BCPCL | 622 | √ | √ | √ | √ | √ | [5 empty] | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ |  | √
38 | Kushiara 163 MW CCPP (KP) | IPP | 163
39 | Haripur 360MW CCPP(HPL) | IPP | 360
40 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [27 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [27 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [8 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [25 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [25 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | [6 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant