## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-03-2025 | during | 25-03-2025 | during | 25-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 22 | 22 | 97.7 | 97.7 | 97.7 | 97.7 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 372 | 362 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 280 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 195 | 202 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25 | 24 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 20 | 29 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 17 | 52.19 | 52.19 | 16 | 16 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 75 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 35 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 34 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 36 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 450 | 550 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2049 | 2356 | 4675.9 | 4645.9 | 3547.95 | 3552.95
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 101 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 48 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 25 | 4 | 32 | 4 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 804 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 9 | 6 | 25 | 24 | 25 | 24 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 770 | 770 | 770 | 770 | 770 | 770 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1867 | 2052 | 3646.47 | 3650.72 | 3646.47 | 3650.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 211 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 359 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 35 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 148 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 20 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 40 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 68 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 68 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 69 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1182 | 1511 | 2415.99 | 2345.99 | 2273.55 | 2203.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-03-2025 | during | 25-03-2025 | during | 25-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 15 | 20 | 210 | 210 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 163 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 108 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.74 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 283.74 | 303 | 653.6 | 601.5 | 463.6 | 411.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 41 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 30 | 30 | 28 | 28 | FGMO
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 153 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 165 | 162 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 15 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 395 | 348 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1543 | 1496 | 1605 | 1605 | 1541 | 1541
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 919 | 871 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 36 | 36 | 36 | 36 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 461 | 453 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1474 | 1341 | 3586.2 | 3506.2 | 1994.02 | 1914.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 8 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 116 | 108 | 130 | 130 | 130 | 130 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 784 | 1050 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1325.65 | 1693 | 2172.12 | 2171.12 | 2172.12 | 2171.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 173 | 169 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 211 | 212 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 210 | 215 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 319 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 4 | 8.8 | 88 | 88 | 88 | 88 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.91 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 959.73 | 1306 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.27 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2160.41 | 2235.3 | 3102.15 | 2935.53 | 3060.36 | 2893.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 62 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 168 | 170 | 170 | 170 | 170 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.5 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 54 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 190 | 0 | 192 | 0 | 192 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 464.5 | 354 | 720.4 | 492 | 686.42 | 458.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12349.3 | 13341.3 | 22577.83 | 21953.96 | 19385.49 | 18796.62
Forecast Scenario (25-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11620 |  | 0 |  | 11620
|  |  |  | 1:00 | 11110 |  | 0 |  | 11110
|  |  |  | 2:00 | 10760 |  | 0 |  | 10760
|  |  |  | 3:00 | 10930 |  | 0 |  | 10930
|  |  |  | 4:00 | 11220 |  | 0 |  | 11220
|  |  |  | 5:00 | 10110 |  | 0 |  | 10110
|  |  |  | 6:00 | 9310 |  | 0 |  | 9310
|  |  |  | 7:00 | 9470 |  | 0 |  | 9470
|  |  |  | 8:00 | 9950 |  | 0 |  | 9950
|  |  |  | 9:00 | 10750 |  | 0 |  | 10750
|  |  |  | 10:00 | 11500 |  | 0 |  | 11500
|  |  |  | 11:00 | 11750 |  | 0 |  | 11750
|  |  |  | 12:00 | 12300 |  | 0 |  | 12300
|  |  |  | 13:00 | 12500 |  | 0 |  | 12500
|  |  |  | 14:00 | 12660 |  | 0 |  | 12660
|  |  |  | 15:00 | 12580 |  | 0 |  | 12580
|  |  |  | 16:00 | 12470 |  | 0 |  | 12470
|  |  |  | 17:00 | 12520 |  | 0 |  | 12520
|  |  |  | 18:00 | 12680 |  | 0 |  | 12680
|  |  |  | 18:30 | 12700 |  | 0 |  | 12700
|  |  |  | 19:00 | 12870 |  | 0 |  | 12870
|  |  |  | 19:30 | 12860 |  | 0 |  | 12860
|  |  |  | 20:00 | 12920 |  | 0 |  | 12920
|  |  |  | 21:00 | 12960 |  | 0 |  | 12960
|  |  |  | 22:00 | 12840 |  | 0 |  | 12840
|  |  |  | 23:00 | 12610 |  | 0 |  | 12610
Probable Maximum Temperature: |  |  | 33.40°C
Probable Maximum Demand at Day Peak: |  |  | 12300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12960.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12960.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 280.39 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:33 hrs on 25-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-03-2025 | [28 empty] | Date: | 24-03-2025 | [28 empty] | Date: | 24-03-2025 | [28 empty] | Date: | 24-03-2025 | [28 empty] | Date: | 24-03-2025 | [18 empty] | Date: | 24-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 374 | 0 | 0 | 0 | 41 | 0 | 54 | 32 | 0 | 0 | 0 | 0 | 24 | 0 | 450 | 280 | 583 | 0 | 0 | 20 | 220 | 99 | 0 | 0 | 35 | 23.5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 34 | 0 | 0 | 72 | 24 | 0 | 46 | 0 | 22 | 758 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 953 | 0 | 35 | 0 | 24 | 0 | 360 | 285 | 19 | 183 | 36 | 50 | 50 | 34 | 3 | 20 | 17 | 70 | 0 | 0 | 0 | 280 | 320 | 290 | 0 | 43 | 0 | 5 | 133 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 65 | 125 | 12 | 0 | 0 | 12 | 7165.5 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 916.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 197 | 0 | 190 | 0 | 314 | 0 | 0 | 2.5 | 180 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 108 | 220 | 0 | 0 | 962 | 0 | 4882.95 | 12048.45 | 86
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 374 | 0 | 0 | 0 | 41 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 278 | 500 | 0 | 0 | 20 | 220 | 39 | 0 | 0 | 35 | 23.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 72 | 12 | 0 | 46 | 0 | 24 | 756 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 906 | 0 | 35 | 0 | 27 | 0 | 360 | 285 | 10 | 182 | 36 | 34 | 50 | 17 | 0 | 20 | 17 | 66 | 0 | 0 | 0 | 280 | 320 | 291 | 0 | 43 | 0 | 5 | 133 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 45 | 95 | 12 | 0 | 0 | 12 | 6769.5 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 918.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 196 | 0 | 140 | 0 | 314 | 0 | 0 | 2.5 | 179 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 8 | 90 | 180 | 0 | 0 | 910 | 0 | 4687.95 | 11457.45 | 85.99
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 374 | 0 | 0 | 0 | 36 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 280 | 450 | 0 | 0 | 20 | 220 | 38 | 0 | 0 | 17 | 21.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 0 | 60 | 12 | 0 | 46 | 0 | 24 | 750 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 800 | 0 | 35 | 0 | 27 | 0 | 320 | 285 | 10 | 182 | 36 | 34 | 50 | 17 | 0 | 20 | 17 | 62 | 0 | 0 | 0 | 290 | 320 | 291 | 0 | 43 | 0 | 5 | 133 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 45 | 95 | 12 | 0 | 0 | 12 | 6479.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 827.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 150 | 0 | 140 | 0 | 314 | 0 | 0 | 2.5 | 180 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 90 | 180 | 0 | 0 | 895 | 0 | 4511.75 | 10991.25 | 85.99
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 374 | 0 | 0 | 0 | 36 | 0 | 37 | 49 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 283 | 500 | 0 | 0 | 20 | 220 | 39 | 0 | 0 | 17 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 60 | 12 | 0 | 46 | 0 | 24 | 758 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 808 | 0 | 43 | 0 | 27 | 0 | 360 | 285 | 10 | 182 | 36 | 34 | 50 | 17 | 0 | 20 | 17 | 60 | 0 | 0 | 0 | 280 | 320 | 347 | 0 | 43 | 0 | 5 | 133 | 21 | 0 | 72 | 30 | 0 | 18 | 164 | 0 | 45 | 134 | 17 | 0 | 0 | 12 | 6750 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 818.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 140 | 0 | 370 | 0 | 0 | 2.5 | 182 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 108 | 220 | 0 | 0 | 890 | 0 | 4614.19 | 11364.19 | 85.98
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 366 | 0 | 0 | 0 | 36 | 0 | 48 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 264 | 583 | 0 | 0 | 20 | 217 | 98 | 0 | 0 | 17 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 35 | 655 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 740 | 0 | 43 | 0 | 27 | 0 | 360 | 285 | 10 | 181 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 62 | 0 | 0 | 0 | 290 | 320 | 349 | 0 | 43 | 0 | 5 | 149 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 69 | 137 | 17 | 0 | 0 | 12 | 6674 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 816.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 183 | 0 | 172 | 0 | 373 | 0 | 0 | 2.5 | 182 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 108 | 220 | 0 | 0 | 942 | 0 | 4682.06 | 11356.06 | 85.98
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 21 | 358 | 0 | 0 | 0 | 25 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 262 | 450 | 0 | 0 | 20 | 215 | 96 | 0 | 0 | 0 | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 35 | 658 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 618 | 0 | 43 | 0 | 27 | 0 | 360 | 285 | 10 | 181 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 58 | 0 | 0 | 0 | 275 | 320 | 303 | 0 | 43 | 0 | 2 | 138 | 21 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 45 | 95 | 19 | 0 | 0 | 12 | 6116 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 824.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 309 | 0 | 0 | 2.5 | 180 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 108 | 180 | 0 | 0 | 672 | 0 | 4219.2 | 10335.2 | 85.97
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 21 | 327 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 253 | 300 | 0 | 0 | 20 | 0 | 40 | 0 | 0 | 0 | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 35 | 654 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 611 | 0 | 43 | 0 | 27 | 0 | 320 | 285 | 10 | 181 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 42 | 0 | 0 | 0 | 265 | 320 | 303 | 0 | 43 | 0 | 2 | 133 | 21 | 0 | 22 | 30 | 0 | 18 | 164 | 0 | 45 | 65 | 21 | 0 | 0.06 | 12 | 5427.06 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 822.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 250 | 0 | 0 | 2.5 | 184 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 78 | 180 | 0 | 0 | 572 | 0 | 4028.44 | 9455.5 | 85.97
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 21 | 321 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 300 | 279 | 250 | 0 | 0 | 7 | 0 | 80 | 0 | 4 | 0 | 24.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 14 | 658 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 610 | 3 | 43 | 0 | 26 | 0 | 320 | 285 | 10 | 182 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 46 | 0 | 11 | 0 | 290 | 320 | 299 | 0 | 43 | 0 | 2 | 132 | 16 | 0 | 22 | 30 | 0 | 18 | 164 | 0 | 45 | 70 | 21 | 0 | 7.98 | 12 | 5472.48 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 386 | 0 | 828.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 7 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 0.58 | 2.5 | 181 | 60 | 0 | 3 | 0 | 0 | 0 | 0 | 22 | 0.03 | 0 | 150 | 5 | 78 | 180 | 0 | 0 | 582 | 0 | 4145.74 | 9618.22 | 85.96
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 21 | 362 | 0 | 0 | 0 | 19 | 0 | 35 | 0 | 0 | 0 | 39 | 0 | 17 | 0 | 300 | 287 | 350 | 0 | 0 | 16 | 0 | 81 | 0 | 12 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 7 | 654 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 610 | 8 | 43 | 0 | 26 | 0 | 320 | 285 | 10 | 184 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 44 | 0 | 29 | 0 | 295 | 320 | 299 | 0 | 41 | 0 | 2 | 133 | 16 | 0 | 86 | 30 | 0 | 18 | 164 | 0 | 59 | 135 | 20 | 1 | 22.18 | 12 | 5838.68 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.83 | 384 | 0 | 826.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 23.77 | 164 | 0 | 215 | 0 | 220 | 0 | 310 | 0 | 2.07 | 2.5 | 178 | 62 | 0 | 11 | 0 | 0 | 0 | 2.8 | 63 | 0.27 | 0 | 150 | 4 | 78 | 180 | 0 | 0 | 597 | 0 | 4409.27 | 10247.95 | 85.96
09:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 362 | 0 | 0 | 0 | 36 | 0 | 51 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 300 | 300 | 450 | 0 | 0 | 16 | 0 | 199 | 0 | 21 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 48 | 0 | 2 | 46 | 0 | 6 | 760 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 700 | 13 | 43 | 0 | 26 | 0 | 360 | 285 | 10 | 195 | 36 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 47 | 0 | 310 | 320 | 323 | 0 | 41 | 0 | 2 | 140 | 16 | 0 | 86 | 30 | 0 | 18 | 165 | 0 | 69 | 136 | 17 | 2 | 36.8 | 12 | 6479.1 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.19 | 384 | 0 | 828.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 40.71 | 174 | 0 | 218 | 0 | 220 | 0 | 327 | 0 | 3.58 | 2.5 | 124 | 62 | 0 | 21 | 0 | 0 | 0 | 4.8 | 109 | 0.39 | 0 | 250 | 4 | 116 | 220 | 0 | 0 | 601 | 0 | 4699.44 | 11178.54 | 85.95
10:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 368 | 0 | 0 | 0 | 36 | 0 | 61 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 300 | 274 | 450 | 0 | 0 | 16 | 0 | 189 | 0 | 28 | 35 | 24.3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 48 | 0 | 3 | 46 | 0 | 6 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 700 | 16 | 43 | 0 | 26 | 0 | 360 | 285 | 19 | 182 | 27 | 0 | 50 | 0 | 0 | 20 | 0 | 58 | 0 | 60 | 0 | 305 | 320 | 349 | 0 | 40 | 0 | 2 | 152 | 16 | 0 | 86 | 30 | 0 | 18 | 165 | 0 | 68 | 126 | 17 | 2 | 46.59 | 12 | 6564.89 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 384 | 0 | 928.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 55.2 | 174 | 0 | 216 | 0 | 200 | 0 | 359 | 0 | 4.92 | 5.5 | 175 | 61 | 0 | 29 | 0 | 0 | 0 | 6.1 | 150 | 0.53 | 0 | 227 | 5 | 108 | 220 | 0 | 0 | 620 | 0 | 5010.53 | 11575.42 | 85.95
11:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 370 | 0 | 0 | 0 | 36 | 0 | 70 | 16 | 0 | 0 | 35 | 0 | 17 | 0 | 350 | 292 | 400 | 0 | 0 | 20 | 0 | 195 | 0 | 32 | 35 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 48 | 0 | 4 | 46 | 0 | 5 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 730 | 18 | 43 | 0 | 26 | 0 | 355 | 285 | 45 | 208 | 27 | 0 | 50 | 0 | 0 | 20 | 0 | 54 | 0 | 68 | 0 | 305 | 320 | 352 | 0 | 40 | 0 | 2 | 156 | 16 | 0 | 86 | 30 | 0 | 18 | 165 | 0 | 68 | 134 | 15 | 2 | 50.29 | 12 | 6726.29 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 418 | 0 | 921.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 61.98 | 174 | 0 | 213 | 0 | 150 | 0 | 364 | 0 | 5.59 | 5.5 | 115 | 63 | 0 | 34 | 0 | 0 | 0 | 7.1 | 178 | 0.61 | 0 | 200 | 4 | 120 | 220 | 0 | 0 | 705 | 0 | 5074.8 | 11801.09 | 85.94
12:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 372 | 0 | 0 | 0 | 36 | 0 | 70 | 16 | 0 | 0 | 35 | 0 | 17 | 0 | 350 | 296 | 450 | 0 | 0 | 20 | 0 | 195 | 0 | 34 | 52 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 48 | 0 | 4 | 46 | 0 | 5 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 804 | 19 | 43 | 0 | 26 | 0 | 341 | 285 | 49 | 211 | 30 | 0 | 50 | 0 | 0 | 20 | 0 | 58 | 0 | 69 | 0 | 315 | 320 | 395 | 0 | 40 | 0 | 2 | 156 | 16 | 0 | 86 | 30 | 0 | 18 | 165 | 0 | 69 | 135 | 15 | 2 | 50.74 | 12 | 6924.74 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 461 | 0 | 959.73 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 112 | 0 | 65.27 | 173 | 0 | 211 | 0 | 210 | 0 | 414 | 0 | 5.91 | 5.5 | 170 | 62 | 0 | 35 | 0 | 0 | 0 | 7.5 | 190 | 0.65 | 0 | 200 | 5 | 116 | 220 | 0 | 0 | 784 | 0 | 5424.56 | 12349.3 | 85.94
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 371 | 0 | 0 | 0 | 36 | 0 | 70 | 32 | 0 | 0 | 39 | 60 | 22 | 35 | 350 | 260 | 500 | 0 | 5 | 20 | 0 | 195 | 0 | 32 | 52 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 48 | 0 | 4 | 46.94 | 0 | 14 | 770 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 806 | 18 | 43 | 17 | 26 | 0 | 355 | 285 | 48 | 184 | 30 | 21 | 50 | 35 | 0 | 20 | 34 | 62 | 0 | 69 | 0 | 310 | 377 | 338 | 0 | 40 | 0 | 2 | 154 | 16 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 68 | 135 | 15 | 2 | 50.84 | 12 | 7160.78 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 525 | 0 | 1064.5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 108 | 0 | 59.24 | 173 | 0 | 209 | 0 | 211 | 0 | 387 | 0 | 5.49 | 5.5 | 170 | 60 | 0 | 34 | 0 | 0 | 0 | 7.1 | 184 | 0.62 | 0 | 200 | 6 | 108 | 220 | 0 | 0 | 825 | 0 | 5574.45 | 12735.23 | 85.94
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 362 | 0 | 0 | 0 | 17 | 0 | 70 | 32 | 0 | 0 | 55 | 90 | 22 | 65 | 400 | 297 | 400 | 0 | 35 | 17 | 0 | 195 | 0 | 28 | 90 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 48 | 0 | 3 | 46 | 0 | 7 | 772 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 807 | 17 | 43 | 50 | 26 | 0 | 355 | 285 | 46 | 189 | 32 | 54 | 50 | 46 | 0 | 20 | 34 | 64 | 0 | 59 | 39 | 300 | 320 | 338 | 0 | 39 | 0 | 5 | 144 | 16 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 69 | 135 | 11 | 2 | 46.32 | 12 | 7265.32 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 560 | 0 | 1122 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 99 | 0 | 46.27 | 171 | 0 | 209 | 0 | 212 | 0 | 393 | 0 | 4.88 | 5.5 | 167 | 60 | 0 | 30 | 0 | 0 | 0 | 6.4 | 166 | 0.55 | 0 | 250 | 7 | 112 | 220 | 0 | 0 | 912 | 0 | 5752.6 | 13017.92 | 85.93
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 360 | 0 | 0 | 0 | 18 | 0 | 82 | 48 | 0 | 0 | 55 | 72 | 22 | 83 | 370 | 291 | 500 | 0 | 35 | 20 | 0 | 195 | 0 | 23 | 90 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 48 | 0 | 2 | 46 | 0 | 4 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 809 | 13 | 43 | 50 | 45 | 0 | 354 | 285 | 43 | 183 | 32 | 68 | 50 | 95 | 0 | 19 | 34 | 62 | 0 | 45 | 38 | 305 | 320 | 351 | 0 | 40 | 0 | 5 | 152 | 16 | 0 | 85 | 30 | 0 | 16 | 164 | 0 | 69 | 134 | 11 | 2 | 37.17 | 12 | 7417.17 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 525 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 75 | 0 | 44.39 | 170 | 0 | 209 | 0 | 212 | 0 | 316 | 0 | 4.12 | 5.5 | 170 | 62 | 0 | 24 | 0 | 0 | 0 | 5.2 | 128 | 0.42 | 0 | 250 | 6 | 116 | 220 | 0 | 0 | 952 | 0 | 5598.13 | 13015.3 | 85.92
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 365 | 0 | 0 | 0 | 18 | 0 | 88 | 48 | 0 | 0 | 41 | 35 | 22 | 52 | 370 | 300 | 500 | 0 | 17 | 20 | 0 | 195 | 0 | 16 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 48 | 0 | 2 | 46 | 0 | 9 | 770 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 800 | 9 | 43 | 40 | 102 | 0 | 347 | 285 | 44 | 201 | 32 | 79 | 50 | 68 | 0 | 19 | 41 | 62 | 0 | 28 | 39 | 310 | 320 | 384 | 0 | 40 | 0 | 5 | 153 | 21 | 0 | 85 | 30 | 0 | 18 | 164 | 0 | 69 | 134 | 11 | 1 | 22.45 | 12 | 7398.45 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 464 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 48 | 0 | 26.8 | 170 | 0 | 208 | 0 | 211 | 0 | 344 | 0 | 2.37 | 5.5 | 170 | 61 | 0 | 15 | 0 | 0 | 0 | 3.4 | 82 | 0.26 | 0 | 250 | 6 | 120 | 220 | 0 | 0 | 952 | 0 | 5441.23 | 12839.68 | 85.92
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 365 | 0 | 0 | 11 | 18 | 0 | 88 | 81 | 0 | 0 | 17 | 35 | 22 | 45 | 370 | 294 | 540 | 0 | 17 | 20 | 0 | 193 | 0 | 6 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 22 | 770 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 804 | 3 | 51 | 20 | 120 | 0 | 348 | 285 | 46 | 202 | 35 | 90 | 50 | 68 | 0 | 19 | 52 | 60 | 0 | 10 | 39 | 310 | 320 | 385 | 0 | 40 | 0 | 5 | 153 | 22 | 0 | 85 | 30 | 0 | 15 | 164 | 0 | 97 | 142 | 11 | 0 | 8.14 | 12 | 7465.14 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 461 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 20 | 0 | 9.16 | 170 | 0 | 209 | 0 | 211 | 0 | 414 | 0 | 0.82 | 5.5 | 167 | 61 | 35 | 7 | 34 | 0 | 0 | 1.5 | 31 | 0.98 | 0 | 250 | 6 | 116 | 220 | 0 | 0 | 953 | 0 | 5445.76 | 12910.9 | 85.91
18:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 20 | 401 | 0 | 0 | 17 | 19 | 0 | 88 | 112 | 15 | 0 | 17 | 35 | 22 | 45 | 370 | 276 | 540 | 0 | 17 | 20 | 0 | 200 | 0 | 0 | 90 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 26 | 770 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 905 | 0 | 51 | 20 | 120 | 0 | 360 | 285 | 47 | 183 | 35 | 90 | 45 | 68 | 28 | 19 | 52 | 70 | 0 | 0 | 39 | 310 | 320 | 356 | 0 | 40 | 10 | 5 | 153 | 22 | 0 | 85 | 30 | 0 | 15 | 163 | 0 | 107 | 161 | 11 | 0 | 0.38 | 12 | 7685.38 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 459 | 17 | 1165 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0.7 | 170 | 0 | 210 | 0 | 213 | 0 | 386 | 0 | 0.06 | 5.5 | 170 | 61 | 50 | 1 | 70 | 0 | 0 | 0.2 | 3 | 0.01 | 0 | 243 | 7 | 108 | 220 | 0 | 0 | 923 | 0 | 5411.88 | 13097.26 | 85.91
19:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 20 | 401 | 0 | 0 | 17 | 36 | 0 | 88 | 96 | 0 | 0 | 20 | 35 | 22 | 34 | 320 | 269 | 500 | 0 | 0 | 22 | 0 | 205 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 33 | 0 | 0 | 50 | 0 | 0 | 46 | 0 | 21 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 952 | 0 | 51 | 20 | 148 | 0 | 341 | 285 | 47 | 182 | 32 | 90 | 40 | 68 | 26 | 20 | 52 | 64 | 0 | 0 | 39 | 300 | 320 | 348 | 0 | 41 | 10 | 5 | 153 | 22 | 0 | 85 | 30 | 0 | 15 | 162 | 0 | 107 | 163 | 18 | 0 | 0 | 12 | 7577 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 17 | 1316 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 207 | 0 | 214 | 0 | 319 | 0 | 0 | 5.5 | 167 | 62 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 8 | 108 | 220 | 0 | 0 | 943 | 0 | 5551.3 | 13128.3 | 85.9
19:30 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 22 | 362 | 0 | 0 | 17 | 36 | 0 | 75 | 80 | 0 | 0 | 35 | 17 | 22 | 34 | 380 | 280 | 550 | 0 | 0 | 29 | 0 | 202 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 25 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1000 | 0 | 51 | 20 | 148 | 0 | 359 | 285 | 47 | 182 | 35 | 69 | 40 | 68 | 28 | 20 | 52 | 68 | 0 | 0 | 39 | 295 | 320 | 348 | 0 | 41 | 20 | 5 | 153 | 22 | 0 | 85 | 30 | 0 | 15 | 162 | 0 | 108 | 163 | 20 | 0 | 0 | 12 | 7718 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453 | 17 | 1306 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 212 | 0 | 215 | 0 | 319 | 0 | 0 | 5.5 | 168 | 62 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 220 | 0 | 0 | 1050 | 0 | 5623.3 | 13341.3 | 85.9
20:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 22 | 370 | 0 | 0 | 17 | 36 | 0 | 72 | 48 | 0 | 0 | 17 | 17 | 22 | 34 | 380 | 292 | 550 | 0 | 0 | 28 | 0 | 202 | 0 | 0 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 28 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 950 | 0 | 51 | 20 | 148 | 0 | 359 | 285 | 48 | 190 | 35 | 68 | 40 | 51 | 27 | 20 | 34 | 60 | 0 | 0 | 40 | 290 | 320 | 350 | 0 | 41 | 20 | 5 | 151 | 22 | 0 | 86 | 30 | 0 | 15 | 163 | 0 | 85 | 145 | 20 | 0 | 0 | 12 | 7551 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463 | 17 | 1310 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 213 | 0 | 216 | 0 | 330 | 0 | 0 | 5.5 | 167 | 62 | 54 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 8 | 110 | 220 | 0 | 0 | 1049 | 0 | 5578.3 | 13129.3 | 85.9
21:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 22 | 348 | 0 | 0 | 17 | 36 | 0 | 70 | 48 | 0 | 0 | 0 | 17 | 22 | 34 | 450 | 273 | 583 | 0 | 0 | 28 | 0 | 206 | 0 | 0 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 34 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 28 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 950 | 0 | 51 | 10 | 120 | 0 | 359 | 285 | 37 | 182 | 36 | 68 | 45 | 51 | 28 | 20 | 34 | 64 | 0 | 0 | 40 | 295 | 320 | 350 | 0 | 41 | 20 | 5 | 151 | 22 | 0 | 86 | 30 | 0 | 15 | 162 | 0 | 75 | 155 | 20 | 0 | 0 | 12 | 7552 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 1312.65 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 213 | 0 | 217 | 0 | 389 | 0 | 0 | 5.5 | 166 | 62 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 220 | 0 | 0 | 1029 | 0 | 5627.95 | 13179.95 | 85.89
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 22 | 352 | 0 | 0 | 17 | 36 | 0 | 70 | 48 | 0 | 0 | 0 | 17 | 22 | 34 | 450 | 285 | 540 | 0 | 0 | 28 | 0 | 202 | 0 | 0 | 90 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 28 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 951 | 0 | 51 | 0 | 83 | 0 | 359 | 285 | 30 | 182 | 36 | 68 | 45 | 51 | 29 | 20 | 34 | 70 | 0 | 0 | 40 | 300 | 320 | 348 | 0 | 41 | 20 | 5 | 152 | 22 | 0 | 86 | 30 | 0 | 15 | 163 | 0 | 75 | 145 | 18 | 0 | 0 | 12 | 7434 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 1313.1 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 216 | 0 | 218 | 0 | 393 | 0 | 0 | 5.5 | 166 | 61 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 108 | 220 | 0 | 0 | 1037 | 0 | 5643.4 | 13077.4 | 85.89
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 22 | 346 | 0 | 0 | 0 | 36 | 0 | 60 | 48 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 294 | 583 | 0 | 0 | 26 | 0 | 201 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 31 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 904 | 0 | 51 | 0 | 83 | 0 | 359 | 285 | 30 | 190 | 36 | 68 | 30 | 51 | 28 | 20 | 34 | 70 | 0 | 0 | 0 | 290 | 320 | 353 | 0 | 41 | 20 | 5 | 152 | 22 | 0 | 86 | 30 | 0 | 15 | 163 | 0 | 75 | 145 | 18 | 0 | 0 | 12 | 7283 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1261.21 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 218 | 0 | 221 | 0 | 404 | 0 | 0 | 2.5 | 167 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 114 | 220 | 0 | 0 | 1000 | 0 | 5459.51 | 12742.51 | 85.89
Total KWH | 0 | 689280 | 286560 | 0 | 0 | 0 | 0 | 518545.46 | 8769600 | 0 | 0 | 112680 | 721800 | 0 | 1418688 | 868320 | 17815 | 0 | 511456 | 442080 | 470520 | 468480 | 8893000 | 6849484 | 11455000 | 0 | 141958 | 488100 | 1162546 | 3703000 | 0 | 239293 | 1214400 | 541200 | 208440 | 0 | 0 | 0 | 0 | 0 | 0 | 389760 | 256294 | 0 | 0 | 1317120 | 50880 | 27480 | 1105140 | 0 | 470880 | 18007272.73 | 0 | 0 | 0 | 0 | 0 | 3460556 | 0 | 0 | 0 | 19298180 | 136890 | 975252 | 324509 | 1388364 | 0 | 8714300 | 6924000 | 705600 | 4605000 | 823032 | 973440 | 1119560 | 847200 | 146160 | 459450 | 534660 | 1427520 | 0 | 501609 | 348960 | 7230000 | 7708200 | 8538000 | 0 | 980000 | 93120 | 92832 | 3515236 | 438480 | 0 | 1907520 | 714528 | 0 | 408000 | 3398720 | 0 | 1702800 | 3072000 | 363840 | 15800 | 380970 | 300480 | 166391840.19 | 21997570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640800 | 10494550 | 52800 | 24557227 | 0 | 0 | 0 | 0 | 0 | 92400 | 0 | 0 | 0 | 790710 | 0 | 449248 | 4031273 | 0 | 4925973 | 0 | 4836982 | 0 | 8383709 | 0 | 39960 | 95220 | 4115000 | 1435200 | 216985 | 246334 | 318691 | 0 | 0 | 52621.56 | 1310400 | 4389 | 0 | 5455000 | 163936 | 2566000 | 5228020 | 0 | 0 | 21012363.64 | 0 | 123513362.2 | 289905202.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12349.3 | MW | 12:00 Hr. | Energy Generated |  |  | 289.9052 |  | MKWHr.
| Day Peak Demand |  |  | 12349.3 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13341.3 | MW | 19:30 Hr. | Energy Demand |  |  | 289.9052 |  | MKWHr.
| Evening Peak Demand |  |  | 13341.3 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 9455.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1014.16 |  | MMCFD
| Maximum Generation of the Day |  |  | 13341.3 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.6872 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.0594 | 0 | 6.8935 | 0 | 0 | 0.23929 | 0 | 0 | 50.1922 | Gas | 138.325 | Gas | 450408656.021
| Chattogram Zone |  |  | 3.9314 | 37.3055 | 1.6243 | 0 | 1.1051 | 0.16437 | 0 | 0.38976 | 44.5205 | Coal | 79.8176 | Coal | 567229789.5966
| Cumilla Zone |  |  | 25.7146 | 0 | 3.1749 | 0 | 0 | 0.50161 | 1.4275 | 0 | 30.8186 | HFO | 17.4489 | HFO | 302533448.48
| Mymensingh Zone |  |  | 0.36384 | 0 | 5.0753 | 0 | 0 | 0.39677 | 0 | 0 | 5.8359 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0246 | Hydro | 1.1051 | Hydro | 110514
| Khulna Zone |  |  | 0 | 10.4946 | 0.0528 | 0 | 0 | 0.6408 | 21.9976 | 0 | 33.1857 | Solar | 4.8365 | Solar | 78613748.2516
| Barishal Zone |  |  | 7.958 | 26.4674 | 0 | 0 | 0 | 0.004389 | 0 | 0 | 34.4297 | Import | 47.9823 | Import | 244140856.1
| Rajshahi Zone |  |  | 22.2732 | 0 | 0.0924 | 0 | 0 | 1.2799 | 24.5572 | 0 | 48.2027 | Wind | 0.38976 | Wind | 5706086.4
| Rangpur Zone |  |  | 0 | 5.5502 | 0.53568 | 0 | 0 | 1.6094 | 0 | 0 | 7.6952
| Total |  |  | 138.325 | 79.8176 | 17.4489 | 0 | 1.1051 | 4.8365 | 47.9823 | 0.38976 | 289.9052
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 450408656.021 |  | Hydro | 110514
|  |  |  | Coal | 567229789.5966 |  | Solar | 78613748.2516
|  |  |  | HFO | 302533448.48 |  | Import | 244140856.1
|  |  |  | HSD | 0 |  | Wind | 5706086.4
[5 empty] | Total: | 164,87,43,098 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9976 | Peak Hr Flow | 871.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 30815718.62 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.5572 | Peak Hr Flow | 1306.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 754 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4275 | Peak Hr Flow | 68.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 934 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.9823 | Peak Hr Flow | 2245.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4697
|  |  |  | Chattogram |  | 0 |  | 1372
|  |  |  | Cumilla |  | 0 |  | 1200
|  |  |  | Mymensingh |  | 0 |  | 1119
|  |  |  | Sylhet |  | 0 |  | 459
|  |  |  | Khulna |  | 0 |  | 1476
|  |  |  | Barishal |  | 0 |  | 361
|  |  |  | Rajshahi |  | 0 |  | 1287
|  |  |  | Rangpur |  | 0 |  | 839
|  |  |  | Total |  | 0 |  | 12810
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 | 17:51 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Project Work S/D Due to ISD-NATORE-1
reconductoring
| 08:17 | 13:17 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Blast Wall Work
| 08:17 | 13:17 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Blast Wall Work
| 08:18 | 13:20 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast Wall Work
| 08:18 | 13:20 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast Wall Work
| 08:20 | 11:20 | Chowmuhani 132/33kV S/S TR1 Scheduled S/D Due to 33kv Incoming VCB High Temperature | [7 empty] | 15.0MW load
|  |  | Maintenance | [7 empty] | interrup.
|  | 08:22 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 is restored.
| 08:48 | 12:38 | Natore 132/33kV S/S Rajlanka Project Work S/D Due to Re conducting of Ishurdi ckt-1
| 09:58 | 11:17 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to Red hot maintenance
|  | 10:39 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
| 10:46 | 12:56 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D Due to Maintenance work. | [7 empty] | 10.0MW load
interrup.
| 11:11 | 15:32 | Barishal 230/132kV S/S 132 kV BUS Scheduled S/D Due to Ds Redhot Repair
| 12:32 | 12:50 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lockout relay -1 & 2, relays Due to 33 kv
pbs agla feeder cable fault.
| 12:35 | 13:57 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to PT MCB Change
| 13:50 | 15:05 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D Due to Maintenance work.
| 22:36 |  | Muktagacha 132/33kV S/S T-2(414T) LT Forced S/D Due to For neutral grounding theft
| 22:36 |  | Muktagacha 132/33kV S/S T-2(414T) HT Forced S/D
| 01:32 | 02:24 | Chattak-Sylhet 132 kV Ckt-1 Tripped from Sylhet 132/33kV end showing Distance Phase-C, | [7 empty] | 21.0MW load
|  |  | Zone 2 relays. | [7 empty] | interrup. Sylhet
132/33kV end
| 06:00 |  | Minimum Generation is 9802 MW
| 07:07 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Red Hot Maintenance
| 07:07 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Red Hot Maintenance
| 07:35 |  | Bheramara P/S-Ishurdi 132 kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to Project
Work and from Bheramara 230/132kV end Due to Project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 22 | 518545.46 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 362 | 8769600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8893000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 6849484 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 202 | 3703000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1162546 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 112680 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 868320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 511456 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 141958 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 541200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 208440 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 470520 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 29 | 488100 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 286560 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 17815 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 75 | 1418688 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 689280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 34 | 468480 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 442080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 239293 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 721800 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 550 | 11455000 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1214400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2356 | 50192245.46
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 136890 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1105140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 101 | 3460556 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 256294 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 1317120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 470880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 27480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 50880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 19298180 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 389760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 770 | 18007272.73 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 2052 | 44520452.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4605000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 359 | 8714300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6924000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 823032 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 705600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 148 | 1388364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 975252 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 324509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 348960 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1119560 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 847200 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 68 | 1427520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 459450 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 534660 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 146160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 973440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 501609 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1511 | 30818616
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 20 | 363840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 3072000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 1702800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 380970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 300480 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 303 | 5835890
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 980000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 93120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3515236 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 92832 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 714528 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1907520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 162 | 3398720 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 408000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 438480 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7230000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8538000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7708200 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2368.568 | 1496 | 35024636
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 871 | 21997570 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 52800 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 640800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 453 | 10494550 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1341 | 33185720
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 163936 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 108 | 2566000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 21012363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5228020 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5455000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4389 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1693 | 34429708.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 169 | 4031273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 212 | 4925973 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 215 | 4836982 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 319 | 8383709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 95220 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 8.8 | 92400 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1306 | 24557227 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 449248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 790710 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2235.3 | 48202702
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 62 | 1435200 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 168 | 4115000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 318691 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52621.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 54 | 216985 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 246334 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1310400 | -
Rangpur Area Total |  |  |  |  | 950 | 354 | 7695231.56
Eastern Grid Total |  |  |  |  | 16921.242 | 7718 | 166391840.19
Western Grid Total |  |  |  |  | 11614.5 | 5623.3 | 123513362.2
National Grid Total |  |  |  |  | 28535.742 | 13341.3 | 289905202.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-03-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8847.02 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3962.1 | MW
i) Dhaka area |  |  | 4696.82 |  | MW | i) Khulna area |  |  |  | 1476 | MW
ii) Chattogram area |  |  | 1372.2 |  | MW | ii) Barishal area |  |  |  | 360.9 | MW
iii) Cumilla area |  |  | 1200 |  | MW | iii) Rajshahi area |  |  |  | 1286.6 | MW
iv) Mymensingh area |  |  | 1119 |  | MW | iv) Rangpur area |  |  |  | 838.6 | MW
v) Sylhet area |  |  | 459 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12809.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 72 | 18:00 | 133 | Payra | 26 | 21:00
2 | AKSML | 125.4 | 16:00 | 68 | Jamalpur | 119 | 18:00 | 134 | Postogola | 51 | 00:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 128 | 19:00 | 135 | Purbachal | 16 | 19:00
4 | Agargaon | 93 | 14:00 | 70 | Jhenaidah | 117 | 19:00 | 136 | Purbasadipur | 120 | 13:00
5 | Agrabad | 88 | 15:00 | 71 | Joydebpur | 145 | 15:00 | 137 | Rahanpur | 27 | 19:30
6 | Amnura | 42 | 13:00 | 72 | Joypurhat | 59 | 20:00 | 138 | Rahim | 41 | 10:00
7 | Ashuganj | 83 | 21:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 56 | 19:00
8 | BSRM | 202 | 19:30 | 74 | KSRM | 21 | 19:00 | 140 | Rajendrapur | 113 | 18:00
9 | Bagerhat | 74 | 19:30 | 75 | Kabirpur | 238 | 14:00 | 141 | Rajshahi | 96 | 03:00
10 | Bajitpur | 42 | 18:30 | 76 | Kachua | 70 | 20:00 | 142 | Rajshahi-230 | 72 | 13:00
11 | Bakulia | 89 | 19:30 | 77 | Kallyanpur | 120 | 23:00 | 143 | Ramganj | 100 | 21:00
12 | Banani | 42 | 12:00 | 78 | Kalurghat | 40 | 11:00 | 144 | Rampur | 38 | 23:00
13 | Bangabhaban | 14 | 10:00 | 79 | Kamrangirchar | 66 | 19:30 | 145 | Rangamati | 16 | 18:30
14 | Barapukuria | 66 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 142 | 18:00
15 | Barguna | 16 | 18:30 | 81 | Kasba | 31 | 19:00 | 147 | Ruppur | 6.8 | 12:00
16 | Barishal | 93 | 19:00 | 82 | Kazla | 94 | 16:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 78 | 19:00 | 83 | Keranigonj | 70 | 19:30 | 149 | Saidpur | 114 | 11:00
18 | Baroaulia | 60 | 13:00 | 84 | Khagrachori | 28 | 18:00 | 150 | Satkhira | 120 | 19:00
19 | Baroirhat | 54 | 18:30 | 85 | Khulna | 81 | 19:00 | 151 | Satmasjid | 86 | 19:30
20 | Bashundhara | 153 | 14:00 | 86 | Khulshi | 153 | 14:00 | 152 | Savar | 223 | 16:00
21 | BashundharaCement | 9 | 07:00 | 87 | Kishoreganj | 125 | 18:00 | 153 | SevenRings | 18.98 | 20:00
22 | Beanibazar | 54 | 18:30 | 88 | Kodda | 295 | 12:00 | 154 | ShahCement | 33 | 23:00
23 | Benapole | 60 | 19:00 | 89 | Kulaura | 36 | 18:30 | 155 | Shahjadpur | 75 | 19:30
24 | Bhaluka | 148 | 16:00 | 90 | Kurigram | 66 | 18:00 | 156 | Shahjibazar | 110 | 21:00
25 | Bhandaria | 42 | 21:00 | 91 | Kushtia | 108 | 19:00 | 157 | Shahmirpur | 59 | 23:00
26 | Bhangura | 34 | 13:00 | 92 | Lalbag | 61 | 13:00 | 158 | Shariatpur | 67 | 18:00
27 | Bheramara(GK) | 46 | 19:00 | 93 | Lalmonirhat | 58 | 18:00 | 159 | Sherpur | 158 | 18:00
28 | Bhulta | 244 | 23:00 | 94 | MI_Cement | 18 | 15:00 | 160 | Shikalbaha | 29 | 00:00
29 | Bog-Sherpur | 62 | 13:00 | 95 | Madanganj | 44 | 21:00 | 161 | Shitalakhya | 75 | 15:00
30 | Bogura | 142 | 21:00 | 96 | Madaripur | 80 | 23:00 | 162 | Sholosohor | 41 | 14:00
31 | Borhanuddin | 66 | 22:00 | 97 | Madartek | 73.73 | 23:00 | 163 | Shyampur | 146 | 00:00
32 | Brahmanbaria | 111 | 18:30 | 98 | Madunaghat | 46 | 19:00 | 164 | Siddhirganj | 117 | 11:00
33 | Cantonment | 94 | 19:30 | 99 | Magura | 55 | 18:30 | 165 | Sirajganj | 104 | 18:00
34 | Chandpur | 56 | 21:00 | 100 | Mahasthangarh | 64 | 21:00 | 166 | Sonargaon | 93 | 11:00
35 | Chandraghona | 33 | 19:00 | 101 | Manikganj | 108 | 21:00 | 167 | Sreemongol | 57 | 18:00
36 | Chapai | 58 | 09:00 | 102 | Maniknagar | 61 | 13:00 | 168 | Sreepur | 76 | 16:00
37 | Charsaidpur | 47 | 03:00 | 103 | Matarbari | 48 | 03:00 | 169 | Srinagar | 36.32 | 20:00
38 | Chauddagram | 68 | 18:00 | 104 | Matuail | 68 | 15:00 | 170 | Sunamganj | 45 | 18:00
39 | Chhatak | 26 | 14:00 | 105 | Millgate | 74 | 15:00 | 171 | Sylhet | 32 | 19:00
40 | Chowmuhani | 191 | 18:30 | 106 | Mirpur | 119 | 20:00 | 172 | Sylhet-132 | 95 | 15:00
41 | Chuadanga | 88 | 19:00 | 107 | Mirsorai | 9 | 13:00 | 173 | TK | 20 | 19:30
42 | Coxsbazar | 130 | 21:00 | 108 | Mirzapur | 43 | 18:00 | 174 | Tangail | 174 | 13:00
43 | Cumilla(N) | 140 | 19:00 | 109 | Mithapukur | 58 | 18:00 | 175 | Thakurgaon | 86 | 18:00
44 | Cumilla(S) | 154 | 14:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 114 | 12:00
45 | Daudkandi | 136 | 18:00 | 111 | Mogbazar | 123.6 | 14:00 | 177 | Ullahpara | 31 | 03:00
46 | Dhaka | 46 | 12:00 | 112 | Mongla | 31 | 19:30 | 178 | Ullon | 40 | 20:00
47 | Dhamrai | 128 | 10:00 | 113 | Motijheel | 33 | 13:00 | 179 | Uttara | 70 | 13:00
48 | Dhanmondi | 126 | 13:00 | 114 | Muktagacha | 34 | 18:00 | 180 | UttaraNew | 40 | 20:00
49 | Dohazari | 103 | 18:30 | 115 | Munshiganj | 95 | 19:30 | 181 | Zigatola | 59 | 21:00
50 | Faridpur | 132 | 19:00 | 116 | Muradnagar | 24 | 19:00
51 | Fatullah | 91 | 15:00 | 117 | Mymensingh | 200 | 18:00
52 | Fenchuganj | 29 | 19:00 | 118 | Naogaon | 114 | 13:00
53 | Feni | 101 | 18:30 | 119 | Narail | 50 | 18:30
54 | GPH | 78 | 17:00 | 120 | Narinda | 74 | 13:00
55 | Ghatail | 80 | 18:00 | 121 | Narshingdi | 162 | 20:00
56 | Ghorashal | 15 | 08:00 | 122 | Natore | 124 | 21:00
57 | Ghorashal-230 | 82 | 22:00 | 123 | Nawabganj | 44.8 | 21:00
58 | Goalpara | 26 | 19:00 | 124 | Netrakona | 143 | 18:00
59 | Gollamari | 64 | 19:00 | 125 | New | 79.8 | 13:00
60 | Gopalganj | 96.2 | 21:00 | 126 | Niamatpur | 93 | 18:00
61 | Gulshan | 100 | 14:00 | 127 | Noapara | 45 | 19:00
62 | Halishahar | 71 | 14:00 | 128 | PHP | 9 | 08:00
63 | HaripurSBU | 154 | 08:00 | 129 | Pabna | 90 | 18:00
64 | Hasnabad | 72 | 19:30 | 130 | Palashbari | 110 | 18:00
65 | Hathazari | 73 | 14:00 | 131 | Panchagarh | 48 | 19:00
66 | Ishurdi | 60 | 19:00 | 132 | Patuakhali | 60 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12048.45 | 0 |  | 12048.45
1:00 | 11457.45 | 0 |  | 11457.45
2:00 | 10991.25 | 0 |  | 10991.25
3:00 | 11364.19 | 0 |  | 11364.19
4:00 | 11356.06 | 0 |  | 11356.06
5:00 | 10335.2 | 0 |  | 10335.2
6:00 | 9455.5 | 0 |  | 9455.5
7:00 | 9618.22 | 0 |  | 9618.22
8:00 | 10247.95 | 0 |  | 10247.95
9:00 | 11178.54 | 0 |  | 11178.54
10:00 | 11575.42 | 0 |  | 11575.42
11:00 | 11801.09 | 0 |  | 11801.09
12:00 | 12349.3 | 0 |  | 12349.3
13:00 | 12735.23 | 0 |  | 12735.23
14:00 | 13017.92 | 0 |  | 13017.92
15:00 | 13015.3 | 0 |  | 13015.3
16:00 | 12839.68 | 0 |  | 12839.68
17:00 | 12910.9 | 0 |  | 12910.9
18:00 | 13097.26 | 0 |  | 13097.26
19:00 | 13128.3 | 0 |  | 13128.3
19:30 | 13341.3 | 0 |  | 13341.3
20:00 | 13129.3 | 0 |  | 13129.3
21:00 | 13179.95 | 0 |  | 13179.95
22:00 | 13077.4 | 0 |  | 13077.4
23:00 | 12742.51 | 0 |  | 12742.51
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7165.5 | 4882.95 | 12048.45 | DAILY GENERATION CURVE
00:30 | 6967.5 | 4785.45 | 11752.95
01:00 | 6769.5 | 4687.95 | 11457.45 | 24-03-2025
01:30 | 6624.5 | 4599.85 | 11224.35
02:00 | 6479.5 | 4511.75 | 10991.25
02:30 | 6614.75 | 4562.97 | 11177.72
03:00 | 6750 | 4614.19 | 11364.19
03:30 | 6712 | 4648.125 | 11360.125
04:00 | 6674 | 4682.06 | 11356.06
04:30 | 6395 | 4450.63 | 10845.63
05:00 | 6116 | 4219.2 | 10335.2
05:30 | 5771.53 | 4123.82 | 9895.35
06:00 | 5427.06 | 4028.44 | 9455.5
06:30 | 5449.77 | 4087.09 | 9536.86
07:00 | 5472.48 | 4145.74 | 9618.22
07:30 | 5655.58 | 4277.505 | 9933.085
08:00 | 5838.68 | 4409.27 | 10247.95
08:30 | 6158.89 | 4554.355 | 10713.245
09:00 | 6479.1 | 4699.44 | 11178.54
09:30 | 6521.995 | 4854.985 | 11376.98
10:00 | 6564.89 | 5010.53 | 11575.42
10:30 | 6645.59 | 5042.665 | 11688.255
11:00 | 6726.29 | 5074.8 | 11801.09
11:30 | 6825.515 | 5249.68 | 12075.195
12:00 | 6924.74 | 5424.56 | 12349.3
12:30 | 7042.76 | 5499.505 | 12542.265
13:00 | 7160.78 | 5574.45 | 12735.23
13:30 | 7213.05 | 5663.525 | 12876.575
14:00 | 7265.32 | 5752.6 | 13017.92
14:30 | 7341.245 | 5675.365 | 13016.61
15:00 | 7417.17 | 5598.13 | 13015.3
15:30 | 7407.81 | 5519.68 | 12927.49
16:00 | 7398.45 | 5441.23 | 12839.68
16:30 | 7431.795 | 5443.495 | 12875.29
17:00 | 7465.14 | 5445.76 | 12910.9
17:30 | 7575.26 | 5428.82 | 13004.08
18:00 | 7685.38 | 5411.88 | 13097.26
18:30 | 7631.19 | 5481.59 | 13112.78
19:00 | 7577 | 5551.3 | 13128.3
19:30 | 7718 | 5623.3 | 13341.3
20:00 | 7551 | 5578.3 | 13129.3
20:30 | 7551.5 | 5603.125 | 13154.625 |  | Executive Engineer
21:00 | 7552 | 5627.95 | 13179.95 |  | Network Operation Division
21:30 | 7493 | 5635.675 | 13128.675
22:00 | 7434 | 5643.4 | 13077.4
22:30 | 7358.5 | 5551.455 | 12909.955
23:00 | 7283 | 5459.51 | 12742.51

## En-Curve
QF-LDC-12
Date | 24-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3632 | 2291 | 913 | 0 | 70 | 916.45 | 46 | 3548 | 0 | 126 | 497 | 0 | 0 | 9 | 0 | DAILY ENERGY CURVE
00:30 | 3567.5 | 2185 | 913.5 | 0 | 68 | 917.45 | 46 | 3479 | 0 | 126 | 438 | 0 | 0 | 12.5 | 0 | 24-03-2025
01:00 | 3503 | 2079 | 914 | 0 | 66 | 918.45 | 46 | 3410 | 0 | 126 | 379 | 0 | 0 | 16 | 0
01:30 | 3452 | 2044 | 916.5 | 0 | 64 | 872.85 | 46 | 3339.5 | 0 | 100.5 | 371 | 0 | 0 | 18 | 0 | Energy Generated | 289.9052 |  | MKWHr
02:00 | 3401 | 2009 | 919 | 0 | 62 | 827.25 | 46 | 3269 | 0 | 75 | 363 | 0 | 0 | 20 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3488 | 2070.25 | 919 | 0 | 61 | 822.97 | 46 | 3276.5 | 0 | 91.5 | 383.5 | 0 | 0 | 19 | 0 | Total Energy Requirement | 289.9052 |  | MKWHr
03:00 | 3575 | 2131.5 | 919 | 0 | 60 | 818.69 | 46 | 3284 | 0 | 108 | 404 | 0 | 0 | 18 | 0
03:30 | 3633.5 | 2164 | 919.5 | 0 | 61 | 817.625 | 46 | 3199 | 0 | 115 | 383 | 0 | 0 | 21.5 | 0
04:00 | 3692 | 2196.5 | 920 | 0 | 62 | 816.56 | 46 | 3114 | 0 | 122 | 362 | 0 | 0 | 25 | 0
04:30 | 3584.5 | 2094 | 919.5 | 0 | 60 | 820.63 | 46 | 2919.5 | 0 | 73.5 | 308 | 0 | 0 | 20 | 0
05:00 | 3477 | 1991.5 | 919 | 0 | 58 | 824.7 | 46 | 2725 | 0 | 25 | 254 | 0 | 0 | 15 | 0
05:30 | 3262.5 | 1846.5 | 918.5 | 0 | 50 | 823.82 | 46 | 2671 | 0.03 | 25 | 235.5 | 0 | 0 | 16.5 | 0
06:00 | 3048 | 1701.5 | 918 | 0 | 42 | 822.94 | 46 | 2617 | 0.06 | 25 | 217 | 0 | 0 | 18 | 0
06:30 | 3088.5 | 1684.75 | 918.5 | 0 | 44 | 825.785 | 46 | 2622 | 39.825 | 25 | 222 | 0 | 0 | 20.5 | 0
07:00 | 3129 | 1668 | 919 | 0 | 46 | 828.63 | 46 | 2627 | 79.59 | 25 | 227 | 0 | 0 | 23 | 0
07:30 | 3244 | 1754 | 892 | 0 | 45 | 827.33 | 46 | 2631 | 162.755 | 25 | 287 | 0 | 0 | 19 | 0
08:00 | 3359 | 1840 | 865 | 0 | 44 | 826.03 | 46 | 2635 | 245.92 | 25 | 347 | 0 | 0 | 15 | 0
08:30 | 3488.5 | 1925.4 | 865 | 0 | 48 | 827.15 | 46 | 2758 | 335.695 | 38.5 | 367 | 0 | 0 | 14 | 0
09:00 | 3618 | 2010.8 | 865 | 0 | 52 | 828.27 | 46 | 2881 | 425.47 | 52 | 387 | 0 | 0 | 13 | 0
09:30 | 3618.5 | 2011.3 | 890.5 | 0 | 55 | 878.275 | 46 | 2909 | 496.405 | 69.5 | 386.5 | 0 | 0 | 16 | 0
10:00 | 3619 | 2011.8 | 916 | 0 | 58 | 928.28 | 46 | 2937 | 567.34 | 87 | 386 | 0 | 0 | 19 | 0
10:30 | 3616 | 2038.65 | 918 | 0 | 56 | 924.65 | 46 | 2969 | 611.955 | 95 | 394.5 | 0 | 0 | 18.5 | 0
11:00 | 3613 | 2065.5 | 920 | 0 | 54 | 921.02 | 46 | 3001 | 656.57 | 103 | 403 | 0 | 0 | 18 | 0
11:30 | 3683 | 2100.5 | 919.5 | 0 | 56 | 940.375 | 46 | 3126 | 672.82 | 113.5 | 404 | 0 | 0 | 13.5 | 0
12:00 | 3753 | 2135.5 | 919 | 0 | 58 | 959.73 | 46 | 3251 | 689.07 | 124 | 405 | 0 | 0 | 9 | 0
12:30 | 3728.5 | 2145 | 918.5 | 0 | 60 | 1012.115 | 46.47 | 3303.5 | 676.18 | 132 | 510 | 0 | 0 | 10 | 0
13:00 | 3704 | 2154.5 | 918 | 0 | 62 | 1064.5 | 46.94 | 3356 | 663.29 | 140 | 615 | 0 | 0 | 11 | 0
13:30 | 3676.5 | 2135.5 | 919 | 0 | 63 | 1093.25 | 46.47 | 3442 | 623.355 | 165 | 697.5 | 0 | 0 | 15 | 0
14:00 | 3649 | 2116.5 | 920 | 0 | 64 | 1122 | 46 | 3528 | 583.42 | 190 | 780 | 0 | 0 | 19 | 0
14:30 | 3612.5 | 2160.5 | 919.5 | 0 | 63 | 1119 | 46 | 3533 | 523.86 | 199.25 | 817.5 | 0 | 0 | 22.5 | 0
15:00 | 3576 | 2204.5 | 919 | 0 | 62 | 1116 | 46 | 3538 | 464.3 | 208.5 | 855 | 0 | 0 | 26 | 0
15:30 | 3616.5 | 2249.5 | 919.5 | 0 | 62 | 1116 | 46 | 3502.5 | 378.79 | 209.7 | 798.5 | 0 | 0 | 28.5 | 0
16:00 | 3657 | 2294.5 | 920 | 0 | 62 | 1116 | 46 | 3467 | 293.28 | 210.9 | 742 | 0 | 0 | 31 | 0
16:30 | 3691.5 | 2332.5 | 919.5 | 0 | 61 | 1117.5 | 46 | 3466.5 | 203.44 | 227.35 | 785.5 | 0 | 0 | 24.5 | 0
17:00 | 3726 | 2370.5 | 919 | 0 | 60 | 1119 | 46 | 3466 | 113.6 | 243.8 | 829 | 0 | 0 | 18 | 0
17:30 | 3715 | 2359 | 919 | 0 | 65 | 1142 | 46 | 3498.5 | 60.28 | 281.3 | 902.5 | 0 | 0 | 15.5 | 0
18:00 | 3704 | 2347.5 | 919 | 0 | 70 | 1165 | 46 | 3531 | 6.96 | 318.8 | 976 | 0 | 0 | 13 | 0
18:30 | 3626 | 2312 | 895.5 | 0 | 67 | 1240.5 | 46 | 3610 | 3.48 | 336.3 | 965.5 | 0 | 0 | 10.5 | 0
19:00 | 3548 | 2276.5 | 872 | 0 | 64 | 1316 | 46 | 3689 | 0 | 353.8 | 955 | 0 | 0 | 8 | 0
19:30 | 3545 | 2405.5 | 871 | 0 | 68 | 1306 | 46 | 3810 | 0 | 338.8 | 945 | 0 | 0 | 6 | 0
20:00 | 3578 | 2414.5 | 872 | 0 | 60 | 1310 | 46 | 3717 | 0 | 291.8 | 825 | 0 | 0 | 15 | 0
20:30 | 3596.5 | 2439.5 | 896 | 0 | 62 | 1311.325 | 46 | 3730.5 | 0 | 290.8 | 768 | 0 | 0 | 14 | 0
21:00 | 3615 | 2464.5 | 920 | 0 | 64 | 1312.65 | 46 | 3744 | 0 | 289.8 | 711 | 0 | 0 | 13 | 0
21:30 | 3618 | 2428.5 | 919 | 0 | 67 | 1312.875 | 46 | 3749 | 0 | 289.8 | 690.5 | 0 | 0 | 8 | 0
22:00 | 3621 | 2392.5 | 918 | 0 | 70 | 1313.1 | 46 | 3754 | 0 | 289.8 | 670 | 0 | 0 | 3 | 0
22:30 | 3627 | 2414 | 918.5 | 0 | 70 | 1287.155 | 46 | 3671 | 0 | 260.8 | 613.5 | 0 | 0 | 2 | 0
23:00 | 3633 | 2435.5 | 919 | 0 | 70 | 1261.21 | 46 | 3588 | 0 | 231.8 | 557 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 407 | 05:00 | 384 | 12:00 | Payra | 422 | 05:00 | 412 | 21:00
Ashuganj | 415 | 5:00 | 383 | 12:00 | Rahanpur | 401 | 06:00 | 386 | 17:00
Bhulta | 409 | 05:00 | 380 | 12:00 | Rampal | 415 | 06:00 | 395 | 14:00
Bibiana | 400 | 05:00 | 386 | 12:00
BIPTC | 399 | 03:00 | 390 | 10:00
Bogura | 389 | 05:00 | 369 | 18:00
Gopalganj | 414 | 05:00 | 395 | 14:00
Kaliakoir | 376 | 04:00 | 354 | 12:00
Madunaghat | 402 | 05:00 | 391 | 13:00
Meghnaghat | 407 | 05:00 | 386 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 221 | 12:00 | Keranigonj | 235 | 05:00 | 219 | 12:00
AKSML | 239 | 05:00 | 224 | 12:00 | Khulna(S) | 241 | 06:00 | 226 | 14:00
Aminbazar | 238 | 05:00 | 224 | 14:00 | Madunaghat | 237 | 06:00 | 228 | 14:00
Ashuganj | 238 | 05:00 | 224 | 12:00 | Madunaghat-400 | 238 | 07:00 | 229 | 14:00
Ashuganj-400 | 238 | 05:00 | 224 | 12:00 | Maniknagar | 232 | 05:00 | 215 | 12:00
Baghabari | 238 | 20:00 | 227 | 11:00 | Meghnaghat | 238 | 03:00 | 225 | 12:00
Barapukuria | 225 | 02:00 | 216 | 13:00 | Meghnaghat-400 | 234 | 05:00 | 221 | 12:00
Barapukuria-230 | 225 | 02:00 | 216 | 13:00 | Mirsorai | 234 | 07:00 | 221 | 12:00
Barishal | 241 | 06:00 | 232 | 14:00 | Rajshahi | 236 | 00:00 | 221 | 11:00
Bheramara | 236 | 00:00 | 221 | 11:00 | Rampal | 239 | 06:00 | 225 | 14:00
Bhulta | 233 | 05:00 | 215 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 05:00 | 222 | 12:00 | Rampura | 232 | 05:00 | 213 | 12:00
BIPTC | 238 | 01:00 | 222 | 11:00 | Shikalbaha | 233 | 09:00 | 226 | 13:00
Bogura | 238 | 02:00 | 227 | 13:00 | Shyampur | 234 | 05:00 | 218 | 12:00
Bogura-400 | 238 | 05:00 | 226 | 18:00 | Siddhirganj | 234 | 05:00 | 219 | 12:00
Borhanuddin | 245 | 07:00 | 239 | 21:00 | Sirajgonj | 243 | 05:00 | 234 | 21:00
BSRM | 235 | 07:00 | 220 | 12:00 | Sreepur | 236 | 05:00 | 222 | 12:00
Cumilla(N) | 230 | 06:00 | 216 | 12:00 | Tongi | 232 | 04:00 | 213 | 15:00
Faridpur | 241 | 06:00 | 229 | 12:00
Fenchuganj | 232 | 00:00 | 226 | 14:00
Ghorashal | 230 | 01:00 | 220 | 00:00
Ghorashal-230 | 232 | 05:00 | 215 | 12:00
Gopalganj | 239 | 05:00 | 220 | 13:00
GPH | 237 | 07:00 | 224 | 12:00
Haripur | 233 | 05:00 | 217 | 12:00
Hasnabad | 235 | 05:00 | 219 | 12:00
Hathazari | 238 | 05:00 | 228 | 13:00
Ishurdi | 238 | 02:00 | 225 | 11:00
Jhenaidah | 235 | 06:00 | 220 | 14:00
Kaliakoir | 236 | 06:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 126 | 12:00 | Madunaghat | 135 | 05:00 | 130 | 12:00
Agargaon | 142 | 05:00 | 132 | 12:00 | Magura | 137 | 05:00 | 124 | 16:00
Agrabad | 135 | 05:00 | 127 | 14:00 | Mahasthangarh | 134 | 05:00 | 124 | 13:00
AKS | 132 | 05:00 | 126 | 12:00 | Manikganj | 131 | 04:00 | 122 | 12:00
Aminbazar | 139 | 05:00 | 129 | 12:00 | Maniknagar | 137 | 05:00 | 125 | 12:00
Amnura | 136 | 00:00 | 126 | 13:00 | Matarbari | 123 | 06:00 | 112 | 18:30
Ashuganj | 140 | 05:00 | 133 | 12:00 | Matuail | 135.6 | 05:00 | 126 | 12:00
Bagerhat | 137 | 04:00 | 124 | 17:00 | Millgate | 139 | 04:00 | 125 | 12:00
Bajitpur | 135 | 05:00 | 125 | 12:00 | Mirpur | 138 | 05:00 | 126 | 12:00
Bakulia | 136 | 07:00 | 129 | 12:00 | Mirzapur | 132 | 04:00 | 122 | 12:00
Banani | 138 | 05:00 | 125 | 12:00 | Mithapukur | 133 | 05:00 | 121 | 13:00
Bangabhaban | 137 | 05:00 | 125 | 12:00 | MI_Cement | 136 | 05:00 | 126 | 12:00
Barapukuria | 139 | 05:00 | 130 | 09:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 138 | 05:00 | 133 | 13:00 | Mogbazar | 139 | 05:00 | 125 | 12:00
Barishal | 136 | 03:00 | 128 | 14:00 | Mongla | 135 | 05:00 | 125 | 17:00
Barishal-230 | 137 | 06:00 | 129 | 14:00 | Motijheel | 137 | 05:00 | 125 | 12:00
Baroaulia | 135 | 06:00 | 128 | 12:00 | Muktagacha | 133 | 03:00 | 117 | 16:00
Baroirhat | 125 | 03:00 | 117 | 12:00 | Munshiganj | 135 | 05:00 | 125 | 12:00
Bashundhara | 139 | 04:00 | 125 | 12:00 | Muradnagar | 130 | 05:00 | 121 | 12:00
BashundharaCement | 134 | 11:00 | 122 | 12:00 | Mymensingh | 134 | 03:00 | 112 | 16:00
Beanibazar | 133 | 05:00 | 127 | 13:00 | Naogaon | 131 | 05:00 | 121 | 12:00
Benapole | 133 | 01:00 | 120 | 14:00 | Narail | 137 | 05:00 | 123 | 14:00
Bhaluka | 130 | 05:00 | 119 | 12:00 | Narinda | 137 | 05:00 | 125 | 12:00
Bhandaria | 133 | 06:00 | 123 | 15:00 | Narshingdi | 132 | 03:00 | 119 | 12:00
Bhangura | 135 | 00:00 | 127 | 12:00 | Natore | 135 | 05:00 | 126 | 11:00
Bheramara | 136 | 02:00 | 128 | 11:00 | Nawabganj | 138 | 05:00 | 127 | 12:00
Bheramara(GK) | 136 | 02:00 | 128 | 12:00 | Netrakona | 125 | 00:00 | 111 | 17:00
Bhulta | 130 | 05:00 | 120 | 04:00 | New | 141 | 05:00 | 126 | 12:00
Bog-Sherpur | 134 | 05:00 | 125 | 17:00 | Niamatpur | 137 | 04:00 | 129 | 18:00
Bogura | 135 | 05:00 | 127 | 17:00 | Noapara | 137 | 06:00 | 125 | 14:00
Bogura-230 | 135 | 02:00 | 127 | 13:00 | Pabna | 137 | 02:00 | 128 | 13:00
Brahmanbaria | 134 | 05:00 | 123 | 12:00 | Palashbari | 130 | 05:00 | 119 | 17:00
Cantonment | 142 | 05:00 | 132 | 12:00 | Panchagarh | 136 | 18:30 | 116 | 11:00
Chandpur | 155 | 11:00 | 113 | 12:00 | Patuakhali | 136 | 04:00 | 133 | 15:00
Chandraghona | 136 | 05:00 | 129 | 13:00 | Payra | 138 | 05:00 | 135 | 12:00
Chapai | 135 | 04:00 | 127 | 18:00 | PHP | 126 | 06:00 | 116 | 14:00
Charsaidpur | 136 | 05:00 | 126 | 12:00 | Postogola | 138 | 05:00 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 128 | 05:00 | 117 | 12:00 | Purbachal | 139 | 05:00 | 124 | 12:00
Chhatak | 134 | 06:00 | 126 | 12:00 | Purbasadipur | 132 | 02:00 | 116 | 08:00
Chowmuhani | 120 | 06:00 | 112 | 12:00 | Rahanpur | 137 | 01:00 | 131 | 17:00
Chuadanga | 136 | 05:00 | 122 | 17:00 | Rahanpur-400 | 138 | 05:00 | 131 | 13:00
Coxsbazar | 122 | 07:00 | 114 | 19:00 | Rahim | 135 | 06:00 | 126 | 12:00
Cumilla(N) | 132 | 06:00 | 122 | 12:00 | Rajbari | 135 | 05:00 | 127 | 12:00
Cumilla(S) | 130 | 03:00 | 120 | 12:00 | Rajendrapur | 133 | 06:00 | 122 | 12:00
Daudkandi | 129 | 05:00 | 119 | 12:00 | Rajshahi | 137 | 03:00 | 128 | 11:00
Dhaka | 139 | 05:00 | 125 | 12:00 | Rajshahi-230 | 137 | 06:00 | 121 | 13:00
Dhamrai | 134 | 05:00 | 122 | 12:00 | Ramganj | 120 | 06:00 | 107 | 12:00
Dhanmondi | 139 | 05:00 | 126 | 12:00 | Rampur | 135 | 06:00 | 127 | 14:00
Dohazari | 131 | 06:00 | 124 | 14:00 | Rampura | 138 | 05:00 | 125 | 12:00
Faridpur | 135 | 05:00 | 128 | 17:00 | Rangamati | 136 | 06:00 | 128 | 13:00
Fatullah | 137 | 05:00 | 127 | 12:00 | Rangpur | 132 | 06:00 | 120 | 13:00
Fenchuganj | 136 | 02:00 | 131 | 12:00 | Ruppur | 138 | 05:00 | 130 | 11:00
Feni | 124 | 06:00 | 116 | 12:00 | Saidpur | 135 | 05:00 | 120 | 13:00
Ghatail | 131 | 04:00 | 117 | 17:00 | Satkhira | 136 | 06:00 | 123 | 17:00
Ghorashal | 139 | 05:00 | 129 | 12:00 | Satmasjid | 142 | 05:00 | 132 | 12:00
Goalpara | 139 | 05:00 | 127 | 14:00 | Savar | 136 | 05:00 | 125 | 12:00
Gollamari | 139 | 05:00 | 127 | 12:00 | SevenRings | 139 | 05:00 | 129 | 12:00
Gopalganj | 139 | 05:00 | 131 | 14:00 | ShahCement | 136 | 05:00 | 126 | 12:00
Gopalganj-400 | 141 | 05:00 | 134 | 12:00 | Shahjadpur | 141 | 01:00 | 131 | 12:00
Gulshan | 138 | 05:00 | 125 | 12:00 | Shahjibazar | 135 | 05:00 | 126 | 14:00
Halishahar | 133 | 08:00 | 128 | 12:00 | Shahmirpur | 136 | 05:00 | 129 | 14:00
Haripur | 135 | 05:00 | 126 | 12:00 | Shariatpur | 140 | 07:00 | 131 | 14:00
HaripurSBU | 135 | 05:00 | 126 | 12:00 | Sherpur | 134 | 04:00 | 123 | 17:00
Hasnabad | 138 | 04:00 | 128 | 11:00 | Shikalbaha | 126 | 07:00 | 119 | 13:00
Hathazari | 137 | 05:00 | 130 | 13:00 | Shikalbaha-230 | 137 | 05:00 | 130 | 13:00
Ishurdi | 139 | 02:00 | 130 | 11:00 | Shitalakhya | 136 | 05:00 | 126 | 12:00
Jaldhaka | 132 | 05:00 | 118 | 13:00 | Sholosohor | 136 | 06:00 | 129 | 12:00
Jamalpur | 139 | 19:30 | 125 | 12:00 | Shyampur | 134 | 08:00 | 128 | 12:00
Jashore | 134 | 05:00 | 122 | 14:00 | Shyampur-230 | 136 | 05:00 | 127 | 12:00
Jhenaidah | 137 | 05:00 | 126 | 13:00 | Siddhirganj | 136 | 05:00 | 127 | 11:00
Jhenaidah-230 | 137 | 05:00 | 126 | 17:00 | Sirajganj | 133 | 00:00 | 124 | 17:00
Joydebpur | 135 | 05:00 | 122 | 12:00 | Sonargaon | 134 | 18:00 | 125 | 05:00
Joypurhat | 130 | 05:00 | 118 | 12:00 | Sreemongol | 133 | 04:00 | 127 | 12:00
Juldah | 134 | 01:00 | 129 | 13:00 | Sreepur | 132 | 05:00 | 122 | 12:00
Kabirpur | 138 | 05:00 | 122 | 12:00 | Srinagar | 139 | 05:00 | 127 | 12:00
Kachua | 125 | 06:00 | 115 | 12:00 | SSM | 138 | 05:00 | 130 | 22:00
Kaliakoir | 137 | 04:00 | 125 | 12:00 | Sunamganj | 132 | 05:00 | 125 | 13:00
Kallyanpur | 138 | 05:00 | 127 | 12:00 | Sylhet | 133 | 05:00 | 127 | 14:00
Kalurghat | 136 | 06:00 | 130 | 13:00 | Sylhet-132 | 133 | 04:00 | 128 | 14:00
Kamrangirchar | 138 | 05:00 | 127 | 12:00 | Tangail | 129 | 19:00 | 118 | 17:00
Kaptai | 137 | 8:00 | 132 | 13:00 | Thakurgaon | 134 | 05:00 | 115 | 09:00
Kasba | 131 | 07:00 | 120 | 12:00 | TK | 136 | 05:00 | 130 | 14:00
Kazla | 136 | 05:00 | 125 | 13:00 | Tongi | 141 | 04:00 | 129 | 15:00
Keranigonj | 138 | 05:00 | 127 | 12:00 | Ullahpara | 135 | 01:00 | 127 | 11:00
Khagrachori | 135 | 06:00 | 126 | 14:00 | Ullon | 138 | 05:00 | 125 | 12:00
Khulna | 136 | 02:00 | 126 | 14:00 | Uttara | 137 | 05:00 | 127 | 12:00
Khulna(S) | 140 | 06:00 | 129 | 17:00 | UttaraNew | 140 | 05:00 | 127 | 14:00
Khulshi | 135 | 06:00 | 126 | 14:00 | Zigatola | 138 | 05:00 | 127.99 | 13:00
Kishoreganj | 133 | 03:00 | 122 | 13:00
Kodda | 134 | 18:00 | 123 | 12:00
KSRM | 135 | 02:00 | 128 | 13:00
Kulaura | 134 | 03:00 | 129 | 13:00
Kurigram | 133 | 05:00 | 119 | 13:00
Kushtia | 136 | 05:00 | 127 | 17:00
Lalbag | 138 | 05:00 | 126 | 12:00
Lalmonirhat | 132 | 05:00 | 120 | 23:00
Madanganj | 131 | 03:00 | 122 | 12:00
Madaripur | 138 | 05:00 | 133 | 14:00
Madartek | 138 | 05:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division