## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-03-2025 | during | 26-03-2025 | during | 26-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 20 | 22 | 97.3 | 97.3 | 22 | 22 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 349 | 339 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 300 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 194 | 197 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 109 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 19 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 32 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 15 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 17 | 52.19 | 52.19 | 17 | 17 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 71 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 51 | 105 | 105 | 35 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 83 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2232 | 2585 | 5274.5 | 5240.5 | 3477.24 | 3460.24
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 60 | 101 | 100 | 100 | 100 | 100 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 2 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 8 | 31 | 5 | 21 | 5 | 21 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.01 | 0 | 4.01 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 900 | 1160 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 0 | 24 | 24 | 24 | 24 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 772 | 575 | 575 | 575 | 770 | 770 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1817 | 2017 | 3389.73 | 3382.72 | 3584.73 | 3577.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 197 | 184 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 325 | 358 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 31 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 128 | 88 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 20 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 25 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 25 | 163 | 163 | 30 | 30 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 100 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 68 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 90 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1280 | 1461 | 2413.99 | 2345.99 | 2250.55 | 2182.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-03-2025 | during | 26-03-2025 | during | 26-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 17 | 18 | 210 | 210 | 17 | 17 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 174 | 200 | 200 | 135 | 135 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 107 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.04 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 281.04 | 328 | 653.6 | 601.5 | 385.6 | 333.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 40 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 38 | 30 | 30 | 20 | 20 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 152 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 164 | 160 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 20 | 20 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 350 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1513 | 1511 | 1583 | 1583 | 1506 | 1506
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 919 | 871 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92.93 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 512 | 553 | 1234.2 | 1234.2 | 618 | 618 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1523.93 | 1441 | 3600.2 | 3512.2 | 1903.02 | 1815.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 8 | 10.12 | 10.12 | 7 | 7 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 116 | 108 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 802 | 1222 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1344.66 | 1865 | 2172.12 | 2171.12 | 2157 | 2156
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 158 | 158 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 204 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 211 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 384 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 24 | 24 | 24 | 24 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8.9 | 8.9 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.82 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1115 | 1359.25 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.75 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2286.97 | 2330.65 | 3111.28 | 2944.53 | 3069.49 | 2902.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 61 | 60 | 62 | 62 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 165 | 150 | 150 | 170 | 170 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.5 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 194 | 0 | 195 | 0 | 195 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 460.5 | 330 | 705.4 | 474 | 689.42 | 458.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12739.1 | 13868.65 | 22903.82 | 22255.56 | 19023.05 | 18391.79
Forecast Scenario (26-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12400 |  | 0 |  | 12400
|  |  |  | 1:00 | 12050 |  | 0 |  | 12050
|  |  |  | 2:00 | 11440 |  | 0 |  | 11440
|  |  |  | 3:00 | 11540 |  | 0 |  | 11540
|  |  |  | 4:00 | 11200 |  | 0 |  | 11200
|  |  |  | 5:00 | 10200 |  | 0 |  | 10200
|  |  |  | 6:00 | 9220 |  | 0 |  | 9220
|  |  |  | 7:00 | 8800 |  | 0 |  | 8800
|  |  |  | 8:00 | 9180 |  | 0 |  | 9180
|  |  |  | 9:00 | 9830 |  | 0 |  | 9830
|  |  |  | 10:00 | 10090 |  | 0 |  | 10090
|  |  |  | 11:00 | 10410 |  | 0 |  | 10410
|  |  |  | 12:00 | 11400 |  | 0 |  | 11400
|  |  |  | 13:00 | 12060 |  | 0 |  | 12060
|  |  |  | 14:00 | 12260 |  | 0 |  | 12260
|  |  |  | 15:00 | 11810 |  | 0 |  | 11810
|  |  |  | 16:00 | 11640 |  | 0 |  | 11640
|  |  |  | 17:00 | 11730 |  | 0 |  | 11730
|  |  |  | 18:00 | 12340 |  | 0 |  | 12340
|  |  |  | 18:30 | 12400 |  | 0 |  | 12400
|  |  |  | 19:00 | 12580 |  | 0 |  | 12580
|  |  |  | 19:30 | 12700 |  | 0 |  | 12700
|  |  |  | 20:00 | 12150 |  | 0 |  | 12150
|  |  |  | 21:00 | 12470 |  | 0 |  | 12470
|  |  |  | 22:00 | 12050 |  | 0 |  | 12050
|  |  |  | 23:00 | 12020 |  | 0 |  | 12020
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 11400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 270.87 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:30 hrs on 26-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-03-2025 | [28 empty] | Date: | 25-03-2025 | [28 empty] | Date: | 25-03-2025 | [28 empty] | Date: | 25-03-2025 | [28 empty] | Date: | 25-03-2025 | [17 empty] | Date: | 25-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 346 | 0 | 0 | 0 | 35 | 0 | 53 | 48 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 285 | 583 | 0 | 0 | 26 | 0 | 202 | 0 | 0 | 70 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 33 | 770 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 83 | 0 | 359 | 285 | 30 | 187 | 36 | 68 | 32 | 51 | 5 | 20 | 34 | 68 | 0 | 0 | 0 | 295 | 320 | 351 | 41 | 20 | 5 | 152 | 22 | 0 | 86 | 30 | 0 | 15 | 163 | 0 | 75 | 115 | 18 | 0 | 0 | 12 | 7121 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1164.94 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 218 | 0 | 220 | 0 | 393 | 0 | 0 | 2.5 | 165 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 108 | 220 | 0 | 0 | 900 | 0 | 5186.24 | 12307.24 | 85.88
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 346 | 0 | 0 | 0 | 36 | 0 | 52 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 293 | 583 | 0 | 0 | 26 | 0 | 202 | 0 | 0 | 52 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 32 | 773 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 803 | 0 | 51 | 0 | 83 | 0 | 359 | 285 | 30 | 190 | 33 | 60 | 32 | 51 | 0 | 20 | 20 | 62 | 0 | 0 | 0 | 290 | 320 | 300 | 41 | 20 | 5 | 149 | 21 | 0 | 86 | 30 | 0 | 0 | 164 | 0 | 65 | 85 | 19 | 0 | 0 | 12 | 6929 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1057.11 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 218 | 0 | 220 | 0 | 333 | 0 | 0 | 2.5 | 167 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 8 | 108 | 220 | 0 | 0 | 815 | 0 | 4903.41 | 11832.41 | 85.87
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 350 | 0 | 0 | 0 | 36 | 0 | 52 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 283 | 583 | 0 | 0 | 26 | 0 | 204 | 0 | 0 | 52 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 32 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 82 | 0 | 359 | 285 | 30 | 182 | 35 | 17 | 32 | 51 | 0 | 20 | 17 | 64 | 0 | 0 | 0 | 295 | 320 | 309 | 43 | 20 | 5 | 132 | 0 | 0 | 86 | 30 | 0 | 0 | 164 | 0 | 65 | 85 | 20 | 0 | 0 | 12 | 6753 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 1023.48 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 170 | 0 | 170 | 0 | 320 | 0 | 0 | 2.5 | 165 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 108 | 180 | 0 | 0 | 760 | 0 | 4641.78 | 11394.78 | 85.87
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 345 | 0 | 0 | 0 | 36 | 0 | 52 | 52 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 308 | 583 | 0 | 0 | 26 | 0 | 202 | 0 | 0 | 52 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 34 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 32 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 760 | 0 | 51 | 0 | 82 | 0 | 359 | 285 | 30 | 202 | 35 | 17 | 30 | 51 | 0 | 20 | 17 | 62 | 0 | 0 | 0 | 310 | 320 | 355 | 43 | 20 | 5 | 138 | 6.5 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 65 | 120 | 21 | 0 | 0 | 12 | 6921.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 1018.86 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 192 | 0 | 180 | 0 | 414 | 0 | 0 | 2.5 | 162 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 8 | 112 | 220 | 0 | 0 | 760 | 0 | 4835.16 | 11756.66 | 85.86
04:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 22 | 344 | 0 | 0 | 0 | 36 | 0 | 42 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 293 | 583 | 0 | 0 | 26 | 0 | 80 | 0 | 0 | 35 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 32 | 770 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 82 | 0 | 359 | 285 | 30 | 181 | 35 | 33 | 36 | 34 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 305 | 320 | 350 | 43 | 20 | 5 | 153 | 16 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 65 | 137 | 21 | 0 | 0 | 12 | 6831 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 | 930.26 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 209 | 0 | 200 | 0 | 312 | 0 | 0 | 2.5 | 162 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 220 | 0 | 0 | 872 | 0 | 4915.56 | 11746.56 | 85.86
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 342 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 270 | 583 | 0 | 0 | 26 | 0 | 80 | 0 | 0 | 0 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 613 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 655 | 0 | 51 | 0 | 82 | 0 | 360 | 285 | 30 | 181 | 35 | 16 | 36 | 0 | 0 | 20 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 350 | 43 | 20 | 2 | 151 | 16 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 45 | 137 | 21 | 0 | 0 | 12 | 6090 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 832.07 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 217 | 0 | 150 | 0 | 312 | 0 | 0 | 2.5 | 161 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 7 | 108 | 220 | 0 | 0 | 684 | 0 | 4407.37 | 10497.37 | 85.85
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 325 | 0 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 270 | 400 | 0 | 0 | 26 | 0 | 75 | 0 | 0 | 0 | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 586 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 658 | 0 | 51 | 0 | 88 | 0 | 280 | 285 | 30 | 181 | 35 | 0 | 36 | 0 | 0 | 4 | 0 | 50 | 0 | 0 | 0 | 300 | 320 | 327 | 43 | 20 | 2 | 133 | 16 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 45 | 105 | 23 | 0 | 0.1 | 12 | 5685.1 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 831.78 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 150 | 0 | 150 | 0 | 311 | 0 | 0 | 2.5 | 161 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 100 | 180 | 0 | 0 | 542 | 0 | 4119.08 | 9804.18 | 85.85
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 302 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 370 | 311 | 400 | 0 | 0 | 26 | 0 | 125 | 0 | 0 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 14 | 570 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 655 | 3 | 51 | 0 | 88 | 0 | 280 | 285 | 30 | 196 | 35 | 0 | 36 | 0 | 0 | 20 | 0 | 40 | 0 | 10 | 0 | 305 | 320 | 378 | 43 | 20 | 2 | 137 | 16 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 45 | 105 | 23 | 0 | 6.82 | 12 | 5816.82 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.65 | 381 | 0 | 824.99 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 13 | 0 | 6.9 | 162 | 0 | 150 | 0 | 150 | 0 | 410 | 0 | 0.58 | 2.5 | 157 | 63 | 0 | 4 | 0 | 0 | 0 | 0.9 | 25 | 0.07 | 0 | 150 | 5 | 112 | 180 | 0 | 0 | 520 | 0 | 4256.39 | 10073.21 | 85.84
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 324 | 0 | 0 | 0 | 22 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 312 | 583 | 0 | 0 | 26 | 0 | 204 | 0 | 0 | 0 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 7 | 586 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 660 | 9 | 51 | 0 | 90 | 0 | 360 | 285 | 30 | 197 | 36 | 0 | 35 | 0 | 0 | 20 | 0 | 54 | 0 | 27 | 0 | 310 | 320 | 360 | 43 | 20 | 2 | 158 | 16 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 65 | 135 | 23 | 1 | 20.23 | 12 | 6397.23 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.99 | 381 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 42 | 0 | 23.83 | 162 | 0 | 179 | 0 | 176 | 0 | 414 | 0 | 2.04 | 2.5 | 160 | 63 | 0 | 14 | 0 | 0 | 0 | 3 | 73 | 0.24 | 0 | 150 | 5 | 112 | 220 | 0 | 0 | 521 | 0 | 4432.4 | 10829.63 | 85.84
09:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 347 | 0 | 0 | 0 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 303 | 583 | 0 | 0 | 26 | 0 | 199 | 0 | 0 | 17 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 6 | 705 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 658 | 14 | 51 | 0 | 127 | 0 | 360 | 285 | 30 | 197 | 30 | 0 | 30 | 0 | 0 | 20 | 0 | 58 | 0 | 43 | 0 | 310 | 320 | 381 | 42 | 20 | 2 | 160 | 21 | 0 | 86 | 30 | 0 | 0 | 163 | 0 | 65 | 137 | 21 | 2 | 33.44 | 12 | 6677.44 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5 | 381 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 72 | 0 | 40.91 | 160 | 0 | 207 | 0 | 216 | 0 | 414 | 0 | 3.59 | 2.5 | 163 | 63 | 0 | 23 | 0 | 0 | 0 | 4.8 | 121 | 0.42 | 0 | 200 | 5 | 112 | 220 | 0 | 0 | 540 | 0 | 4702.52 | 11379.96 | 85.83
10:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 348 | 0 | 0 | 0 | 35 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 304 | 583 | 0 | 0 | 24 | 0 | 197 | 0 | 29 | 35 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 7 | 700 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 725 | 18 | 51 | 0 | 127 | 0 | 360 | 285 | 30 | 200 | 26 | 0 | 30 | 0 | 0 | 18 | 0 | 58 | 0 | 55 | 0 | 320 | 320 | 371 | 42 | 20 | 2 | 159 | 21 | 0 | 86 | 30 | 0 | 0 | 164 | 0 | 65 | 137 | 20 | 2 | 45 | 12 | 6829 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.84 | 423 | 0 | 923 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 94 | 0 | 53.27 | 158 | 0 | 204 | 0 | 215 | 0 | 414 | 0 | 4.75 | 5.5 | 163 | 62 | 0 | 30 | 0 | 0 | 0 | 6.2 | 163 | 0.56 | 0 | 200 | 4 | 120 | 220 | 0 | 0 | 648 | 0 | 5114.92 | 11943.92 | 85.83
11:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 348 | 0 | 0 | 0 | 35 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 296 | 583 | 0 | 0 | 24 | 0 | 195 | 0 | 33 | 62 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 7 | 702 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 820 | 19 | 51 | 0 | 125 | 0 | 355 | 285 | 30 | 200 | 29 | 2 | 30 | 3 | 0 | 18 | 0 | 64 | 0 | 65 | 0 | 310 | 320 | 382 | 40 | 20 | 2 | 155 | 23 | 0 | 86 | 30 | 0 | 0 | 164 | 0 | 65 | 135 | 18 | 2 | 48.76 | 12 | 6946.76 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2 | 423 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 108 | 0 | 60.28 | 158 | 0 | 140 | 0 | 213 | 0 | 414 | 0 | 5.14 | 5.5 | 158 | 61 | 0 | 35 | 0 | 0 | 0 | 7.1 | 184 | 0.62 | 0 | 200 | 5 | 120 | 220 | 0 | 0 | 760 | 0 | 5307.74 | 12254.5 | 85.82
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 20 | 349 | 0 | 0 | 0 | 35 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 298 | 583 | 0 | 0 | 24 | 0 | 194 | 0 | 34 | 70 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 4 | 46 | 0 | 8 | 772 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 900 | 19 | 51 | 0 | 128 | 0 | 325 | 285 | 30 | 197 | 30 | 34 | 30 | 17 | 0 | 20 | 0 | 68 | 0 | 65 | 0 | 310 | 320 | 363 | 40 | 20 | 2 | 155 | 24 | 0 | 85 | 30 | 0 | 0 | 164 | 0 | 65 | 135 | 17 | 2 | 50.04 | 12 | 7123.04 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.93 | 512 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 110 | 0 | 63.75 | 158 | 0 | 195 | 0 | 211 | 0 | 414 | 0 | 5.82 | 5.5 | 161 | 61 | 0 | 37 | 0 | 0 | 0 | 7.5 | 194 | 0.66 | 0 | 200 | 6 | 116 | 220 | 0 | 0 | 802 | 0 | 5616.06 | 12739.1 | 85.81
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 349 | 0 | 0 | 1 | 35 | 0 | 70 | 32 | 0 | 0 | 2 | 80 | 24 | 0 | 420 | 300 | 583 | 0 | 0 | 22 | 0 | 194 | 0 | 33 | 90 | 23 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 24 | 0 | 4 | 46 | 0 | 16 | 720 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 900 | 19 | 51 | 20 | 127 | 0 | 325 | 285 | 30 | 189 | 30 | 55 | 30 | 30 | 0 | 19 | 34 | 72 | 0 | 60 | 0 | 315 | 320 | 350 | 41 | 30 | 2 | 154 | 24 | 0 | 85 | 30 | 0 | 0 | 164 | 0 | 65 | 135 | 17 | 2 | 48.01 | 12 | 7312.01 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.34 | 510 | 0 | 1213 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 109 | 0 | 63.42 | 158 | 0 | 207 | 0 | 209 | 0 | 391 | 0 | 5.62 | 5.5 | 160 | 60 | 0 | 34 | 0 | 0 | 0 | 7.2 | 185 | 0.65 | 0 | 228 | 6 | 108 | 220 | 0 | 0 | 842 | 0 | 5739.63 | 13051.64 | 85.8
14:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 346 | 0 | 0 | 35 | 19 | 0 | 85 | 71 | 0 | 14 | 47 | 90 | 24 | 12 | 350 | 301 | 583 | 0 | 17 | 22 | 0 | 193 | 0 | 29 | 90 | 23 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 24 | 0 | 3 | 46 | 0 | 14 | 581 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 950 | 17 | 51 | 20 | 127 | 0 | 354 | 285 | 30 | 183 | 31 | 70 | 30 | 54 | 0 | 20 | 34 | 82 | 0 | 54 | 0 | 305 | 320 | 350 | 41 | 20 | 2 | 152 | 24 | 0 | 85 | 30 | 0 | 0 | 160 | 0 | 68 | 135 | 17 | 2 | 44.75 | 12 | 7375.75 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.69 | 558 | 0 | 1269.61 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 94 | 0 | 55.79 | 158 | 0 | 207 | 0 | 209 | 0 | 382 | 0 | 5 | 5.5 | 160 | 61 | 0 | 32 | 0 | 0 | 0 | 6.6 | 165 | 0.57 | 0 | 250 | 7 | 112 | 220 | 0 | 0 | 920 | 0 | 5882.66 | 13258.41 | 85.79
15:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 341 | 0 | 0 | 48 | 18 | 0 | 79 | 78 | 0 | 30 | 55 | 162 | 24 | 52 | 350 | 292 | 520 | 0 | 0 | 22 | 0 | 190 | 0 | 24 | 90 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 0 | 0 | 24 | 0 | 2 | 46 | 0 | 18 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 960 | 14 | 51 | 20 | 108 | 0 | 345 | 285 | 18 | 190 | 33 | 68 | 30 | 100 | 0 | 20 | 52 | 72 | 0 | 42 | 30 | 295 | 320 | 387 | 41 | 20 | 2 | 133 | 24 | 0 | 85 | 30 | 0 | 0 | 161 | 2 | 68 | 135 | 17 | 2 | 38.5 | 12 | 7500.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.46 | 501 | 0 | 1263.38 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 76 | 0 | 43.88 | 158 | 0 | 208 | 0 | 209 | 0 | 398 | 0 | 4.03 | 5.5 | 161 | 61 | 0 | 25 | 0 | 0 | 0 | 5.3 | 129 | 0.46 | 0 | 250 | 7 | 120 | 220 | 0 | 0 | 970 | 0 | 5805.91 | 13306.41 | 85.78
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 344 | 0 | 0 | 53 | 18 | 0 | 71 | 92 | 0 | 15 | 55 | 126 | 30 | 80 | 350 | 299 | 450 | 0 | 0 | 22 | 0 | 193 | 0 | 15 | 90 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 0 | 0 | 24 | 0 | 1 | 46 | 0 | 15 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1001 | 3 | 51 | 20 | 108 | 0 | 346 | 285 | 10 | 194 | 33 | 69 | 30 | 100 | 0 | 20 | 52 | 68 | 0 | 24 | 30 | 310 | 320 | 375 | 39 | 20 | 2 | 149 | 24 | 0 | 85 | 30 | 0 | 0 | 160 | 17 | 77 | 134 | 16 | 1 | 23.07 | 12 | 7427.07 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.4 | 504 | 0 | 1257.89 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 48 | 0 | 28.66 | 158 | 0 | 206 | 0 | 207 | 0 | 400 | 0 | 2.69 | 5.5 | 162 | 61 | 0 | 16 | 0 | 0 | 0 | 3.2 | 80 | 0.28 | 0 | 307 | 7 | 116 | 220 | 0 | 0 | 1026 | 0 | 5782.52 | 13209.59 | 85.77
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 340 | 0 | 0 | 54 | 18 | 0 | 71 | 107 | 0 | 15 | 17 | 108 | 30 | 80 | 380 | 301 | 500 | 0 | 0 | 22 | 0 | 194 | 0 | 6 | 90 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 26 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1000 | 2 | 51 | 20 | 108 | 0 | 346 | 285 | 10 | 196 | 33 | 69 | 30 | 100 | 0 | 20 | 52 | 60 | 0 | 9 | 31 | 315 | 320 | 350 | 39 | 40 | 2 | 152 | 24 | 0 | 85 | 30 | 0 | 0 | 160 | 17 | 77 | 135 | 16 | 0 | 8.49 | 12 | 7417.49 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.62 | 509 | 0 | 1299.79 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 19 | 0 | 12.11 | 158 | 0 | 207 | 0 | 208 | 0 | 400 | 0 | 1.14 | 5.5 | 167 | 61 | 35 | 6 | 34 | 0 | 0 | 1.4 | 33 | 0.11 | 0 | 307 | 6 | 120 | 220 | 0 | 0 | 1092 | 0 | 5847.57 | 13265.06 | 85.76
18:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 22 | 340 | 0 | 0 | 54 | 12 | 0 | 70 | 107 | 15 | 15 | 17 | 72 | 30 | 70 | 380 | 300 | 583 | 0 | 17 | 15 | 0 | 195 | 0 | 1 | 108 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1050 | 0 | 51 | 20 | 88 | 0 | 354 | 285 | 10 | 215 | 30 | 77 | 25 | 100 | 2 | 20 | 52 | 78 | 8 | 0 | 31 | 310 | 320 | 362 | 39 | 40 | 2 | 153 | 24 | 0 | 85 | 30 | 0 | 0 | 160 | 17 | 105 | 172 | 11 | 0 | 0.5 | 12 | 7687.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 510 | 17 | 1338.44 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0.84 | 158 | 0 | 206 | 0 | 209 | 0 | 356 | 0 | 0.08 | 5.5 | 167 | 60 | 35 | 0 | 70 | 0 | 0 | 0.2 | 3 | 0.01 | 0 | 298 | 7 | 112 | 220 | 0 | 0 | 1052 | 0 | 5754.53 | 13442.03 | 85.75
19:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 22 | 348 | 0 | 0 | 41 | 20 | 0 | 71 | 107 | 15 | 15 | 17 | 72 | 30 | 75 | 400 | 305 | 583 | 0 | 17 | 15 | 0 | 196 | 0 | 0 | 108 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 55 | 0 | 0 | 46 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1190 | 0 | 51 | 20 | 88 | 0 | 353 | 285 | 10 | 186 | 31 | 90 | 25 | 100 | 28 | 20 | 59 | 72 | 8 | 0 | 31 | 295 | 320 | 358 | 42 | 38 | 2 | 152 | 24 | 0 | 85 | 30 | 0 | 0 | 160 | 17 | 107 | 173 | 18 | 0 | 0 | 12 | 7880 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 17 | 1356.54 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 209 | 0 | 209 | 0 | 394 | 0 | 0 | 5.5 | 167 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 112 | 220 | 0 | 0 | 1082 | 0 | 5848.94 | 13728.94 | 85.74
19:30 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 22 | 339 | 0 | 0 | 35 | 54 | 0 | 71 | 109 | 15 | 15 | 17 | 72 | 32 | 83 | 400 | 300 | 583 | 0 | 17 | 15 | 0 | 197 | 0 | 0 | 108 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1160 | 0 | 51 | 20 | 88 | 0 | 358 | 285 | 10 | 184 | 31 | 90 | 25 | 100 | 28 | 20 | 70 | 68 | 8 | 0 | 25 | 310 | 320 | 350 | 40 | 38 | 2 | 152 | 24 | 0 | 85 | 30 | 0 | 0 | 160 | 17 | 107 | 174 | 18 | 0 | 0 | 12 | 7902 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 17 | 1359.25 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 204 | 0 | 211 | 0 | 384 | 0 | 0 | 5.5 | 165 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 220 | 0 | 0 | 1222 | 0 | 5966.65 | 13868.65
20:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 22 | 343 | 0 | 0 | 35 | 54 | 0 | 70 | 92 | 0 | 0 | 17 | 54 | 32 | 82 | 350 | 307 | 530 | 0 | 0 | 15 | 0 | 197 | 0 | 0 | 90 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 34 | 575 | 0 | 0 | 0 | 1 | 0 | 101 | 0 | 0 | 0 | 1166 | 0 | 51 | 27 | 88 | 0 | 357 | 285 | 10 | 185 | 31 | 90 | 30 | 85 | 27 | 20 | 70 | 72 | 8 | 0 | 32 | 290 | 320 | 362 | 40 | 38 | 2 | 152 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 17 | 107 | 175 | 20 | 0 | 0 | 12 | 7733 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 564.99 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 203 | 0 | 209 | 0 | 325 | 0 | 0 | 5.5 | 165 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 116 | 220 | 0 | 0 | 1244 | 0 | 5159.39 | 12892.39 | 85.73
21:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 22 | 334 | 0 | 0 | 0 | 54 | 0 | 70 | 92 | 0 | 0 | 20 | 108 | 32 | 83 | 350 | 302 | 550 | 0 | 17 | 15 | 0 | 198 | 0 | 0 | 90 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 87 | 0 | 0 | 46 | 8 | 34 | 575 | 0 | 0 | 0 | 8 | 7 | 101 | 0 | 0 | 0 | 1224 | 0 | 51 | 45 | 125 | 0 | 359 | 285 | 10 | 185 | 31 | 90 | 30 | 108 | 29 | 20 | 70 | 68 | 17 | 0 | 32 | 310 | 320 | 362 | 40 | 38 | 2 | 153 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 17 | 107 | 176 | 20 | 0 | 0 | 12 | 7996 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 716 | 0 | 0 | 0 | 35 | 0 | 8.9 | 70 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 204 | 0 | 211 | 0 | 386 | 0 | 0 | 5.5 | 165 | 60 | 71 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 112 | 220 | 0 | 0 | 1244 | 0 | 5632.4 | 13628.4 | 85.72
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 22 | 326 | 0 | 0 | 0 | 54 | 0 | 70 | 80 | 0 | 0 | 35 | 108 | 32 | 83 | 350 | 284 | 550 | 0 | 35 | 15 | 0 | 200 | 0 | 0 | 90 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 98 | 0 | 0 | 46 | 32 | 34 | 576 | 0 | 0 | 0 | 8 | 32 | 101 | 0 | 0 | 0 | 1150 | 0 | 51 | 100 | 127 | 0 | 359 | 285 | 10 | 190 | 32 | 43 | 30 | 120 | 28 | 20 | 52 | 72 | 25 | 0 | 32 | 290 | 320 | 348 | 40 | 38 | 5 | 151 | 24 | 0 | 86 | 30 | 0 | 18 | 162 | 17 | 107 | 177 | 20 | 0 | 0 | 12 | 7971 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 719 | 0 | 0 | 0 | 89 | 0 | 8.9 | 70 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 205 | 0 | 211 | 0 | 384 | 0 | 0 | 5.5 | 161 | 60 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 220 | 0 | 0 | 1244 | 0 | 5679.4 | 13650.4 | 85.71
23:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 22 | 322 | 0 | 0 | 0 | 36 | 0 | 58 | 80 | 0 | 0 | 35 | 108 | 32 | 93 | 400 | 310 | 583 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 90 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 98 | 0 | 0 | 46 | 34 | 36 | 576 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 100 | 127 | 0 | 360 | 285 | 10 | 196 | 30 | 34 | 25 | 85 | 29 | 20 | 34 | 68 | 16 | 0 | 32 | 300 | 320 | 340 | 40 | 40 | 5 | 152 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 17 | 75 | 167 | 19 | 0 | 0 | 12 | 7602 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 0 | 719 | 0 | 0 | 0 | 70 | 0 | 8.9 | 35 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 205 | 0 | 190 | 0 | 399 | 0 | 0 | 5.5 | 163 | 61 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 0 | 1150 | 0 | 5417.4 | 13019.4 | 85.7
Total KWH | 10224 | 705600 | 283680 | 0 | 0 | 0 | 0 | 539454.55 | 8197200 | 0 | 0 | 324360 | 727200 | 0 | 1400256 | 1274400 | 35378 | 133789 | 380236 | 1140480 | 550080 | 810240 | 9318500 | 7112436 | 13215909 | 0 | 197288 | 508100 | 0 | 4823000 | 0 | 210876 | 1508400 | 508200 | 256320 | 0 | 0 | 0 | 0 | 0 | 0 | 329280 | 357119 | 0 | 0 | 877440 | 0 | 25500 | 1094400 | 112900 | 596160 | 15381818.18 | 0 | 0 | 0 | 29820.6 | 110399 | 2250153 | 0 | 0 | 0 | 21534543 | 138510 | 1102840 | 568727 | 2525818 | 0 | 8646800 | 6918000 | 536160 | 4717000 | 780120 | 981120 | 715670 | 1335840 | 149520 | 453250 | 664620 | 1549440 | 97104 | 456864 | 291808 | 7430500 | 7699400 | 8879000 | 972000 | 603360 | 71520 | 3598036 | 462264 | 0 | 2047680 | 713664 | 0 | 75000 | 4377960 | 162000 | 1785600 | 3249600 | 436800 | 16200 | 369000 | 300240 | 172750174.33 | 22127272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653760 | 11476360 | 44640 | 24806182 | 0 | 0 | 0 | 293376 | 0 | 200480 | 194112 | 0 | 0 | 811250 | 0 | 454504 | 3880727 | 0 | 4940127 | 0 | 5018000 | 0 | 9133090 | 0 | 40200 | 106398 | 3989000 | 1415127 | 406555 | 259786 | 600316 | 0 | 0 | 52734.12 | 1362240 | 4654 | 0 | 5891000 | 168876 | 2707000 | 5265840 | 0 | 0 | 22014545.45 | 0 | 128318151.57 | 301068325.9

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12739.1 | MW | 12:00 Hr. | Energy Generated |  |  | 301.0683 |  | MKWHr.
| Day Peak Demand |  |  | 12739.1 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.392 |  | MKWHr.
| Evening Peak Generation |  |  | 13868.65 | MW | 19:30 Hr. | Energy Demand |  |  | 301.4603 |  | MKWHr.
| Evening Peak Demand |  |  | 13868.65 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.7 |  | °C
| Minimum Generation of the Day |  |  | 9804.18 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 996.55 |  | MMCFD
| Maximum Generation of the Day |  |  | 13868.65 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.834 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.0292 | 0 | 8.9315 | 0 | 0 | 0.21088 | 0 | 0 | 54.1716 | Gas | 142.8584 | Gas | 466093369.7325
| Chattogram Zone |  |  | 2.8463 | 36.9164 | 1.4877 | 0 | 1.0944 | 0.16401 | 0 | 0.32928 | 42.838 | Coal | 81.7024 | Coal | 581330122.5679
| Cumilla Zone |  |  | 26.3957 | 0 | 4.0887 | 0 | 0 | 0.45686 | 1.5494 | 0 | 32.4907 | HFO | 21.7449 | HFO | 377408571.472
| Mymensingh Zone |  |  | 0.4368 | 0 | 5.4974 | 0 | 0 | 0.3852 | 0 | 0 | 6.3194 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.9304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9304 | Hydro | 1.0944 | Hydro | 109440
| Khulna Zone |  |  | 0 | 11.4764 | 0.04464 | 0 | 0 | 0.65376 | 22.1273 | 0 | 34.302 | Solar | 4.8561 | Solar | 79219778.1632
| Barishal Zone |  |  | 8.1417 | 27.9055 | 0 | 0 | 0 | 0.004654 | 0 | 0 | 36.0519 | Import | 48.4829 | Import | 247443850.88
| Rajshahi Zone |  |  | 23.0783 | 0 | 0.68797 | 0 | 0 | 1.306 | 24.8062 | 0 | 49.8784 | Wind | 0.32928 | Wind | 4820659.2
| Rangpur Zone |  |  | 0 | 5.4041 | 1.0069 | 0 | 0 | 1.6748 | 0 | 0 | 8.0858
| Total |  |  | 142.8584 | 81.7024 | 21.7449 | 0 | 1.0944 | 4.8561 | 48.4829 | 0.32928 | 301.0683
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 466093369.7325 |  | Hydro | 109440
|  |  |  | Coal | 581330122.5679 |  | Solar | 79219778.1632
|  |  |  | HFO | 377408571.472 |  | Import | 247443850.88
|  |  |  | HSD | 0 |  | Wind | 4820659.2
[5 empty] | Total: | 175,64,25,792 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1273 | Peak Hr Flow | 871.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31225490.98 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.8062 | Peak Hr Flow | 1359.25 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 452 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5494 | Peak Hr Flow | 68.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 922 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.4829 | Peak Hr Flow | 2298.25 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4870
|  |  |  | Chattogram |  | 0 |  | 1405
|  |  |  | Cumilla |  | 0 |  | 1264
|  |  |  | Mymensingh |  | 0 |  | 1121
|  |  |  | Sylhet |  | 0 |  | 495
|  |  |  | Khulna |  | 0 |  | 1568
|  |  |  | Barishal |  | 0 |  | 374
|  |  |  | Rajshahi |  | 0 |  | 1385
|  |  |  | Rangpur |  | 0 |  | 864
|  |  |  | Total |  | 0 |  | 13346
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 10:37 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D
| 08:06 | 10:37 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D
| 08:16 | 10:38 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D
| 08:17 | 10:38 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D
| 08:22 | 10:33 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to LT bushing over temperature.
| 08:22 | 10:33 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to LT bushing over temperature.
|  | 09:02 | Bheramara P/S-Ishurdi 132 kV Ckt-2 is restored.
| 09:10 | 15:46 | Ishurdi 132/33kV S/S 132 kV Bus-2 Scheduled S/D
| 09:20 | 15:40 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to Project work
|  | 09:41 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT is restored.
| 09:48 | 15:02 | GPH 230/33kV S/S ABUL KHAIR Scheduled S/D Due to Insulator Cleaning
|  | 10:29 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT is restored.
|  | 10:30 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT is restored.
| 11:30 |  | Bajitpur 132/33kV S/S Tr-1(404T) HT Forced S/D Due to 33 kV Bus section -1 Red hot remove | [7 empty] | 25.0MW load
|  |  | maintenance . | [7 empty] | interrup.
| 12:00 |  | Day Peak Gen. 12739 MW
|  | 12:04 | Kachua 132/33kV S/S Main Bus-1 is restored.
| 12:36 | 20:07 | Bhulta 400/230kV S/S 230kV Bus-02 Project Work S/D Due to Project work.
| 13:23 | 14:45 | Bajitpur 132/33kV S/S Tr-2(414T) HT Forced S/D Due to 33 kV Bus Section-2 nest cleaning | [7 empty] | 8.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 14:23 |  | Matarbari 2*600 MW (CPGCBL) Shutdown with remarks:- U1
| 14:23 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U1 sd-14:23 at 25.3.25
| 14:23 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U1 sd-14:23
|  | 17:36 | Barishal-Barishal(N) 132 kV Ckt-2 is restored.
| 19:34 | 19:48 | Kodda 132/33kV S/S Tr-1 (406T) LT Forced S/D Due to Rope remove from 33 kv B phase | [7 empty] | 55.0MW load
|  |  | bushing | [7 empty] | interrup.
| 19:35 | 19:47 | Kodda 132/33kV S/S Tr-1 (406T) HT Forced S/D Due to Rope remove from 33 kv B phase | [7 empty] | 55.0MW load
|  |  | bushing | [7 empty] | interrup.
| 19:50 | 19:57 | Bhaluka 132/33kV S/S Transformer- 01 LT Tripped showing No relays Due to Opened by NLDC | [7 empty] | 130.0MW load
interrup.
| 19:50 | 19:58 | Bhaluka 132/33kV S/S Transformer- 02 LT Tripped showing df/dt relays Due to Low frequency | [7 empty] | 130.0MW load
interrup.
| 23:20 |  | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to Under Ground Cable problem
| 23:21 |  | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to Under Ground Cable problem
| 01:49 |  | Cumilla(S) 132/33kV S/S TR-2 HT Tripped showing RET-650 RET 670 relays.
| 01:49 |  | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing Reset Close Block relays.
| 01:58 |  | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D
| 01:58 |  | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D
| 07:02 | 07:08 | Sylhet 132/33kV S/S T1 LT Tripped showing Over current relay. relays Due to Trip Ins O/C | [7 empty] | 18.0MW load
|  |  | due to 33 KV MC College feeder fault. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 22 | 539454.55 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 339 | 8197200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9318500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7112436 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 133789 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 197 | 4823000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 10224 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 324360 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 109 | 1274400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 380236 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 197288 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 508200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 256320 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 550080 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 15 | 508100 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 283680 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 35378 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 71 | 1400256 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 705600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 83 | 810240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1140480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 210876 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 727200 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 13215909 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1508400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2585 | 54171606.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 29820.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138510 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1094400 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 101 | 2250153 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 110399 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 357119 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 877440 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 31 | 596160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25500 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 112900 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 21534543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 329280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 15381818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 2017 | 42838042.78
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 184 | 4717000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 358 | 8646800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6918000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 31 | 780120 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 536160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 88 | 2525818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1102840 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 568727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 25 | 291808 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 25 | 715670 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1335840 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 68 | 1549440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 97104 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 453250 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 664620 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 149520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 981120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456864 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1461 | 32490701
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 436800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 16200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 174 | 3249600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 1785600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 369000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 300240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 162000 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 328 | 6319440
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 972000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 603360 | FGMO
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3598036 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 71520 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 713664 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2047680 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 160 | 4377960 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 75000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 462264 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7430500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8879000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7699400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1511 | 36930384
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 871 | 22127272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 44640 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 653760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 553 | 11476360 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1441 | 34302032
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 168876 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 108 | 2707000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 22014545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5265840 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5891000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4654 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1865 | 36051915.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 158 | 3880727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 204 | 4940127 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 211 | 5018000 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 384 | 9133090 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 106398 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 8.9 | 200480 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 293376 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 194112 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 40200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1359.25 | 24806182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 454504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 811250 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2330.65 | 49878446
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 1415127 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 3989000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 600316 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52734.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 406555 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 259786 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1362240 | -
Rangpur Area Total |  |  |  |  | 950 | 330 | 8085758.12
Eastern Grid Total |  |  |  |  | 16921.242 | 7902 | 172750174.33
Western Grid Total |  |  |  |  | 11614.5 | 5966.65 | 128318151.57
National Grid Total |  |  |  |  | 28535.742 | 13868.65 | 301068325.9
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-03-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9154.66 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4190.8 | MW
i) Dhaka area |  |  | 4869.66 |  | MW | i) Khulna area |  |  |  | 1568 | MW
ii) Chattogram area |  |  | 1405 |  | MW | ii) Barishal area |  |  |  | 374 | MW
iii) Cumilla area |  |  | 1264 |  | MW | iii) Rajshahi area |  |  |  | 1384.8 | MW
iv) Mymensingh area |  |  | 1121 |  | MW | iv) Rangpur area |  |  |  | 864 | MW
v) Sylhet area |  |  | 495 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13345.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 77 | 18:00 | 133 | Payra | 28 | 21:00
2 | AKSML | 105 | 16:00 | 68 | Jamalpur | 129 | 18:00 | 134 | Postogola | 47 | 13:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 133 | 21:00 | 135 | Purbachal | 16 | 18:00
4 | Agargaon | 95 | 13:00 | 70 | Jhenaidah | 120 | 19:00 | 136 | Purbasadipur | 122 | 13:00
5 | Agrabad | 90 | 19:30 | 71 | Joydebpur | 140 | 22:00 | 137 | Rahanpur | 31 | 03:00
6 | Amnura | 50 | 19:30 | 72 | Joypurhat | 65 | 22:00 | 138 | Rahim | 43 | 14:00
7 | Ashuganj | 86 | 23:00 | 73 | Juldah | 12 | 10:00 | 139 | Rajbari | 64 | 19:00
8 | BSRM | 198 | 02:00 | 74 | KSRM | 27 | 00:00 | 140 | Rajendrapur | 113 | 18:00
9 | Bagerhat | 77 | 19:00 | 75 | Kabirpur | 236 | 16:00 | 141 | Rajshahi | 90 | 21:00
10 | Bajitpur | 47 | 17:00 | 76 | Kachua | 73 | 21:00 | 142 | Rajshahi-230 | 81 | 22:00
11 | Bakulia | 92 | 19:30 | 77 | Kallyanpur | 120 | 00:00 | 143 | Ramganj | 106 | 18:30
12 | Banani | 36.6 | 15:00 | 78 | Kalurghat | 39 | 14:00 | 144 | Rampur | 39 | 23:00
13 | Bangabhaban | 14 | 10:00 | 79 | Kamrangirchar | 65.8 | 19:00 | 145 | Rangamati | 15 | 18:30
14 | Barapukuria | 66 | 21:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 150 | 18:00
15 | Barguna | 16 | 01:00 | 81 | Kasba | 33 | 21:00 | 147 | Ruppur | 7 | 10:00
16 | Barishal | 93 | 19:00 | 82 | Kazla | 94 | 15:00 | 148 | SSM | 10 | 00:00
17 | Barishal-230 | 82 | 20:00 | 83 | Keranigonj | 81 | 14:00 | 149 | Saidpur | 106 | 12:00
18 | Baroaulia | 54 | 14:00 | 84 | Khagrachori | 28 | 18:00 | 150 | Satkhira | 128 | 19:00
19 | Baroirhat | 57 | 18:00 | 85 | Khulna | 81 | 19:00 | 151 | Satmasjid | 90 | 19:30
20 | Bashundhara | 159 | 14:00 | 86 | Khulshi | 143 | 22:00 | 152 | Savar | 197 | 14:00
21 | BashundharaCement | 7 | 10:00 | 87 | Kishoreganj | 128 | 22:00 | 153 | SevenRings | 19.74 | 16:00
22 | Beanibazar | 58 | 18:30 | 88 | Kodda | 296 | 11:00 | 154 | ShahCement | 38 | 00:00
23 | Benapole | 62 | 22:00 | 89 | Kulaura | 38 | 19:00 | 155 | Shahjadpur | 78 | 18:00
24 | Bhaluka | 153 | 18:00 | 90 | Kurigram | 66 | 17:00 | 156 | Shahjibazar | 113 | 22:00
25 | Bhandaria | 43 | 21:00 | 91 | Kushtia | 120 | 19:30 | 157 | Shahmirpur | 59 | 00:00
26 | Bhangura | 37 | 13:00 | 92 | Lalbag | 61 | 13:00 | 158 | Shariatpur | 70 | 20:00
27 | Bheramara(GK) | 51 | 21:00 | 93 | Lalmonirhat | 59 | 18:00 | 159 | Sherpur | 154 | 18:00
28 | Bhulta | 246 | 14:00 | 94 | MI_Cement | 18.1 | 13:00 | 160 | Shikalbaha | 28 | 15:00
29 | Bog-Sherpur | 120 | 10:00 | 95 | Madanganj | 45 | 15:00 | 161 | Shitalakhya | 78.5 | 16:00
30 | Bogura | 158 | 22:00 | 96 | Madaripur | 80 | 19:30 | 162 | Sholosohor | 42 | 15:00
31 | Borhanuddin | 67 | 21:00 | 97 | Madartek | 77.22 | 22:00 | 163 | Shyampur | 162 | 13:00
32 | Brahmanbaria | 119 | 21:00 | 98 | Madunaghat | 47 | 18:30 | 164 | Siddhirganj | 115 | 11:00
33 | Cantonment | 102 | 14:00 | 99 | Magura | 57 | 19:00 | 165 | Sirajganj | 102 | 19:30
34 | Chandpur | 61 | 21:00 | 100 | Mahasthangarh | 70 | 21:00 | 166 | Sonargaon | 97 | 15:00
35 | Chandraghona | 32 | 20:00 | 101 | Manikganj | 113 | 19:30 | 167 | Sreemongol | 62 | 18:30
36 | Chapai | 62.5 | 22:00 | 102 | Maniknagar | 63 | 14:00 | 168 | Sreepur | 80 | 17:00
37 | Charsaidpur | 45 | 01:00 | 103 | Matarbari | 47 | 22:00 | 169 | Srinagar | 38.5 | 20:00
38 | Chauddagram | 69 | 13:00 | 104 | Matuail | 68 | 15:00 | 170 | Sunamganj | 48 | 20:00
39 | Chhatak | 27 | 18:00 | 105 | Millgate | 78 | 16:00 | 171 | Sylhet | 30 | 00:00
40 | Chowmuhani | 208 | 18:30 | 106 | Mirpur | 121 | 15:00 | 172 | Sylhet-132 | 110 | 21:00
41 | Chuadanga | 96 | 20:00 | 107 | Mirsorai | 9 | 14:00 | 173 | TK | 21 | 19:30
42 | Coxsbazar | 129 | 19:00 | 108 | Mirzapur | 43 | 18:00 | 174 | Tangail | 176 | 18:00
43 | Cumilla(N) | 142 | 18:00 | 109 | Mithapukur | 58 | 18:00 | 175 | Thakurgaon | 90 | 18:00
44 | Cumilla(S) | 160 | 18:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 122 | 10:00
45 | Daudkandi | 128 | 14:00 | 111 | Mogbazar | 124.7 | 14:00 | 177 | Ullahpara | 33 | 03:00
46 | Dhaka | 48 | 13:00 | 112 | Mongla | 38 | 19:30 | 178 | Ullon | 43 | 21:00
47 | Dhamrai | 126 | 15:00 | 113 | Motijheel | 34 | 14:00 | 179 | Uttara | 72 | 13:00
48 | Dhanmondi | 130 | 13:00 | 114 | Muktagacha | 38 | 18:00 | 180 | UttaraNew | 42 | 21:00
49 | Dohazari | 102 | 21:00 | 115 | Munshiganj | 97 | 19:30 | 181 | Zigatola | 60 | 19:00
50 | Faridpur | 134 | 19:00 | 116 | Muradnagar | 26 | 20:00
51 | Fatullah | 91 | 15:00 | 117 | Mymensingh | 213 | 18:00
52 | Fenchuganj | 32 | 18:00 | 118 | Naogaon | 122 | 22:00
53 | Feni | 103 | 21:00 | 119 | Narail | 52 | 19:00
54 | GPH | 92 | 07:00 | 120 | Narinda | 75 | 13:00
55 | Ghatail | 80 | 18:00 | 121 | Narshingdi | 167 | 19:30
56 | Ghorashal | 15 | 12:00 | 122 | Natore | 134 | 19:30
57 | Ghorashal-230 | 84 | 19:30 | 123 | Nawabganj | 46.8 | 21:00
58 | Goalpara | 26 | 18:00 | 124 | Netrakona | 142 | 20:00
59 | Gollamari | 66 | 19:30 | 125 | New | 77 | 14:00
60 | Gopalganj | 92.6 | 19:00 | 126 | Niamatpur | 101 | 21:00
61 | Gulshan | 102 | 13:00 | 127 | Noapara | 42 | 19:00
62 | Halishahar | 64.5 | 10:00 | 128 | PHP | 6 | 23:00
63 | HaripurSBU | 158 | 12:00 | 129 | Pabna | 100 | 19:00
64 | Hasnabad | 76 | 19:30 | 130 | Palashbari | 108 | 13:00
65 | Hathazari | 75 | 20:00 | 131 | Panchagarh | 52 | 18:00
66 | Ishurdi | 60 | 19:00 | 132 | Patuakhali | 60.2 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12307.24 | 0 |  | 12307.24
1:00 | 11832.41 | 0 |  | 11832.41
2:00 | 11394.78 | 0 |  | 11394.78
3:00 | 11756.66 | 0 |  | 11756.66
4:00 | 11746.56 | 0 |  | 11746.56
5:00 | 10497.37 | 0 |  | 10497.37
6:00 | 9804.18 | 0 |  | 9804.18
7:00 | 10073.21 | 0 |  | 10073.21
8:00 | 10829.63 | 0 |  | 10829.63
9:00 | 11379.96 | 0 |  | 11379.96
10:00 | 11943.92 | 0 |  | 11943.92
11:00 | 12254.5 | 0 |  | 12254.5
12:00 | 12739.1 | 0 |  | 12739.1
13:00 | 13051.64 | 0 |  | 13051.64
14:00 | 13258.41 | 0 |  | 13258.41
15:00 | 13306.41 | 0 |  | 13306.41
16:00 | 13209.59 | 0 |  | 13209.59
17:00 | 13265.06 | 0 |  | 13265.06
18:00 | 13442.03 | 0 |  | 13442.03
19:00 | 13728.94 | 0 |  | 13728.94
19:30 | 13868.65 | 0 |  | 13868.65
20:00 | 12892.39 | 392 |  | 13302.39
21:00 | 13628.4 | 0 |  | 13628.4
22:00 | 13650.4 | 0 |  | 13650.4
23:00 | 13019.4 | 0 |  | 13019.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7121 | 5186.24 | 12307.24 | DAILY GENERATION CURVE
00:30 | 7025 | 5044.825 | 12069.825
01:00 | 6929 | 4903.41 | 11832.41 | 25-03-2025
01:30 | 6841 | 4772.595 | 11613.595
02:00 | 6753 | 4641.78 | 11394.78
02:30 | 6837.25 | 4738.47 | 11575.72
03:00 | 6921.5 | 4835.16 | 11756.66
03:30 | 6876.25 | 4875.36 | 11751.61
04:00 | 6831 | 4915.56 | 11746.56
04:30 | 6460.5 | 4661.465 | 11121.965
05:00 | 6090 | 4407.37 | 10497.37
05:30 | 5887.55 | 4263.225 | 10150.775
06:00 | 5685.1 | 4119.08 | 9804.18
06:30 | 5750.96 | 4187.735 | 9938.695
07:00 | 5816.82 | 4256.39 | 10073.21
07:30 | 6107.025 | 4344.395 | 10451.42
08:00 | 6397.23 | 4432.4 | 10829.63
08:30 | 6537.335 | 4567.46 | 11104.795
09:00 | 6677.44 | 4702.52 | 11379.96
09:30 | 6753.22 | 4908.72 | 11661.94
10:00 | 6829 | 5114.92 | 11943.92
10:30 | 6887.88 | 5211.33 | 12099.21
11:00 | 6946.76 | 5307.74 | 12254.5
11:30 | 7034.9 | 5461.9 | 12496.8
12:00 | 7123.04 | 5616.06 | 12739.1
12:30 | 7217.525 | 5677.845 | 12895.37
13:00 | 7312.01 | 5739.63 | 13051.64
13:30 | 7343.88 | 5811.145 | 13155.025
14:00 | 7375.75 | 5882.66 | 13258.41
14:30 | 7438.125 | 5844.285 | 13282.41
15:00 | 7500.5 | 5805.91 | 13306.41
15:30 | 7463.785 | 5794.215 | 13258
16:00 | 7427.07 | 5782.52 | 13209.59
16:30 | 7422.28 | 5815.045 | 13237.325
17:00 | 7417.49 | 5847.57 | 13265.06
17:30 | 7552.495 | 5801.05 | 13353.545
18:00 | 7687.5 | 5754.53 | 13442.03
18:30 | 7783.75 | 5801.735 | 13585.485
19:00 | 7880 | 5848.94 | 13728.94
19:30 | 7902 | 5966.65 | 13868.65
20:00 | 7733 | 5159.39 | 12892.39
20:30 | 7864.5 | 5395.895 | 13260.395 |  | Executive Engineer
21:00 | 7996 | 5632.4 | 13628.4 |  | Network Operation Division
21:30 | 7983.5 | 5655.9 | 13639.4
22:00 | 7971 | 5679.4 | 13650.4
22:30 | 7786.5 | 5548.4 | 13334.9
23:00 | 7602 | 5417.4 | 13019.4

## En-Curve
QF-LDC-12
Date | 25-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3612 | 2422.5 | 919 | 0 | 68 | 1164.94 | 46 | 3380 | 0 | 185.8 | 496 | 0 | 0 | 13 | 0 | DAILY ENERGY CURVE
00:30 | 3549.5 | 2422 | 919 | 0 | 65 | 1111.025 | 46 | 3299.5 | 0 | 176.8 | 462.5 | 0 | 0 | 18.5 | 0 | 25-03-2025
01:00 | 3487 | 2421.5 | 919 | 0 | 62 | 1057.11 | 46 | 3219 | 0 | 167.8 | 429 | 0 | 0 | 24 | 0
01:30 | 3437 | 2351 | 919 | 0 | 63 | 1040.295 | 46 | 3153 | 0 | 167.8 | 406 | 0 | 0 | 30.5 | 0 | Energy Generated | 301.0683 |  | MKWHr
02:00 | 3387 | 2280.5 | 919 | 0 | 64 | 1023.48 | 46 | 3087 | 0 | 167.8 | 383 | 0 | 0 | 37 | 0 | Energy not Served | 0.392 |  | MKWHr
02:30 | 3481 | 2336.75 | 919 | 0 | 63 | 1021.17 | 46 | 3105.5 | 0 | 169.8 | 400.5 | 0 | 0 | 33 | 0 | Total Energy Requirement | 301.4603 |  | MKWHr
03:00 | 3575 | 2393 | 919 | 0 | 62 | 1018.86 | 46 | 3124 | 0 | 171.8 | 418 | 0 | 0 | 29 | 0
03:30 | 3469 | 2395.25 | 919 | 0 | 63 | 974.56 | 46 | 3263 | 0 | 185.3 | 412.5 | 0 | 0 | 24 | 0
04:00 | 3363 | 2397.5 | 919 | 0 | 64 | 930.26 | 46 | 3402 | 0 | 198.8 | 407 | 0 | 0 | 19 | 0
04:30 | 3340.5 | 2351.5 | 919 | 0 | 60 | 881.165 | 46 | 3068.5 | 0 | 116.3 | 320 | 0 | 0 | 19 | 0
05:00 | 3318 | 2305.5 | 919 | 0 | 56 | 832.07 | 46 | 2735 | 0 | 33.8 | 233 | 0 | 0 | 19 | 0
05:30 | 3217.5 | 2185.5 | 919.5 | 0 | 53 | 831.925 | 46 | 2638.5 | 0.05 | 33.8 | 207.5 | 0 | 0 | 17.5 | 0
06:00 | 3117 | 2065.5 | 920 | 0 | 50 | 831.78 | 46 | 2542 | 0.1 | 33.8 | 182 | 0 | 0 | 16 | 0
06:30 | 3219 | 2084 | 919.5 | 0 | 45 | 828.385 | 46 | 2519 | 41.01 | 33.8 | 189 | 0 | 0 | 14 | 0
07:00 | 3321 | 2102.5 | 919 | 0 | 40 | 824.99 | 46 | 2496 | 81.92 | 33.8 | 196 | 0 | 0 | 12 | 0
07:30 | 3432.5 | 2254 | 894.5 | 0 | 47 | 820.995 | 46 | 2508.5 | 165.625 | 33.8 | 238.5 | 0 | 0 | 10 | 0
08:00 | 3544 | 2405.5 | 870 | 0 | 54 | 817 | 46 | 2521 | 249.33 | 33.8 | 281 | 0 | 0 | 8 | 0
08:30 | 3589.5 | 2424.5 | 870 | 0 | 56 | 817 | 46 | 2615.5 | 333.495 | 55.3 | 290.5 | 0 | 0 | 7 | 0
09:00 | 3635 | 2443.5 | 870 | 0 | 58 | 817 | 46 | 2710 | 417.66 | 76.8 | 300 | 0 | 0 | 6 | 0
09:30 | 3630 | 2448 | 894.5 | 0 | 58 | 870 | 46 | 2815.5 | 498.64 | 93.8 | 300 | 0 | 0 | 7.5 | 0
10:00 | 3625 | 2452.5 | 919 | 0 | 58 | 923 | 46 | 2921 | 579.62 | 110.8 | 300 | 0 | 0 | 9 | 0
10:30 | 3578 | 2443.5 | 919 | 0 | 61 | 968 | 46 | 3022.5 | 620.36 | 124.35 | 306 | 0 | 0 | 10.5 | 0
11:00 | 3531 | 2434.5 | 919 | 0 | 64 | 1013 | 46 | 3124 | 661.1 | 137.9 | 312 | 0 | 0 | 12 | 0
11:30 | 3524.5 | 2438 | 919 | 0 | 66 | 1064 | 46 | 3266 | 673.4 | 149.9 | 341 | 0 | 0 | 9 | 0
12:00 | 3518 | 2441.5 | 919 | 0 | 68 | 1115 | 46 | 3408 | 685.7 | 161.9 | 370 | 0 | 0 | 6 | 0
12:30 | 3503 | 2451.5 | 919 | 0 | 70 | 1164 | 46 | 3414 | 672.97 | 171.9 | 466.5 | 0 | 0 | 16.5 | 0
13:00 | 3488 | 2461.5 | 919 | 0 | 72 | 1213 | 46 | 3420 | 660.24 | 181.9 | 563 | 0 | 0 | 27 | 0
13:30 | 3508.5 | 2421 | 918.5 | 0 | 77 | 1241.305 | 46 | 3450 | 623.32 | 188.4 | 653.5 | 0 | 0 | 27.5 | 0
14:00 | 3529 | 2380.5 | 918 | 0 | 82 | 1269.61 | 46 | 3480 | 586.4 | 194.9 | 744 | 0 | 0 | 28 | 0
14:30 | 3556.5 | 2317 | 918 | 0 | 77 | 1266.495 | 46 | 3479 | 528.015 | 221.9 | 838.5 | 0 | 0 | 34 | 0
15:00 | 3584 | 2253.5 | 918 | 0 | 72 | 1263.38 | 46 | 3478 | 469.63 | 248.9 | 933 | 0 | 0 | 40 | 0
15:30 | 3578.5 | 2235 | 918.5 | 0 | 70 | 1260.635 | 46 | 3557 | 376.965 | 255.9 | 928 | 0 | 0 | 31.5 | 0
16:00 | 3573 | 2216.5 | 919 | 0 | 68 | 1257.89 | 46 | 3636 | 284.3 | 262.9 | 923 | 0 | 0 | 23 | 0
16:30 | 3573 | 2266.5 | 919 | 0 | 64 | 1278.84 | 46 | 3673.5 | 200.085 | 270.9 | 930.5 | 0 | 0 | 15 | 0
17:00 | 3573 | 2316.5 | 919 | 0 | 60 | 1299.79 | 46 | 3711 | 115.87 | 278.9 | 938 | 0 | 0 | 7 | 0
17:30 | 3560.5 | 2346 | 919 | 0 | 69 | 1319.115 | 46 | 3711.5 | 61.53 | 309.4 | 1007.5 | 0 | 0 | 4 | 0
18:00 | 3548 | 2375.5 | 919 | 0 | 78 | 1338.44 | 46 | 3712 | 7.19 | 339.9 | 1077 | 0 | 0 | 1 | 0
18:30 | 3560.5 | 2377.5 | 895 | 0 | 75 | 1347.49 | 46 | 3826 | 3.595 | 348.4 | 1105.5 | 0 | 0 | 0.5 | 0
19:00 | 3573 | 2379.5 | 871 | 0 | 72 | 1356.54 | 46 | 3940 | 0 | 356.9 | 1134 | 0 | 0 | 0 | 0
19:30 | 3541 | 2391.5 | 871 | 0 | 68 | 1359.25 | 46 | 4042 | 0 | 352.9 | 1197 | 0 | 0 | 0 | 0
20:00 | 3528 | 2282.5 | 871 | 0 | 72 | 564.99 | 46 | 4107 | 0 | 324.9 | 1096 | 0 | 0 | 0 | 392
20:30 | 3555.5 | 2319.5 | 895 | 0 | 70 | 640.495 | 46 | 4150 | 0 | 324.9 | 1259 | 0 | 0 | 0 | 196
21:00 | 3583 | 2356.5 | 919 | 0 | 68 | 716 | 46 | 4193 | 0 | 324.9 | 1422 | 0 | 0 | 0 | 0
21:30 | 3574 | 2339 | 919 | 0 | 70 | 717.5 | 46 | 4154.5 | 0 | 319.4 | 1500 | 0 | 0 | 0 | 0
22:00 | 3565 | 2321.5 | 919 | 0 | 72 | 719 | 46 | 4116 | 0 | 313.9 | 1578 | 0 | 0 | 0 | 0
22:30 | 3410 | 2381 | 919 | 0 | 70 | 719 | 46 | 4049.5 | 0 | 291.9 | 1448 | 0 | 0 | 0.5 | 0
23:00 | 3255 | 2440.5 | 919 | 0 | 68 | 719 | 46 | 3983 | 0 | 269.9 | 1318 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 05:00 | 383 | 16:00 | Payra | 422 | 06:00 | 409 | 18:30
Ashuganj | 415 | 18:00 | 392 | 11:00 | Rahanpur | 402 | 20:00 | 383 | 13:00
Bhulta | 405 | 04:00 | 381 | 12:00 | Rampal | 414 | 06:00 | 394 | 14:00
Bibiana | 397 | 05:00 | 386 | 12:00
BIPTC | 397 | 02:00 | 388 | 11:00
Bogura | 396 | 05:00 | 366 | 13:00
Gopalganj | 413 | 06:00 | 392 | 16:00
Kaliakoir | 373 | 04:00 | 354 | 12:00
Madunaghat | 402 | 06:00 | 390 | 13:00
Meghnaghat | 406 | 05:00 | 385 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 06:00 | 220 | 15:00 | Keranigonj | 234 | 06:00 | 219 | 12:00
AKSML | 237 | 06:00 | 225 | 12:00 | Khulna(S) | 240 | 06:00 | 223 | 14:00
Aminbazar | 236 | 05:00 | 223 | 11:00 | Madunaghat | 238 | 06:00 | 228 | 12:00
Ashuganj | 236 | 05:00 | 223 | 13:00 | Madunaghat-400 | 238 | 07:00 | 228 | 13:00
Ashuganj-400 | 236 | 05:00 | 223 | 13:00 | Maniknagar | 229 | 07:00 | 215 | 12:00
Baghabari | 236 | 03:00 | 226 | 12:00 | Meghnaghat | 238 | 05:00 | 224 | 16:00
Barapukuria | 226 | 21:00 | 215 | 13:00 | Meghnaghat-400 | 234 | 06:00 | 221 | 12:00
Barapukuria-230 | 226 | 21:00 | 215 | 13:00 | Mirsorai | 232 | 05:00 | 220 | 13:00
Barishal | 241 | 06:00 | 231 | 14:00 | Rajshahi | 235 | 01:00 | 221 | 12:00
Bheramara | 235 | 01:00 | 222 | 12:00 | Rampal | 237 | 05:00 | 223 | 14:00
Bhulta | 231 | 05:00 | 216 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 05:00 | 221 | 14:00 | Rampura | 230 | 06:00 | 214 | 12:00
BIPTC | 237 | 01:00 | 222 | 12:00 | Shikalbaha | 234 | 06:00 | 224 | 12:00
Bogura | 238 | 06:00 | 225 | 13:00 | Shyampur | 233 | 06:00 | 219 | 12:00
Bogura-400 | 237 | 05:00 | 224 | 13:00 | Siddhirganj | 231 | 04:00 | 217 | 11:00
Borhanuddin | 245 | 05:00 | 238 | 12:00 | Sirajgonj | 242 | 20:00 | 235 | 15:00
BSRM | 233 | 05:00 | 219 | 12:00 | Sreepur | 232 | 04:00 | 224 | 16:00
Cumilla(N) | 228 | 07:00 | 216 | 12:00 | Tongi | 228 | 04:00 | 212 | 15:00
Faridpur | 240 | 05:00 | 227 | 16:00
Fenchuganj | 233 | 18:00 | 226 | 15:00
Ghorashal | 225 | 01:00 | 2 | 08:00
Ghorashal-230 | 231 | 06:00 | 215 | 13:00
Gopalganj | 239 | 06:00 | 226 | 16:00
GPH | 236 | 06:00 | 223 | 12:00
Haripur | 229 | 18:30 | 217 | 16:00
Hasnabad | 232 | 03:00 | 219 | 12:00
Hathazari | 235 | 04:00 | 226 | 14:00
Ishurdi | 237 | 01:00 | 224 | 12:00
Jhenaidah | 233 | 06:00 | 218 | 13:00
Kaliakoir | 234 | 04:00 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 124 | 12:00 | Madunaghat | 137 | 06:00 | 130 | 12:00
Agargaon | 141 | 05:00 | 42 | 16:00 | Magura | 134 | 05:00 | 121 | 15:00
Agrabad | 135 | 06:00 | 127 | 12:00 | Mahasthangarh | 133 | 22:00 | 123 | 12:00
AKS | 132 | 05:00 | 126 | 11:00 | Manikganj | 132 | 04:00 | 121 | 11:00
Aminbazar | 137 | 04:00 | 129 | 11:00 | Maniknagar | 135 | 05:00 | 125 | 12:00
Amnura | 136 | 05:00 | 125 | 12:00 | Matarbari | 125 | 08:00 | 112 | 18:30
Ashuganj | 139 | 05:00 | 131 | 17:00 | Matuail | 134.6 | 05:00 | 126.5 | 12:00
Bagerhat | 136 | 05:00 | 120 | 15:00 | Millgate | 138 | 05:00 | 126 | 12:00
Bajitpur | 130 | 00:00 | 123 | 16:00 | Mirpur | 137 | 06:00 | 126 | 12:00
Bakulia | 137 | 06:00 | 129 | 15:00 | Mirzapur | 130 | 02:00 | 120 | 13:00
Banani | 136 | 04:00 | 125 | 12:00 | Mithapukur | 135 | 22:00 | 120 | 13:00
Bangabhaban | 135 | 06:00 | 125 | 12:00 | MI_Cement | 135 | 06:00 | 126 | 16:00
Barapukuria | 139 | 21:00 | 129 | 13:00 | Modern | 0 | 0:00 | 0 | 0:00
Barguna | 138 | 06:00 | 133 | 15:00 | Mogbazar | 137 | 05:00 | 32 | 18:00
Barishal | 136 | 05:00 | 128 | 14:00 | Mongla | 135 | 05:00 | 122 | 17:00
Barishal-230 | 136 | 06:00 | 128 | 14:00 | Motijheel | 135 | 06:00 | 125 | 12:00
Baroaulia | 135 | 05:00 | 128 | 12:00 | Muktagacha | 131 | 04:00 | 119 | 17:00
Baroirhat | 129 | 20:00 | 117 | 12:00 | Munshiganj | 134 | 05:00 | 125 | 12:00
Bashundhara | 138 | 05:00 | 124 | 12:00 | Muradnagar | 130 | 06:00 | 121 | 12:00
BashundharaCement | 138 | 02:00 | 120 | 17:00 | Mymensingh | 133 | 20:00 | 112 | 15:00
Beanibazar | 132 | 07:00 | 126 | 14:00 | Naogaon | 130 | 05:00 | 119 | 12:00
Benapole | 133 | 06:00 | 118 | 14:00 | Narail | 134 | 05:00 | 121 | 14:00
Bhaluka | 129 | 20:00 | 117 | 17:00 | Narinda | 135 | 05:00 | 125 | 12:00
Bhandaria | 131 | 06:00 | 123 | 17:00 | Narshingdi | 131 | 18:30 | 118 | 17:00
Bhangura | 134 | 02:00 | 127 | 12:00 | Natore | 133 | 20:00 | 125 | 12:00
Bheramara | 135 | 01:00 | 127 | 12:00 | Nawabganj | 137 | 06:00 | 125 | 13:00
Bheramara(GK) | 135 | 04:00 | 127 | 12:00 | Netrakona | 124 | 07:00 | 109 | 16:00
Bhulta | 129 | 05:00 | 121 | 12:00 | New | 139 | 04:00 | 126 | 12:00
Bog-Sherpur | 133 | 05:00 | 125 | 12:00 | Niamatpur | 136 | 20:00 | 128 | 13:00
Bogura | 135 | 22:00 | 127 | 12:00 | Noapara | 136 | 05:00 | 123 | 14:00
Bogura-230 | 135 | 21:00 | 126 | 12:00 | Pabna | 135 | 01:00 | 127 | 12:00
Brahmanbaria | 132 | 05:00 | 122 | 16:00 | Palashbari | 131 | 22:00 | 117 | 13:00
Cantonment | 142 | 06:00 | 130 | 12:00 | Panchagarh | 140 | 21:00 | 117 | 14:00
Chandpur | 127 | 21:00 | 115 | 11:00 | Patuakhali | 137 | 07:00 | 16 | 15:00
Chandraghona | 160 | 15:00 | 129 | 11:00 | Payra | 139 | 06:00 | 134 | 16:00
Chapai | 133 | 04:00 | 127 | 13:00 | PHP | 126 | 07:00 | 116 | 12:00
Charsaidpur | 134 | 05:00 | 125 | 13:00 | Postogola | 138 | 06:00 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 130 | 20:00 | 116 | 11:00 | Purbachal | 137 | 04:00 | 124 | 12:00
Chhatak | 131 | 05:00 | 125 | 15:00 | Purbasadipur | 135 | 21:00 | 115 | 14:00
Chowmuhani | 125 | 20:00 | 111 | 14:00 | Rahanpur | 138 | 23:00 | 38 | 23:00
Chuadanga | 133 | 04:00 | 120 | 16:00 | Rahanpur-400 | 137 | 20:00 | 130 | 13:00
Coxsbazar | 124 | 08:00 | 113 | 18:00 | Rahim | 134 | 06:00 | 125 | 13:00
Cumilla(N) | 131 | 06:00 | 123 | 12:00 | Rajbari | 135 | 06:00 | 125 | 16:00
Cumilla(S) | 131 | 05:00 | 120 | 12:00 | Rajendrapur | 130 | 02:00 | 121 | 16:00
Daudkandi | 129 | 06:00 | 118 | 14:00 | Rajshahi | 134 | 01:00 | 127 | 12:00
Dhaka | 136 | 05:00 | 125 | 12:00 | Rajshahi-230 | 136 | 05:00 | 119 | 13:00
Dhamrai | 133 | 04:00 | 123 | 14:00 | Ramganj | 121 | 20:00 | 109 | 12:00
Dhanmondi | 138 | 06:00 | 127 | 12:00 | Rampur | 135 | 07:00 | 127 | 12:00
Dohazari | 131 | 06:00 | 124 | 16:00 | Rampura | 137 | 06:00 | 125 | 12:00
Faridpur | 134 | 06:00 | 127 | 16:00 | Rangamati | 136 | 06:00 | 128 | 12:00
Fatullah | 136 | 06:00 | 125 | 13:00 | Rangpur | 133 | 22:00 | 118 | 14:00
Fenchuganj | 134 | 01:00 | 130 | 14:00 | Ruppur | 136 | 05:00 | 130 | 12:00
Feni | 127 | 20:00 | 117 | 14:00 | Saidpur | 135 | 05:00 | 118 | 13:00
Ghatail | 129 | 02:00 | 117 | 12:00 | Satkhira | 137 | 06:00 | 120 | 19:30
Ghorashal | 137 | 05:00 | 130 | 12:00 | Satmasjid | 141 | 06:00 | 128 | 13:00
Goalpara | 137 | 06:00 | 125 | 14:00 | Savar | 135 | 05:00 | 124 | 12:00
Gollamari | 138 | 04:00 | 127 | 15:00 | SevenRings | 138 | 06:00 | 128 | 13:00
Gopalganj | 139 | 06:00 | 129 | 14:00 | ShahCement | 134 | 05:00 | 125 | 13:00
Gopalganj-400 | 141 | 06:00 | 133 | 13:00 | Shahjadpur | 136 | 22:00 | 130 | 14:00
Gulshan | 136 | 04:00 | 125 | 12:00 | Shahjibazar | 134 | 05:00 | 126 | 14:00
Halishahar | 133 | 09:00 | 128 | 11:00 | Shahmirpur | 139 | 14:00 | 130 | 12:00
Haripur | 134 | 18:30 | 127 | 15:00 | Shariatpur | 139 | 06:00 | 130 | 17:00
HaripurSBU | 134 | 04:00 | 127 | 15:00 | Sherpur | 136 | 19:30 | 123 | 15:00
Hasnabad | 136 | 05:00 | 129 | 13:00 | Shikalbaha | 125 | 06:00 | 118 | 12:00
Hathazari | 137 | 07:00 | 131 | 13:00 | Shikalbaha-230 | 137 | 06:00 | 130 | 12:00
Ishurdi | 137 | 01:00 | 130 | 12:00 | Shitalakhya | 135 | 06:00 | 126 | 16:00
Jaldhaka | 133 | 05:00 | 116 | 13:00 | Sholosohor | 136 | 06:00 | 129 | 12:00
Jamalpur | 138 | 22:00 | 124 | 17:00 | Shyampur | 135 | 06:00 | 130 | 10:00
Jashore | 134 | 06:00 | 120 | 14:00 | Shyampur-230 | 136 | 06:00 | 125 | 12:00
Jhenaidah | 136 | 05:00 | 123 | 15:00 | Siddhirganj | 134 | 02:00 | 127 | 11:00
Jhenaidah-230 | 136 | 06:00 | 124 | 14:00 | Sirajganj | 130 | 04:00 | 124 | 18:00
Joydebpur | 132 | 04:00 | 124 | 12:00 | Sonargaon | 132 | 04:00 | 124 | 12:00
Joypurhat | 128 | 05:00 | 116 | 12:00 | Sreemongol | 134 | 05:00 | 126 | 14:00
Juldah | 134 | 22:00 | 130 | 10:00 | Sreepur | 131 | 22:00 | 123 | 16:00
Kabirpur | 136 | 04:00 | 123 | 12:00 | Srinagar | 137 | 05:00 | 126 | 12:00
Kachua | 128 | 20:00 | 116 | 12:00 | SSM | 139 | 08:00 | 130 | 17:00
Kaliakoir | 135 | 04:00 | 125 | 12:00 | Sunamganj | 131 | 05:00 | 125 | 13:00
Kallyanpur | 136 | 01:00 | 127 | 12:00 | Sylhet | 132 | 05:00 | 127 | 13:00
Kalurghat | 135 | 05:00 | 129 | 16:00 | Sylhet-132 | 132 | 07:00 | 128 | 14:00
Kamrangirchar | 137 | 05:00 | 125 | 12:00 | Tangail | 134 | 21:00 | 114 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 21:00 | 114 | 14:00
Kasba | 130 | 06:00 | 120 | 12:00 | TK | 136 | 19:30 | 131 | 12:00
Kazla | 135 | 05:00 | 124 | 13:00 | Tongi | 138 | 19:30 | 129 | 13:00
Keranigonj | 138 | 06:00 | 127 | 12:00 | Ullahpara | 135 | 05:00 | 127 | 12:00
Khagrachori | 135 | 06:00 | 127 | 12:00 | Ullon | 136 | 04:00 | 125 | 11:00
Khulna | 137 | 06:00 | 124 | 19:00 | Uttara | 136 | 05:00 | 126 | 12:00
Khulna(S) | 139 | 06:00 | 127 | 17:00 | UttaraNew | 139 | 03:00 | 126 | 11:00
Khulshi | 133 | 02:00 | 126 | 12:00 | Zigatola | 137 | 05:00 | 127 | 12:00
Kishoreganj | 132 | 05:00 | 119 | 17:00
Kodda | 134 | 04:00 | 120 | 11:00
KSRM | 135 | 05:00 | 128 | 13:00
Kulaura | 134 | 05:00 | 129 | 14:00
Kurigram | 132 | 01:00 | 116 | 09:00
Kushtia | 134 | 03:00 | 126 | 12:00
Lalbag | 137 | 05:00 | 126 | 12:00
Lalmonirhat | 130 | 21:00 | 116 | 14:00
Madanganj | 131 | 18:30 | 120 | 17:00
Madaripur | 138 | 07:00 | 132 | 14:00
Madartek | 137 | 06:00 | 124 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division