## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-03-2025 | during | 27-03-2025 | during | 27-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 22 | 32 | 97.3 | 97.3 | 32 | 32 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 322 | 326 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 295 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 194 | 98 | 208.13 | 208.13 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 204 | 324 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 108 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13.5 | 12.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 26 | 28 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 51 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 90 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 450 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2294.5 | 2660.5 | 5274.5 | 5240.5 | 3819.31 | 3785.31
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 86 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 42 | 35 | 2 | 33 | 2 | 33 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.02 | 0 | 4.02 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 805 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 0 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 575 | 575 | 575 | 770 | 770 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1502 | 1978 | 3264.74 | 3270.72 | 3459.74 | 3465.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 192 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 351 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 115 | 88 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 80 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 32 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 25 | 163 | 163 | 30 | 30 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 40 | 155 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 98 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 31 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 38 | 79 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1419 | 1532 | 2410.99 | 2345.99 | 2222.55 | 2157.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-03-2025 | during | 27-03-2025 | during | 27-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 60 | 210 | 210 | 41 | 41 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 164 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 106 | 116 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.54 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 294.54 | 352 | 653.6 | 601.5 | 484.6 | 432.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 40 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 134 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 161 | 158 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 360 | 377 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1535 | 1544 | 1613 | 1613 | 1553 | 1553
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 919 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90.72 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 409 | 618 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1419.72 | 1537 | 3604.2 | 3512.2 | 1907.02 | 1815.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 112 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 852 | 1242 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.63 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1495.63 | 1899 | 2171.12 | 2171.12 | 2159.12 | 2159.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 177 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 209 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 181 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 393 | 405 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.19 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 818.59 | 1359.05 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.08 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1899.36 | 2336.55 | 3109.15 | 2942.53 | 3067.36 | 2900.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 59 | 58 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 160 | 150 | 150 | 162 | 162 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 194 | 0 | 194 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 504.9 | 440 | 702.4 | 472 | 680.42 | 450.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12364.65 | 14279.05 | 22803.7 | 22169.56 | 19353.12 | 18718.98
Forecast Scenario (27-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13000 |  | 0 |  | 13000
|  |  |  | 1:00 | 12530 |  | 0 |  | 12530
|  |  |  | 2:00 | 12090 |  | 0 |  | 12090
|  |  |  | 3:00 | 12450 |  | 0 |  | 12450
|  |  |  | 4:00 | 12440 |  | 0 |  | 12440
|  |  |  | 5:00 | 11190 |  | 0 |  | 11190
|  |  |  | 6:00 | 10500 |  | 0 |  | 10500
|  |  |  | 7:00 | 10770 |  | 0 |  | 10770
|  |  |  | 8:00 | 11530 |  | 0 |  | 11530
|  |  |  | 9:00 | 12080 |  | 0 |  | 12080
|  |  |  | 10:00 | 12640 |  | 0 |  | 12640
|  |  |  | 11:00 | 12950 |  | 0 |  | 12950
|  |  |  | 12:00 | 13430 |  | 0 |  | 13430
|  |  |  | 13:00 | 13750 |  | 0 |  | 13750
|  |  |  | 14:00 | 13950 |  | 0 |  | 13950
|  |  |  | 15:00 | 14000 |  | 0 |  | 14000
|  |  |  | 16:00 | 13910 |  | 0 |  | 13910
|  |  |  | 17:00 | 13960 |  | 0 |  | 13960
|  |  |  | 18:00 | 14140 |  | 0 |  | 14140
|  |  |  | 18:30 | 14300 |  | 0 |  | 14300
|  |  |  | 19:00 | 14420 |  | 0 |  | 14420
|  |  |  | 19:30 | 14560 |  | 0 |  | 14560
|  |  |  | 20:00 | 14000 |  | 0 |  | 14000
|  |  |  | 21:00 | 14320 |  | 0 |  | 14320
|  |  |  | 22:00 | 14350 |  | 0 |  | 14350
|  |  |  | 23:00 | 13710 |  | 0 |  | 13710
Probable Maximum Temperature: |  |  | 38.30°C
Probable Maximum Demand at Day Peak: |  |  | 13430.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14560.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14560.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.11 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 10:49 hrs on 27-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-03-2025 | [28 empty] | Date: | 26-03-2025 | [28 empty] | Date: | 26-03-2025 | [28 empty] | Date: | 26-03-2025 | [28 empty] | Date: | 26-03-2025 | [17 empty] | Date: | 26-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 323 | 0 | 0 | 0 | 36 | 0 | 53 | 80 | 0 | 0 | 35 | 108 | 32 | 100 | 400 | 275 | 583 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 90 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 98 | 0 | 0 | 46 | 34 | 27 | 575 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 100 | 68 | 0 | 359 | 285 | 10 | 221 | 26 | 24 | 25 | 51 | 1 | 20 | 34 | 68 | 16 | 0 | 32 | 315 | 320 | 347 | 40 | 38 | 5 | 156 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 17 | 75 | 147 | 19 | 0 | 0 | 12 | 7436 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 927 | 0 | 0 | 0 | 70 | 0 | 8.9 | 35 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 206 | 0 | 203 | 0 | 383 | 0 | 0 | 2.5 | 162 | 60 | 35 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 220 | 0 | 0 | 1120 | 0 | 5578.4 | 13014.4 | 85.69
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 327 | 0 | 0 | 15 | 36 | 0 | 53 | 80 | 0 | 0 | 0 | 54 | 32 | 50 | 350 | 277 | 585 | 0 | 0 | 16 | 13 | 98 | 0 | 0 | 70 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 98 | 0 | 0 | 46 | 0 | 36 | 575 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 50 | 68 | 0 | 360 | 285 | 10 | 182 | 36 | 17 | 24 | 51 | 0 | 20 | 34 | 64 | 16 | 0 | 32 | 285 | 320 | 347 | 40 | 40 | 5 | 151 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 0 | 75 | 59 | 20 | 0 | 0 | 12 | 6965 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 0 | 1204 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 204 | 0 | 205 | 0 | 318 | 0 | 0 | 2.5 | 157 | 61 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 108 | 220 | 0 | 0 | 1020 | 0 | 5380.4 | 12345.4 | 85.68
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 322 | 0 | 0 | 17 | 36 | 0 | 39 | 80 | 0 | 0 | 0 | 17 | 32 | 34 | 350 | 286 | 460 | 0 | 0 | 18 | 13 | 99 | 0 | 0 | 70 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 98 | 0 | 0 | 46 | 0 | 37 | 576 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 68 | 0 | 300 | 285 | 10 | 181 | 36 | 17 | 22 | 51 | 0 | 20 | 34 | 60 | 16 | 0 | 32 | 300 | 320 | 302 | 40 | 40 | 5 | 137 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 0 | 75 | 59 | 20 | 0 | 0 | 7 | 6601 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 1223 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 204 | 0 | 202 | 0 | 318 | 0 | 0 | 2.5 | 161 | 61 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 108 | 180 | 0 | 0 | 1010 | 0 | 5251.4 | 11852.4 | 85.67
03:00 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 22 | 322 | 0 | 0 | 17 | 36 | 0 | 34 | 114 | 0 | 0 | 0 | 17 | 32 | 34 | 350 | 277 | 460 | 0 | 0 | 18 | 220 | 99 | 0 | 0 | 70 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 37 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 51 | 0 | 68 | 0 | 300 | 285 | 10 | 181 | 36 | 19 | 22 | 51 | 0 | 20 | 34 | 66 | 16 | 0 | 32 | 290 | 320 | 310 | 40 | 40 | 5 | 132 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 0 | 75 | 72 | 21 | 0 | 0 | 12 | 6761 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 1210 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 207 | 0 | 202 | 0 | 319 | 0 | 0 | 2.5 | 160 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 108 | 180 | 0 | 0 | 1040 | 0 | 5331.4 | 12092.4 | 85.66
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 22 | 319 | 0 | 0 | 0 | 17 | 0 | 17 | 144 | 0 | 0 | 0 | 0 | 32 | 0 | 400 | 298 | 540 | 0 | 0 | 18 | 223 | 99 | 0 | 0 | 52 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 38 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 68 | 0 | 360 | 285 | 10 | 188 | 36 | 51 | 25 | 51 | 0 | 20 | 17 | 64 | 8 | 0 | 0 | 300 | 320 | 301 | 39 | 40 | 5 | 133 | 24 | 0 | 86 | 30 | 0 | 18 | 161 | 0 | 69 | 135 | 21 | 0 | 0 | 12 | 6805 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 1158 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 209 | 0 | 205 | 0 | 388 | 0 | 0 | 2.5 | 162 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 8 | 108 | 220 | 0 | 0 | 1022 | 0 | 5294.4 | 12099.4 | 85.65
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 340 | 280 | 470 | 0 | 0 | 23 | 225 | 80 | 0 | 0 | 17 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 68 | 0 | 360 | 285 | 10 | 181 | 36 | 34 | 25 | 17 | 0 | 20 | 0 | 30 | 0 | 0 | 0 | 285 | 320 | 301 | 39 | 40 | 5 | 132 | 24 | 0 | 5 | 20 | 0 | 18 | 161 | 0 | 45 | 135 | 23 | 0 | 0 | 12 | 6116 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 999 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 209 | 0 | 204 | 0 | 318 | 0 | 0 | 2.5 | 163 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 108 | 180 | 0 | 0 | 825 | 0 | 4773.4 | 10889.4 | 85.64
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 340 | 280 | 420 | 0 | 0 | 24 | 224 | 80 | 0 | 0 | 0 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 68 | 0 | 320 | 285 | 10 | 181 | 36 | 0 | 25 | 0 | 0 | 20 | 0 | 32 | 0 | 0 | 0 | 290 | 320 | 303 | 39 | 40 | 5 | 132 | 24 | 0 | 5 | 20 | 0 | 18 | 160 | 0 | 45 | 85 | 23 | 0 | 0.1 | 12 | 5783.1 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 897 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 150 | 0 | 150 | 0 | 318 | 0 | 0 | 2.5 | 162 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 108 | 180 | 0 | 0 | 762 | 0 | 4438.4 | 10221.5 | 85.63
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 340 | 303 | 420 | 0 | 0 | 26 | 220 | 80 | 0 | 4 | 0 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 2 | 51 | 0 | 68 | 0 | 320 | 285 | 10 | 201 | 36 | 0 | 30 | 0 | 0 | 20 | 0 | 30 | 0 | 9 | 0 | 305 | 320 | 331 | 40 | 40 | 5 | 135 | 24 | 0 | 5 | 20 | 0 | 18 | 160 | 0 | 45 | 85 | 23 | 0 | 7.06 | 12 | 5749.06 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 415 | 0 | 899 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 11 | 0 | 7.08 | 155 | 0 | 150 | 0 | 150 | 0 | 358 | 0 | 0.6 | 2.5 | 162 | 61 | 0 | 3 | 0 | 0 | 0 | 0.4 | 23 | 0 | 0 | 150 | 5 | 120 | 180 | 0 | 0 | 696 | 0 | 4487.48 | 10236.54 | 85.62
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 340 | 312 | 420 | 0 | 0 | 26 | 216 | 80 | 0 | 11 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 42 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 6 | 51 | 0 | 68 | 0 | 320 | 285 | 10 | 213 | 36 | 0 | 30 | 0 | 0 | 20 | 0 | 28 | 0 | 25 | 0 | 320 | 320 | 405 | 40 | 40 | 5 | 143 | 8 | 0 | 5 | 20 | 0 | 18 | 160 | 0 | 45 | 85 | 23 | 1 | 21.18 | 12 | 5886.18 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 413 | 0 | 827.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 21.59 | 156 | 0 | 150 | 0 | 150 | 0 | 382 | 0 | 1.8 | 5.5 | 162 | 61 | 0 | 11 | 0 | 0 | 0 | 2.5 | 69 | 0 | 0 | 150 | 5 | 130 | 180 | 0 | 0 | 697 | 0 | 4515.36 | 10401.54 | 85.61
09:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 420 | 253 | 583 | 0 | 0 | 8 | 216 | 80 | 0 | 19 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 42 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735 | 11 | 51 | 0 | 68 | 0 | 360 | 285 | 11 | 191 | 33 | 1 | 25 | 1 | 0 | 20 | 0 | 30 | 0 | 44 | 0 | 305 | 320 | 355 | 40 | 40 | 5 | 149 | 16 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 69 | 134 | 11 | 2 | 34.51 | 12 | 6259.51 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 414 | 0 | 824.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 36.18 | 156 | 0 | 157 | 0 | 165 | 0 | 397 | 0 | 0 | 5.5 | 122 | 61 | 4 | 19 | 10 | 0 | 0 | 4.3 | 110 | 0.37 | 0 | 200 | 5 | 112 | 220 | 0 | 0 | 714 | 0 | 4729.87 | 10989.38 | 85.6
10:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 328 | 0 | 0 | 0 | 11 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 420 | 209 | 583 | 0 | 0 | 21 | 214 | 199 | 0 | 24 | 25 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 42 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 15 | 51 | 6 | 68 | 0 | 357 | 285 | 28 | 189 | 35 | 19 | 23 | 17 | 0 | 14 | 7 | 38 | 0 | 57 | 0 | 305 | 320 | 358 | 40 | 40 | 5 | 153 | 16 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 87 | 87 | 18 | 2 | 43.13 | 12 | 6519.13 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.76 | 413 | 0 | 828.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 47.15 | 156 | 0 | 155 | 0 | 180 | 0 | 391 | 0 | 0 | 5.5 | 118 | 60 | 35 | 26 | 34 | 0 | 0 | 5.7 | 145 | 0.57 | 0 | 241 | 5 | 112 | 220 | 0 | 0 | 760 | 0 | 5021.18 | 11540.31 | 85.59
11:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 328 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 420 | 210 | 583 | 0 | 0 | 20 | 210 | 196 | 0 | 29 | 35 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 42 | 574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 16 | 51 | 60 | 86 | 0 | 353 | 285 | 30 | 192 | 34 | 34 | 25 | 33 | 0 | 20 | 34 | 32 | 0 | 65 | 0 | 310 | 320 | 380 | 40 | 40 | 5 | 153 | 24 | 0 | 83 | 30 | 0 | 18 | 161 | 0 | 107 | 89 | 16 | 2 | 47.27 | 12 | 6795.77 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.19 | 408 | 0 | 820.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 54.58 | 156 | 0 | 155 | 0 | 180 | 0 | 393 | 0 | 4.82 | 5.5 | 118 | 60 | 35 | 31 | 34 | 0 | 0 | 6.6 | 167 | 0.6 | 0 | 307 | 6 | 108 | 220 | 0 | 0 | 757 | 0 | 5134.55 | 11930.32 | 85.58
12:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 322 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 420 | 299 | 583 | 0 | 0 | 26 | 204 | 194 | 0 | 30 | 35 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 42 | 576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 17 | 51 | 80 | 115 | 0 | 351 | 285 | 30 | 192 | 34 | 38 | 30 | 40 | 0 | 17 | 52 | 36 | 0 | 68 | 0 | 300 | 320 | 360 | 40 | 40 | 5 | 153 | 24 | 0 | 84 | 30 | 0 | 18 | 161 | 0 | 106 | 95 | 30 | 2 | 49.54 | 12 | 7045.04 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.72 | 409 | 0 | 818.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 56.08 | 156 | 0 | 205 | 0 | 175 | 0 | 393 | 0 | 5.19 | 5.5 | 158 | 59 | 35 | 33 | 34 | 0 | 0 | 6.9 | 179 | 0.63 | 0 | 307 | 4 | 112 | 220 | 0 | 0 | 852 | 0 | 5319.61 | 12364.65 | 85.57
13:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 22 | 317 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 298 | 583 | 0 | 0 | 13 | 0 | 193 | 0 | 29 | 52 | 13.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992 | 16 | 51 | 80 | 118 | 0 | 333 | 285 | 30 | 209 | 33 | 51 | 30 | 66 | 0 | 19 | 52 | 44 | 0 | 63 | 0 | 310 | 320 | 389 | 39 | 40 | 5 | 153 | 24 | 0 | 84 | 30 | 0 | 18 | 161 | 0 | 106 | 113 | 29 | 2 | 48.61 | 12 | 7152.11 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.98 | 464 | 0 | 916.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 56.28 | 156 | 0 | 204 | 0 | 184 | 0 | 405 | 0 | 4.97 | 5.5 | 162 | 59 | 35 | 33 | 34 | 0 | 0 | 6.7 | 175 | 0.62 | 0 | 307 | 7 | 120 | 220 | 0 | 0 | 1033 | 0 | 5700.16 | 12852.27 | 85.56
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 315 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 296 | 583 | 0 | 0 | 13 | 21 | 192 | 0 | 25 | 52 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 15 | 51 | 0 | 137 | 0 | 345 | 285 | 30 | 196 | 32 | 51 | 30 | 108 | 0 | 16 | 70 | 46 | 0 | 56 | 0 | 305 | 320 | 371 | 39 | 38 | 5 | 152 | 24 | 0 | 83 | 30 | 0 | 18 | 161 | 0 | 88 | 105 | 41 | 2 | 44.97 | 8 | 7130.97 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.15 | 516 | 0 | 1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 45.29 | 156 | 0 | 203 | 0 | 190 | 0 | 394 | 0 | 4.21 | 5.5 | 163 | 59 | 35 | 29 | 34 | 0 | 0 | 6.2 | 151 | 0.55 | 0 | 307 | 8 | 116 | 220 | 0 | 0 | 1212 | 0 | 6040.9 | 13171.87 | 85.55
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 22 | 315 | 0 | 0 | 0 | 17 | 0 | 22 | 20 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 299 | 583 | 0 | 0 | 26 | 1 | 190 | 0 | 17 | 70 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 12 | 51 | 0 | 137 | 0 | 335 | 285 | 30 | 208 | 32 | 50 | 30 | 120 | 0 | 16 | 70 | 42 | 0 | 41 | 0 | 320 | 320 | 391 | 39 | 38 | 5 | 152 | 24 | 0 | 83 | 30 | 0 | 18 | 159 | 0 | 77 | 103 | 41 | 1 | 34.84 | 7 | 7152.84 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.31 | 510 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 34.48 | 156 | 0 | 203 | 0 | 188 | 0 | 406 | 0 | 3.06 | 5.5 | 160 | 59 | 35 | 22 | 34 | 0 | 0 | 4.5 | 113 | 0.38 | 0 | 307 | 8 | 120 | 220 | 0 | 0 | 1244 | 0 | 5994.23 | 13147.07 | 85.54
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 311 | 0 | 0 | 29 | 17 | 0 | 33 | 47 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 297 | 583 | 0 | 0 | 26 | 1 | 192 | 0 | 10 | 70 | 11.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 42 | 576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 8 | 51 | 0 | 88 | 0 | 347 | 285 | 30 | 204 | 32 | 51 | 30 | 120 | 0 | 16 | 70 | 44 | 7 | 27 | 0 | 315 | 320 | 366 | 40 | 38 | 5 | 152 | 24 | 0 | 84 | 25 | 0 | 18 | 161 | 0 | 87 | 122 | 42 | 1 | 20.3 | 12 | 7196.8 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2 | 511 | 0 | 1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 20.64 | 156 | 0 | 203 | 0 | 183 | 0 | 390 | 0 | 1.86 | 5.5 | 160 | 59 | 35 | 13 | 34 | 0 | 0 | 2.5 | 73 | 0.26 | 0 | 307 | 8 | 120 | 220 | 0 | 0 | 1242 | 0 | 5949.96 | 13146.76 | 85.53
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 309 | 0 | 0 | 54 | 17 | 0 | 33 | 62 | 0 | 0 | 9 | 35 | 30 | 8 | 450 | 298 | 583 | 0 | 17 | 26 | 98 | 193 | 0 | 4 | 76 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 2 | 51 | 0 | 88 | 0 | 348 | 285 | 30 | 194 | 32 | 58 | 30 | 120 | 0 | 17 | 70 | 44 | 16 | 10 | 30 | 315 | 320 | 350 | 40 | 38 | 5 | 152 | 24 | 0 | 84 | 25 | 0 | 18 | 161 | 0 | 87 | 140 | 42 | 0 | 7.53 | 12 | 7403.53 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.81 | 559 | 0 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 6.96 | 162 | 0 | 203 | 0 | 185 | 0 | 377 | 0 | 0.62 | 5.5 | 160 | 57 | 35 | 5 | 34 | 0 | 0 | 1.1 | 25 | 0.1 | 0 | 307 | 8 | 110 | 220 | 0 | 0 | 1202 | 0 | 5883.09 | 13286.62 | 85.52
18:00 | 0 | 23 | 9 | 0 | 0 | 0 | 0 | 32 | 309 | 0 | 0 | 54 | 17 | 0 | 33 | 108 | 0 | 0 | 54 | 35 | 30 | 16 | 400 | 294 | 583 | 0 | 35 | 26 | 310 | 138 | 0 | 0 | 108 | 12 | 12 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 20 | 0 | 0 | 46 | 0 | 35 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 88 | 0 | 320 | 285 | 30 | 204 | 33 | 71 | 25 | 120 | 1 | 17 | 70 | 48 | 16 | 0 | 31 | 300 | 320 | 325 | 39 | 38 | 5 | 152 | 24 | 0 | 84 | 25 | 0 | 18 | 159 | 0 | 115 | 161 | 31 | 0 | 0.4 | 12 | 7653.4 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 562 | 0 | 1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 180 | 0 | 205 | 0 | 173 | 0 | 379 | 0 | 0 | 5.5 | 162 | 59 | 51 | 0 | 100 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 250 | 9 | 110 | 180 | 0 | 0 | 1152 | 0 | 5758.73 | 13412.13 | 85.51
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 32 | 307 | 0 | 0 | 54 | 17 | 0 | 33 | 108 | 0 | 0 | 55 | 50 | 30 | 16 | 450 | 297 | 583 | 0 | 35 | 28 | 318 | 98 | 0 | 0 | 116 | 12 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 5 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 35 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 353 | 285 | 30 | 213 | 33 | 91 | 25 | 122 | 28 | 17 | 70 | 42 | 16 | 0 | 31 | 310 | 320 | 313 | 40 | 38 | 5 | 145 | 24 | 0 | 84 | 25 | 0 | 18 | 159 | 0 | 115 | 162 | 31 | 0 | 0 | 12 | 7975 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 0 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 207 | 0 | 172 | 0 | 388 | 0 | 0 | 5.5 | 162 | 58 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 110 | 220 | 0 | 0 | 1132 | 0 | 5968.5 | 13943.5 | 85.5
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 32 | 310 | 0 | 0 | 54 | 17 | 0 | 45 | 108 | 0 | 0 | 55 | 90 | 30 | 16 | 450 | 289 | 583 | 0 | 35 | 28 | 320 | 99 | 0 | 0 | 150 | 12 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 0 | 0 | 0 | 96 | 0 | 0 | 46 | 0 | 35 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 354 | 285 | 30 | 200 | 34 | 90 | 25 | 155 | 28 | 17 | 98 | 40 | 16 | 0 | 31 | 310 | 320 | 346 | 40 | 38 | 5 | 135 | 24 | 0 | 85 | 30 | 0 | 18 | 159 | 0 | 116 | 163 | 31 | 0 | 0 | 12 | 8171 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 208 | 0 | 169 | 0 | 320 | 0 | 0 | 5.5 | 161 | 59 | 110 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 110 | 220 | 0 | 0 | 1200 | 0 | 5955.5 | 14126.5 | 85.5
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 32 | 311 | 0 | 0 | 54 | 17 | 0 | 48 | 108 | 0 | 0 | 55 | 90 | 30 | 16 | 450 | 290 | 450 | 0 | 35 | 28 | 320 | 98 | 0 | 0 | 160 | 12.5 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 0 | 0 | 0 | 96 | 0 | 0 | 46 | 0 | 35 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 354 | 285 | 30 | 187 | 34 | 89 | 25 | 155 | 30 | 19 | 98 | 42 | 16 | 0 | 31 | 300 | 320 | 365 | 40 | 38 | 5 | 137 | 24 | 0 | 85 | 30 | 0 | 18 | 159 | 0 | 116 | 163 | 52 | 0 | 0 | 12 | 8074.5 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 208 | 0 | 171 | 0 | 337 | 0 | 0 | 5.5 | 161 | 58 | 115 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 0 | 1202 | 0 | 5929.5 | 14004 | 85.49
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 32 | 326 | 0 | 0 | 0 | 17 | 0 | 51 | 108 | 0 | 0 | 55 | 90 | 30 | 16 | 450 | 295 | 450 | 0 | 35 | 28 | 324 | 98 | 0 | 0 | 160 | 12.5 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 46 | 0 | 35 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 356 | 285 | 30 | 188 | 35 | 79 | 25 | 155 | 31 | 19 | 98 | 44 | 16 | 0 | 32 | 315 | 320 | 377 | 40 | 38 | 5 | 134 | 24 | 0 | 85 | 30 | 0 | 18 | 158 | 0 | 116 | 164 | 60 | 0 | 0 | 12 | 8066.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1359.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 209 | 0 | 181 | 0 | 405 | 0 | 0 | 5.5 | 160 | 58 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1242 | 0 | 6212.55 | 14279.05 | 85.48
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 32 | 326 | 0 | 0 | 0 | 17 | 0 | 51 | 80 | 0 | 0 | 17 | 90 | 30 | 0 | 450 | 291 | 583 | 0 | 17 | 28 | 325 | 100 | 0 | 0 | 160 | 10 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 46 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 360 | 285 | 30 | 183 | 35 | 45 | 25 | 120 | 29 | 20 | 114 | 44 | 16 | 0 | 32 | 310 | 320 | 346 | 40 | 38 | 5 | 134 | 24 | 0 | 85 | 30 | 0 | 18 | 159 | 0 | 115 | 155 | 62 | 0 | 0 | 12 | 8006 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 1356.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 210 | 0 | 180 | 0 | 386 | 0 | 0 | 5.5 | 126 | 58 | 75 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1244 | 0 | 6085.62 | 14091.62 | 85.47
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 32 | 325 | 0 | 0 | 0 | 35 | 0 | 40 | 48 | 0 | 0 | 0 | 72 | 30 | 0 | 450 | 304 | 583 | 0 | 0 | 30 | 329 | 100 | 0 | 0 | 90 | 12.5 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 46 | 0 | 43 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 355 | 285 | 30 | 176 | 36 | 34 | 25 | 120 | 29 | 20 | 114 | 40 | 16 | 0 | 32 | 305 | 320 | 385 | 40 | 38 | 5 | 134 | 24 | 0 | 85 | 0 | 0 | 18 | 159 | 0 | 115 | 155 | 60 | 0 | 0 | 12 | 7823.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 1251.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 212 | 0 | 176 | 0 | 414 | 0 | 0 | 5.5 | 155 | 59 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1244 | 0 | 5929.71 | 13753.21 | 85.46
Total KWH | 0 | 708480 | 236160 | 0 | 0 | 0 | 0 | 632499.67 | 7711200 | 0 | 0 | 324000 | 456480 | 0 | 625536 | 1273920 | 0 | 0 | 289457 | 609120 | 735840 | 235200 | 9625000 | 6826065 | 12676818 | 0 | 213175 | 555700 | 4433356 | 3227000 | 0 | 205688 | 1634400 | 351600 | 312480 | 0 | 0 | 0 | 0 | 83520 | 0 | 103200 | 60390 | 0 | 0 | 792960 | 0 | 24481 | 1094220 | 28400 | 940320 | 13156363.64 | 0 | 0 | 0 | 1441.8 | 74436 | 0 | 0 | 0 | 0 | 23972725 | 121635 | 1117116 | 384727 | 2057455 | 0 | 8617400 | 6898000 | 545760 | 4711000 | 825624 | 976320 | 616330 | 1820160 | 155400 | 436770 | 1214100 | 1025280 | 209803 | 472127 | 358848 | 7407500 | 7713800 | 8745000 | 946000 | 922080 | 113472 | 3460664 | 517752 | 0 | 1669440 | 594048 | 0 | 433000 | 3337500 | 3240 | 2100000 | 2798400 | 720960 | 14600 | 358470 | 282000 | 168933413.11 | 22055272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 648720 | 11847270 | 0 | 25875636 | 0 | 0 | 0 | 36288 | 0 | 70176 | 10464 | 0 | 0 | 696270 | 0 | 386248 | 3903727 | 0 | 4870755 | 0 | 4597036 | 0 | 9009309 | 0 | 26640 | 113832 | 3758000 | 1374982 | 809284 | 227241 | 926217 | 0 | 0 | 47576.28 | 1234080 | 4338 | 0 | 6393000 | 181140 | 2710000 | 5204390 | 0 | 0 | 24741818.18 | 0 | 131759709.46 | 300693122.57

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12364.65 | MW | 12:00 Hr. | Energy Generated |  |  | 300.6931 |  | MKWHr.
| Day Peak Demand |  |  | 12364.65 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 14279.05 | MW | 21:00 Hr. | Energy Demand |  |  | 300.6931 |  | MKWHr.
| Evening Peak Demand |  |  | 14279.05 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 10221.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1029.71 |  | MMCFD
| Maximum Generation of the Day |  |  | 14279.05 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.7452 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 47.0876 | 0 | 6.6059 | 0 | 0 | 0.20569 | 0 | 0 | 53.8992 | Gas | 141.0247 | Gas | 456873960.6245
| Chattogram Zone |  |  | 0.94032 | 37.1291 | 1.0411 | 0 | 1.0942 | 0.14612 | 0 | 0.1032 | 40.4541 | Coal | 85.2442 | Coal | 605276535.8346
| Cumilla Zone |  |  | 25.8255 | 0 | 5.1194 | 0 | 0 | 0.47213 | 1.0253 | 0 | 32.4422 | HFO | 19.8025 | HFO | 340115960.136
| Mymensingh Zone |  |  | 0.72096 | 0 | 5.1836 | 0 | 0 | 0.37307 | 0 | 0 | 6.2777 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8603 | Hydro | 1.0942 | Hydro | 109422
| Khulna Zone |  |  | 0 | 11.8473 | 0 | 0 | 0 | 0.64872 | 22.0553 | 0 | 34.5513 | Solar | 4.4681 | Solar | 72837663.2708
| Barishal Zone |  |  | 8.0955 | 31.1348 | 0 | 0 | 0 | 0.004338 | 0 | 0 | 39.2347 | Import | 48.9562 | Import | 250802990.48
| Rajshahi Zone |  |  | 22.4947 | 0 | 0.11693 | 0 | 0 | 1.1092 | 25.8756 | 0 | 49.5964 | Wind | 0.1032 | Wind | 1510848
| Rangpur Zone |  |  | 0 | 5.133 | 1.7355 | 0 | 0 | 1.5089 | 0 | 0 | 8.3774
| Total |  |  | 141.0247 | 85.2442 | 19.8025 | 0 | 1.0942 | 4.4681 | 48.9562 | 0.1032 | 300.6931
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 456873960.6245 |  | Hydro | 109422
|  |  |  | Coal | 605276535.8346 |  | Solar | 72837663.2708
|  |  |  | HFO | 340115960.136 |  | Import | 250802990.48
|  |  |  | HSD | 0 |  | Wind | 1510848
[5 empty] | Total: | 172,75,27,380 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0553 | Peak Hr Flow | 919.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9171708.8 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.8756 | Peak Hr Flow | 1359.05 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 616 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0253 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 798 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.9562 | Peak Hr Flow | 2322.05 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4743
|  |  |  | Chattogram |  | 0 |  | 1456
|  |  |  | Cumilla |  | 0 |  | 1346
|  |  |  | Mymensingh |  | 0 |  | 1234
|  |  |  | Sylhet |  | 0 |  | 520
|  |  |  | Khulna |  | 0 |  | 1668
|  |  |  | Barishal |  | 0 |  | 406
|  |  |  | Rajshahi |  | 0 |  | 1499
|  |  |  | Rangpur |  | 0 |  | 850
|  |  |  | Total |  | 0 |  | 13722
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1074 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1509.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:34 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO minimum.
| 09:10 | 13:21 | Halishahar 132/33kV S/S 423T(TR-3) HT Scheduled S/D Due to Pdb cable maintenance work
| 10:22 | 16:17 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Bay Extension
|  | 10:33 | Tangail 132/33kV S/S Tr-4 HT is restored.
|  | 10:34 | Tangail 132/33kV S/S Tr-4 LT is restored.
| 11:18 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Demand Full.
|  | 11:23 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt is restored.
| 12:00 |  | Day Peak Generation: 12360 MW.
| 12:25 |  | Siddhirganj CCPP 335 MW GT was shutdown.
| 13:35 |  | Siddhirganj CCPP 335 MW GT was sync.
| 16:25 |  | Siddhirganj CCPP 335 MW ST was sync.
| 18:20 |  | Siddhirganj GT-1 was shut down.
| 21:00 |  | Evening Peak Gen. 14279 MW
| 05:22 |  | Sirajgonj 400 MW CCPP Unit-4 ST Planned Shutdown with remarks:- 60 hours maintenance
outage of the plant for overhauling the lube oil pump of the gas turbine.
| 05:22 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
| 05:34 |  | Sirajgonj 400 MW CCPP Unit-4 GT Planned Shutdown with remarks:- 60 hours maintenance
outage of the plant for overhauling the lube oil pump of the gas turbine.
| 05:34 |  | Sirajganj Unit-4 was forced shut down due to high vibration in Lube oil Pump.
| 05:34 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- GT
| 06:54 |  | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Bay Equipment hot spot | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 06:54 |  | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Bay Equipment hot spot
maintenance.
| 07:01 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Forced S/D Due to Redhot Maintenance | [7 empty] | 40.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:01 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Forced S/D Due to Redhot Maintenance | [7 empty] | 40.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:11 |  | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to High temperature maintenance work
| 07:12 |  | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to High temperature maintenance work
| 07:15 |  | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to Red Hot at 33kV Bus Section
DS (2nd).
| 07:16 |  | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to Red Hot at 33kV Bus section
DS (2nd Section)
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 32 | 632499.67 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 326 | 7711200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9625000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 295 | 6826065 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 98 | 3227000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 4433356 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 108 | 1273920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 289457 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 213175 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12.5 | 351600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 312480 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 735840 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 555700 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 236160 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 625536 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 708480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 235200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 609120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 205688 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 456480 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 450 | 12676818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1634400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2660.5 | 53899174.67
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 1441.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121635 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1094220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 74436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 60390 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 86 | 792960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 940320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 83520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24481 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 28400 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 23972725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 103200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 13156363.64 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1978 | 40454092.44
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4711000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8617400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6898000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 825624 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 545760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 88 | 2057455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1117116 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 384727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 32 | 358848 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 25 | 616330 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 1820160 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 44 | 1025280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 209803 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 436770 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1214100 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 31 | 155400 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 79 | 976320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 472127 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1532 | 32442220
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 60 | 720960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2798400 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 116 | 2100000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 358470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 282000 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 3240 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 352 | 6277670
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 946000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 922080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 134 | 3460664 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 113472 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 594048 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1669440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 158 | 3337500 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 517752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7407500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 377 | 8745000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7713800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1544 | 35860256
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 919 | 22055272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 648720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 618 | 11847270 | U1 under RSD as per BPDB Instruction
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1537 | 34551262
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 181140 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 120 | 2710000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1242 | 24741818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5204390 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6393000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4338 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1899 | 39234686.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 3903727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 209 | 4870755 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 181 | 4597036 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 405 | 9009309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 113832 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 70176 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 36288 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 10464 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1359.05 | 25875636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 386248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 696270 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2336.55 | 49596381
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1374982 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3758000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 926217 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47576.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 809284 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 227241 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1234080 | -
Rangpur Area Total |  |  |  |  | 950 | 440 | 8377380.28
Eastern Grid Total |  |  |  |  | 16921.242 | 8066.5 | 168933413.11
Western Grid Total |  |  |  |  | 11614.5 | 6212.55 | 131759709.46
National Grid Total |  |  |  |  | 28535.742 | 14279.05 | 300693122.57
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9298.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4423.3 | MW
i) Dhaka area |  |  | 4742.75 |  | MW | i) Khulna area |  |  |  | 1668.2 | MW
ii) Chattogram area |  |  | 1456 |  | MW | ii) Barishal area |  |  |  | 406.5 | MW
iii) Cumilla area |  |  | 1346 |  | MW | iii) Rajshahi area |  |  |  | 1498.6 | MW
iv) Mymensingh area |  |  | 1234 |  | MW | iv) Rangpur area |  |  |  | 850 | MW
v) Sylhet area |  |  | 520 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13722.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 17:00 | 67 | Jaldhaka | 80 | 17:00 | 133 | Payra | 28 | 21:00
2 | AKSML | 136 | 01:00 | 68 | Jamalpur | 138 | 18:00 | 134 | Postogola | 48 | 20:00
3 | Aftabnagar | 32 | 18:30 | 69 | Jashore | 142 | 21:00 | 135 | Purbachal | 16 | 18:30
4 | Agargaon | 93 | 21:00 | 70 | Jhenaidah | 128 | 19:00 | 136 | Purbasadipur | 128 | 13:00
5 | Agrabad | 88 | 19:00 | 71 | Joydebpur | 132 | 22:00 | 137 | Rahanpur | 26 | 21:00
6 | Amnura | 51 | 22:00 | 72 | Joypurhat | 67 | 21:00 | 138 | Rahim | 34 | 13:00
7 | Ashuganj | 90 | 21:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 69 | 19:00
8 | BSRM | 199 | 19:30 | 74 | KSRM | 33 | 23:00 | 140 | Rajendrapur | 109 | 22:00
9 | Bagerhat | 80 | 19:00 | 75 | Kabirpur | 193 | 00:00 | 141 | Rajshahi | 96 | 22:00
10 | Bajitpur | 49 | 21:00 | 76 | Kachua | 80 | 21:00 | 142 | Rajshahi-230 | 84 | 21:00
11 | Bakulia | 92 | 19:00 | 77 | Kallyanpur | 99 | 20:00 | 143 | Ramganj | 114 | 19:00
12 | Banani | 26.4 | 18:30 | 78 | Kalurghat | 30 | 00:00 | 144 | Rampur | 38 | 00:00
13 | Bangabhaban | 4 | 09:00 | 79 | Kamrangirchar | 64.82 | 16:00 | 145 | Rangamati | 16 | 19:00
14 | Barapukuria | 67 | 11:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 143 | 18:00
15 | Barguna | 18 | 18:30 | 81 | Kasba | 35 | 21:00 | 147 | Ruppur | 6 | 15:00
16 | Barishal | 94 | 19:30 | 82 | Kazla | 92 | 12:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 84 | 19:00 | 83 | Keranigonj | 73 | 19:00 | 149 | Saidpur | 100 | 18:00
18 | Baroaulia | 55 | 23:00 | 84 | Khagrachori | 34 | 18:30 | 150 | Satkhira | 131 | 19:30
19 | Baroirhat | 56 | 19:00 | 85 | Khulna | 81 | 19:00 | 151 | Satmasjid | 90 | 19:00
20 | Bashundhara | 155 | 19:30 | 86 | Khulshi | 157 | 23:00 | 152 | Savar | 163 | 21:00
21 | BashundharaCement | 13 | 21:00 | 87 | Kishoreganj | 144 | 20:00 | 153 | SevenRings | 17.63 | 20:00
22 | Beanibazar | 60 | 18:30 | 88 | Kodda | 257 | 00:00 | 154 | ShahCement | 35 | 06:00
23 | Benapole | 67 | 21:00 | 89 | Kulaura | 40 | 18:30 | 155 | Shahjadpur | 89 | 21:00
24 | Bhaluka | 142 | 18:00 | 90 | Kurigram | 67 | 18:00 | 156 | Shahjibazar | 117 | 22:00
25 | Bhandaria | 46 | 21:00 | 91 | Kushtia | 114 | 21:00 | 157 | Shahmirpur | 54 | 00:00
26 | Bhangura | 41 | 14:00 | 92 | Lalbag | 59 | 11:00 | 158 | Shariatpur | 75 | 21:00
27 | Bheramara(GK) | 55 | 21:00 | 93 | Lalmonirhat | 63 | 18:00 | 159 | Sherpur | 168 | 18:00
28 | Bhulta | 244 | 23:00 | 94 | MI_Cement | 17.9 | 12:00 | 160 | Shikalbaha | 30 | 23:00
29 | Bog-Sherpur | 66 | 03:00 | 95 | Madanganj | 42 | 00:00 | 161 | Shitalakhya | 72.5 | 16:00
30 | Bogura | 168 | 22:00 | 96 | Madaripur | 99 | 19:00 | 162 | Sholosohor | 36 | 19:00
31 | Borhanuddin | 78 | 21:00 | 97 | Madartek | 79.42 | 23:00 | 163 | Shyampur | 166 | 14:00
32 | Brahmanbaria | 123 | 21:00 | 98 | Madunaghat | 46 | 18:30 | 164 | Siddhirganj | 104 | 00:00
33 | Cantonment | 98 | 19:00 | 99 | Magura | 62 | 19:00 | 165 | Sirajganj | 114 | 19:30
34 | Chandpur | 64 | 20:00 | 100 | Mahasthangarh | 74 | 21:00 | 166 | Sonargaon | 91 | 22:00
35 | Chandraghona | 33 | 19:30 | 101 | Manikganj | 110 | 19:30 | 167 | Sreemongol | 64 | 18:30
36 | Chapai | 68 | 21:00 | 102 | Maniknagar | 54 | 00:00 | 168 | Sreepur | 64 | 21:00
37 | Charsaidpur | 42 | 00:00 | 103 | Matarbari | 47 | 22:00 | 169 | Srinagar | 42.7 | 21:00
38 | Chauddagram | 72 | 18:00 | 104 | Matuail | 62 | 15:00 | 170 | Sunamganj | 49 | 18:30
39 | Chhatak | 33 | 21:00 | 105 | Millgate | 67 | 00:00 | 171 | Sylhet | 31 | 19:00
40 | Chowmuhani | 194 | 19:00 | 106 | Mirpur | 118 | 19:30 | 172 | Sylhet-132 | 107 | 21:00
41 | Chuadanga | 110 | 22:00 | 107 | Mirsorai | 8 | 00:00 | 173 | TK | 21 | 18:30
42 | Coxsbazar | 124 | 18:30 | 108 | Mirzapur | 46 | 19:00 | 174 | Tangail | 192 | 18:00
43 | Cumilla(N) | 173 | 21:00 | 109 | Mithapukur | 62 | 10:00 | 175 | Thakurgaon | 95 | 14:00
44 | Cumilla(S) | 147 | 00:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 113 | 00:00
45 | Daudkandi | 127 | 21:00 | 111 | Mogbazar | 105.8 | 14:00 | 177 | Ullahpara | 32 | 21:00
46 | Dhaka | 34 | 13:00 | 112 | Mongla | 34 | 01:00 | 178 | Ullon | 43 | 20:00
47 | Dhamrai | 112 | 22:00 | 113 | Motijheel | 31 | 21:00 | 179 | Uttara | 73 | 19:30
48 | Dhanmondi | 113 | 20:00 | 114 | Muktagacha | 39 | 18:00 | 180 | UttaraNew | 42 | 23:00
49 | Dohazari | 104 | 21:00 | 115 | Munshiganj | 99 | 20:00 | 181 | Zigatola | 62 | 21:00
50 | Faridpur | 144 | 21:00 | 116 | Muradnagar | 27 | 21:00
51 | Fatullah | 80 | 00:00 | 117 | Mymensingh | 212 | 18:00
52 | Fenchuganj | 34 | 18:30 | 118 | Naogaon | 125 | 21:00
53 | Feni | 108 | 19:00 | 119 | Narail | 57 | 19:30
54 | GPH | 96 | 06:00 | 120 | Narinda | 71 | 13:00
55 | Ghatail | 88 | 18:00 | 121 | Narshingdi | 169 | 21:00
56 | Ghorashal | 13 | 00:00 | 122 | Natore | 150 | 21:00
57 | Ghorashal-230 | 84 | 21:00 | 123 | Nawabganj | 53.2 | 21:00
58 | Goalpara | 28 | 18:30 | 124 | Netrakona | 143 | 03:00
59 | Gollamari | 78 | 20:00 | 125 | New | 66 | 00:00
60 | Gopalganj | 100 | 19:00 | 126 | Niamatpur | 106 | 13:00
61 | Gulshan | 80 | 19:00 | 127 | Noapara | 44 | 19:30
62 | Halishahar | 44 | 03:00 | 128 | PHP | 9 | 00:00
63 | HaripurSBU | 164 | 22:00 | 129 | Pabna | 108 | 19:30
64 | Hasnabad | 77 | 21:00 | 130 | Palashbari | 116 | 18:00
65 | Hathazari | 74 | 21:00 | 131 | Panchagarh | 52 | 18:00
66 | Ishurdi | 65 | 21:00 | 132 | Patuakhali | 67 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13014.4 | 0 |  | 13014.4
1:00 | 12345.4 | 0 |  | 12345.4
2:00 | 11852.4 | 0 |  | 11852.4
3:00 | 12092.4 | 0 |  | 12092.4
4:00 | 12099.4 | 0 |  | 12099.4
5:00 | 10889.4 | 0 |  | 10889.4
6:00 | 10221.5 | 0 |  | 10221.5
7:00 | 10236.54 | 0 |  | 10236.54
8:00 | 10401.54 | 0 |  | 10401.54
9:00 | 10989.38 | 0 |  | 10989.38
10:00 | 11540.31 | 0 |  | 11540.31
11:00 | 11930.32 | 0 |  | 11930.32
12:00 | 12364.65 | 0 |  | 12364.65
13:00 | 12852.27 | 0 |  | 12852.27
14:00 | 13171.87 | 0 |  | 13171.87
15:00 | 13147.07 | 0 |  | 13147.07
16:00 | 13146.76 | 0 |  | 13146.76
17:00 | 13286.62 | 0 |  | 13286.62
18:00 | 13412.13 | 0 |  | 13412.13
19:00 | 13943.5 | 0 |  | 13943.5
19:30 | 14126.5 | 0 |  | 14126.5
20:00 | 14004 | 0 |  | 14004
21:00 | 14279.05 | 0 |  | 14279.05
22:00 | 14091.62 | 0 |  | 14091.62
23:00 | 13753.21 | 0 |  | 13753.21
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7436 | 5578.4 | 13014.4 | DAILY GENERATION CURVE
00:30 | 7200.5 | 5479.4 | 12679.9
01:00 | 6965 | 5380.4 | 12345.4 | 26-03-2025
01:30 | 6783 | 5315.9 | 12098.9
02:00 | 6601 | 5251.4 | 11852.4
02:30 | 6681 | 5291.4 | 11972.4
03:00 | 6761 | 5331.4 | 12092.4
03:30 | 6783 | 5312.9 | 12095.9
04:00 | 6805 | 5294.4 | 12099.4
04:30 | 6460.5 | 5033.9 | 11494.4
05:00 | 6116 | 4773.4 | 10889.4
05:30 | 5949.55 | 4605.9 | 10555.45
06:00 | 5783.1 | 4438.4 | 10221.5
06:30 | 5766.08 | 4462.94 | 10229.02
07:00 | 5749.06 | 4487.48 | 10236.54
07:30 | 5817.62 | 4501.42 | 10319.04
08:00 | 5886.18 | 4515.36 | 10401.54
08:30 | 6072.845 | 4622.615 | 10695.46
09:00 | 6259.51 | 4729.87 | 10989.38
09:30 | 6389.32 | 4875.525 | 11264.845
10:00 | 6519.13 | 5021.18 | 11540.31
10:30 | 6657.45 | 5077.865 | 11735.315
11:00 | 6795.77 | 5134.55 | 11930.32
11:30 | 6920.405 | 5227.08 | 12147.485
12:00 | 7045.04 | 5319.61 | 12364.65
12:30 | 7098.575 | 5509.885 | 12608.46
13:00 | 7152.11 | 5700.16 | 12852.27
13:30 | 7141.54 | 5870.53 | 13012.07
14:00 | 7130.97 | 6040.9 | 13171.87
14:30 | 7141.905 | 6017.565 | 13159.47
15:00 | 7152.84 | 5994.23 | 13147.07
15:30 | 7174.82 | 5972.095 | 13146.915
16:00 | 7196.8 | 5949.96 | 13146.76
16:30 | 7300.165 | 5916.525 | 13216.69
17:00 | 7403.53 | 5883.09 | 13286.62
17:30 | 7528.465 | 5820.91 | 13349.375
18:00 | 7653.4 | 5758.73 | 13412.13
18:30 | 7814.2 | 5863.615 | 13677.815
19:00 | 7975 | 5968.5 | 13943.5
19:30 | 8171 | 5955.5 | 14126.5
20:00 | 8074.5 | 5929.5 | 14004
20:30 | 8070.5 | 6071.025 | 14141.525 |  | Executive Engineer
21:00 | 8066.5 | 6212.55 | 14279.05 |  | Network Operation Division
21:30 | 8036.25 | 6149.085 | 14185.335
22:00 | 8006 | 6085.62 | 14091.62
22:30 | 7914.75 | 6007.665 | 13922.415
23:00 | 7823.5 | 5929.71 | 13753.21

## En-Curve
QF-LDC-12
Date | 26-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3267 | 2353.5 | 919 | 0 | 68 | 927 | 46 | 3954 | 0 | 252.9 | 1227 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3279 | 2317.5 | 918.5 | 0 | 66 | 1065.5 | 46 | 3786.5 | 0 | 242.9 | 958 | 0 | 0 | 0 | 0 | 26-03-2025
01:00 | 3291 | 2281.5 | 918 | 0 | 64 | 1204 | 46 | 3619 | 0 | 232.9 | 689 | 0 | 0 | 0 | 0
01:30 | 3233.5 | 2205.5 | 918 | 0 | 62 | 1213.5 | 46 | 3567 | 0 | 232.9 | 620.5 | 0 | 0 | 0 | 0 | Energy Generated | 300.6931 |  | MKWHr
02:00 | 3176 | 2129.5 | 918 | 0 | 60 | 1223 | 46 | 3515 | 0 | 232.9 | 552 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3285.5 | 2117 | 918.5 | 0 | 63 | 1216.5 | 46 | 3537.5 | 0 | 251.4 | 537 | 0 | 0 | 0 | 0 | Total Energy Requirement | 300.6931 |  | MKWHr
03:00 | 3395 | 2104.5 | 919 | 0 | 66 | 1210 | 46 | 3560 | 0 | 269.9 | 522 | 0 | 0 | 0 | 0
03:30 | 3462 | 2206.5 | 919 | 0 | 65 | 1184 | 46 | 3499.5 | 0 | 258.4 | 455.5 | 0 | 0 | 0 | 0
04:00 | 3529 | 2308.5 | 919 | 0 | 64 | 1158 | 46 | 3439 | 0 | 246.9 | 389 | 0 | 0 | 0 | 0
04:30 | 3472.5 | 2167.5 | 919 | 0 | 47 | 1078.5 | 46 | 3289 | 0 | 152.9 | 322 | 0 | 0 | 0 | 0
05:00 | 3416 | 2026.5 | 919 | 0 | 30 | 999 | 46 | 3139 | 0 | 58.9 | 255 | 0 | 0 | 0 | 0
05:30 | 3336 | 2004.5 | 918.5 | 0 | 31 | 948 | 46 | 3030.5 | 0.05 | 42.4 | 198.5 | 0 | 0 | 0 | 0
06:00 | 3256 | 1982.5 | 918 | 0 | 32 | 897 | 46 | 2922 | 0.1 | 25.9 | 142 | 0 | 0 | 0 | 0
06:30 | 3310 | 2000.5 | 919 | 0 | 31 | 898 | 46 | 2818 | 38.62 | 25.9 | 142 | 0 | 0 | 0 | 0
07:00 | 3364 | 2018.5 | 920 | 0 | 30 | 899 | 46 | 2714 | 77.14 | 25.9 | 142 | 0 | 0 | 0 | 0
07:30 | 3425.5 | 2031 | 895.5 | 0 | 29 | 863.485 | 46 | 2706.5 | 158.605 | 21.45 | 142 | 0 | 0 | 0 | 0
08:00 | 3487 | 2043.5 | 871 | 0 | 28 | 827.97 | 46 | 2699 | 240.07 | 17 | 142 | 0 | 0 | 0 | 0
08:30 | 3482.5 | 2185.5 | 871.5 | 0 | 29 | 826.245 | 46 | 2712.5 | 321.715 | 34 | 186.5 | 0 | 0 | 0 | 0
09:00 | 3478 | 2327.5 | 872 | 0 | 30 | 824.52 | 46 | 2726 | 403.36 | 51 | 231 | 0 | 0 | 0 | 0
09:30 | 3545 | 2319.5 | 895.5 | 0 | 34 | 826.51 | 46 | 2784 | 467.835 | 72 | 274.5 | 0 | 0 | 0 | 0
10:00 | 3612 | 2311.5 | 919 | 0 | 38 | 828.5 | 46 | 2842 | 532.31 | 93 | 318 | 0 | 0 | 0 | 0
10:30 | 3616 | 2329.75 | 919 | 0 | 35 | 824.38 | 46 | 2898 | 574.185 | 98 | 395 | 0 | 0 | 0 | 0
11:00 | 3620 | 2348 | 919 | 0 | 32 | 820.26 | 46 | 2954 | 616.06 | 103 | 472 | 0 | 0 | 0 | 0
11:30 | 3636 | 2403 | 919.5 | 0 | 34 | 819.425 | 46 | 3060 | 621.56 | 103 | 499 | 0 | 0 | 6 | 0
12:00 | 3652 | 2458 | 920 | 0 | 36 | 818.59 | 46 | 3166 | 627.06 | 103 | 526 | 0 | 0 | 12 | 0
12:30 | 3573.5 | 2475 | 919.5 | 0 | 40 | 867.35 | 46 | 3379 | 629.61 | 111.5 | 554.5 | 0 | 0 | 12.5 | 0
13:00 | 3495 | 2492 | 919 | 0 | 44 | 916.11 | 46 | 3592 | 632.16 | 120 | 583 | 0 | 0 | 13 | 0
13:30 | 3494 | 2488.25 | 919 | 0 | 45 | 1019.555 | 46 | 3737 | 579.265 | 106.5 | 558 | 0 | 0 | 19.5 | 0
14:00 | 3493 | 2484.5 | 919 | 0 | 46 | 1123 | 46 | 3882 | 526.37 | 93 | 533 | 0 | 0 | 26 | 0
14:30 | 3499 | 2507 | 919 | 0 | 44 | 1119.5 | 46 | 3893.5 | 468.97 | 104 | 534 | 0 | 0 | 24.5 | 0
15:00 | 3505 | 2529.5 | 919 | 0 | 42 | 1116 | 46 | 3905 | 411.57 | 115 | 535 | 0 | 0 | 23 | 0
15:30 | 3484.5 | 2506.75 | 919 | 0 | 43 | 1159.5 | 46 | 3931.5 | 336.665 | 128.5 | 576 | 0 | 0 | 15.5 | 0
16:00 | 3464 | 2484 | 919 | 0 | 44 | 1203 | 46 | 3958 | 261.76 | 142 | 617 | 0 | 0 | 8 | 0
16:30 | 3492 | 2485.25 | 919 | 0 | 44 | 1235.5 | 46 | 3960.5 | 178.94 | 167.5 | 681 | 0 | 0 | 7 | 0
17:00 | 3520 | 2486.5 | 919 | 0 | 44 | 1268 | 46 | 3963 | 96.12 | 193 | 745 | 0 | 0 | 6 | 0
17:30 | 3573 | 2428 | 918.5 | 0 | 46 | 1263.5 | 46 | 3914 | 50.375 | 236 | 867 | 0 | 0 | 7 | 0
18:00 | 3626 | 2369.5 | 918 | 0 | 48 | 1259 | 46 | 3865 | 4.63 | 279 | 989 | 0 | 0 | 8 | 0
18:30 | 3617.5 | 2420 | 894.5 | 0 | 45 | 1314.5 | 46 | 3973.5 | 2.315 | 301 | 1057 | 0 | 0 | 6.5 | 0
19:00 | 3609 | 2470.5 | 871 | 0 | 42 | 1370 | 46 | 4082 | 0 | 323 | 1125 | 0 | 0 | 5 | 0
19:30 | 3573 | 2453.5 | 872 | 0 | 40 | 1350 | 46 | 4144 | 0 | 357 | 1288 | 0 | 0 | 3 | 0
20:00 | 3630 | 2316 | 871 | 0 | 42 | 1359 | 46 | 4145 | 0 | 367 | 1227 | 0 | 0 | 1 | 0
20:30 | 3700 | 2325 | 895 | 0 | 43 | 1359.025 | 46 | 4164.5 | 0 | 367.5 | 1241 | 0 | 0 | 0.5 | 0
21:00 | 3770 | 2334 | 919 | 0 | 44 | 1359.05 | 46 | 4184 | 0 | 368 | 1255 | 0 | 0 | 0 | 0
21:30 | 3749 | 2394.25 | 919 | 0 | 44 | 1357.585 | 46 | 4168.5 | 0 | 354 | 1153 | 0 | 0 | 0 | 0
22:00 | 3728 | 2454.5 | 919 | 0 | 44 | 1356.12 | 46 | 4153 | 0 | 340 | 1051 | 0 | 0 | 0 | 0
22:30 | 3741.5 | 2465.75 | 919 | 0 | 42 | 1303.665 | 46 | 4133.5 | 0 | 280 | 991 | 0 | 0 | 0 | 0
23:00 | 3755 | 2477 | 919 | 0 | 40 | 1251.21 | 46 | 4114 | 0 | 220 | 931 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 06:00 | 383 | 15:00 | Payra | 421 | 06:00 | 409 | 12:00
Ashuganj | 411 | 6:00 | 387 | 14:00 | Rahanpur | 406 | 00:00 | 380 | 17:00
Bhulta | 406 | 06:00 | 383 | 15:00 | Rampal | 412 | 05:00 | 391 | 21:00
Bibiana | 397 | 04:00 | 387 | 14:00
BIPTC | 398 | 03:00 | 387 | 13:00
Bogura | 390 | 00:00 | 363 | 17:00
Gopalganj | 412 | 06:00 | 391 | 15:00
Kaliakoir | 373 | 04:00 | 357 | 15:00
Madunaghat | 403 | 07:00 | 389 | 16:00
Meghnaghat | 405 | 05:00 | 385 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 05:00 | 222 | 14:00 | Keranigonj | 233 | 06:00 | 219 | 15:00
AKSML | 234 | 05:00 | 222 | 15:00 | Khulna(S) | 239 | 05:00 | 220 | 21:00
Aminbazar | 236 | 05:00 | 222 | 15:00 | Madunaghat | 236 | 05:00 | 227 | 15:00
Ashuganj | 236 | 06:00 | 224 | 14:00 | Madunaghat-400 | 238 | 08:00 | 227 | 15:00
Ashuganj-400 | 236 | 06:00 | 224 | 14:00 | Maniknagar | 229 | 05:00 | 216 | 15:00
Baghabari | 236 | 04:00 | 225 | 17:00 | Meghnaghat | 238 | 05:00 | 229 | 17:00
Barapukuria | 225 | 00:00 | 212 | 17:00 | Meghnaghat-400 | 233 | 05:00 | 221 | 14:00
Barapukuria-230 | 225 | 00:00 | 212 | 17:00 | Mirsorai | 233 | 08:00 | 220 | 15:00
Barishal | 241 | 05:00 | 230 | 15:00 | Rajshahi | 233 | 05:00 | 221 | 10:00
Bheramara | 234 | 05:00 | 222 | 11:00 | Rampal | 237 | 05:00 | 221 | 21:00
Bhulta | 232 | 06:00 | 217 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 04:00 | 221 | 15:00 | Rampura | 229 | 05:00 | 216 | 14:00
BIPTC | 236 | 05:00 | 223 | 10:00 | Shikalbaha | 234 | 07:00 | 221 | 15:00
Bogura | 238 | 00:00 | 222 | 17:00 | Shyampur | 232 | 06:00 | 219 | 15:00
Bogura-400 | 238 | 00:00 | 222 | 17:00 | Siddhirganj | 232 | 05:00 | 219 | 15:00
Borhanuddin | 245 | 06:00 | 236 | 13:00 | Sirajgonj | 242 | 00:00 | 235 | 17:00
BSRM | 231 | 05:00 | 219 | 15:00 | Sreepur | 231 | 00:00 | 223 | 15:00
Cumilla(N) | 229 | 06:00 | 216 | 15:00 | Tongi | 229 | 04:00 | 217 | 15:00
Faridpur | 240 | 07:00 | 226 | 15:00
Fenchuganj | 233 | 05:00 | 227 | 01:00
Ghorashal | 230 | 01:00 | 220 | 14:00
Ghorashal-230 | 230 | 05:00 | 218 | 14:00
Gopalganj | 237 | 05:00 | 223 | 16:00
GPH | 234 | 05:00 | 222 | 15:00
Haripur | 231 | 05:00 | 218 | 15:00
Hasnabad | 230 | 07:00 | 219 | 15:00
Hathazari | 236 | 05:00 | 225 | 14:00
Ishurdi | 236 | 05:00 | 225 | 10:00
Jhenaidah | 234 | 06:00 | 218 | 19:00
Kaliakoir | 234 | 06:00 | 220 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 128 | 14:00 | Madunaghat | 136 | 06:00 | 129 | 15:00
Agargaon | 139 | 05:00 | 130 | 15:00 | Magura | 133 | 05:00 | 122 | 13:00
Agrabad | 134 | 05:00 | 127 | 15:00 | Mahasthangarh | 133 | 00:00 | 120 | 17:00
AKS | 133 | 08:00 | 125 | 15:00 | Manikganj | 132 | 04:00 | 122 | 14:00
Aminbazar | 137 | 04:00 | 129 | 15:00 | Maniknagar | 135 | 05:00 | 126 | 15:00
Amnura | 136 | 05:00 | 122 | 21:00 | Matarbari | 123 | 09:00 | 110 | 19:00
Ashuganj | 138 | 06:00 | 132 | 15:00 | Matuail | 134 | 05:00 | 126.2 | 15:00
Bagerhat | 136 | 06:00 | 118 | 20:00 | Millgate | 137 | 04:00 | 128 | 14:00
Bajitpur | 132 | 05:00 | 123 | 15:00 | Mirpur | 136 | 06:00 | 128 | 13:00
Bakulia | 135 | 07:00 | 128 | 15:00 | Mirzapur | 129 | 04:00 | 119 | 15:00
Banani | 165 | 10:00 | 127 | 15:00 | Mithapukur | 133 | 00:00 | 120 | 17:00
Bangabhaban | 135 | 05:00 | 126 | 14:00 | MI_Cement | 134.2 | 05:00 | 125.6 | 15:00
Barapukuria | 138 | 00:00 | 127 | 17:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 05:00 | 131 | 15:00 | Mogbazar | 139 | 06:00 | 129 | 14:00
Barishal | 136 | 06:00 | 126 | 19:30 | Mongla | 135 | 05:00 | 120 | 21:00
Barishal-230 | 136 | 06:00 | 127 | 21:00 | Motijheel | 135 | 05:00 | 126 | 14:00
Baroaulia | 135 | 07:00 | 128 | 15:00 | Muktagacha | 132 | 22:00 | 116 | 13:00
Baroirhat | 126 | 06:00 | 118 | 15:00 | Munshiganj | 133 | 05:00 | 126 | 14:00
Bashundhara | 137 | 06:00 | 127 | 16:00 | Muradnagar | 129 | 05:00 | 119 | 15:00
BashundharaCement | 134 | 06:00 | 116 | 13:00 | Mymensingh | 143 | 02:00 | 110 | 16:00
Beanibazar | 132 | 06:00 | 126 | 13:00 | Naogaon | 129 | 00:00 | 118 | 17:00
Benapole | 134 | 05:00 | 117 | 21:00 | Narail | 134 | 05:00 | 119 | 21:00
Bhaluka | 128 | 05:00 | 117 | 17:00 | Narinda | 135 | 05:00 | 126 | 15:00
Bhandaria | 133 | 06:00 | 120 | 21:00 | Narshingdi | 131 | 06:00 | 119 | 21:00
Bhangura | 134 | 05:00 | 126 | 17:00 | Natore | 133 | 05:00 | 124 | 17:00
Bheramara | 135 | 05:00 | 127 | 13:00 | Nawabganj | 136 | 05:00 | 127 | 13:00
Bheramara(GK) | 135 | 05:00 | 127 | 17:00 | Netrakona | 125 | 05:00 | 108 | 16:00
Bhulta | 128 | 03:00 | 120 | 15:00 | New | 138 | 04:00 | 129 | 15:00
Bog-Sherpur | 133 | 00:00 | 122 | 17:00 | Niamatpur | 136 | 00:00 | 127 | 19:00
Bogura | 135 | 00:00 | 124 | 17:00 | Noapara | 137 | 06:00 | 121 | 21:00
Bogura-230 | 135 | 00:00 | 124 | 17:00 | Pabna | 135 | 05:00 | 127 | 15:00
Brahmanbaria | 129 | 06:00 | 122 | 15:00 | Palashbari | 130 | 00:00 | 115 | 17:00
Cantonment | 139 | 05:00 | 130 | 15:00 | Panchagarh | 137 | 21:00 | 117 | 09:00
Chandpur | 125 | 19:30 | 116 | 15:00 | Patuakhali | 136 | 08:00 | 132 | 14:00
Chandraghona | 136 | 05:00 | 129 | 15:00 | Payra | 138 | 06:00 | 134 | 13:00
Chapai | 132 | 00:00 | 123 | 20:00 | PHP | 126 | 02:00 | 116 | 15:00
Charsaidpur | 134 | 06:00 | 126 | 14:00 | Postogola | 137 | 05:00 | 128 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 06:00 | 115 | 15:00 | Purbachal | 137 | 04:00 | 128 | 14:00
Chhatak | 132 | 06:00 | 125 | 13:00 | Purbasadipur | 132 | 21:00 | 116 | 08:00
Chowmuhani | 120 | 05:00 | 108 | 15:00 | Rahanpur | 138 | 00:00 | 129 | 17:00
Chuadanga | 133 | 05:00 | 117 | 21:00 | Rahanpur-400 | 138 | 00:00 | 129 | 17:00
Coxsbazar | 123 | 07:00 | 110 | 21:00 | Rahim | 134 | 05:00 | 126 | 15:00
Cumilla(N) | 130 | 05:00 | 122 | 15:00 | Rajbari | 133 | 05:00 | 124 | 15:00
Cumilla(S) | 135 | 05:00 | 119 | 15:00 | Rajendrapur | 129 | 01:00 | 120 | 17:00
Daudkandi | 128 | 04:00 | 118 | 15:00 | Rajshahi | 135 | 05:00 | 126 | 21:00
Dhaka | 138 | 05:00 | 128 | 15:00 | Rajshahi-230 | 134 | 05:00 | 117 | 17:00
Dhamrai | 132 | 03:00 | 123 | 15:00 | Ramganj | 119 | 05:00 | 110 | 15:00
Dhanmondi | 138 | 05:00 | 128.5 | 15:00 | Rampur | 135 | 05:00 | 126 | 15:00
Dohazari | 130 | 05:00 | 122 | 15:00 | Rampura | 138 | 05:00 | 128 | 14:00
Faridpur | 134 | 05:00 | 127 | 15:00 | Rangamati | 136 | 06:00 | 127 | 15:00
Fatullah | 135 | 04:00 | 127 | 15:00 | Rangpur | 131 | 02:00 | 116 | 17:00
Fenchuganj | 135 | 05:00 | 130 | 17:00 | Ruppur | 137 | 06:00 | 129 | 21:00
Feni | 125 | 06:00 | 115 | 16:00 | Saidpur | 132 | 00:00 | 118 | 17:00
Ghatail | 128 | 04:00 | 115 | 13:00 | Satkhira | 136 | 06:00 | 117 | 21:00
Ghorashal | 137 | 05:00 | 130 | 14:00 | Satmasjid | 139 | 05:00 | 130 | 14:00
Goalpara | 136 | 04:00 | 124 | 20:00 | Savar | 135 | 06:00 | 127 | 15:00
Gollamari | 139 | 06:00 | 126 | 19:00 | SevenRings | 137 | 05:00 | 130 | 15:00
Gopalganj | 139 | 06:00 | 127 | 19:00 | ShahCement | 134 | 06:00 | 126 | 14:00
Gopalganj-400 | 140 | 05:00 | 132 | 13:00 | Shahjadpur | 136 | 00:00 | 131 | 17:00
Gulshan | 138 | 06:00 | 128 | 15:00 | Shahjibazar | 131 | 04:00 | 125 | 15:00
Halishahar | 135 | 07:00 | 127 | 15:00 | Shahmirpur | 136 | 06:00 | 128 | 15:00
Haripur | 134 | 05:00 | 126 | 15:00 | Shariatpur | 139 | 06:00 | 129 | 15:00
HaripurSBU | 134 | 05:00 | 126 | 15:00 | Sherpur | 134 | 22:00 | 117 | 13:00
Hasnabad | 136 | 05:00 | 129 | 17:00 | Shikalbaha | 126 | 06:00 | 117 | 16:00
Hathazari | 137 | 03:00 | 130 | 14:00 | Shikalbaha-230 | 137 | 07:00 | 128 | 15:00
Ishurdi | 137 | 05:00 | 130 | 17:00 | Shitalakhya | 134.5 | 06:00 | 125.6 | 15:00
Jaldhaka | 131 | 01:00 | 116 | 17:00 | Sholosohor | 135 | 05:00 | 128 | 15:00
Jamalpur | 139 | 23:00 | 115 | 13:00 | Shyampur | 132 | 09:00 | 127 | 14:00
Jashore | 135 | 05:00 | 119 | 21:00 | Shyampur-230 | 136 | 07:00 | 127 | 14:00
Jhenaidah | 136 | 05:00 | 122 | 21:00 | Siddhirganj | 135 | 06:00 | 127 | 14:00
Jhenaidah-230 | 136 | 05:00 | 124 | 21:00 | Sirajganj | 133 | 02:00 | 122 | 17:00
Joydebpur | 131 | 02:00 | 123 | 16:00 | Sonargaon | 129 | 07:00 | 125 | 00:00
Joypurhat | 128 | 05:00 | 114 | 17:00 | Sreemongol | 130 | 01:00 | 126 | 13:00
Juldah | 135 | 01:00 | 129 | 15:00 | Sreepur | 129 | 00:00 | 122 | 16:00
Kabirpur | 136 | 03:00 | 124 | 15:00 | Srinagar | 137 | 06:00 | 126 | 15:00
Kachua | 125 | 19:30 | 116 | 15:00 | SSM | 139 | 02:00 | 134 | 07:00
Kaliakoir | 136 | 04:00 | 127 | 14:00 | Sunamganj | 130 | 05:00 | 124 | 13:00
Kallyanpur | 137 | 06:00 | 129 | 13:00 | Sylhet | 131 | 04:00 | 127 | 15:00
Kalurghat | 136 | 06:00 | 129 | 14:00 | Sylhet-132 | 132 | 03:00 | 128 | 14:00
Kamrangirchar | 136 | 05:00 | 126 | 15:00 | Tangail | 128 | 04:00 | 116 | 15:00
Kaptai | 135 | 5:00 | 124 | 12:00 | Thakurgaon | 136 | 21:00 | 116 | 09:00
Kasba | 128 | 05:00 | 119 | 14:00 | TK | 138 | 15:00 | 129 | 16:00
Kazla | 135 | 05:00 | 126 | 15:00 | Tongi | 139 | 04:00 | 131 | 15:00
Keranigonj | 137 | 06:00 | 127 | 15:00 | Ullahpara | 133 | 00:00 | 125 | 17:00
Khagrachori | 134 | 07:00 | 125 | 15:00 | Ullon | 138 | 06:00 | 128 | 15:00
Khulna | 137 | 05:00 | 122 | 21:00 | Uttara | 136 | 06:00 | 127 | 15:00
Khulna(S) | 139 | 05:00 | 125 | 20:00 | UttaraNew | 138 | 06:00 | 128 | 14:00
Khulshi | 134 | 06:00 | 126 | 15:00 | Zigatola | 137 | 05:00 | 127 | 15:00
Kishoreganj | 128 | 00:00 | 119 | 17:00
Kodda | 135 | 04:00 | 121 | 15:00
KSRM | 135 | 05:00 | 128 | 14:00
Kulaura | 133 | 04:00 | 129 | 15:00
Kurigram | 130 | 00:00 | 112 | 17:00
Kushtia | 135 | 05:00 | 124 | 13:00
Lalbag | 136 | 05:00 | 126 | 14:00
Lalmonirhat | 128 | 19:00 | 116 | 17:00
Madanganj | 134 | 06:00 | 125 | 14:00
Madaripur | 138 | 06:00 | 131 | 16:00
Madartek | 137 | 05:00 | 127 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division