## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-03-2025 | [28 empty] | Date: | 27-03-2025 | [28 empty] | Date: | 27-03-2025 | [28 empty] | Date: | 27-03-2025 | [28 empty] | Date: | 27-03-2025 | [17 empty] | Date: | 27-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 326 | 0 | 0 | 0 | 36 | 0 | 34 | 95 | 0 | 0 | 0 | 17 | 30 | 0 | 450 | 287 | 583 | 0 | 0 | 30 | 329 | 102 | 0 | 0 | 90 | 13 | 14 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 46 | 0 | 42 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 88 | 0 | 360 | 285 | 30 | 175 | 36 | 31 | 25 | 120 | 0 | 20 | 114 | 42 | 16 | 0 | 32 | 305 | 320 | 350 | 43 | 38 | 5 | 150 | 24 | 0 | 85 | 0 | 0 | 18 | 165 | 0 | 95 | 135 | 59 | 0 | 0 | 12 | 7653 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 1314.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 212 | 0 | 183 | 0 | 388 | 0 | 0 | 5.5 | 152 | 59 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 108 | 220 | 0 | 0 | 1244 | 0 | 5837.35 | 13490.35 | 85.45
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 317 | 0 | 0 | 0 | 36 | 0 | 34 | 95 | 0 | 0 | 0 | 17 | 30 | 0 | 450 | 293 | 500 | 0 | 0 | 30 | 280 | 101 | 0 | 0 | 90 | 13 | 15 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 46 | 0 | 42 | 527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1065 | 0 | 51 | 0 | 88 | 0 | 360 | 285 | 30 | 177 | 36 | 17 | 25 | 120 | 0 | 20 | 114 | 34 | 16 | 0 | 32 | 300 | 320 | 365 | 41 | 38 | 5 | 133 | 24 | 0 | 85 | 0 | 0 | 18 | 163 | 0 | 48 | 58 | 58 | 0 | 0 | 11 | 7192 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 1315.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 212 | 0 | 174 | 0 | 340 | 0 | 0 | 5.5 | 150 | 58 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 108 | 220 | 0 | 0 | 1244 | 0 | 5710.09 | 12902.09 | 85.44
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 312 | 0 | 0 | 0 | 36 | 0 | 27 | 95 | 0 | 0 | 0 | 17 | 30 | 0 | 450 | 288 | 450 | 0 | 0 | 31 | 280 | 102 | 0 | 0 | 90 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 88 | 0 | 360 | 285 | 30 | 180 | 36 | 17 | 25 | 120 | 0 | 20 | 114 | 40 | 16 | 0 | 32 | 300 | 320 | 347 | 41 | 38 | 5 | 133 | 24 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 48 | 58 | 60 | 0 | 0 | 9 | 7098 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 0 | 1206.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 175 | 0 | 318 | 0 | 0 | 5.5 | 152 | 59 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 108 | 180 | 0 | 0 | 1200 | 0 | 5380.61 | 12478.61 | 85.43
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 309 | 0 | 0 | 0 | 36 | 0 | 15 | 95 | 0 | 0 | 0 | 17 | 30 | 0 | 400 | 288 | 500 | 0 | 0 | 31 | 324 | 101 | 0 | 0 | 90 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 88 | 0 | 359 | 285 | 30 | 182 | 36 | 17 | 25 | 120 | 0 | 20 | 114 | 34 | 16 | 0 | 32 | 295 | 320 | 349 | 41 | 38 | 5 | 141 | 24 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 48 | 60 | 62 | 0 | 0 | 12 | 7135 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 1213.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 165 | 0 | 164 | 0 | 387 | 0 | 0 | 5.5 | 152 | 59 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 116 | 220 | 0 | 0 | 1150 | 0 | 5508.91 | 12643.91 | 85.42
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 306 | 0 | 0 | 0 | 23 | 0 | 15 | 48 | 0 | 0 | 0 | 0 | 30 | 0 | 400 | 297 | 500 | 0 | 0 | 31 | 328 | 100 | 0 | 0 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 88 | 0 | 360 | 285 | 30 | 183 | 36 | 44 | 30 | 120 | 0 | 20 | 90 | 36 | 0 | 0 | 32 | 310 | 320 | 377 | 41 | 38 | 5 | 146 | 24 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 69 | 135 | 63 | 0 | 0 | 12 | 7112 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 0 | 1213.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 204 | 0 | 181 | 0 | 407 | 0 | 0 | 5.5 | 152 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 116 | 220 | 0 | 0 | 1002 | 0 | 5442.11 | 12554.11 | 85.41
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 307 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 279 | 583 | 0 | 0 | 32 | 335 | 101 | 0 | 0 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 88 | 0 | 360 | 285 | 30 | 187 | 36 | 51 | 30 | 51 | 0 | 20 | 52 | 36 | 0 | 0 | 32 | 305 | 320 | 361 | 41 | 38 | 5 | 136 | 24 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 45 | 105 | 66 | 0 | 0 | 12 | 6784 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 1109.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 160 | 0 | 181 | 0 | 132 | 0 | 0 | 5.5 | 155 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 116 | 180 | 0 | 0 | 892 | 0 | 4762.49 | 11546.49 | 85.4
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 304 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 302 | 450 | 0 | 0 | 32 | 330 | 101 | 0 | 0 | 90 | 16.6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 40 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 68 | 0 | 320 | 285 | 10 | 190 | 36 | 16 | 30 | 17 | 0 | 20 | 17 | 36 | 0 | 0 | 0 | 305 | 320 | 361 | 41 | 38 | 5 | 139 | 24 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 45 | 45 | 66 | 0 | 0 | 12 | 6180.6 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1022.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 160 | 0 | 186 | 0 | 0 | 0 | 0 | 5.5 | 152 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 116 | 180 | 0 | 0 | 800 | 0 | 4442.95 | 10623.55 | 85.39
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 301 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 306 | 500 | 0 | 0 | 31 | 325 | 100 | 0 | 4 | 90 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 21 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 3 | 51 | 0 | 68 | 0 | 335 | 285 | 10 | 196 | 36 | 17 | 30 | 17 | 0 | 20 | 17 | 30 | 0 | 9 | 0 | 315 | 320 | 405 | 41 | 38 | 5 | 140 | 24 | 0 | 85 | 30 | 0 | 18 | 163 | 0 | 65 | 75 | 66 | 0 | 5.09 | 12 | 6348.09 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.29 | 408 | 0 | 1015.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5.27 | 176 | 0 | 160 | 0 | 185 | 0 | 0 | 0 | 0.48 | 5.5 | 151 | 60 | 0 | 3 | 0 | 0 | 0 | 0.4 | 18 | 0.07 | 0 | 250 | 6 | 130 | 180 | 0 | 0 | 798 | 0 | 4488.62 | 10836.71 | 85.39
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 297 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 340 | 307 | 550 | 0 | 0 | 31 | 326 | 101 | 0 | 10 | 52 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 14 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825 | 8 | 51 | 0 | 86 | 0 | 360 | 285 | 12 | 194 | 36 | 17 | 30 | 17 | 0 | 20 | 17 | 30 | 0 | 24 | 0 | 315 | 320 | 385 | 41 | 38 | 5 | 143 | 24 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 75 | 105 | 64 | 1 | 15.61 | 12 | 6559.61 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.62 | 408 | 0 | 1118.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 17.86 | 180 | 0 | 205 | 0 | 171 | 0 | 0 | 0 | 1.52 | 5.5 | 156 | 60 | 0 | 8 | 0 | 0 | 0 | 1.1 | 49 | 0.22 | 0 | 250 | 5 | 130 | 180 | 0 | 0 | 841 | 0 | 4721.93 | 11281.54 | 85.37
09:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 32 | 296 | 0 | 0 | 0 | 4 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 30 | 0 | 450 | 306 | 583 | 0 | 0 | 30 | 327 | 99 | 0 | 18 | 70 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 46 | 0 | 12 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 13 | 51 | 0 | 115 | 0 | 357 | 285 | 23 | 198 | 36 | 16 | 25 | 17 | 0 | 10 | 17 | 28 | 0 | 39 | 0 | 305 | 320 | 372 | 41 | 38 | 5 | 153 | 16 | 0 | 85 | 30 | 0 | 18 | 165 | 0 | 69 | 119 | 36 | 1 | 27.23 | 12 | 6950.23 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 405 | 0 | 1224.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 32.81 | 180 | 0 | 207 | 0 | 171 | 0 | 0 | 0 | 2.83 | 5.5 | 155 | 60 | 0 | 15 | 0 | 0 | 0 | 3.2 | 86 | 0.39 | 0 | 307 | 6 | 108 | 220 | 0 | 0 | 920 | 0 | 5093.66 | 12043.89 | 85.36
10:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 32 | 307 | 0 | 0 | 0 | 18 | 0 | 87 | 80 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 305 | 583 | 0 | 0 | 30 | 326 | 98 | 0 | 24 | 90 | 23.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 46 | 0 | 12 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 16 | 51 | 0 | 150 | 0 | 351 | 285 | 29 | 195 | 29 | 16 | 30 | 33 | 0 | 12 | 34 | 34 | 0 | 53 | 0 | 310 | 320 | 381 | 41 | 38 | 5 | 158 | 24 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 69 | 135 | 29 | 2 | 37.19 | 12 | 7327.69 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 407 | 0 | 1355.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 43.82 | 181 | 0 | 207 | 0 | 176 | 0 | 0 | 0 | 3.9 | 5.5 | 158 | 58 | 0 | 0 | 0 | 0 | 0 | 3.4 | 122 | 0.52 | 0 | 307 | 6 | 120 | 220 | 0 | 0 | 990 | 0 | 5438.41 | 12766.1 | 85.35
11:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 32 | 323 | 0 | 0 | 17 | 18 | 0 | 87 | 79 | 0 | 0 | 14 | 17 | 22 | 32 | 450 | 300 | 583 | 0 | 0 | 25 | 325 | 98 | 0 | 28 | 90 | 22.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 48 | 0 | 3 | 46 | 0 | 11 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1029 | 19 | 51 | 16 | 180 | 0 | 351 | 285 | 30 | 184 | 35 | 17 | 30 | 80 | 0 | 12 | 70 | 40 | 16 | 60 | 0 | 315 | 320 | 350 | 40 | 38 | 5 | 153 | 24 | 0 | 82 | 30 | 0 | 18 | 164 | 0 | 69 | 135 | 32 | 2 | 43.41 | 12 | 7652.91 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 458 | 0 | 1364.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 51.71 | 182 | 0 | 202 | 0 | 208 | 0 | 0 | 0 | 4.57 | 5.5 | 156 | 58 | 0 | 0 | 0 | 0 | 0 | 5.5 | 145 | 0.6 | 0 | 307 | 7 | 116 | 220 | 0 | 0 | 1076 | 0 | 5669.45 | 13322.36 | 85.34
12:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 32 | 334 | 0 | 0 | 17 | 35 | 0 | 87 | 90 | 0 | 0 | 24 | 122 | 22 | 32 | 450 | 268 | 583 | 0 | 0 | 25 | 321 | 98 | 0 | 29 | 108 | 22.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 72 | 6 | 3 | 46 | 0 | 13 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 18 | 51 | 47 | 180 | 0 | 360 | 285 | 30 | 214 | 34 | 19 | 35 | 93 | 0 | 20 | 90 | 34 | 25 | 64 | 20 | 310 | 320 | 350 | 40 | 38 | 5 | 158 | 24 | 0 | 80 | 30 | 0 | 18 | 146 | 0 | 69 | 118 | 32 | 2 | 44.87 | 12 | 8003.37 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 508 | 15 | 1460.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 52.38 | 181 | 0 | 202 | 0 | 208 | 0 | 0 | 0 | 4.7 | 5.5 | 158 | 58 | 27 | 15 | 36 | 0 | 0 | 3.5 | 156 | 0.61 | 0 | 278 | 7 | 116 | 220 | 0 | 0 | 1101 | 0 | 5923.58 | 13926.95 | 85.33
13:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 32 | 333 | 0 | 0 | 17 | 35 | 0 | 87 | 121 | 45 | 0 | 54 | 144 | 22 | 80 | 450 | 270 | 583 | 0 | 17 | 25 | 315 | 97 | 0 | 28 | 108 | 22.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 74 | 30 | 3 | 46 | 0 | 21 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 18 | 51 | 58 | 170 | 0 | 358 | 285 | 22 | 198 | 34 | 34 | 50 | 120 | 0 | 19 | 98 | 36 | 25 | 62 | 31 | 280 | 320 | 362 | 40 | 37 | 5 | 155 | 24 | 0 | 80 | 30 | 0 | 18 | 146 | 0 | 77 | 114 | 32 | 2 | 42.41 | 12 | 8266.91 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 495 | 17 | 1570.52 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 48.93 | 180 | 0 | 207 | 0 | 198 | 0 | 0 | 0 | 4.52 | 5.5 | 162 | 58 | 52 | 19 | 44 | 0 | 0 | 5.3 | 155 | 0.6 | 0 | 250 | 8 | 116 | 220 | 0 | 0 | 1062 | 0 | 6002.37 | 14269.28 | 85.33
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 333 | 0 | 0 | 17 | 35 | 0 | 87 | 136 | 45 | 0 | 55 | 144 | 22 | 102 | 450 | 288 | 583 | 0 | 17 | 25 | 318 | 96 | 0 | 24 | 108 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 89 | 36 | 3 | 46 | 0 | 19 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 16 | 51 | 73 | 162 | 0 | 348 | 285 | 9 | 196 | 33 | 34 | 50 | 123 | 0 | 7 | 114 | 44 | 25 | 54 | 29 | 305 | 320 | 362 | 40 | 38 | 5 | 153 | 24 | 0 | 79 | 30 | 0 | 18 | 146 | 0 | 78 | 114 | 32 | 2 | 36.08 | 12 | 8442.08 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 512 | 34 | 1571 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 45 | 181 | 0 | 202 | 0 | 205 | 0 | 0 | 0 | 3.74 | 5.5 | 161 | 57 | 52 | 20 | 49 | 0 | 0 | 4.4 | 133 | 0.55 | 0 | 270 | 8 | 116 | 220 | 0 | 0 | 1022 | 0 | 5991.19 | 14433.27 | 85.33
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 334 | 0 | 0 | 17 | 35 | 0 | 88 | 120 | 45 | 0 | 55 | 144 | 22 | 103 | 450 | 293 | 583 | 0 | 35 | 25 | 320 | 96 | 0 | 18 | 125 | 21 | 15 | 0 | 0 | 0 | 5 | 0 | 0 | 2 | 16 | 0 | 0 | 89 | 36 | 2 | 46 | 0 | 22 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 11 | 51 | 75 | 162 | 0 | 343 | 285 | 5 | 209 | 32 | 34 | 50 | 146 | 0 | 19 | 114 | 38 | 25 | 40 | 29 | 305 | 320 | 351 | 41 | 38 | 5 | 152 | 24 | 0 | 79 | 30 | 0 | 18 | 147 | 0 | 77 | 113 | 32 | 1 | 25.81 | 12 | 8456.81 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 621 | 34 | 1366 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 33.21 | 180 | 0 | 200 | 0 | 203 | 0 | 0 | 0 | 2.95 | 5.5 | 161 | 55 | 74 | 16 | 82 | 0 | 0 | 3.6 | 66 | 0.41 | 0 | 307 | 9 | 108 | 220 | 0 | 0 | 1032 | 0 | 5857.67 | 14314.48 | 85.32
16:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 41 | 333 | 0 | 0 | 21 | 35 | 0 | 118 | 134 | 75 | 6 | 55 | 144 | 30 | 103 | 450 | 264 | 583 | 0 | 35 | 16 | 318 | 98 | 0 | 11 | 160 | 22 | 15 | 0 | 0 | 1 | 15 | 1 | 0 | 3 | 16 | 16 | 17 | 89 | 88 | 1 | 46 | 12 | 30 | 575 | 17 | 0 | 3 | 5 | 13 | 0 | 0 | 0 | 0 | 1224 | 7 | 51 | 70 | 108 | 0 | 351 | 285 | 5 | 198 | 32 | 34 | 50 | 164 | 0 | 19 | 114 | 36 | 28 | 24 | 29 | 290 | 320 | 290 | 41 | 37 | 5 | 139 | 24 | 0 | 83 | 30 | 0 | 18 | 147 | 28 | 77 | 134 | 32 | 1 | 14.02 | 12 | 8599.02 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 620 | 35 | 1367 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 39 | 0 | 21.39 | 180 | 0 | 194 | 0 | 142 | 0 | 0 | 0 | 1.9 | 5.5 | 161 | 55 | 74 | 10 | 106 | 0 | 0 | 2.2 | 59 | 0.25 | 0 | 307 | 9 | 88 | 220 | 0 | 0 | 872 | 5 | 5607.24 | 14206.26 | 85.32
17:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 41 | 333 | 0 | 0 | 35 | 35 | 0 | 122 | 137 | 75 | 15 | 55 | 144 | 30 | 103 | 450 | 291 | 583 | 0 | 35 | 25 | 316 | 97 | 0 | 4 | 125 | 22 | 15 | 0 | 0 | 17 | 15 | 9 | 0 | 4 | 17 | 24 | 17 | 96 | 100 | 0 | 46 | 15 | 25 | 575 | 17 | 0 | 5 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 2 | 51 | 70 | 108 | 0 | 349 | 285 | 5 | 184 | 32 | 33 | 50 | 175 | 0 | 19 | 114 | 30 | 16 | 9 | 30 | 310 | 320 | 287 | 41 | 38 | 5 | 145 | 24 | 0 | 83 | 30 | 0 | 18 | 145 | 54.5 | 77 | 152 | 32 | 0 | 4.82 | 12 | 8692.32 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 619 | 35 | 1274 | 0 | 0 | 40 | 50 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8.22 | 180 | 0 | 164 | 0 | 155 | 0 | 0 | 0 | 0.72 | 5.5 | 162 | 55 | 54 | 4 | 82 | 0 | 0 | 0.7 | 23 | 0.1 | 16 | 307 | 8 | 88 | 220 | 0 | 0 | 902 | 17 | 5420.24 | 14112.56 | 85.31
18:00 | 8 | 21 | 10 | 0 | 0 | 0 | 0 | 42 | 350 | 0 | 0 | 35 | 35 | 0 | 122 | 137 | 75 | 15 | 55 | 144 | 30 | 103 | 380 | 296 | 500 | 0 | 35 | 25 | 320 | 98 | 0 | 0 | 125 | 20 | 15 | 0 | 0 | 17 | 15 | 12 | 0 | 9 | 17 | 24 | 17 | 96 | 100 | 0 | 46 | 14 | 37 | 575 | 17 | 0 | 6 | 8 | 17 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 70 | 108 | 0 | 320 | 285 | 5 | 183 | 30 | 63 | 50 | 197 | 6 | 19 | 114 | 34 | 16 | 0 | 30 | 300 | 320 | 288 | 40 | 37 | 5 | 152 | 24 | 0 | 84 | 30 | 0 | 18 | 144 | 54.3 | 115 | 163 | 32 | 0 | 0.38 | 12 | 8572.68 | 916 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 551 | 35 | 1265 | 0 | 0 | 45 | 50 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 0.54 | 178 | 0 | 155 | 0 | 150 | 0 | 0 | 0 | 0.05 | 5.5 | 161 | 55 | 84 | 0 | 107 | 0 | 0 | 0 | 2 | 0.01 | 16 | 250 | 8 | 88 | 220 | 0 | 0 | 1045 | 17 | 5478.1 | 14050.78 | 85.3
19:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 42 | 401 | 0 | 0 | 35 | 35 | 0 | 122 | 137 | 75 | 15 | 55 | 162 | 30 | 103 | 420 | 284 | 450 | 0 | 35 | 25 | 321 | 99 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 17 | 15 | 12 | 0 | 2 | 17 | 24 | 17 | 98 | 100 | 0 | 46 | 14 | 37 | 575 | 17 | 0 | 6 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 137 | 0 | 353 | 285 | 5 | 182 | 35 | 90 | 50 | 200 | 28 | 20 | 114 | 32 | 16 | 0 | 30 | 290 | 320 | 348 | 40 | 38 | 5 | 139 | 24 | 0 | 84 | 30 | 0 | 18 | 145 | 54.5 | 115 | 162 | 33 | 0 | 0 | 12 | 8861.5 | 871 | 0 | 0 | 28 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 36 | 1373 | 0 | 50 | 45 | 50 | 4 | 82 | 0 | 27 | 16 | 0 | 22 | 0 | 177 | 0 | 156 | 0 | 148 | 0 | 0 | 0 | 0 | 5.5 | 160 | 55 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 110 | 220 | 0 | 0 | 1122 | 17 | 5990.5 | 14852 | 85.3
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 46 | 338 | 0 | 0 | 35 | 35 | 0 | 85 | 137 | 45 | 0 | 55 | 162 | 30 | 103 | 450 | 270 | 583 | 0 | 35 | 25 | 322 | 97 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 17 | 15 | 12 | 0 | 0 | 17 | 24 | 0 | 98 | 48 | 0 | 46 | 14 | 37 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 137 | 0 | 360 | 285 | 5 | 182 | 35 | 90 | 50 | 200 | 56 | 20 | 114 | 32 | 16 | 0 | 30 | 275 | 320 | 348 | 40 | 38 | 5 | 152 | 24 | 0 | 84 | 30 | 0 | 18 | 145 | 17 | 115 | 164 | 33 | 0 | 0 | 12 | 8764 | 870 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 50 | 1361 | 0 | 50 | 50 | 50 | 5 | 87 | 0 | 33 | 0 | 0 | 22 | 0 | 176 | 0 | 152 | 0 | 146 | 0 | 0 | 0 | 0 | 5.5 | 160 | 55 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 110 | 220 | 0 | 0 | 1200 | 17 | 6027.5 | 14791.5 | 0
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 51 | 345 | 0 | 0 | 35 | 35 | 0 | 90 | 137 | 45 | 0 | 55 | 162 | 30 | 103 | 450 | 276 | 583 | 0 | 35 | 25 | 328 | 99 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 24 | 0 | 98 | 48 | 0 | 46 | 14 | 37 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 137 | 0 | 360 | 285 | 5 | 182 | 35 | 90 | 50 | 200 | 53 | 20 | 114 | 34 | 16 | 0 | 30 | 275 | 320 | 348 | 40 | 38 | 5 | 151 | 24 | 0 | 84 | 30 | 0 | 18 | 145 | 17 | 115 | 164 | 33 | 0 | 0 | 12 | 8781 | 869 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 75 | 1359 | 0 | 50 | 50 | 50 | 5 | 87 | 0 | 37 | 0 | 0 | 22 | 0 | 176 | 0 | 162 | 0 | 156 | 0 | 0 | 0 | 0 | 5.5 | 160 | 54 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 110 | 220 | 0 | 0 | 1195 | 17 | 6070.5 | 14851.5 | 85.3
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 52 | 328 | 0 | 0 | 35 | 35 | 0 | 82 | 140 | 45 | 0 | 55 | 126 | 30 | 96 | 450 | 297 | 583 | 0 | 35 | 28 | 326 | 99 | 0 | 0 | 108 | 16 | 15 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 24 | 0 | 98 | 48 | 0 | 46 | 14 | 38 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 184 | 0 | 355 | 285 | 13 | 188 | 35 | 90 | 50 | 200 | 57 | 20 | 114 | 38 | 16 | 0 | 30 | 280 | 320 | 351 | 41 | 39 | 5 | 151 | 24 | 0 | 85 | 30 | 0 | 18 | 145 | 17 | 115 | 164 | 33 | 0 | 0 | 12 | 8796 | 917 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 55 | 1362.16 | 0 | 49 | 50 | 35 | 15 | 87 | 0 | 0 | 0 | 0 | 22 | 0 | 176 | 0 | 208 | 0 | 210 | 0 | 0 | 0 | 0 | 5.5 | 163 | 54 | 74 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 110 | 220 | 0 | 0 | 1200 | 17 | 6080.66 | 14876.66 | 85.29
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 60 | 319 | 0 | 0 | 35 | 17 | 0 | 78 | 140 | 45 | 0 | 46 | 126 | 30 | 50 | 450 | 277 | 583 | 0 | 35 | 28 | 330 | 99 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 24 | 0 | 98 | 48 | 0 | 46 | 14 | 39 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 185 | 0 | 360 | 285 | 32 | 182 | 36 | 90 | 50 | 200 | 57 | 20 | 114 | 36 | 16 | 0 | 30 | 295 | 320 | 351 | 41 | 39 | 5 | 151 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 17 | 115 | 164 | 33 | 0 | 0 | 12 | 8712 | 916 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 35 | 1364.28 | 0 | 49 | 50 | 35 | 21 | 87 | 0 | 26 | 0 | 0 | 22 | 0 | 177 | 0 | 209 | 0 | 210 | 0 | 0 | 0 | 0 | 5.5 | 164 | 54 | 74 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 108 | 220 | 0 | 0 | 1200 | 17 | 6094.78 | 14806.78 | 85.29
23:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 61 | 306 | 0 | 0 | 0 | 17 | 0 | 71 | 140 | 45 | 0 | 17 | 35 | 30 | 50 | 450 | 307 | 583 | 0 | 35 | 28 | 327 | 99 | 0 | 0 | 108 | 15.5 | 15 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 24 | 0 | 98 | 48 | 0 | 46 | 14 | 40 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 155 | 0 | 358 | 285 | 38 | 197 | 36 | 59 | 50 | 200 | 57 | 20 | 114 | 36 | 16 | 0 | 31 | 300 | 320 | 385 | 41 | 39 | 5 | 152 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 17 | 115 | 164 | 33 | 0 | 0 | 12 | 8548.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 35 | 1361.1 | 0 | 49 | 50 | 35 | 16 | 87 | 0 | 26 | 0 | 0 | 22 | 0 | 177 | 0 | 210 | 0 | 197 | 0 | 0 | 0 | 0 | 5.5 | 163 | 55 | 74 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 120 | 220 | 0 | 0 | 1220 | 17 | 6079.6 | 14628.1 | 85.28
Total KWH | 31680 | 677760 | 286080 | 0 | 0 | 0 | 0 | 909545.46 | 7750800 | 0 | 0 | 324000 | 617040 | 0 | 1633104 | 2255520 | 676953 | 57127 | 621270 | 1671840 | 694800 | 1058880 | 9802000 | 7048204 | 12941364 | 0 | 388226 | 666200 | 7696431 | 2450000 | 0 | 199816 | 2437200 | 441600 | 351360 | 0 | 0 | 138000 | 150545 | 54720 | 0 | 37920 | 186465 | 187432 | 79358 | 1581120 | 719040 | 23688 | 1092660 | 130500 | 752640 | 12800000 | 61891 | 0 | 23040 | 74790 | 153055 | 0 | 0 | 0 | 0 | 25821816 | 132435 | 1067720 | 853090 | 3027636 | 0 | 8763800 | 6926000 | 494400 | 4687000 | 831672 | 976320 | 927700 | 2965440 | 275520 | 436220 | 2112420 | 843840 | 341995 | 443482 | 540256 | 7342000 | 7689700 | 8879000 | 971000 | 902640 | 115488 | 3535936 | 532512 | 0 | 1994880 | 668448 | 0 | 432000 | 4214610 | 292320 | 1923600 | 2913600 | 989760 | 12400 | 297530 | 294240 | 188406090.46 | 22013818 | 0 | 0 | 127200 | 42624 | 0 | 0 | 0 | 0 | 0 | 0 | 663120 | 12465450 | 456480 | 30992727 | 0 | 262991 | 355000 | 564672 | 67390 | 485328 | 37920 | 117295 | 23203 | 670560 | 113866 | 362256 | 4229909 | 0 | 4727673 | 0 | 4582255 | 0 | 1721236 | 0 | 31860 | 134316 | 3834000 | 1314763 | 986433 | 117543 | 1148736 | 0 | 0 | 35323.8 | 1014480 | 4321 | 116928 | 6785000 | 206485 | 2665000 | 5196050 | 0 | 0 | 26013090.91 | 141600 | 134828902.71 | 323234993.17

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-03-2025 | during | 28-03-2025 | during | 28-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 32 | 52 | 97.3 | 97.3 | 35 | 35 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 334 | 328 | 400.75 | 400.75 | 330 | 340 | DP High
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 268 | 297 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 98 | 99 | 208.13 | 208.13 | 98 | 98 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 90 | 140 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 24 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.5 | 16 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 30 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 87 | 82 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 32 | 96 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 122 | 126 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2766.5 | 3049 | 5274.5 | 5240.5 | 3749.56 | 3725.56
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 17 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 72 | 98 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 13 | 38 | 35 | 42 | 35 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.62 | 0 | 3.62 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 14 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 6 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 575 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1839 | 2141 | 3409.34 | 3394.72 | 3294.34 | 3279.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 214 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 360 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 285 | 285 | 285 | 285 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 35 | 35 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 13 | 55 | 55 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 180 | 184 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 47 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 20 | 30 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 35 | 50 | 163 | 163 | 30 | 30 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 93 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 90 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 57 | 113 | 113 | 1 | 53 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 19 | 90 | 115 | 115 | 52 | 90 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1601 | 1776 | 2410.99 | 2345.99 | 2050.05 | 2075.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-03-2025 | during | 28-03-2025 | during | 28-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 33 | 210 | 210 | 40 | 40 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 118 | 164 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 115 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.87 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 277.87 | 341 | 653.6 | 601.5 | 446.1 | 394
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 41 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 39 | 40 | 40 | 38 | 38 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 151 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 146 | 145 | 165 | 165 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 351 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1519 | 1489 | 1613 | 1613 | 1542 | 1542
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 917 | 917 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 29 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 15 | 55 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 93 | 0 | 93 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 508 | 619 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1534 | 1620 | 3605.2 | 3512.2 | 1908.03 | 1815.03
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 116 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1101 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1722.61 | 1880 | 2172.12 | 2171.12 | 2160.12 | 2159.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 50 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 49 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 15 | 32 | 32 | 5 | 5 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 176 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 202 | 208 | 220 | 220 | 200 | 200 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 210 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 87 | 90 | 90 | 87 | 87 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.7 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1460.89 | 1362.16 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.38 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2213.47 | 2219.66 | 2688.39 | 2521.74 | 2618.39 | 2451.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 54 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 163 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 36 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.5 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 27 | 74 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 156 | 0 | 180 | 0 | 180 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 453.5 | 361 | 688.4 | 472 | 654.42 | 438.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 13926.95 | 14876.66 | 22515.54 | 21872.77 | 18423.01 | 17880.24
Forecast Scenario (28-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13390 |  | 0 |  | 13390
|  |  |  | 1:00 | 12820 |  | 0 |  | 12820
|  |  |  | 2:00 | 12500 |  | 0 |  | 12500
|  |  |  | 3:00 | 12680 |  | 0 |  | 12680
|  |  |  | 4:00 | 12600 |  | 0 |  | 12600
|  |  |  | 5:00 | 11710 |  | 0 |  | 11710
|  |  |  | 6:00 | 11060 |  | 0 |  | 11060
|  |  |  | 7:00 | 10670 |  | 0 |  | 10670
|  |  |  | 8:00 | 10870 |  | 0 |  | 10870
|  |  |  | 9:00 | 11210 |  | 0 |  | 11210
|  |  |  | 10:00 | 11280 |  | 0 |  | 11280
|  |  |  | 11:00 | 11580 |  | 0 |  | 11580
|  |  |  | 12:00 | 12270 |  | 0 |  | 12270
|  |  |  | 13:00 | 12770 |  | 0 |  | 12770
|  |  |  | 14:00 | 12100 |  | 0 |  | 12100
|  |  |  | 15:00 | 12230 |  | 0 |  | 12230
|  |  |  | 16:00 | 12520 |  | 0 |  | 12520
|  |  |  | 17:00 | 12630 |  | 0 |  | 12630
|  |  |  | 18:00 | 12730 |  | 0 |  | 12730
|  |  |  | 18:30 | 13150 |  | 0 |  | 13150
|  |  |  | 19:00 | 13640 |  | 0 |  | 13640
|  |  |  | 19:30 | 13660 |  | 0 |  | 13660
|  |  |  | 20:00 | 13740 |  | 0 |  | 13740
|  |  |  | 21:00 | 13900 |  | 0 |  | 13900
|  |  |  | 22:00 | 13890 |  | 0 |  | 13890
|  |  |  | 23:00 | 13630 |  | 0 |  | 13630
Probable Maximum Temperature: |  |  | 38.30°C
Probable Maximum Demand at Day Peak: |  |  | 12270.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 298.42 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:23 hrs on 28-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13926.95 | MW | 12:00 Hr. | Energy Generated |  |  | 323.235 |  | MKWHr.
| Day Peak Demand |  |  | 13947.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.19 |  | MKWHr.
| Evening Peak Generation |  |  | 14876.66 | MW | 21:00 Hr. | Energy Demand |  |  | 323.425 |  | MKWHr.
| Evening Peak Demand |  |  | 14876.66 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36 |  | °C
| Minimum Generation of the Day |  |  | 10623.55 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1011.52 |  | MMCFD
| Maximum Generation of the Day |  |  | 14876.66 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.3898 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 50.7523 | 0 | 12.7367 | 0 | 0 | 0.19982 | 0 | 0 | 63.6888 | Gas | 140.753 | Gas | 480906297.591
| Chattogram Zone |  |  | 0.75264 | 38.6218 | 3.54 | 0 | 1.0927 | 0.15612 | 0 | 0.03792 | 44.2011 | Coal | 89.0341 | Coal | 631636228.2533
| Cumilla Zone |  |  | 27.1621 | 0 | 8.065 | 0 | 0 | 0.44348 | 0.84384 | 0 | 36.5145 | HFO | 34.4581 | HFO | 598662033.42
| Mymensingh Zone |  |  | 0.98976 | 0 | 5.4238 | 0 | 0 | 0.30993 | 0 | 0 | 6.7234 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 37.2782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2782 | Hydro | 1.0927 | Hydro | 109266
| Khulna Zone |  |  | 0 | 12.4655 | 0.6263 | 0 | 0 | 0.66312 | 22.0138 | 0 | 35.7687 | Solar | 4.0088 | Solar | 64591090.878
| Barishal Zone |  |  | 8.0675 | 32.7981 | 0.25853 | 0 | 0 | 0.004321 | 0 | 0 | 41.1285 | Import | 53.8504 | Import | 288961963.22
| Rajshahi Zone |  |  | 15.7504 | 0 | 1.6727 | 0 | 0 | 1.0647 | 30.9927 | 0 | 49.4805 | Wind | 0.03792 | Wind | 555148.8
| Rangpur Zone |  |  | 0 | 5.1488 | 2.1352 | 0 | 0 | 1.1673 | 0 | 0 | 8.4513
| Total |  |  | 140.753 | 89.0341 | 34.4581 | 0 | 1.0927 | 4.0088 | 53.8504 | 0.03792 | 323.235
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 480906297.591 |  | Hydro | 109266
|  |  |  | Coal | 631636228.2533 |  | Solar | 64591090.878
|  |  |  | HFO | 598662033.42 |  | Import | 288961963.22
|  |  |  | HSD | 0 |  | Wind | 555148.8
[5 empty] | Total: | 206,54,22,028 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0138 | Peak Hr Flow | 917.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 27743690.95 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.9927 | Peak Hr Flow | 1362.16 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 364 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.84384 | Peak Hr Flow | 38.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 696 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.8504 | Peak Hr Flow | 2317.16 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4850
|  |  |  | Chattogram |  | 0 |  | 1422
|  |  |  | Cumilla |  | 0 |  | 1461
|  |  |  | Mymensingh |  | 0 |  | 1258
|  |  |  | Sylhet |  | 0 |  | 559
|  |  |  | Khulna |  | 0 |  | 1796
|  |  |  | Barishal |  | 0 |  | 482
|  |  |  | Rajshahi |  | 0 |  | 1586
|  |  |  | Rangpur |  | 0 |  | 867
|  |  |  | Total |  | 0 |  | 14281
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1074 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1509.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:41 | Ramganj 132/33kV S/S Transformer-01 HT is restored.
|  | 08:41 | Ramganj 132/33kV S/S Transformer-01 LT is restored.
| 08:51 | 12:08 | Chandraghona 132/33kV S/S MAIN BUS-2 Scheduled S/D Due to Oil leakage maintenance work at
Y phase of Main Bus -2.
|  | 09:09 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT is restored.
|  | 09:10 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT is restored.
|  | 09:48 | Madaripur 132/33kV S/S T1-405T LT is restored.
|  | 09:48 | Madaripur 132/33kV S/S T1-405T HT is restored.
| 10:15 | 16:42 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D Due to Project devolvement work
|  | 11:25 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT is restored.
| 11:26 | 13:58 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to Maintenance work
|  | 11:27 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT is restored.
| 11:29 | 13:26 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Maintenance work
| 11:32 | 13:15 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to Maintenance work
| 11:33 | 13:26 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Maintenance work
| 12:00 |  | Day peak Generation is 13922 MW
| 12:08 | 13:59 | Khulna(C )-Khulna (S) 132kV Ckt-1 Forced S/D from Khulna (C) end Due to RED HOT
MAINTENANCE. and from Khulna(S) 230/132kV end Due to Red hot maintenance work
| 12:32 | 13:19 | BIPTC S/S 20DF43 Scheduled S/D Due to CB General Fault
| 13:13 | 14:42 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Maintenance work
| 13:14 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to INSTRUCTION FORM NLDC
| 13:42 | 16:05 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to Fenchuganj
ckt-2 S/D take this maintenance Red Hot
| 14:33 | 17:08 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Hotspot maintenance | [7 empty] | 10.0MW load
interrup.
| 14:33 | 17:02 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Hotspot maintenance | [7 empty] | 10.0MW load
interrup.
| 14:44 | 15:57 | Narshingdi 132/33kV S/S 132 kV Main Bus-2 Scheduled S/D Due to Hotspot maintenance
| 21:00 |  | Evening Peak Generation: 14876 MW.
| 04:34 | 04:44 | BSRM-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Distance
protection A-Phase Earth Fault (Yellow Led) relays Due to None
| 04:47 |  | Aminbazar-Manikgonj PP 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing
Zone-1 relays Due to Conductor Broken of Y-Phage
| 05:50 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 HT Scheduled S/D Due to High Temp. Removed
Purposed.
| 05:50 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 LT Scheduled S/D Due to High Temp. Removed
Purposed.
| 06:15 |  | Mirpur 132/33kV S/S T2 LT Scheduled S/D Due to Hotspot maintenance work
| 06:17 | 07:55 | Mirpur 132/33kV S/S T2 HT Scheduled S/D Due to Hotspot maintenance work
| 06:55 |  | Ramganj 132/33kV S/S Transformer -02 HT Scheduled S/D Due to hotspot maintenance of bay
equipments
| 06:55 |  | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to hotspot maintenance of bay | [7 empty] | 10.0MW load
|  |  | equipments | [7 empty] | interrup.
| 07:00 |  | Min. Gen. 11119 MW
| 07:04 |  | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to Maintenance work due to
Red-hot
| 07:04 |  | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to Maintenance work due to | [7 empty] | 10.0MW load
|  |  | Red-hot | [7 empty] | interrup.
| 07:50 |  | BSRM-GPH 230 kV Ckt-1 Scheduled S/D from BSRM 230/33kV end Due to Line maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 52 | 909545.46 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 328 | 7750800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9802000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 297 | 7048204 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 57127 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 99 | 2450000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7696431 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 31680 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 2255520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 621270 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 388226 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 441600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 351360 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 694800 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 666200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 286080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 676953 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 82 | 1633104 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 677760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 96 | 1058880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1671840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199816 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 617040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 12941364 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2437200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3049 | 63688800.46
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 74790 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132435 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 23040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1092660 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 153055 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 187432 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 186465 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 98 | 1581120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 38 | 752640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 54720 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23688 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 150545 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 79358 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 14 | 130500 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 719040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 138000 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 61891 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25821816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 37920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12800000 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2141 | 44201115
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4687000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8763800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6926000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 831672 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 13 | 494400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 184 | 3027636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1067720 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 853090 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 30 | 540256 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 927700 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2965440 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 843840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 341995 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 436220 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2112420 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 275520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 976320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 443482 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1776 | 36514511
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 989760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2913600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1923600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 297530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 292320 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 341 | 6723450
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 41 | 971000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 902640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3535936 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 115488 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 668448 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1994880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 145 | 4214610 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 532512 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7342000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 351 | 8879000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7689700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1489 | 37278214
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 917 | 22013818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 29 | 127200 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 42624 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 456480 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 663120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 619 | 12465450 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1620 | 35768692
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 116928 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 206485 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2665000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 26013090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5196050 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 141600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6785000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4321 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1880 | 41128474.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 50 | 355000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 49 | 262991 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 15 | 67390 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 117295 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 176 | 4229909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 208 | 4727673 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 210 | 4582255 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 1721236 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 113866 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 134316 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 23203 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 485328 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 564672 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 37920 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1362.16 | 30992727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 362256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 670560 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2219.66 | 49480457
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1314763 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 3834000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 1148736 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35323.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 74 | 986433 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 117543 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1014480 | -
Rangpur Area Total |  |  |  |  | 950 | 361 | 8451278.8
Eastern Grid Total |  |  |  |  | 16921.242 | 8796 | 188406090.46
Western Grid Total |  |  |  |  | 11614.5 | 6080.66 | 134828902.71
National Grid Total |  |  |  |  | 28535.742 | 14876.66 | 323234993.17
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9549.63 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4731.2 | MW
i) Dhaka area |  |  | 4849.93 |  | MW | i) Khulna area |  |  |  | 1796.5 | MW
ii) Chattogram area |  |  | 1421.7 |  | MW | ii) Barishal area |  |  |  | 481.5 | MW
iii) Cumilla area |  |  | 1461 |  | MW | iii) Rajshahi area |  |  |  | 1586.2 | MW
iv) Mymensingh area |  |  | 1258 |  | MW | iv) Rangpur area |  |  |  | 867 | MW
v) Sylhet area |  |  | 559 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14280.83 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 12:00 | 67 | Jaldhaka | 92 | 13:00 | 133 | Payra | 31 | 21:00
2 | AKSML | 117 | 04:00 | 68 | Jamalpur | 129 | 15:00 | 134 | Postogola | 50 | 19:00
3 | Aftabnagar | 32 | 12:00 | 69 | Jashore | 149 | 19:30 | 135 | Purbachal | 17 | 18:30
4 | Agargaon | 104 | 13:00 | 70 | Jhenaidah | 134 | 19:30 | 136 | Purbasadipur | 126 | 14:00
5 | Agrabad | 92 | 19:00 | 71 | Joydebpur | 148 | 17:00 | 137 | Rahanpur | 29 | 00:00
6 | Amnura | 57 | 22:00 | 72 | Joypurhat | 65 | 00:00 | 138 | Rahim | 23 | 01:00
7 | Ashuganj | 90 | 22:00 | 73 | Juldah | 14 | 13:00 | 139 | Rajbari | 74 | 19:00
8 | BSRM | 206 | 21:00 | 74 | KSRM | 24 | 05:00 | 140 | Rajendrapur | 115 | 21:00
9 | Bagerhat | 89 | 21:00 | 75 | Kabirpur | 219 | 16:00 | 141 | Rajshahi | 106 | 20:00
10 | Bajitpur | 53 | 19:00 | 76 | Kachua | 92 | 22:00 | 142 | Rajshahi-230 | 91 | 21:00
11 | Bakulia | 95 | 19:00 | 77 | Kallyanpur | 105 | 00:00 | 143 | Ramganj | 120 | 20:00
12 | Banani | 39.4 | 13:00 | 78 | Kalurghat | 36 | 09:00 | 144 | Rampur | 41 | 19:00
13 | Bangabhaban | 15 | 11:00 | 79 | Kamrangirchar | 63.2 | 16:00 | 145 | Rangamati | 16 | 19:00
14 | Barapukuria | 67 | 12:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 150 | 19:00
15 | Barguna | 22 | 21:00 | 81 | Kasba | 37 | 19:00 | 147 | Ruppur | 7.2 | 15:00
16 | Barishal | 108 | 20:00 | 82 | Kazla | 97 | 16:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 102 | 21:00 | 83 | Keranigonj | 75 | 20:00 | 149 | Saidpur | 106 | 15:00
18 | Baroaulia | 63 | 10:00 | 84 | Khagrachori | 32 | 18:30 | 150 | Satkhira | 135 | 19:00
19 | Baroirhat | 61 | 19:00 | 85 | Khulna | 74 | 19:00 | 151 | Satmasjid | 100 | 19:00
20 | Bashundhara | 167 | 19:00 | 86 | Khulshi | 165 | 18:00 | 152 | Savar | 195 | 12:00
21 | BashundharaCement | 13 | 00:00 | 87 | Kishoreganj | 144 | 23:00 | 153 | SevenRings | 19.66 | 16:00
22 | Beanibazar | 62 | 21:00 | 88 | Kodda | 285 | 09:00 | 154 | ShahCement | 38 | 11:00
23 | Benapole | 74 | 14:00 | 89 | Kulaura | 42 | 19:00 | 155 | Shahjadpur | 89 | 19:30
24 | Bhaluka | 161 | 15:00 | 90 | Kurigram | 70 | 17:00 | 156 | Shahjibazar | 127 | 19:00
25 | Bhandaria | 55 | 21:00 | 91 | Kushtia | 133 | 19:30 | 157 | Shahmirpur | 57 | 00:00
26 | Bhangura | 41 | 19:00 | 92 | Lalbag | 64 | 19:30 | 158 | Shariatpur | 90 | 22:00
27 | Bheramara(GK) | 57 | 19:30 | 93 | Lalmonirhat | 64 | 18:00 | 159 | Sherpur | 160 | 18:00
28 | Bhulta | 248 | 00:00 | 94 | MI_Cement | 18 | 12:00 | 160 | Shikalbaha | 28 | 16:00
29 | Bog-Sherpur | 70 | 13:00 | 95 | Madanganj | 46 | 15:00 | 161 | Shitalakhya | 81.6 | 15:00
30 | Bogura | 172 | 20:00 | 96 | Madaripur | 118 | 22:00 | 162 | Sholosohor | 41 | 15:00
31 | Borhanuddin | 87 | 23:00 | 97 | Madartek | 84.36 | 19:00 | 163 | Shyampur | 168 | 10:00
32 | Brahmanbaria | 135 | 22:00 | 98 | Madunaghat | 49 | 20:00 | 164 | Siddhirganj | 123 | 13:00
33 | Cantonment | 112 | 12:00 | 99 | Magura | 67 | 19:00 | 165 | Sirajganj | 114 | 20:00
34 | Chandpur | 77 | 21:00 | 100 | Mahasthangarh | 76 | 20:00 | 166 | Sonargaon | 103 | 15:00
35 | Chandraghona | 34 | 19:00 | 101 | Manikganj | 129 | 22:00 | 167 | Sreemongol | 70 | 19:00
36 | Chapai | 71 | 22:00 | 102 | Maniknagar | 66 | 13:00 | 168 | Sreepur | 76 | 11:00
37 | Charsaidpur | 42 | 12:00 | 103 | Matarbari | 50 | 21:00 | 169 | Srinagar | 50.4 | 21:00
38 | Chauddagram | 79 | 22:00 | 104 | Matuail | 66 | 11:00 | 170 | Sunamganj | 53 | 21:00
39 | Chhatak | 31 | 21:00 | 105 | Millgate | 82 | 12:00 | 171 | Sylhet | 32 | 19:00
40 | Chowmuhani | 240 | 21:00 | 106 | Mirpur | 126 | 20:00 | 172 | Sylhet-132 | 114 | 19:30
41 | Chuadanga | 110 | 21:00 | 107 | Mirsorai | 8 | 00:00 | 173 | TK | 31.8 | 22:00
42 | Coxsbazar | 127 | 18:00 | 108 | Mirzapur | 49 | 19:30 | 174 | Tangail | 206 | 21:00
43 | Cumilla(N) | 184 | 23:00 | 109 | Mithapukur | 64 | 17:00 | 175 | Thakurgaon | 97 | 14:00
44 | Cumilla(S) | 145 | 22:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 137 | 12:00
45 | Daudkandi | 138 | 20:00 | 111 | Mogbazar | 132.8 | 13:00 | 177 | Ullahpara | 36 | 19:00
46 | Dhaka | 50 | 12:00 | 112 | Mongla | 38 | 15:00 | 178 | Ullon | 47 | 19:00
47 | Dhamrai | 122 | 14:00 | 113 | Motijheel | 36 | 13:00 | 179 | Uttara | 79 | 14:00
48 | Dhanmondi | 141.1 | 13:00 | 114 | Muktagacha | 39 | 15:00 | 180 | UttaraNew | 45 | 20:00
49 | Dohazari | 102 | 19:00 | 115 | Munshiganj | 117 | 21:00 | 181 | Zigatola | 65 | 19:00
50 | Faridpur | 158 | 21:00 | 116 | Muradnagar | 30 | 19:30
51 | Fatullah | 92 | 12:00 | 117 | Mymensingh | 219 | 18:00
52 | Fenchuganj | 37 | 18:30 | 118 | Naogaon | 140 | 22:00
53 | Feni | 123 | 21:00 | 119 | Narail | 61 | 19:00
54 | GPH | 97 | 05:00 | 120 | Narinda | 80 | 13:00
55 | Ghatail | 88 | 17:00 | 121 | Narshingdi | 172 | 21:00
56 | Ghorashal | 13 | 14:00 | 122 | Natore | 163 | 19:30
57 | Ghorashal-230 | 89 | 19:30 | 123 | Nawabganj | 61.8 | 21:00
58 | Goalpara | 30 | 19:30 | 124 | Netrakona | 139 | 21:00
59 | Gollamari | 84 | 13:00 | 125 | New | 71 | 10:00
60 | Gopalganj | 111 | 22:00 | 126 | Niamatpur | 109 | 20:00
61 | Gulshan | 112 | 13:00 | 127 | Noapara | 46 | 19:00
62 | Halishahar | 40 | 06:00 | 128 | PHP | 5 | 01:00
63 | HaripurSBU | 160 | 11:00 | 129 | Pabna | 114 | 18:00
64 | Hasnabad | 79 | 23:00 | 130 | Palashbari | 120 | 19:00
65 | Hathazari | 80 | 20:00 | 131 | Panchagarh | 51 | 17:00
66 | Ishurdi | 72 | 19:30 | 132 | Patuakhali | 81.5 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13490.35 | 0 |  | 13490.35
1:00 | 12902.09 | 0 |  | 12902.09
2:00 | 12478.61 | 0 |  | 12478.61
3:00 | 12643.91 | 0 |  | 12643.91
4:00 | 12554.11 | 0 |  | 12554.11
5:00 | 11546.49 | 0 |  | 11546.49
6:00 | 10623.55 | 0 |  | 10623.55
7:00 | 10836.71 | 0 |  | 10836.71
8:00 | 11281.54 | 0 |  | 11281.54
9:00 | 12043.89 | 0 |  | 12043.89
10:00 | 12766.1 | 0 |  | 12766.1
11:00 | 13322.36 | 0 |  | 13322.36
12:00 | 13926.95 | 20 |  | 13947.95
13:00 | 14269.28 | 30 |  | 14300.28
14:00 | 14433.27 | 50 |  | 14485.27
15:00 | 14314.48 | 70 |  | 14387.48
16:00 | 14206.26 | 20 |  | 14227.26
17:00 | 14112.56 | 0 |  | 14112.56
18:00 | 14050.78 | 0 |  | 14050.78
19:00 | 14852 | 0 |  | 14852
19:30 | 14791.5 | 0 |  | 14791.5
20:00 | 14851.5 | 0 |  | 14851.5
21:00 | 14876.66 | 0 |  | 14876.66
22:00 | 14806.78 | 0 |  | 14806.78
23:00 | 14628.1 | 0 |  | 14628.1
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7653 | 5837.35 | 13490.35 | DAILY GENERATION CURVE
00:30 | 7422.5 | 5773.72 | 13196.22
01:00 | 7192 | 5710.09 | 12902.09 | 27-03-2025
01:30 | 7145 | 5545.35 | 12690.35
02:00 | 7098 | 5380.61 | 12478.61
02:30 | 7116.5 | 5444.76 | 12561.26
03:00 | 7135 | 5508.91 | 12643.91
03:30 | 7123.5 | 5475.51 | 12599.01
04:00 | 7112 | 5442.11 | 12554.11
04:30 | 6948 | 5102.3 | 12050.3
05:00 | 6784 | 4762.49 | 11546.49
05:30 | 6482.3 | 4602.72 | 11085.02
06:00 | 6180.6 | 4442.95 | 10623.55
06:30 | 6264.345 | 4465.785 | 10730.13
07:00 | 6348.09 | 4488.62 | 10836.71
07:30 | 6453.85 | 4605.275 | 11059.125
08:00 | 6559.61 | 4721.93 | 11281.54
08:30 | 6754.92 | 4907.795 | 11662.715
09:00 | 6950.23 | 5093.66 | 12043.89
09:30 | 7138.96 | 5266.035 | 12404.995
10:00 | 7327.69 | 5438.41 | 12766.1
10:30 | 7490.3 | 5553.93 | 13044.23
11:00 | 7652.91 | 5669.45 | 13322.36
11:30 | 7828.14 | 5796.515 | 13624.655
12:00 | 8003.37 | 5923.58 | 13926.95
12:30 | 8135.14 | 5962.975 | 14098.115
13:00 | 8266.91 | 6002.37 | 14269.28
13:30 | 8354.495 | 5996.78 | 14351.275
14:00 | 8442.08 | 5991.19 | 14433.27
14:30 | 8449.445 | 5924.43 | 14373.875
15:00 | 8456.81 | 5857.67 | 14314.48
15:30 | 8527.915 | 5732.455 | 14260.37
16:00 | 8599.02 | 5607.24 | 14206.26
16:30 | 8645.67 | 5513.74 | 14159.41
17:00 | 8692.32 | 5420.24 | 14112.56
17:30 | 8632.5 | 5449.17 | 14081.67
18:00 | 8572.68 | 5478.1 | 14050.78
18:30 | 8717.09 | 5734.3 | 14451.39
19:00 | 8861.5 | 5990.5 | 14852
19:30 | 8764 | 6027.5 | 14791.5
20:00 | 8781 | 6070.5 | 14851.5
20:30 | 8788.5 | 6075.58 | 14864.08 |  | Executive Engineer
21:00 | 8796 | 6080.66 | 14876.66 |  | Network Operation Division
21:30 | 8754 | 6087.72 | 14841.72
22:00 | 8712 | 6094.78 | 14806.78
22:30 | 8630.25 | 6087.19 | 14717.44
23:00 | 8548.5 | 6079.6 | 14628.1

## En-Curve
QF-LDC-12
Date | 27-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3704 | 2474.5 | 919 | 0 | 42 | 1314.85 | 46 | 4019 | 0 | 242 | 729 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3641 | 2425.5 | 919 | 0 | 38 | 1315.22 | 46 | 3911 | 0 | 242 | 658.5 | 0 | 0 | 0 | 0 | 27-03-2025
01:00 | 3578 | 2376.5 | 919 | 0 | 34 | 1315.59 | 46 | 3803 | 0 | 242 | 588 | 0 | 0 | 0 | 0
01:30 | 3538 | 2329 | 919 | 0 | 37 | 1260.85 | 46 | 3752 | 0 | 242 | 566.5 | 0 | 0 | 0 | 0 | Energy Generated | 323.235 |  | MKWHr
02:00 | 3498 | 2281.5 | 919 | 0 | 40 | 1206.11 | 46 | 3701 | 0 | 242 | 545 | 0 | 0 | 0 | 0 | Energy not Served | 0.19 |  | MKWHr
02:30 | 3561 | 2303 | 919 | 0 | 37 | 1209.76 | 46 | 3702 | 0 | 242 | 541.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 323.425 |  | MKWHr
03:00 | 3624 | 2324.5 | 919 | 0 | 34 | 1213.41 | 46 | 3703 | 0 | 242 | 538 | 0 | 0 | 0 | 0
03:30 | 3680 | 2340 | 919 | 0 | 35 | 1213.51 | 46 | 3582.5 | 0 | 218.5 | 564.5 | 0 | 0 | 0 | 0
04:00 | 3736 | 2355.5 | 919 | 0 | 36 | 1213.61 | 46 | 3462 | 0 | 195 | 591 | 0 | 0 | 0 | 0
04:30 | 3580 | 2331 | 919 | 0 | 36 | 1161.8 | 46 | 3295.5 | 0 | 179 | 502 | 0 | 0 | 0 | 0
05:00 | 3424 | 2306.5 | 919 | 0 | 36 | 1109.99 | 46 | 3129 | 0 | 163 | 413 | 0 | 0 | 0 | 0
05:30 | 3347.5 | 2231.8 | 918.5 | 0 | 36 | 1066.22 | 46 | 3004 | 0 | 139 | 296 | 0 | 0 | 0 | 0
06:00 | 3271 | 2157.1 | 918 | 0 | 36 | 1022.45 | 46 | 2879 | 0 | 115 | 179 | 0 | 0 | 0 | 0
06:30 | 3305.5 | 2179.3 | 918.5 | 0 | 33 | 1019.03 | 46 | 2876.5 | 32.8 | 115 | 204.5 | 0 | 0 | 0 | 0
07:00 | 3340 | 2201.5 | 919 | 0 | 30 | 1015.61 | 46 | 2874 | 65.6 | 115 | 230 | 0 | 0 | 0 | 0
07:30 | 3358 | 2238 | 894.5 | 0 | 30 | 1066.86 | 46 | 2935 | 133.265 | 104 | 253.5 | 0 | 0 | 0 | 0
08:00 | 3376 | 2274.5 | 870 | 0 | 30 | 1118.11 | 46 | 2996 | 200.93 | 93 | 277 | 0 | 0 | 0 | 0
08:30 | 3342.5 | 2375.5 | 870 | 0 | 29 | 1171.52 | 46 | 3121.5 | 277.695 | 127.5 | 301.5 | 0 | 0 | 0 | 0
09:00 | 3309 | 2476.5 | 870 | 0 | 28 | 1224.93 | 46 | 3247 | 354.46 | 162 | 326 | 0 | 0 | 0 | 0
09:30 | 3318 | 2502.25 | 893.5 | 0 | 31 | 1290.1 | 46 | 3351 | 410.145 | 192 | 371 | 0 | 0 | 0 | 0
10:00 | 3327 | 2528 | 917 | 0 | 34 | 1355.27 | 46 | 3455 | 465.83 | 222 | 416 | 0 | 0 | 0 | 0
10:30 | 3329 | 2536.5 | 917.5 | 0 | 37 | 1359.92 | 46 | 3557 | 506.31 | 221.5 | 532 | 0 | 0 | 1.5 | 0
11:00 | 3331 | 2545 | 918 | 0 | 40 | 1364.57 | 46 | 3659 | 546.79 | 221 | 648 | 0 | 0 | 3 | 0
11:30 | 3346.5 | 2533 | 917.5 | 0 | 37 | 1412.73 | 46 | 3718.5 | 566.425 | 245.5 | 797 | 0 | 0 | 4.5 | 10
12:00 | 3362 | 2521 | 917 | 0 | 34 | 1460.89 | 46 | 3778 | 586.06 | 270 | 946 | 0 | 0 | 6 | 20
12:30 | 3359 | 2500.5 | 917 | 0 | 35 | 1515.705 | 46 | 3740 | 580.91 | 299.5 | 1100 | 0 | 0 | 4.5 | 25
13:00 | 3356 | 2480 | 917 | 0 | 36 | 1570.52 | 46 | 3702 | 575.76 | 329 | 1254 | 0 | 0 | 3 | 30
13:30 | 3352.5 | 2481.75 | 917 | 0 | 40 | 1570.76 | 46 | 3761.5 | 542.265 | 322 | 1312 | 0 | 0 | 5.5 | 40
14:00 | 3349 | 2483.5 | 917 | 0 | 44 | 1571 | 46 | 3821 | 508.77 | 315 | 1370 | 0 | 0 | 8 | 50
14:30 | 3343 | 2491.5 | 917 | 0 | 41 | 1468.5 | 46 | 3898 | 426.375 | 315 | 1422.5 | 0 | 0 | 5 | 60
15:00 | 3337 | 2499.5 | 917 | 0 | 38 | 1366 | 46 | 3975 | 343.98 | 315 | 1475 | 0 | 0 | 2 | 70
15:30 | 3260.5 | 2454.5 | 917 | 0 | 37 | 1366.5 | 46 | 3894.5 | 288.37 | 347.5 | 1646 | 0 | 0 | 2.5 | 45
16:00 | 3184 | 2409.5 | 917 | 0 | 36 | 1367 | 46 | 3814 | 232.76 | 380 | 1817 | 0 | 0 | 3 | 20
16:30 | 3184 | 2437.5 | 917 | 0 | 33 | 1320.5 | 46 | 3829 | 161.16 | 369 | 1858.75 | 0 | 0 | 3.5 | 10
17:00 | 3184 | 2465.5 | 917 | 0 | 30 | 1274 | 46 | 3844 | 89.56 | 358 | 1900.5 | 0 | 0 | 4 | 0
17:30 | 3172.5 | 2396 | 916.5 | 0 | 32 | 1269.5 | 46 | 3815.5 | 46.77 | 393.5 | 1986.9 | 0 | 0 | 6.5 | 0
18:00 | 3161 | 2326.5 | 916 | 0 | 34 | 1265 | 46 | 3787 | 3.98 | 429 | 2073.3 | 0 | 0 | 9 | 0
18:30 | 3247.5 | 2317.5 | 893.5 | 0 | 33 | 1319 | 46 | 3927 | 1.99 | 531.5 | 2128.9 | 0 | 0 | 5.5 | 0
19:00 | 3334 | 2308.5 | 871 | 0 | 32 | 1373 | 46 | 4067 | 0 | 634 | 2184.5 | 0 | 0 | 2 | 0
19:30 | 3275 | 2459.5 | 870 | 0 | 32 | 1361 | 46 | 4141 | 0 | 614 | 1993 | 0 | 0 | 0 | 0
20:00 | 3310 | 2469.5 | 869 | 0 | 34 | 1359 | 46 | 4136 | 0 | 620 | 2008 | 0 | 0 | 0 | 0
20:30 | 3353.5 | 2513.5 | 893 | 0 | 36 | 1360.58 | 46 | 4139 | 0 | 604.5 | 1918 | 0 | 0 | 0 | 0
21:00 | 3397 | 2557.5 | 917 | 0 | 38 | 1362.16 | 46 | 4142 | 0 | 589 | 1828 | 0 | 0 | 0 | 0
21:30 | 3394 | 2568 | 916.5 | 0 | 37 | 1363.22 | 46 | 4142.5 | 0 | 605 | 1769.5 | 0 | 0 | 0 | 0
22:00 | 3391 | 2578.5 | 916 | 0 | 36 | 1364.28 | 46 | 4143 | 0 | 621 | 1711 | 0 | 0 | 0 | 0
22:30 | 3406.5 | 2585.75 | 917 | 0 | 36 | 1362.69 | 46 | 4153 | 0 | 596 | 1614.5 | 0 | 0 | 0 | 0
23:00 | 3422 | 2593 | 918 | 0 | 36 | 1361.1 | 46 | 4163 | 0 | 571 | 1518 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 403 | 05:00 | 386 | 12:00 | Payra | 419 | 05:00 | 410 | 14:00
Ashuganj | 412 | 18:00 | 390 | 12:00 | Rahanpur | 395 | 05:00 | 369 | 13:00
Bhulta | 406 | 05:00 | 387 | 10:00 | Rampal | 411 | 05:00 | 392 | 23:00
Bibiana | 397 | 05:00 | 387 | 13:00
BIPTC | 396 | 05:00 | 387 | 16:00
Bogura | 381 | 05:00 | 354 | 13:00
Gopalganj | 409 | 05:00 | 393 | 23:00
Kaliakoir | 373 | 18:00 | 358 | 14:00
Madunaghat | 402 | 06:00 | 391 | 00:00
Meghnaghat | 404 | 05:00 | 388 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 05:00 | 224 | 10:00 | Keranigonj | 232 | 05:00 | 221 | 10:00
AKSML | 234 | 16:00 | 224 | 14:00 | Khulna(S) | 236 | 05:00 | 221 | 21:00
Aminbazar | 260 | 22:00 | 224 | 11:00 | Madunaghat | 237 | 18:00 | 229 | 00:00
Ashuganj | 237 | 18:30 | 225 | 10:00 | Madunaghat-400 | 237 | 19:00 | 229 | 00:00
Ashuganj-400 | 237 | 18:30 | 225 | 10:00 | Maniknagar | 229 | 05:00 | 218 | 11:00
Baghabari | 234 | 04:00 | 223 | 12:00 | Meghnaghat | 238 | 05:00 | 228 | 12:00
Barapukuria | 222 | 05:00 | 212 | 13:00 | Meghnaghat-400 | 233 | 05:00 | 222 | 11:00
Barapukuria-230 | 222 | 05:00 | 212 | 13:00 | Mirsorai | 234 | 18:30 | 223 | 00:00
Barishal | 240 | 06:00 | 230 | 14:00 | Rajshahi | 232 | 01:00 | 221 | 11:00
Bheramara | 235 | 01:00 | 223 | 09:00 | Rampal | 236 | 05:00 | 222 | 22:00
Bhulta | 230 | 05:00 | 220 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 05:00 | 222 | 12:00 | Rampura | 229 | 05:00 | 218 | 10:00
BIPTC | 236 | 01:00 | 223 | 11:00 | Shikalbaha | 235 | 18:00 | 225 | 11:00
Bogura | 234 | 05:00 | 217 | 13:00 | Shyampur | 231 | 05:00 | 221 | 10:00
Bogura-400 | 234 | 18:30 | 218 | 13:00 | Siddhirganj | 232 | 05:00 | 22 | 23:00
Borhanuddin | 243 | 06:00 | 237 | 13:00 | Sirajgonj | 241 | 05:00 | 231 | 13:00
BSRM | 232 | 18:30 | 222 | 14:00 | Sreepur | 235 | 05:00 | 223 | 11:00
Cumilla(N) | 228 | 18:00 | 219 | 14:00 | Tongi | 229 | 04:00 | 217 | 10:00
Faridpur | 237 | 06:00 | 226 | 23:00
Fenchuganj | 232 | 04:00 | 228 | 16:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 231 | 18:30 | 27 | 07:00
Gopalganj | 236 | 05:00 | 226 | 23:00
GPH | 234 | 18:00 | 225 | 12:00
Haripur | 230 | 18:30 | 220 | 12:00
Hasnabad | 230 | 06:00 | 222 | 10:00
Hathazari | 237 | 18:00 | 228 | 00:00
Ishurdi | 236 | 18:30 | 225 | 11:00
Jhenaidah | 231 | 05:00 | 216 | 13:00
Kaliakoir | 232 | 05:00 | 222 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 129 | 14:00 | Madunaghat | 135 | 18:00 | 130 | 00:00
Agargaon | 139 | 05:00 | 131 | 10:00 | Magura | 133 | 05:00 | 118 | 14:00
Agrabad | 135 | 17:00 | 127 | 14:00 | Mahasthangarh | 130 | 05:00 | 120 | 13:00
AKS | 132 | 04:00 | 126 | 11:00 | Manikganj | 129 | 00:00 | 123 | 12:00
Aminbazar | 138 | 05:00 | 131 | 09:00 | Maniknagar | 134 | 05:00 | 127 | 12:00
Amnura | 136 | 19:30 | 119 | 13:00 | Matarbari | 122 | 08:00 | 110 | 00:00
Ashuganj | 137 | 05:00 | 132 | 12:00 | Matuail | 134 | 05:00 | 127 | 10:00
Bagerhat | 132 | 05:00 | 118 | 23:00 | Millgate | 135 | 04:00 | 126 | 12:00
Bajitpur | 133 | 06:00 | 125 | 12:00 | Mirpur | 137 | 06:00 | 129 | 11:00
Bakulia | 136 | 18:00 | 129 | 11:00 | Mirzapur | 129 | 00:00 | 122 | 12:00
Banani | 137 | 03:00 | 128 | 12:00 | Mithapukur | 131 | 05:00 | 118 | 11:00
Bangabhaban | 136 | 05:00 | 128 | 10:00 | MI_Cement | 134 | 05:00 | 127 | 10:00
Barapukuria | 136 | 05:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 136 | 06:00 | 131 | 23:00 | Mogbazar | 138 | 05:00 | 130 | 10:00
Barishal | 134 | 05:00 | 125 | 15:00 | Mongla | 133 | 05:00 | 120 | 21:00
Barishal-230 | 135 | 05:00 | 126 | 22:00 | Motijheel | 136 | 05:00 | 128 | 10:00
Baroaulia | 133 | 04:00 | 129 | 00:00 | Muktagacha | 132 | 00:00 | 121 | 14:00
Baroirhat | 128 | 18:00 | 120 | 10:00 | Munshiganj | 133 | 05:00 | 127 | 10:00
Bashundhara | 137 | 05:00 | 126 | 12:00 | Muradnagar | 129 | 05:00 | 121 | 10:00
BashundharaCement | 134 | 18:30 | 126 | 10:00 | Mymensingh | 135 | 05:00 | 111 | 14:00
Beanibazar | 131 | 05:00 | 126 | 21:00 | Naogaon | 127 | 05:00 | 114 | 13:00
Benapole | 130 | 05:00 | 109 | 14:00 | Narail | 133 | 05:00 | 119 | 13:00
Bhaluka | 130 | 05:00 | 118 | 11:00 | Narinda | 134 | 6:00 | 126 | 15:00
Bhandaria | 129 | 07:00 | 119 | 22:00 | Narshingdi | 132 | 18:00 | 118 | 14:00
Bhangura | 133 | 05:00 | 124 | 13:00 | Natore | 133 | 05:00 | 123 | 13:00
Bheramara | 133 | 01:00 | 126 | 14:00 | Nawabganj | 136 | 05:00 | 128 | 10:00
Bheramara(GK) | 133 | 01:00 | 126 | 13:00 | Netrakona | 123 | 05:00 | 108 | 13:00
Bhulta | 129 | 18:30 | 122 | 10:00 | New | 139 | 18:00 | 128 | 10:00
Bog-Sherpur | 130 | 05:00 | 122 | 10:00 | Niamatpur | 134 | 05:00 | 125 | 12:00
Bogura | 132 | 05:00 | 123 | 13:00 | Noapara | 134 | 05:00 | 122 | 21:00
Bogura-230 | 132 | 05:00 | 122 | 13:00 | Pabna | 134 | 01:00 | 126 | 11:00
Brahmanbaria | 129 | 05:00 | 123 | 13:00 | Palashbari | 127 | 05:00 | 115 | 11:00
Cantonment | 138 | 05:00 | 131 | 10:00 | Panchagarh | 139 | 18:30 | 116 | 11:00
Chandpur | 129 | 21:00 | 115 | 09:00 | Patuakhali | 136 | 05:00 | 133 | 00:00
Chandraghona | 135 | 06:00 | 129 | 14:00 | Payra | 138 | 06:00 | 135 | 00:00
Chapai | 130 | 05:00 | 119 | 13:00 | PHP | 125 | 18:30 | 118 | 10:00
Charsaidpur | 134 | 05:00 | 126 | 12:00 | Postogola | 136 | 04:00 | 130 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 125 | 07:00 | 118 | 14:00 | Purbachal | 137 | 18:30 | 128 | 12:00
Chhatak | 131 | 05:00 | 125 | 15:00 | Purbasadipur | 133 | 18:30 | 113 | 11:00
Chowmuhani | 120 | 05:00 | 111 | 14:00 | Rahanpur | 135 | 05:00 | 124 | 13:00
Chuadanga | 132 | 05:00 | 116 | 14:00 | Rahanpur-400 | 135 | 05:00 | 125 | 13:00
Coxsbazar | 122 | 07:00 | 112 | 21:00 | Rahim | 135 | 18:00 | 127 | 10:00
Cumilla(N) | 130 | 06:00 | 123 | 14:00 | Rajbari | 132 | 05:00 | 124 | 21:00
Cumilla(S) | 134 | 00:00 | 121 | 10:00 | Rajendrapur | 156 | 08:00 | 120 | 12:00
Daudkandi | 129 | 05:00 | 122 | 10:00 | Rajshahi | 133 | 05:00 | 124 | 13:00
Dhaka | 137 | 06:00 | 129 | 10:00 | Rajshahi-230 | 133 | 01:00 | 111 | 13:00
Dhamrai | 130 | 02:00 | 123 | 10:00 | Ramganj | 121 | 18:30 | 111 | 10:00
Dhanmondi | 138 | 05:00 | 129 | 12:00 | Rampur | 135 | 18:00 | 128 | 14:00
Dohazari | 131 | 06:00 | 123 | 00:00 | Rampura | 137 | 05:00 | 129 | 10:00
Faridpur | 133 | 05:00 | 127 | 15:00 | Rangamati | 135 | 18:30 | 129 | 10:00
Fatullah | 136 | 18:30 | 128 | 10:00 | Rangpur | 130 | 06:00 | 118 | 11:00
Fenchuganj | 135 | 05:00 | 130 | 12:00 | Ruppur | 135 | 04:00 | 128 | 14:00
Feni | 124 | 18:00 | 116 | 10:00 | Saidpur | 132 | 18:30 | 116 | 11:00
Ghatail | 128 | 00:00 | 117 | 14:00 | Satkhira | 133 | 05:00 | 118 | 21:00
Ghorashal | 137 | 05:00 | 132 | 10:00 | Satmasjid | 138 | 05:00 | 130 | 12:00
Goalpara | 136 | 06:00 | 125 | 19:00 | Savar | 136 | 05:00 | 127 | 09:00
Gollamari | 136 | 05:00 | 126 | 21:00 | SevenRings | 139 | 18:30 | 131 | 10:00
Gopalganj | 137 | 05:00 | 126 | 23:00 | ShahCement | 134 | 05:00 | 126 | 12:00
Gopalganj-400 | 139 | 05:00 | 132 | 21:00 | Shahjadpur | 136 | 02:00 | 130 | 10:00
Gulshan | 137 | 05:00 | 128 | 10:00 | Shahjibazar | 131 | 05:00 | 125 | 14:00
Halishahar | 135 | 05:00 | 128 | 10:00 | Shahmirpur | 137 | 17:00 | 130 | 11:00
Haripur | 135 | 18:30 | 128 | 10:00 | Shariatpur | 137 | 05:00 | 128 | 21:00
HaripurSBU | 135 | 18:30 | 128 | 10:00 | Sherpur | 134 | 00:00 | 116 | 13:00
Hasnabad | 136 | 18:00 | 130 | 09:00 | Shikalbaha | 125 | 06:00 | 119 | 00:00
Hathazari | 137 | 17:00 | 131 | 10:00 | Shikalbaha-230 | 137 | 17:00 | 131 | 00:00
Ishurdi | 136 | 01:00 | 129 | 21:00 | Shitalakhya | 134 | 05:00 | 127 | 10:00
Jaldhaka | 131 | 05:00 | 112 | 11:00 | Sholosohor | 135 | 06:00 | 130 | 11:00
Jamalpur | 137 | 00:00 | 123 | 13:00 | Shyampur | 134 | 18:00 | 127 | 10:00
Jashore | 132 | 05:00 | 110 | 14:00 | Shyampur-230 | 135 | 05:00 | 123 | 00:00
Jhenaidah | 133 | 05:00 | 120 | 13:00 | Siddhirganj | 136 | 18:00 | 128 | 10:00
Jhenaidah-230 | 134 | 05:00 | 120 | 23:00 | Sirajganj | 131 | 01:00 | 122 | 13:00
Joydebpur | 137 | 18:30 | 126 | 11:00 | Sonargaon | 136 | 18:00 | 125 | 00:00
Joypurhat | 125 | 05:00 | 112 | 10:00 | Sreemongol | 132 | 05:00 | 126 | 12:00
Juldah | 137 | 17:00 | 130 | 00:00 | Sreepur | 131 | 05:00 | 123 | 11:00
Kabirpur | 135 | 04:00 | 124 | 10:00 | Srinagar | 136 | 05:00 | 128 | 11:00
Kachua | 126 | 20:00 | 118 | 00:00 | SSM | 134 | 00:00 | 134 | 00:00
Kaliakoir | 134 | 04:00 | 126 | 12:00 | Sunamganj | 130 | 06:00 | 123 | 21:00
Kallyanpur | 137 | 05:00 | 130 | 09:00 | Sylhet | 132 | 06:00 | 127 | 13:00
Kalurghat | 136 | 18:00 | 130 | 10:00 | Sylhet-132 | 132 | 05:00 | 128 | 21:00
Kamrangirchar | 136 | 05:00 | 128 | 10:00 | Tangail | 128 | 00:00 | 117 | 14:00
Kaptai | 138 | 5:00 | 133 | 10:00 | Thakurgaon | 139 | 18:30 | 113 | 11:00
Kasba | 129 | 05:00 | 121 | 10:00 | TK | 137 | 18:00 | 130 | 00:00
Kazla | 134 | 05:00 | 127 | 12:00 | Tongi | 138 | 04:00 | 129 | 10:00
Keranigonj | 136 | 05:00 | 129 | 10:00 | Ullahpara | 133 | 02:00 | 124 | 13:00
Khagrachori | 134 | 06:00 | 128 | 12:00 | Ullon | 137 | 05:00 | 129 | 11:00
Khulna | 134 | 06:00 | 123 | 21:00 | Uttara | 136 | 06:00 | 126 | 10:00
Khulna(S) | 137 | 05:00 | 125 | 23:00 | UttaraNew | 136 | 18:00 | 128 | 09:00
Khulshi | 133 | 05:00 | 128 | 00:00 | Zigatola | 135 | 05:00 | 128 | 14:00
Kishoreganj | 128 | 03:00 | 120 | 14:00
Kodda | 136 | 18:30 | 122 | 11:00
KSRM | 137 | 17:00 | 128 | 14:00
Kulaura | 133 | 05:00 | 129 | 12:00
Kurigram | 130 | 05:00 | 115 | 11:00
Kushtia | 133 | 05:00 | 122 | 14:00
Lalbag | 136 | 05:00 | 128 | 11:00
Lalmonirhat | 129 | 05:00 | 118 | 10:00
Madanganj | 134 | 18:30 | 126 | 10:00
Madaripur | 137 | 05:00 | 130 | 22:00
Madartek | 137 | 05:00 | 129 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division