## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-03-2025 | during | 29-03-2025 | during | 29-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 61 | 83 | 97.3 | 97.3 | 72 | 72 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 387 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 279 | 268 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 95 | 99 | 208.13 | 208.13 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 316 | 324 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 136 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 15 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 15 | 15 | 15 | 15 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 0 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 28 | 32 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 16 | 52.19 | 52.19 | 17 | 16 | Line Overload
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 13 | 50 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 35 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 85 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 520 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2451 | 2985 | 5087.7 | 5057.7 | 3742.12 | 3728.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 84 | 84 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 95 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 41 | 40 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.45 | 0 | 3.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1228 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 12 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 575 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1709 | 2175 | 3315.17 | 3291.72 | 3303.17 | 3279.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 188 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 285 | 250 | 250 | 250 | 250 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 43 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 133 | 172 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 115 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 30 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 125 | 170 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 98 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 29 | 113 | 113 | 1 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 90 | 115 | 115 | 52 | 90 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1440 | 1793 | 2370.99 | 2310.99 | 2056.05 | 2061.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-03-2025 | during | 29-03-2025 | during | 29-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 63 | 71 | 210 | 210 | 70 | 70 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 142 | 182 | 200 | 200 | 116 | 160 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 97 | 115 | 115 | 69 | 115 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.86 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 310.86 | 362 | 653.3 | 601.5 | 345.8 | 384
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 40 | 40 | 38 | 38 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 152 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 28 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 144 | 143 | 165 | 165 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 301 | 383 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1436 | 1523 | 1613 | 1613 | 1547 | 1547
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 918 | 919 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 80 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96.42 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 461 | 619 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1475.42 | 1618 | 3606.2 | 3514.2 | 1907.03 | 1815.03
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 90 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1022 | 1232 | 1244 | 1244 | 1244 | 1244 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1615.66 | 1876 | 2171.12 | 2171.12 | 2159.12 | 2159.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 40 | 60 | 50 | 50 | 50 | 50 | -
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 5 | 5 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 30 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 171 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 180 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 203 | 203 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 49 | 88 | 88 | 87 | 87 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.49 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1173 | 1377 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 61.63 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1961.62 | 2217.5 | 3150.18 | 2983.53 | 3100.18 | 2933.53
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 53 | 56 | 56 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 173 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 99 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 166 | 0 | 170 | 0 | 170 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 482.8 | 440 | 640.4 | 434 | 644.42 | 438.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12882.36 | 14989.5 | 22608.06 | 21977.76 | 18804.89 | 18345.59
Forecast Scenario (29-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14200 |  | 0 |  | 14200
|  |  |  | 1:00 | 13700 |  | 0 |  | 13700
|  |  |  | 2:00 | 13200 |  | 0 |  | 13200
|  |  |  | 3:00 | 13400 |  | 0 |  | 13400
|  |  |  | 4:00 | 12900 |  | 0 |  | 12900
|  |  |  | 5:00 | 12100 |  | 0 |  | 12100
|  |  |  | 6:00 | 11100 |  | 0 |  | 11100
|  |  |  | 7:00 | 11010 |  | 0 |  | 11010
|  |  |  | 8:00 | 11310 |  | 0 |  | 11310
|  |  |  | 9:00 | 11350 |  | 0 |  | 11350
|  |  |  | 10:00 | 11430 |  | 0 |  | 11430
|  |  |  | 11:00 | 11590 |  | 0 |  | 11590
|  |  |  | 12:00 | 11970 |  | 0 |  | 11970
|  |  |  | 13:00 | 12420 |  | 0 |  | 12420
|  |  |  | 14:00 | 12880 |  | 0 |  | 12880
|  |  |  | 15:00 | 12810 |  | 0 |  | 12810
|  |  |  | 16:00 | 12660 |  | 0 |  | 12660
|  |  |  | 17:00 | 12590 |  | 0 |  | 12590
|  |  |  | 18:00 | 12650 |  | 0 |  | 12650
|  |  |  | 18:30 | 12900 |  | 0 |  | 12900
|  |  |  | 19:00 | 13570 |  | 0 |  | 13570
|  |  |  | 19:30 | 13320 |  | 0 |  | 13320
|  |  |  | 20:00 | 13250 |  | 0 |  | 13250
|  |  |  | 21:00 | 13500 |  | 0 |  | 13500
|  |  |  | 22:00 | 11330 |  | 0 |  | 11330
|  |  |  | 23:00 | 12960 |  | 0 |  | 12960
Probable Maximum Temperature: |  |  | 39.10°C
Probable Maximum Demand at Day Peak: |  |  | 11970.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13570.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13570.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 299.88 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:08 hrs on 29-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-03-2025 | [28 empty] | Date: | 28-03-2025 | [28 empty] | Date: | 28-03-2025 | [28 empty] | Date: | 28-03-2025 | [28 empty] | Date: | 28-03-2025 | [17 empty] | Date: | 28-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 62 | 295 | 0 | 0 | 0 | 17 | 0 | 60 | 140 | 45 | 0 | 17 | 35 | 30 | 50 | 450 | 295 | 583 | 0 | 35 | 30 | 329 | 99 | 0 | 0 | 108 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 0 | 98 | 48 | 0 | 46 | 15 | 42 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 157 | 0 | 360 | 285 | 47 | 190 | 36 | 31 | 50 | 200 | 0 | 20 | 114 | 38 | 24 | 0 | 32 | 305 | 320 | 350 | 41 | 39 | 5 | 154 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 17 | 115 | 154 | 38 | 0 | 0 | 12 | 8363.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 35 | 1358.57 | 0 | 0 | 50 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 177 | 0 | 209 | 0 | 192 | 0 | 0 | 0 | 0 | 5.5 | 154 | 55 | 74 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1220 | 0 | 5843.07 | 14206.57 | 85.28
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 283 | 0 | 0 | 0 | 17 | 0 | 47 | 140 | 0 | 0 | 55 | 35 | 30 | 16 | 450 | 289 | 583 | 0 | 0 | 30 | 331 | 99 | 0 | 0 | 90 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 72 | 12 | 0 | 46 | 0 | 40 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 15 | 158 | 0 | 360 | 285 | 49 | 177 | 36 | 17 | 50 | 200 | 0 | 18 | 114 | 36 | 34 | 0 | 32 | 300 | 320 | 350 | 40 | 40 | 5 | 136 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 0 | 58 | 58 | 53 | 0 | 0 | 12 | 7917 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1372.42 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 204 | 0 | 180 | 0 | 0 | 0 | 0 | 5.5 | 160 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 0 | 1244 | 0 | 5713.92 | 13630.92 | 85.27
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 278 | 0 | 0 | 0 | 17 | 0 | 34 | 140 | 0 | 0 | 0 | 17 | 30 | 16 | 350 | 302 | 500 | 0 | 0 | 30 | 328 | 99 | 0 | 0 | 90 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 12 | 0 | 46 | 0 | 42 | 565 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 158 | 0 | 360 | 285 | 49 | 164 | 36 | 17 | 50 | 155 | 0 | 18 | 114 | 34 | 34 | 0 | 32 | 305 | 320 | 381 | 40 | 40 | 5 | 134 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 0 | 59 | 58 | 70 | 0 | 0 | 12 | 7610.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 1363.79 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 184 | 0 | 169 | 0 | 0 | 0 | 0 | 5.5 | 161 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1150 | 0 | 5529.29 | 13139.79 | 85.27
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 265 | 0 | 0 | 0 | 17 | 0 | 34 | 140 | 0 | 0 | 0 | 17 | 30 | 16 | 420 | 301 | 583 | 0 | 0 | 30 | 332 | 100 | 0 | 0 | 90 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 12 | 0 | 46 | 0 | 42 | 562 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 158 | 0 | 360 | 285 | 49 | 152 | 36 | 17 | 50 | 155 | 0 | 18 | 114 | 34 | 34 | 0 | 32 | 310 | 320 | 348 | 40 | 40 | 5 | 138 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 0 | 60 | 72 | 70 | 0 | 0 | 12 | 7730.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 1371.94 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 174 | 0 | 151 | 0 | 0 | 0 | 0 | 5.5 | 155 | 56 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 0 | 1170 | 0 | 5577.44 | 13307.94 | 85.26
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 254 | 0 | 0 | 0 | 0 | 0 | 34 | 110 | 0 | 0 | 0 | 0 | 30 | 16 | 420 | 306 | 450 | 0 | 0 | 32 | 328 | 100 | 0 | 0 | 70 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 12 | 0 | 46 | 0 | 42 | 562 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1170 | 0 | 51 | 0 | 108 | 0 | 360 | 285 | 50 | 182 | 36 | 42 | 50 | 155 | 0 | 18 | 70 | 30 | 34 | 0 | 32 | 305 | 320 | 380 | 40 | 40 | 5 | 147 | 24 | 0 | 83 | 30 | 0 | 18 | 144 | 0 | 68 | 134 | 68 | 0 | 0 | 12 | 7513.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 0 | 1296.39 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 166 | 0 | 130 | 0 | 0 | 0 | 0 | 5.5 | 154 | 57 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 10 | 108 | 180 | 0 | 0 | 1244 | 0 | 5431.89 | 12945.39 | 85.26
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 247 | 0 | 0 | 0 | 0 | 0 | 30 | 48 | 0 | 0 | 0 | 0 | 30 | 16 | 370 | 280 | 450 | 0 | 0 | 32 | 335 | 100 | 0 | 0 | 35 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 46 | 0 | 42 | 565 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 51 | 0 | 108 | 0 | 360 | 285 | 50 | 199 | 36 | 52 | 50 | 155 | 0 | 18 | 70 | 28 | 34 | 0 | 32 | 300 | 320 | 350 | 40 | 40 | 5 | 154 | 24 | 0 | 83 | 30 | 0 | 18 | 143 | 0 | 69 | 115 | 70 | 0 | 0 | 12 | 7186.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 1213.92 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 152 | 0 | 119 | 0 | 0 | 0 | 0 | 5.5 | 157 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 10 | 108 | 180 | 0 | 0 | 1100 | 0 | 4937.42 | 12123.92 | 85.25
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 16 | 370 | 307 | 450 | 0 | 0 | 32 | 335 | 100 | 0 | 0 | 0 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 108 | 0 | 360 | 285 | 50 | 210 | 36 | 44 | 50 | 155 | 0 | 18 | 52 | 28 | 36 | 0 | 32 | 290 | 320 | 350 | 40 | 40 | 5 | 152 | 24 | 0 | 83 | 30 | 0 | 18 | 141 | 0 | 45 | 115 | 71 | 0 | 0 | 12 | 6706.5 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 1107 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 148 | 0 | 117 | 0 | 0 | 0 | 0 | 5 | 152 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 108 | 180 | 0 | 0 | 850 | 0 | 4442 | 11148.5 | 85.25
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 30 | 0 | 370 | 298 | 450 | 0 | 0 | 32 | 333 | 100 | 0 | 4 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 3 | 51 | 0 | 108 | 0 | 360 | 285 | 50 | 218 | 33 | 17 | 50 | 155 | 0 | 18 | 52 | 30 | 52.2 | 9 | 32 | 310 | 320 | 370 | 41 | 40 | 5 | 156 | 24 | 0 | 83 | 30 | 0 | 18 | 142 | 0 | 45 | 115 | 72 | 0 | 1.82 | 12 | 6703.02 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.12 | 415 | 0 | 1003 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 7.08 | 180 | 0 | 188 | 0 | 143 | 0 | 0 | 0 | 0.51 | 5.5 | 149 | 57 | 0 | 2 | 0 | 0 | 0 | 0.5 | 17 | 0 | 0 | 150 | 7 | 120 | 180 | 0 | 0 | 800 | 0 | 4416.71 | 11119.73 | 85.24
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 30 | 0 | 370 | 302 | 450 | 0 | 0 | 32 | 333 | 100 | 0 | 12 | 17 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 42 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 8 | 51 | 0 | 108 | 0 | 360 | 285 | 50 | 195 | 33 | 16 | 50 | 120 | 0 | 18 | 52 | 28 | 52.2 | 23 | 32 | 315 | 320 | 370 | 41 | 40 | 5 | 154 | 24 | 0 | 83 | 30 | 0 | 18 | 142 | 0 | 45 | 115 | 66 | 1 | 3.81 | 12 | 6711.01 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.76 | 413 | 0 | 1010 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 19.13 | 184 | 0 | 211 | 0 | 185 | 0 | 0 | 0 | 1.66 | 5.5 | 154 | 57 | 0 | 8 | 0 | 0 | 0 | 1.6 | 50 | 0.2 | 0 | 150 | 7 | 108 | 180 | 0 | 0 | 794 | 0 | 4533.85 | 11244.86 | 85.24
09:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 61 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 30 | 0 | 400 | 305 | 550 | 0 | 0 | 31 | 328 | 98 | 0 | 20 | 17 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 46 | 0 | 40 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 12 | 51 | 0 | 108 | 0 | 355 | 285 | 47 | 200 | 35 | 17 | 50 | 108 | 0 | 19 | 34 | 30 | 24 | 35 | 32 | 310 | 320 | 362 | 42 | 40 | 5 | 157 | 24 | 0 | 83 | 30 | 0 | 18 | 142 | 0 | 45 | 115 | 61 | 1 | 27.85 | 12 | 6786.85 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 411 | 0 | 1015 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 34.36 | 186 | 0 | 209 | 0 | 202 | 0 | 0 | 0 | 2.95 | 5.5 | 151 | 57 | 0 | 16 | 0 | 0 | 0 | 3.1 | 97 | 0.38 | 0 | 200 | 6 | 108 | 220 | 0 | 0 | 830 | 0 | 4797.29 | 11584.14 | 85.23
10:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 61 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 30 | 0 | 400 | 279 | 550 | 0 | 0 | 30 | 327 | 98 | 0 | 26 | 52 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 3 | 46 | 0 | 40 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 17 | 51 | 0 | 108 | 0 | 360 | 285 | 45 | 183 | 35 | 17 | 50 | 120 | 0 | 19 | 34 | 32 | 8 | 52 | 0 | 305 | 320 | 350 | 40 | 40 | 5 | 152 | 24 | 0 | 80 | 30 | 0 | 18 | 144 | 0 | 45 | 115 | 64 | 2 | 39.61 | 12 | 6870.61 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.56 | 413 | 0 | 1015 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 46.41 | 184 | 0 | 207 | 0 | 210 | 0 | 0 | 0 | 4.06 | 5.5 | 154 | 57 | 0 | 23 | 0 | 0 | 0 | 4.5 | 131 | 0.53 | 0 | 200 | 5 | 108 | 220 | 0 | 0 | 895 | 0 | 5022.56 | 11893.17 | 85.22
11:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 61 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 30 | 0 | 450 | 296 | 583 | 0 | 0 | 30 | 318 | 94 | 0 | 29 | 52 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 4 | 46 | 0 | 40 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 13 | 51 | 0 | 133 | 0 | 340 | 285 | 41 | 208 | 34 | 17 | 50 | 120 | 0 | 19 | 34 | 26 | 8 | 61 | 0 | 305 | 320 | 390 | 40 | 38 | 5 | 154 | 24 | 0 | 80 | 30 | 0 | 18 | 144 | 0 | 45 | 115 | 64 | 2 | 46.6 | 12 | 7145.6 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.96 | 412 | 0 | 1018 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 55 | 183 | 0 | 206 | 0 | 208 | 0 | 0 | 0 | 4.86 | 5.5 | 152 | 56 | 0 | 28 | 0 | 0 | 0 | 5.5 | 157 | 0.61 | 0 | 250 | 6 | 120 | 220 | 0 | 0 | 922 | 0 | 5176.43 | 12322.03 | 85.21
12:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 61 | 387 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | 0 | 0 | 17 | 35 | 30 | 0 | 450 | 279 | 520 | 0 | 0 | 28 | 316 | 95 | 0 | 31 | 90 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 12 | 4 | 46 | 0 | 41 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 133 | 0 | 320 | 285 | 42 | 188 | 34 | 18 | 50 | 125 | 0 | 19 | 70 | 32 | 8 | 65 | 0 | 295 | 320 | 301 | 40 | 38 | 5 | 141 | 24 | 0 | 80 | 30 | 0 | 18 | 144 | 0 | 45 | 142 | 63 | 2 | 46.86 | 12 | 7346.86 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.42 | 461 | 0 | 1173 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 61.63 | 181 | 0 | 180 | 0 | 203 | 0 | 0 | 0 | 5.49 | 5.5 | 156 | 56 | 35 | 30 | 34 | 0 | 0 | 5.8 | 166 | 0.66 | 0 | 307 | 6 | 100 | 180 | 0 | 0 | 1022 | 0 | 5535.5 | 12882.36 | 85.21
13:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 61 | 388 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 17 | 35 | 30 | 0 | 450 | 294 | 583 | 0 | 0 | 28 | 314 | 94 | 0 | 31 | 90 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 24 | 12 | 4 | 46 | 0 | 41 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 17 | 51 | 0 | 133 | 0 | 342 | 285 | 42 | 185 | 32 | 35 | 50 | 155 | 0 | 19 | 70 | 30 | 8 | 63 | 0 | 315 | 320 | 351 | 39 | 38 | 5 | 147 | 24 | 0 | 80 | 30 | 0 | 18 | 144 | 0 | 45 | 150 | 63 | 2 | 45.42 | 12 | 7604.42 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.65 | 532 | 0 | 1176 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 58.48 | 182 | 0 | 202 | 0 | 204 | 0 | 0 | 0 | 5.18 | 5.5 | 161 | 56 | 35 | 29 | 34 | 0 | 0 | 5.6 | 161 | 0.61 | 0 | 307 | 9 | 110 | 220 | 0 | 0 | 1058 | 0 | 5702.02 | 13306.44 | 85.21
14:00 | 0 | 17 | 9 | 0 | 0 | 0 | 0 | 61 | 399 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 17 | 35 | 30 | 0 | 420 | 297 | 583 | 0 | 0 | 28 | 312 | 82 | 0 | 27 | 90 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 24 | 0 | 3 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 15 | 51 | 0 | 130 | 0 | 315 | 285 | 38 | 204 | 31 | 34 | 50 | 155 | 0 | 19 | 70 | 36 | 8 | 55 | 0 | 295 | 320 | 374 | 39 | 38 | 5 | 151 | 24 | 0 | 79 | 30 | 0 | 18 | 143 | 0 | 45 | 148 | 64 | 2 | 43.6 | 12 | 7439.6 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.96 | 478 | 0 | 1168 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 47.58 | 180 | 0 | 180 | 0 | 173 | 0 | 0 | 0 | 4.24 | 5.5 | 156 | 55 | 35 | 24 | 34 | 0 | 0 | 5 | 142 | 0.56 | 0 | 210 | 9 | 100 | 220 | 0 | 0 | 1063 | 0 | 5426.84 | 12866.44 | 85.21
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 61 | 397 | 0 | 0 | 0 | 0 | 0 | 32 | 44 | 0 | 0 | 17 | 35 | 0 | 0 | 450 | 296 | 583 | 0 | 0 | 28 | 310 | 96 | 0 | 21 | 90 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 56 | 0 | 2 | 46 | 0 | 41 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 12 | 51 | 0 | 177 | 0 | 343 | 285 | 36 | 183 | 31 | 34 | 50 | 155 | 0 | 19 | 98 | 38 | 8 | 42 | 0 | 300 | 320 | 352 | 39 | 38 | 5 | 151 | 24 | 0 | 78 | 30 | 0 | 18 | 143 | 0 | 58 | 141 | 65 | 1 | 32.3 | 12 | 7637.3 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.86 | 624 | 0 | 1272 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 37.31 | 178 | 0 | 195 | 0 | 197 | 0 | 0 | 0 | 3.33 | 5.5 | 121 | 55 | 35 | 19 | 34 | 0 | 0 | 3.9 | 103 | 0.43 | 0 | 307 | 7 | 88 | 220 | 0 | 0 | 1150 | 0 | 5756.33 | 13393.63 | 85.2
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 62 | 402 | 0 | 0 | 0 | 0 | 0 | 44 | 74 | 0 | 0 | 17 | 35 | 30 | 0 | 450 | 292 | 583 | 0 | 0 | 28 | 312 | 96 | 0 | 13 | 108 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 60 | 0 | 1 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 7 | 51 | 0 | 159 | 0 | 341 | 285 | 36 | 183 | 31 | 34 | 50 | 173 | 0 | 19 | 114 | 36 | 8 | 25 | 0 | 290 | 320 | 352 | 39 | 38 | 5 | 151 | 24 | 0 | 79 | 30 | 0 | 18 | 143 | 0 | 66 | 130 | 68 | 1 | 20.26 | 12 | 7693.26 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.26 | 580 | 0 | 1262 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 25.41 | 177 | 0 | 200 | 0 | 202 | 0 | 0 | 0 | 2.31 | 5.5 | 125 | 54 | 35 | 10 | 34 | 0 | 0 | 2.3 | 62 | 0.3 | 0 | 307 | 10 | 88 | 220 | 0 | 0 | 1200 | 0 | 5643.08 | 13336.34 | 85.2
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 72 | 402 | 0 | 0 | 0 | 0 | 0 | 50 | 104 | 0 | 0 | 17 | 35 | 30 | 0 | 450 | 279 | 583 | 0 | 0 | 28 | 310 | 96 | 0 | 5 | 108 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 60 | 0 | 1 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 2 | 51 | 0 | 167 | 0 | 337 | 285 | 38 | 202 | 31 | 41 | 50 | 180 | 0 | 19 | 114 | 32 | 8 | 9 | 13 | 305 | 320 | 366 | 39 | 38 | 5 | 151 | 24 | 0 | 81 | 30 | 0 | 18 | 143 | 0 | 66 | 140 | 68 | 0 | 7.27 | 12 | 7804.27 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.39 | 560 | 0 | 1257 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 9.77 | 178 | 0 | 199 | 0 | 201 | 0 | 0 | 0 | 0.86 | 5.5 | 170 | 55 | 70 | 4 | 82 | 0 | 0 | 0.9 | 21 | 0.11 | 0 | 307 | 7 | 90 | 220 | 0 | 0 | 1200 | 0 | 5626.53 | 13430.8 | 85.2
18:00 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 72 | 401 | 0 | 0 | 5 | 0 | 0 | 50 | 133 | 15 | 0 | 17 | 54 | 30 | 4 | 450 | 295 | 583 | 0 | 17 | 32 | 313 | 96 | 0 | 0 | 108 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 2 | 0 | 60 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 51 | 16 | 169 | 0 | 345 | 285 | 41 | 194 | 33 | 85 | 50 | 180 | 5 | 19 | 114 | 30 | 8 | 1 | 29 | 310 | 320 | 364 | 39 | 38 | 5 | 152 | 24 | 0 | 81 | 30 | 0 | 18 | 143 | 0 | 95 | 168 | 69 | 0 | 0.49 | 12 | 8097.49 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 556 | 14 | 1257 | 0 | 0 | 35 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 22 | 0.47 | 177 | 0 | 199 | 0 | 202 | 0 | 0 | 0 | 0.06 | 5.5 | 169 | 54 | 115 | 0 | 99 | 0 | 0 | 0 | 2 | 0.01 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1200 | 0 | 5699.7 | 13797.19 | 85.19
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 72 | 401 | 0 | 0 | 26 | 5 | 0 | 50 | 133 | 15 | 0 | 23 | 90 | 0 | 16 | 450 | 292 | 583 | 0 | 35 | 32 | 318 | 97 | 0 | 0 | 108 | 15 | 7 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 34 | 24 | 0 | 98 | 48 | 0 | 46 | 0 | 44 | 575 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 43 | 172 | 0 | 350 | 285 | 42 | 191 | 31 | 91 | 50 | 180 | 27 | 20 | 114 | 32 | 8 | 0 | 22 | 305 | 320 | 364 | 39 | 38 | 5 | 146 | 24 | 0 | 81 | 30 | 0 | 18 | 143 | 0 | 96 | 170 | 69 | 0 | 0 | 12 | 8508 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 35 | 1362 | 0 | 50 | 45 | 2 | 0 | 49 | 0 | 18 | 0 | 0 | 22 | 0 | 175 | 0 | 201 | 0 | 200 | 0 | 0 | 0 | 0 | 5.5 | 167 | 54 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1206 | 3 | 5928.5 | 14436.5 | 85.18
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 72 | 403 | 0 | 0 | 54 | 35 | 0 | 50 | 136 | 45 | 0 | 55 | 108 | 0 | 41 | 450 | 260 | 583 | 0 | 35 | 32 | 315 | 97 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 34 | 24 | 0 | 98 | 48 | 0 | 46 | 4 | 42 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 171 | 0 | 360 | 285 | 42 | 182 | 34 | 90 | 50 | 180 | 28 | 20 | 114 | 34 | 25 | 0 | 22 | 275 | 320 | 350 | 41 | 38 | 5 | 151 | 24 | 0 | 81 | 30 | 0 | 18 | 143 | 10 | 96 | 172 | 71 | 0 | 0 | 12 | 8707 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 53 | 1375 | 0 | 50 | 50 | 70 | 0 | 49 | 0 | 25 | 0 | 0 | 22 | 0 | 175 | 0 | 205 | 0 | 201 | 0 | 0 | 0 | 0 | 5.5 | 169 | 54 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1232 | 17 | 6085.5 | 14792.5 | 85.18
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 82 | 402 | 0 | 0 | 54 | 35 | 0 | 50 | 136 | 45 | 0 | 54 | 108 | 0 | 43 | 450 | 280 | 583 | 0 | 35 | 32 | 324 | 38 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 12 | 15 | 0 | 0 | 3 | 34 | 24 | 0 | 98 | 48 | 0 | 46 | 3 | 34 | 575 | 0 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 1230 | 0 | 51 | 73 | 172 | 0 | 360 | 285 | 43 | 182 | 34 | 90 | 50 | 180 | 27 | 20 | 114 | 34 | 25 | 0 | 28 | 280 | 320 | 350 | 40 | 38 | 5 | 151 | 24 | 0 | 82 | 30 | 0 | 18 | 143 | 14 | 96 | 172 | 71 | 0 | 0 | 12 | 8716 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 53 | 1363 | 0 | 50 | 50 | 70 | 0 | 49 | 0 | 32 | 0 | 0 | 22 | 0 | 174 | 0 | 199 | 0 | 168 | 0 | 0 | 0 | 0 | 5.5 | 164 | 54 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1230 | 17 | 6033.5 | 14749.5 | 85.18
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 83 | 401 | 0 | 0 | 35 | 35 | 0 | 50 | 136 | 0 | 0 | 55 | 108 | 0 | 85 | 450 | 268 | 583 | 0 | 35 | 32 | 324 | 99 | 0 | 0 | 108 | 15 | 15 | 0 | 0 | 17 | 15 | 0 | 0 | 12 | 34 | 24 | 0 | 95 | 48 | 0 | 46 | 16 | 40 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1228 | 0 | 51 | 115 | 172 | 0 | 360 | 285 | 43 | 182 | 35 | 90 | 50 | 170 | 29 | 20 | 98 | 38 | 25 | 0 | 30 | 290 | 320 | 383 | 40 | 38 | 5 | 152 | 24 | 0 | 82 | 28 | 0 | 18 | 143 | 0 | 97 | 182 | 71 | 0 | 0 | 12 | 8838 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 80 | 1377 | 0 | 50 | 60 | 70 | 0 | 49 | 0 | 30 | 0 | 0 | 22 | 0 | 171 | 0 | 180 | 0 | 203 | 0 | 0 | 0 | 0 | 5.5 | 173 | 53 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1232 | 17 | 6151.5 | 14989.5 | 85.17
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 83 | 401 | 0 | 0 | 0 | 17 | 0 | 34 | 92 | 0 | 0 | 17 | 72 | 24 | 101 | 450 | 335 | 583 | 0 | 0 | 32 | 327 | 99 | 0 | 0 | 108 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28 | 0 | 0 | 95 | 24 | 0 | 46 | 17 | 40 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 180 | 0 | 360 | 285 | 45 | 184 | 35 | 70 | 50 | 155 | 28 | 20 | 114 | 40 | 25 | 0 | 30 | 295 | 320 | 387 | 39 | 39 | 5 | 163 | 24 | 0 | 82 | 30 | 0 | 18 | 143 | 0 | 97 | 184 | 83 | 0 | 0 | 12 | 8672 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 70 | 1372 | 0 | 0 | 60 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 169 | 0 | 205 | 0 | 199 | 0 | 69 | 0 | 0 | 5.5 | 176 | 53 | 92 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 130 | 220 | 0 | 0 | 1240 | 0 | 6072.5 | 14744.5 | 85.17
23:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 83 | 403 | 0 | 0 | 0 | 17 | 0 | 34 | 92 | 0 | 0 | 17 | 72 | 24 | 102 | 450 | 294 | 583 | 0 | 0 | 32 | 326 | 98 | 0 | 0 | 108 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 34 | 0 | 0 | 95 | 24 | 0 | 46 | 29 | 42 | 575 | 0 | 0 | 0 | 8 | 26 | 0 | 0 | 0 | 0 | 1225 | 0 | 51 | 125 | 155 | 0 | 355 | 285 | 46 | 215 | 35 | 48 | 50 | 155 | 28 | 20 | 114 | 40 | 25 | 0 | 30 | 305 | 320 | 366 | 39 | 38 | 5 | 156 | 24 | 0 | 83 | 30 | 0 | 18 | 143 | 0 | 96 | 184 | 87 | 0 | 0 | 10 | 8611 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 70 | 1374 | 0 | 0 | 60 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 170 | 0 | 175 | 0 | 190 | 0 | 97 | 0 | 0 | 5.5 | 168 | 53 | 92 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 65 | 220 | 0 | 0 | 1240 | 0 | 5991.5 | 14602.5 | 85.16
Total KWH | 0 | 669120 | 285120 | 0 | 0 | 0 | 0 | 1606863.64 | 8420400 | 0 | 0 | 164520 | 211680 | 0 | 727056 | 1666560 | 115418 | 0 | 467431 | 1029600 | 610920 | 551040 | 9865500 | 7063593 | 12954091 | 0 | 163843 | 704400 | 7796167 | 2376000 | 0 | 219256 | 1872000 | 328800 | 306720 | 0 | 0 | 37636 | 35127 | 0 | 0 | 120000 | 207679 | 104160 | 0 | 1194480 | 322560 | 26277 | 1089240 | 112073 | 1061760 | 12669090.91 | 0 | 0 | 0 | 96483.6 | 187345 | 0 | 0 | 0 | 0 | 25238179 | 100305 | 1061092 | 652363 | 3429090 | 0 | 8807100 | 6912000 | 1066560 | 4643000 | 821880 | 969600 | 1202540 | 3846240 | 152880 | 431120 | 2095320 | 767040 | 561605 | 445155 | 499504 | 7452500 | 7662900 | 9079000 | 952000 | 910920 | 113328 | 3609327 | 553632 | 0 | 1951680 | 710880 | 0 | 437000 | 3020220 | 39960 | 1623600 | 3230400 | 1572480 | 13900 | 316410 | 294240 | 184686960.15 | 22017454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691200 | 12887270 | 380640 | 29607273 | 0 | 126791 | 1120000 | 316896 | 0 | 189152 | 0 | 55796 | 0 | 771544 | 142640 | 404248 | 4288455 | 0 | 4739018 | 0 | 4570709 | 0 | 219127 | 0 | 35160 | 131058 | 3821000 | 1284654 | 1128723 | 192680 | 1142380 | 0 | 0 | 38608.8 | 1112400 | 4447.5 | 0 | 6393000 | 210500 | 2458000 | 5085560 | 0 | 0 | 26849454.55 | 40800 | 132456638.85 | 317143599

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12882.36 | MW | 12:00 Hr. | Energy Generated |  |  | 317.1436 |  | MKWHr.
| Day Peak Demand |  |  | 12882.36 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.445 |  | MKWHr.
| Evening Peak Generation |  |  | 14989.5 | MW | 21:00 Hr. | Energy Demand |  |  | 317.5886 |  | MKWHr.
| Evening Peak Demand |  |  | 14989.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 37.9 |  | °C
| Minimum Generation of the Day |  |  | 11119.73 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1053.03 |  | MMCFD
| Maximum Generation of the Day |  |  | 14989.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.1886 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 52.0335 | 0 | 7.9234 | 0 | 0 | 0.21926 | 0 | 0 | 60.1761 | Gas | 142.3179 | Gas | 496629720.714
| Chattogram Zone |  |  | 1.0618 | 37.9073 | 2.2975 | 0 | 1.0892 | 0.12658 | 0 | 0.12 | 42.6024 | Coal | 89.1426 | Coal | 632533454.7843
| Cumilla Zone |  |  | 28.3744 | 0 | 8.7775 | 0 | 0 | 0.44516 | 0.76704 | 0 | 38.3641 | HFO | 27.7105 | HFO | 483487790.312
| Mymensingh Zone |  |  | 1.5725 | 0 | 5.1882 | 0 | 0 | 0.33031 | 0 | 0 | 7.091 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.4534 | Hydro | 1.0892 | Hydro | 108924
| Khulna Zone |  |  | 0 | 12.8873 | 0.38064 | 0 | 0 | 0.6912 | 22.0175 | 0 | 35.9766 | Solar | 4.3716 | Solar | 70695233.753
| Barishal Zone |  |  | 7.7541 | 33.2425 | 0.0408 | 0 | 0 | 0.0044475 | 0 | 0 | 41.0418 | Import | 52.3918 | Import | 277450762.46
| Rajshahi Zone |  |  | 15.0684 | 0 | 0.83127 | 0 | 0 | 1.211 | 29.6073 | 0 | 46.7179 | Wind | 0.12 | Wind | 1756800
| Rangpur Zone |  |  | 0 | 5.1057 | 2.2711 | 0 | 0 | 1.3437 | 0 | 0 | 8.7204
| Total |  |  | 142.3179 | 89.1426 | 27.7105 | 0 | 1.0892 | 4.3716 | 52.3918 | 0.12 | 317.1436
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 496629720.714 |  | Hydro | 108924
|  |  |  | Coal | 632533454.7843 |  | Solar | 70695233.753
|  |  |  | HFO | 483487790.312 |  | Import | 277450762.46
|  |  |  | HSD | 0 |  | Wind | 1756800
[5 empty] | Total: | 196,26,62,686 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0175 | Peak Hr Flow | 919.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 24642781.86 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.6073 | Peak Hr Flow | 1377.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 260 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.76704 | Peak Hr Flow | 38.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 554 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.3918 | Peak Hr Flow | 2334.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4617
|  |  |  | Chattogram |  | 0 |  | 1443
|  |  |  | Cumilla |  | 0 |  | 1431
|  |  |  | Mymensingh |  | 0 |  | 1322
|  |  |  | Sylhet |  | 0 |  | 587
|  |  |  | Khulna |  | 0 |  | 1844
|  |  |  | Barishal |  | 0 |  | 486
|  |  |  | Rajshahi |  | 0 |  | 1604
|  |  |  | Rangpur |  | 0 |  | 941
|  |  |  | Total |  | 0 |  | 14275
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Mirpur 132/33kV S/S T2 LT is restored.
|  | 08:30 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 LT is restored.
|  | 08:30 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 HT is restored.
| 08:33 | 09:15 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 HT Scheduled S/D Due to High temp. Removed
Purposed.
| 08:33 | 09:15 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 LT Scheduled S/D Due to High Temp. Removed
Purposed.
| 08:37 | 10:06 | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to Preventive maintenance work.
| 08:38 | 10:04 | Mirpur 132/33kV S/S T1 HT Scheduled S/D Due to Preventive maintenance work.
| 08:39 | 17:15 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to Oil leakage from buchholz relay
| 08:39 | 17:16 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to Oil leakage from buchholz relay
| 09:05 | 10:20 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to hotspot maintenance of 33kV | [7 empty] | 35.0MW load
|  |  | Bus Section DS by LPBS | [7 empty] | interrup.
| 09:05 | 10:20 | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to hotspot maintenance of 33kV
Bus Section DS by LPBS
| 09:36 | 11:11 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end.
| 09:50 | 11:20 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to Temperature related work
| 09:50 | 11:20 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to Temperature related work
| 10:07 | 10:15 | Goalpara- Khulna (C) 132kV Ckt-1 Forced S/D from Goalpara 132/33kV end Due to লাইনের
Y-Phase এ current 0(Zero)Amp show করায় ALDC, khulna & XEN Gmd Khulna (North) এর নির্দেশে
Line বন্ধ করা হয়।
| 10:15 | 11:37 | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to Red Hot Maintenance of REB-2 Feeder. | [7 empty] | 16.0MW load
interrup.
| 10:15 | 11:37 | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to Red Hot Maintenance of REB-2 Feeder. | [7 empty] | 16.0MW load
interrup.
|  | 10:20 | Ramganj 132/33kV S/S Transformer -02 LT is restored.
|  | 10:20 | Ramganj 132/33kV S/S Transformer -02 HT is restored.
|  | 11:38 | Mahasthangarh 132/33kV S/S 406T MTR1 HT is restored.
|  | 11:39 | Mahasthangarh 132/33kV S/S 406T MTR1 LT is restored.
|  | 12:53 | BSRM-GPH 230 kV Ckt-1 is restored.
|  | 12:53 | BSRM-GPH 230 kV Ckt-2 is restored.
| 13:03 | 14:49 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing Z1,AR
BLOCK,VT FAIL relays. and from Ghorashal 230kV end showing Distance Protection Relay
relays.
| 18:14 |  | Goalpara- Khulna (C) 132kV Ckt-1 Forced S/D from Khulna (C) end Due to Problem of
circuit breaker
| 21:00 |  | Evening peak Generation is 14989 MW
| 21:37 |  | Sirajgonj 400 MW CCPP Unit-4 GT Synchronized with remarks:- Started after Scheduled 60
Hours Maintenance.
| 21:37 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
| 22:21 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 22:34 |  | Bhola 225 MW CCPP GT-1 tripped.
| 23:24 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 23:24 |  | Sirajgonj 400 MW CCPP Unit-4 ST Synchronized with remarks:- ST synchronized after a 60
hours scheduled Maintenance.
| 23:56 |  | Bhola 225 MW CCPP GT-1 was sync.
|  | 01:20 | Aminbazar-Manikgonj PP 132kV Ckt-1 is restored.
| 04:20 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- ST
| 04:22 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 04:22 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT( false )
| 04:22 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT( false )
| 06:23 |  | Siddhirganj 132/33kV S/S T-2 LT Forced S/D Due to Red hot maintenance work.
| 06:24 |  | Siddhirganj 132/33kV S/S T-2 HT Forced S/D Due to Red hot maintenance work
| 06:39 |  | Mymensingh-Netrokona 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to Due to
high Temperature maintenances of T-clamp and B-Bus DS-R Ph clamp Net ckt-2
| 07:00 |  | Minimum Generation: 11404 MW.
| 07:15 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Due to high
Temperature maintenances of B-Bus DS(412S) Tr-2X-F
| 07:15 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Due to high
Temperature maintenances of B-Bus DS(412S)-B Ph clamp Tr-2 X-F
| 07:26 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Hot Spot Maintenance of TR-2
& Incoming-2 CB
| 07:27 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to High
Temperature Junction Point Maintenance of Line DS.
| 07:27 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Hot Spot Maintenance of TR-2
& Incoming-2 CB
| 07:36 |  | Cumilla(S) 132/33kV S/S 53.2MW Lakthanavi Tripped showing REB500 REC650 relays.
| 07:45 |  | Mymensingh 132/33kV S/S Bus B Scheduled S/D Due to Due to high Temperature maintenances
of T-clamp and B-Bus DS(22-R Ph clamp Net ckt-2 & B-Bus DS(412S) Tr-2X-F
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 83 | 1606863.64 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 8420400 | DP High
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9865500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 268 | 7063593 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 99 | 2376000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7796167 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 164520 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 136 | 1666560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 467431 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 163843 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 328800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 306720 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 610920 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 704400 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 285120 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 115418 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 50 | 727056 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 669120 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 85 | 551040 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1029600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 219256 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 211680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 12954091 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1872000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2985 | 60176098.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 96483.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 100305 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1089240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | Under Maintenance
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 187345 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 104160 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 207679 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 95 | 1194480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 40 | 1061760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26277 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 35127 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 112073 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 322560 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 37636 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1228 | 25238179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 12 | 120000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12669090.91 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2175 | 42602395.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4643000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8807100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 6912000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 821880 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 43 | 1066560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 172 | 3429090 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1061092 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 652363 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 30 | 499504 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1202540 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3846240 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 767040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 561605 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 431120 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 2095320 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 152880 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 969600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 445155 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1793 | 38364089
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 1572480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 182 | 3230400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1623600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 316410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 39960 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 362 | 7090990
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 952000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 910920 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3609327 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 113328 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 28 | 710880 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1951680 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 143 | 3020220 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 437000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 553632 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7452500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 9079000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7662900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1523 | 36453387
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 919 | 22017454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 80 | 380640 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 691200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 619 | 12887270 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1618 | 35976564
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 210500 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 90 | 2458000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 26849454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5085560 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 40800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6393000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4447.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1876 | 41041762.05
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 60 | 1120000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 126791 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 30 | 55796 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 4288455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4739018 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 203 | 4570709 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 219127 | Under Maintenance
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 142640 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 131058 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 49 | 189152 | one Engine (E#12) Under 12K RH Maintenance.
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 316896 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35160 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1377 | 29607273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 404248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 771544 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2217.5 | 46717867
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1284654 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 173 | 3821000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1142380 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38608.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1128723 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 192680 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1112400 | -
Rangpur Area Total |  |  |  |  | 950 | 440 | 8720445.8
Eastern Grid Total |  |  |  |  | 16921.242 | 8838 | 184686960.15
Western Grid Total |  |  |  |  | 11614.5 | 6151.5 | 132456638.85
National Grid Total |  |  |  |  | 28535.742 | 14989.5 | 317143599
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9399.84 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4875 | MW
i) Dhaka area |  |  | 4616.84 |  | MW | i) Khulna area |  |  |  | 1844 | MW
ii) Chattogram area |  |  | 1443 |  | MW | ii) Barishal area |  |  |  | 486.2 | MW
iii) Cumilla area |  |  | 1431 |  | MW | iii) Rajshahi area |  |  |  | 1603.8 | MW
iv) Mymensingh area |  |  | 1322 |  | MW | iv) Rangpur area |  |  |  | 941 | MW
v) Sylhet area |  |  | 587 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14274.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 19:00 | 67 | Jaldhaka | 84 | 17:00 | 133 | Payra | 34 | 22:00
2 | AKSML | 116 | 01:00 | 68 | Jamalpur | 142 | 18:30 | 134 | Postogola | 49 | 19:00
3 | Aftabnagar | 34 | 19:00 | 69 | Jashore | 151 | 21:00 | 135 | Purbachal | 17 | 00:00
4 | Agargaon | 98 | 19:00 | 70 | Jhenaidah | 139 | 22:00 | 136 | Purbasadipur | 123 | 19:30
5 | Agrabad | 86 | 21:00 | 71 | Joydebpur | 143 | 18:00 | 137 | Rahanpur | 30 | 00:00
6 | Amnura | 58 | 19:30 | 72 | Joypurhat | 72 | 21:00 | 138 | Rahim | 2 | 00:00
7 | Ashuganj | 93 | 18:30 | 73 | Juldah | 14 | 00:00 | 139 | Rajbari | 76 | 19:30
8 | BSRM | 194 | 18:30 | 74 | KSRM | 12 | 16:00 | 140 | Rajendrapur | 111 | 00:00
9 | Bagerhat | 90.5 | 20:00 | 75 | Kabirpur | 195 | 00:00 | 141 | Rajshahi | 100 | 00:00
10 | Bajitpur | 52 | 21:00 | 76 | Kachua | 95 | 20:00 | 142 | Rajshahi-230 | 87 | 21:00
11 | Bakulia | 90 | 00:00 | 77 | Kallyanpur | 105 | 00:00 | 143 | Ramganj | 122 | 18:30
12 | Banani | 30 | 19:00 | 78 | Kalurghat | 30 | 12:00 | 144 | Rampur | 40 | 00:00
13 | Bangabhaban | 4 | 13:00 | 79 | Kamrangirchar | 59.4 | 00:00 | 145 | Rangamati | 16 | 18:30
14 | Barapukuria | 72 | 22:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 151 | 18:00
15 | Barguna | 22 | 22:00 | 81 | Kasba | 41 | 21:00 | 147 | Ruppur | 7.2 | 11:00
16 | Barishal | 106 | 21:00 | 82 | Kazla | 87 | 11:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 104 | 21:00 | 83 | Keranigonj | 73 | 00:00 | 149 | Saidpur | 102 | 17:00
18 | Baroaulia | 54 | 22:00 | 84 | Khagrachori | 32 | 18:30 | 150 | Satkhira | 145 | 21:00
19 | Baroirhat | 65 | 21:00 | 85 | Khulna | 90 | 21:00 | 151 | Satmasjid | 97 | 19:00
20 | Bashundhara | 165 | 19:00 | 86 | Khulshi | 152 | 23:00 | 152 | Savar | 174 | 00:00
21 | BashundharaCement | 8 | 09:00 | 87 | Kishoreganj | 156 | 21:00 | 153 | SevenRings | 18.36 | 02:00
22 | Beanibazar | 68 | 18:30 | 88 | Kodda | 240 | 00:00 | 154 | ShahCement | 37 | 00:00
23 | Benapole | 72 | 19:30 | 89 | Kulaura | 46 | 19:00 | 155 | Shahjadpur | 82 | 19:30
24 | Bhaluka | 152 | 19:30 | 90 | Kurigram | 68 | 18:00 | 156 | Shahjibazar | 131 | 22:00
25 | Bhandaria | 57 | 22:00 | 91 | Kushtia | 138 | 19:30 | 157 | Shahmirpur | 44 | 00:00
26 | Bhangura | 41 | 18:00 | 92 | Lalbag | 58 | 00:00 | 158 | Shariatpur | 92 | 21:00
27 | Bheramara(GK) | 58 | 19:00 | 93 | Lalmonirhat | 63 | 18:00 | 159 | Sherpur | 172 | 18:00
28 | Bhulta | 212 | 01:00 | 94 | MI_Cement | 17.8 | 00:00 | 160 | Shikalbaha | 27 | 00:00
29 | Bog-Sherpur | 70 | 03:00 | 95 | Madanganj | 44 | 00:00 | 161 | Shitalakhya | 64.5 | 00:00
30 | Bogura | 170 | 21:00 | 96 | Madaripur | 126 | 23:00 | 162 | Sholosohor | 36 | 00:00
31 | Borhanuddin | 94 | 22:00 | 97 | Madartek | 84.12 | 00:00 | 163 | Shyampur | 156 | 15:00
32 | Brahmanbaria | 139 | 21:00 | 98 | Madunaghat | 49 | 22:00 | 164 | Siddhirganj | 97 | 00:00
33 | Cantonment | 108 | 19:00 | 99 | Magura | 70 | 19:30 | 165 | Sirajganj | 114 | 20:00
34 | Chandpur | 76 | 21:00 | 100 | Mahasthangarh | 80 | 20:00 | 166 | Sonargaon | 81 | 23:00
35 | Chandraghona | 35 | 20:00 | 101 | Manikganj | 124 | 19:30 | 167 | Sreemongol | 72 | 19:00
36 | Chapai | 70 | 00:00 | 102 | Maniknagar | 56 | 00:00 | 168 | Sreepur | 62 | 00:00
37 | Charsaidpur | 41 | 05:00 | 103 | Matarbari | 50 | 03:00 | 169 | Srinagar | 49.98 | 21:00
38 | Chauddagram | 81 | 21:00 | 104 | Matuail | 59.2 | 00:00 | 170 | Sunamganj | 56 | 21:00
39 | Chhatak | 34 | 22:00 | 105 | Millgate | 61 | 00:00 | 171 | Sylhet | 33 | 19:00
40 | Chowmuhani | 237 | 21:00 | 106 | Mirpur | 124 | 19:00 | 172 | Sylhet-132 | 116 | 21:00
41 | Chuadanga | 117 | 22:00 | 107 | Mirsorai | 8 | 00:00 | 173 | TK | 30.4 | 00:00
42 | Coxsbazar | 126 | 19:30 | 108 | Mirzapur | 46 | 19:30 | 174 | Tangail | 200 | 19:00
43 | Cumilla(N) | 193 | 21:00 | 109 | Mithapukur | 66 | 18:00 | 175 | Thakurgaon | 102 | 19:00
44 | Cumilla(S) | 144 | 23:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 121 | 00:00
45 | Daudkandi | 137 | 21:00 | 111 | Mogbazar | 114.2 | 19:00 | 177 | Ullahpara | 35 | 20:00
46 | Dhaka | 28 | 12:00 | 112 | Mongla | 44 | 23:00 | 178 | Ullon | 48 | 19:00
47 | Dhamrai | 110 | 07:00 | 113 | Motijheel | 31 | 19:00 | 179 | Uttara | 81 | 19:00
48 | Dhanmondi | 114 | 19:00 | 114 | Muktagacha | 42 | 18:00 | 180 | UttaraNew | 44 | 00:00
49 | Dohazari | 115 | 21:00 | 115 | Munshiganj | 116 | 23:00 | 181 | Zigatola | 63 | 00:00
50 | Faridpur | 158 | 21:00 | 116 | Muradnagar | 32 | 21:00
51 | Fatullah | 74 | 00:00 | 117 | Mymensingh | 220 | 18:00
52 | Fenchuganj | 40 | 19:00 | 118 | Naogaon | 140 | 21:00
53 | Feni | 124 | 21:00 | 119 | Narail | 62 | 18:30
54 | GPH | 96 | 17:00 | 120 | Narinda | 57 | 00:00
55 | Ghatail | 96 | 18:30 | 121 | Narshingdi | 188 | 22:00
56 | Ghorashal | 14 | 13:00 | 122 | Natore | 166 | 20:00
57 | Ghorashal-230 | 89 | 23:00 | 123 | Nawabganj | 62.8 | 21:00
58 | Goalpara | 32 | 21:00 | 124 | Netrakona | 141 | 18:30
59 | Gollamari | 78 | 00:00 | 125 | New | 59 | 00:00
60 | Gopalganj | 118 | 23:00 | 126 | Niamatpur | 115 | 21:00
61 | Gulshan | 84 | 19:00 | 127 | Noapara | 45 | 22:00
62 | Halishahar | 39.5 | 01:00 | 128 | PHP | 20 | 14:00
63 | HaripurSBU | 150 | 11:00 | 129 | Pabna | 116 | 03:00
64 | Hasnabad | 78 | 00:00 | 130 | Palashbari | 124 | 19:00
65 | Hathazari | 83 | 18:30 | 131 | Panchagarh | 54 | 19:00
66 | Ishurdi | 69 | 19:30 | 132 | Patuakhali | 83.5 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14206.57 | 0 |  | 14206.57
1:00 | 13630.92 | 150 |  | 13787.92
2:00 | 13139.79 | 130 |  | 13275.79
3:00 | 13307.94 | 110 |  | 13422.94
4:00 | 12945.39 | 0 |  | 12945.39
5:00 | 12123.92 | 0 |  | 12123.92
6:00 | 11148.5 | 0 |  | 11148.5
7:00 | 11119.73 | 0 |  | 11119.73
8:00 | 11244.86 | 0 |  | 11244.86
9:00 | 11584.14 | 0 |  | 11584.14
10:00 | 11893.17 | 0 |  | 11893.17
11:00 | 12322.03 | 0 |  | 12322.03
12:00 | 12882.36 | 0 |  | 12882.36
13:00 | 13306.44 | 0 |  | 13306.44
14:00 | 12866.44 | 0 |  | 12866.44
15:00 | 13393.63 | 0 |  | 13393.63
16:00 | 13336.34 | 0 |  | 13336.34
17:00 | 13430.8 | 0 |  | 13430.8
18:00 | 13797.19 | 0 |  | 13797.19
19:00 | 14436.5 | 0 |  | 14436.5
19:30 | 14792.5 | 0 |  | 14792.5
20:00 | 14749.5 | 0 |  | 14749.5
21:00 | 14989.5 | 0 |  | 14989.5
22:00 | 14744.5 | 0 |  | 14744.5
23:00 | 14602.5 | 55 |  | 14659.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8363.5 | 5843.07 | 14206.57 | DAILY GENERATION CURVE
00:30 | 8140.25 | 5778.495 | 13918.745
01:00 | 7917 | 5713.92 | 13630.92 | 28-03-2025
01:30 | 7763.75 | 5621.605 | 13385.355
02:00 | 7610.5 | 5529.29 | 13139.79
02:30 | 7670.5 | 5553.365 | 13223.865
03:00 | 7730.5 | 5577.44 | 13307.94
03:30 | 7622 | 5504.665 | 13126.665
04:00 | 7513.5 | 5431.89 | 12945.39
04:30 | 7350 | 5184.655 | 12534.655
05:00 | 7186.5 | 4937.42 | 12123.92
05:30 | 6946.5 | 4689.71 | 11636.21
06:00 | 6706.5 | 4442 | 11148.5
06:30 | 6704.76 | 4429.355 | 11134.115
07:00 | 6703.02 | 4416.71 | 11119.73
07:30 | 6707.015 | 4475.28 | 11182.295
08:00 | 6711.01 | 4533.85 | 11244.86
08:30 | 6748.93 | 4665.57 | 11414.5
09:00 | 6786.85 | 4797.29 | 11584.14
09:30 | 6828.73 | 4909.925 | 11738.655
10:00 | 6870.61 | 5022.56 | 11893.17
10:30 | 7008.105 | 5099.495 | 12107.6
11:00 | 7145.6 | 5176.43 | 12322.03
11:30 | 7246.23 | 5355.965 | 12602.195
12:00 | 7346.86 | 5535.5 | 12882.36
12:30 | 7475.64 | 5618.76 | 13094.4
13:00 | 7604.42 | 5702.02 | 13306.44
13:30 | 7522.01 | 5564.43 | 13086.44
14:00 | 7439.6 | 5426.84 | 12866.44
14:30 | 7538.45 | 5591.585 | 13130.035
15:00 | 7637.3 | 5756.33 | 13393.63
15:30 | 7665.28 | 5699.705 | 13364.985
16:00 | 7693.26 | 5643.08 | 13336.34
16:30 | 7748.765 | 5634.805 | 13383.57
17:00 | 7804.27 | 5626.53 | 13430.8
17:30 | 7950.88 | 5663.115 | 13613.995
18:00 | 8097.49 | 5699.7 | 13797.19
18:30 | 8302.745 | 5814.1 | 14116.845
19:00 | 8508 | 5928.5 | 14436.5
19:30 | 8707 | 6085.5 | 14792.5
20:00 | 8716 | 6033.5 | 14749.5
20:30 | 8777 | 6092.5 | 14869.5 |  | Executive Engineer
21:00 | 8838 | 6151.5 | 14989.5 |  | Network Operation Division
21:30 | 8755 | 6112 | 14867
22:00 | 8672 | 6072.5 | 14744.5
22:30 | 8641.5 | 6032 | 14673.5
23:00 | 8611 | 5991.5 | 14602.5

## En-Curve
QF-LDC-12
Date | 28-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3360 | 2604 | 918 | 0 | 38 | 1358.57 | 46 | 4154 | 0 | 372 | 1356 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3348 | 2580.75 | 918 | 0 | 37 | 1365.495 | 46 | 4168.5 | 0 | 341.5 | 1113.5 | 0 | 0 | 0 | 75 | 28-03-2025
01:00 | 3336 | 2557.5 | 918 | 0 | 36 | 1372.42 | 46 | 4183 | 0 | 311 | 871 | 0 | 0 | 0 | 150
01:30 | 3339 | 2481.25 | 918 | 0 | 35 | 1368.105 | 46 | 4100.5 | 0 | 299 | 798.5 | 0 | 0 | 0 | 140 | Energy Generated | 317.1436 |  | MKWHr
02:00 | 3342 | 2405 | 918 | 0 | 34 | 1363.79 | 46 | 4018 | 0 | 287 | 726 | 0 | 0 | 0 | 130 | Energy not Served | 0.445 |  | MKWHr
02:30 | 3297 | 2485.5 | 918 | 0 | 34 | 1367.865 | 46 | 4055.5 | 0 | 287 | 733 | 0 | 0 | 0 | 120 | Total Energy Requirement | 317.5886 |  | MKWHr
03:00 | 3252 | 2566 | 918 | 0 | 34 | 1371.94 | 46 | 4093 | 0 | 287 | 740 | 0 | 0 | 0 | 110
03:30 | 3259 | 2460.5 | 918.5 | 0 | 32 | 1334.165 | 46 | 4065.5 | 0 | 262 | 749 | 0 | 0 | 0 | 55
04:00 | 3266 | 2355 | 919 | 0 | 30 | 1296.39 | 46 | 4038 | 0 | 237 | 758 | 0 | 0 | 0 | 0
04:30 | 3247 | 2318 | 919 | 0 | 29 | 1255.155 | 46 | 3836.5 | 0 | 188.5 | 695.5 | 0 | 0 | 0 | 0
05:00 | 3228 | 2281 | 919 | 0 | 28 | 1213.92 | 46 | 3635 | 0 | 140 | 633 | 0 | 0 | 0 | 0
05:30 | 3230 | 2287.25 | 919 | 0 | 28 | 1160.46 | 46 | 3304.5 | 0 | 98.5 | 562.5 | 0 | 0 | 0 | 0
06:00 | 3232 | 2293.5 | 919 | 0 | 28 | 1107 | 46 | 2974 | 0 | 57 | 492 | 0 | 0 | 0 | 0
06:30 | 3288.5 | 2300.5 | 919 | 0 | 29 | 1055 | 46 | 2925 | 34.015 | 57 | 480.1 | 0 | 0 | 0 | 0
07:00 | 3345 | 2307.5 | 919 | 0 | 30 | 1003 | 46 | 2876 | 68.03 | 57 | 468.2 | 0 | 0 | 0 | 0
07:30 | 3362 | 2311 | 895.5 | 0 | 29 | 1006.5 | 46 | 2874.5 | 135.095 | 65.5 | 457.2 | 0 | 0 | 0 | 0
08:00 | 3379 | 2314.5 | 872 | 0 | 28 | 1010 | 46 | 2873 | 202.16 | 74 | 446.2 | 0 | 0 | 0 | 0
08:30 | 3409.5 | 2397 | 872 | 0 | 29 | 1012.5 | 46 | 2842.5 | 287.4 | 87 | 431.6 | 0 | 0 | 0 | 0
09:00 | 3440 | 2479.5 | 872 | 0 | 30 | 1015 | 46 | 2812 | 372.64 | 100 | 417 | 0 | 0 | 0 | 0
09:30 | 3468 | 2458 | 895 | 0 | 31 | 1015 | 46 | 2849.5 | 446.655 | 101.5 | 428 | 0 | 0 | 0 | 0
10:00 | 3496 | 2436.5 | 918 | 0 | 32 | 1015 | 46 | 2887 | 520.67 | 103 | 439 | 0 | 0 | 0 | 0
10:30 | 3518.5 | 2498.5 | 918.5 | 0 | 29 | 1016.5 | 46 | 2975.5 | 562.6 | 103.5 | 439 | 0 | 0 | 0 | 0
11:00 | 3541 | 2560.5 | 919 | 0 | 26 | 1018 | 46 | 3064 | 604.53 | 104 | 439 | 0 | 0 | 0 | 0
11:30 | 3437 | 2491 | 918.5 | 0 | 29 | 1095.5 | 46 | 3320.5 | 615.695 | 131 | 514.5 | 0 | 0 | 3.5 | 0
12:00 | 3333 | 2421.5 | 918 | 0 | 32 | 1173 | 46 | 3577 | 626.86 | 158 | 590 | 0 | 0 | 7 | 0
12:30 | 3382 | 2493 | 918.5 | 0 | 31 | 1174.5 | 46 | 3633 | 620.4 | 158 | 627.5 | 0 | 0 | 10.5 | 0
13:00 | 3431 | 2564.5 | 919 | 0 | 30 | 1176 | 46 | 3689 | 613.94 | 158 | 665 | 0 | 0 | 14 | 0
13:30 | 3401.5 | 2535.5 | 919 | 0 | 33 | 1172 | 46 | 3578 | 582.94 | 145 | 657.5 | 0 | 0 | 16 | 0
14:00 | 3372 | 2506.5 | 919 | 0 | 36 | 1168 | 46 | 3467 | 551.94 | 132 | 650 | 0 | 0 | 18 | 0
14:30 | 3382.5 | 2530.5 | 919.5 | 0 | 37 | 1220 | 46 | 3659.5 | 487.535 | 145.5 | 682.5 | 0 | 0 | 19.5 | 0
15:00 | 3393 | 2554.5 | 920 | 0 | 38 | 1272 | 46 | 3852 | 423.13 | 159 | 715 | 0 | 0 | 21 | 0
15:30 | 3401.5 | 2556.5 | 918.5 | 0 | 37 | 1267 | 46 | 3856.5 | 340.985 | 183 | 738.5 | 0 | 0 | 19.5 | 0
16:00 | 3410 | 2558.5 | 917 | 0 | 36 | 1262 | 46 | 3861 | 258.84 | 207 | 762 | 0 | 0 | 18 | 0
16:30 | 3424 | 2569 | 918 | 0 | 34 | 1259.5 | 46 | 3899 | 177.07 | 228.5 | 818.5 | 0 | 0 | 10 | 0
17:00 | 3438 | 2579.5 | 919 | 0 | 32 | 1257 | 46 | 3937 | 95.3 | 250 | 875 | 0 | 0 | 2 | 0
17:30 | 3439.5 | 2596.5 | 919 | 0 | 31 | 1257 | 46 | 3934 | 50.495 | 329.5 | 1010 | 0 | 0 | 1 | 0
18:00 | 3441 | 2613.5 | 919 | 0 | 30 | 1257 | 46 | 3931 | 5.69 | 409 | 1145 | 0 | 0 | 0 | 0
18:30 | 3448 | 2595 | 895.5 | 0 | 31 | 1309.5 | 46 | 4042.5 | 2.845 | 468.5 | 1278 | 0 | 0 | 0 | 0
19:00 | 3455 | 2576.5 | 872 | 0 | 32 | 1362 | 46 | 4154 | 0 | 528 | 1411 | 0 | 0 | 0 | 0
19:30 | 3458 | 2524.5 | 872 | 0 | 34 | 1375 | 46 | 4181 | 0 | 538 | 1764 | 0 | 0 | 0 | 0
20:00 | 3366 | 2554.5 | 872 | 0 | 34 | 1363 | 46 | 4180 | 0 | 551 | 1780 | 0 | 0 | 3 | 0
20:30 | 3423.5 | 2557.5 | 895.5 | 0 | 36 | 1370 | 46 | 4183.5 | 0 | 551 | 1799 | 0 | 0 | 7.5 | 0
21:00 | 3481 | 2560.5 | 919 | 0 | 38 | 1377 | 46 | 4187 | 0 | 551 | 1818 | 0 | 0 | 12 | 0
21:30 | 3556.5 | 2617.5 | 919 | 0 | 39 | 1374.5 | 46 | 4191 | 0 | 449.5 | 1663 | 0 | 0 | 11 | 0
22:00 | 3632 | 2674.5 | 919 | 0 | 40 | 1372 | 46 | 4195 | 0 | 348 | 1508 | 0 | 0 | 10 | 0
22:30 | 3598.5 | 2645 | 919.5 | 0 | 40 | 1373 | 46 | 4191 | 0 | 342.5 | 1506.5 | 0 | 0 | 11.5 | 27.5
23:00 | 3565 | 2615.5 | 920 | 0 | 40 | 1374 | 46 | 4187 | 0 | 337 | 1505 | 0 | 0 | 13 | 55
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 403 | 05:00 | 387 | 23:00 | Payra | 419 | 06:00 | 409 | 23:00
Ashuganj | 406 | 6:00 | 390 | 12:00 | Rahanpur | 395 | 07:00 | 382 | 22:00
Bhulta | 405 | 06:00 | 393 | 00:00 | Rampal | 411 | 06:00 | 390 | 23:00
Bibiana | 395 | 05:00 | 389 | 21:00
BIPTC | 394 | 04:00 | 386 | 12:00
Bogura | 384 | 06:00 | 369 | 22:00
Gopalganj | 409 | 06:00 | 391 | 23:00
Kaliakoir | 371 | 06:00 | 362 | 15:00
Madunaghat | 403 | 07:00 | 394 | 01:00
Meghnaghat | 405 | 07:00 | 393 | 02:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 06:00 | 226 | 00:00 | Keranigonj | 233 | 07:00 | 223 | 13:00
AKSML | 235 | 07:00 | 227 | 00:00 | Khulna(S) | 236 | 06:00 | 218 | 23:00
Aminbazar | 234 | 06:00 | 227 | 12:00 | Madunaghat | 237 | 09:00 | 230 | 14:00
Ashuganj | 235 | 06:00 | 229 | 00:00 | Madunaghat-400 | 238 | 07:00 | 230 | 13:00
Ashuganj-400 | 235 | 6:00 | 220 | 23:00 | Maniknagar | 228 | 05:00 | 223 | 15:00
Baghabari | 234 | 05:00 | 226 | 12:00 | Meghnaghat | 239 | 07:00 | 233 | 00:00
Barapukuria | 222 | 06:00 | 214 | 16:00 | Meghnaghat-400 | 233 | 06:00 | 226 | 00:00
Barapukuria-230 | 222 | 6:00 | 216 | 15:00 | Mirsorai | 234 | 07:00 | 223 | 13:00
Barishal | 239 | 06:00 | 227 | 23:00 | Rajshahi | 233 | 06:00 | 221 | 17:00
Bheramara | 234 | 06:00 | 224 | 12:00 | Rampal | 235 | 06:00 | 219 | 23:00
Bhulta | 230 | 06:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 06:00 | 222 | 18:30 | Rampura | 229 | 06:00 | 222 | 00:00
BIPTC | 236 | 06:00 | 225 | 12:00 | Shikalbaha | 235 | 07:00 | 226 | 01:00
Bogura | 234 | 06:00 | 225 | 17:00 | Shyampur | 232 | 05:00 | 224 | 00:00
Bogura-400 | 234 | 06:00 | 225 | 17:00 | Siddhirganj | 231 | 05:00 | 225 | 12:00
Borhanuddin | 243 | 07:00 | 232 | 23:00 | Sirajgonj | 240 | 05:00 | 235 | 17:00
BSRM | 233 | 06:00 | 223 | 12:00 | Sreepur | 232 | 06:00 | 225 | 17:00
Cumilla(N) | 229 | 06:00 | 221 | 12:00 | Tongi | 228 | 05:00 | 222 | 15:00
Faridpur | 236 | 06:00 | 223 | 23:00
Fenchuganj | 233 | 05:00 | 227 | 21:00
Ghorashal | 232 | 18:00 | 230 | 00:00
Ghorashal-230 | 230 | 06:00 | 222 | 17:00
Gopalganj | 236 | 06:00 | 224 | 23:00
GPH | 236 | 08:00 | 227 | 00:00
Haripur | 231 | 06:00 | 224 | 00:00
Hasnabad | 233 | 06:00 | 225 | 00:00
Hathazari | 238 | 04:00 | 231 | 17:00
Ishurdi | 236 | 06:00 | 227 | 12:00
Jhenaidah | 232 | 06:00 | 213 | 22:00
Kaliakoir | 233 | 06:00 | 133 | 06:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 130 | 15:00 | Madunaghat | 135 | 06:00 | 131 | 01:00
Agargaon | 139 | 07:00 | 133 | 00:00 | Magura | 132 | 06:00 | 119 | 18:30
Agrabad | 134 | 06:00 | 130 | 01:00 | Mahasthangarh | 129 | 05:00 | 122 | 16:00
AKS | 132 | 05:00 | 127 | 13:00 | Manikganj | 130 | 19:30 | 125 | 10:00
Aminbazar | 136 | 03:00 | 131 | 11:00 | Maniknagar | 135 | 06:00 | 131 | 00:00
Amnura | 134 | 13:00 | 122 | 00:00 | Matarbari | 121 | 06:00 | 112 | 00:00
Ashuganj | 136 | 05:00 | 134 | 17:00 | Matuail | 134 | 06:00 | 131 | 00:00
Bagerhat | 131 | 06:00 | 117 | 23:00 | Millgate | 138 | 06:00 | 132 | 15:00
Bajitpur | 130 | 05:00 | 124 | 17:00 | Mirpur | 137 | 06:00 | 132 | 00:00
Bakulia | 136 | 10:00 | 130 | 12:00 | Mirzapur | 129 | 01:00 | 123 | 16:00
Banani | 136 | 07:00 | 130 | 12:00 | Mithapukur | 129 | 06:00 | 121 | 11:00
Bangabhaban | 136 | 06:00 | 131 | 00:00 | MI_Cement | 135 | 06:00 | 130 | 00:00
Barapukuria | 136 | 06:00 | 129 | 11:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 07:00 | 129 | 23:00 | Mogbazar | 138 | 06:00 | 16 | 02:00
Barishal | 133 | 06:00 | 124 | 23:00 | Mongla | 131 | 06:00 | 119 | 19:00
Barishal-230 | 134 | 06:00 | 124 | 22:00 | Motijheel | 136 | 06:00 | 131 | 00:00
Baroaulia | 135 | 08:00 | 10 | 03:00 | Muktagacha | 132 | 05:00 | 124 | 16:00
Baroirhat | 127 | 08:00 | 120 | 00:00 | Munshiganj | 133 | 07:00 | 130 | 00:00
Bashundhara | 138 | 06:00 | 130 | 13:00 | Muradnagar | 128 | 06:00 | 122 | 13:00
BashundharaCement | 134 | 07:00 | 129 | 00:00 | Mymensingh | 133 | 05:00 | 110 | 22:00
Beanibazar | 131 | 06:00 | 125 | 21:00 | Naogaon | 126 | 06:00 | 118 | 17:00
Benapole | 131 | 06:00 | 115 | 22:00 | Narail | 133 | 04:00 | 117 | 18:30
Bhaluka | 124 | 05:00 | 119 | 22:00 | Narinda | 135 | 6:00 | 131 | 0:00
Bhandaria | 130 | 09:00 | 114 | 23:00 | Narshingdi | 132 | 06:00 | 118 | 22:00
Bhangura | 132 | 05:00 | 126 | 23:00 | Natore | 131 | 05:00 | 123 | 22:00
Bheramara | 134 | 06:00 | 127 | 17:00 | Nawabganj | 136 | 06:00 | 130 | 00:00
Bheramara(GK) | 135 | 06:00 | 127 | 17:00 | Netrakona | 119 | 07:00 | 109 | 12:00
Bhulta | 130 | 04:00 | 126 | 12:00 | New | 138 | 05:00 | 133 | 15:00
Bog-Sherpur | 129 | 05:00 | 124 | 03:00 | Niamatpur | 133 | 05:00 | 126 | 22:00
Bogura | 132 | 06:00 | 125 | 04:00 | Noapara | 133 | 07:00 | 121 | 19:00
Bogura-230 | 132 | 06:00 | 126 | 16:00 | Pabna | 134 | 05:00 | 127 | 18:00
Brahmanbaria | 128 | 05:00 | 122 | 23:00 | Palashbari | 125 | 01:00 | 117 | 16:00
Cantonment | 138 | 06:00 | 133 | 00:00 | Panchagarh | 137 | 18:30 | 115 | 11:00
Chandpur | 126 | 06:00 | 117 | 13:00 | Patuakhali | 136 | 06:00 | 130 | 22:00
Chandraghona | 136 | 07:00 | 131 | 12:00 | Payra | 138 | 07:00 | 134 | 00:00
Chapai | 129 | 06:00 | 123 | 01:00 | PHP | 125 | 08:00 | 116 | 13:00
Charsaidpur | 134 | 06:00 | 130 | 00:00 | Postogola | 137 | 07:00 | 132 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 07:00 | 118 | 12:00 | Purbachal | 137 | 05:00 | 131 | 00:00
Chhatak | 131 | 06:00 | 123 | 22:00 | Purbasadipur | 129 | 18:30 | 118 | 16:00
Chowmuhani | 120 | 10:00 | 110 | 00:00 | Rahanpur | 134 | 06:00 | 129 | 22:00
Chuadanga | 131 | 06:00 | 115 | 22:00 | Rahanpur-400 | 134 | 05:00 | 130 | 22:00
Coxsbazar | 122 | 10:00 | 113 | 00:00 | Rahim | 134 | 07:00 | 131 | 00:00
Cumilla(N) | 130 | 07:00 | 124 | 12:00 | Rajbari | 132 | 06:00 | 122 | 23:00
Cumilla(S) | 133 | 02:00 | 122 | 00:00 | Rajendrapur | 130 | 03:00 | 123 | 00:00
Daudkandi | 128 | 06:00 | 122 | 12:00 | Rajshahi | 134 | 05:00 | 126 | 17:00
Dhaka | 137 | 06:00 | 131 | 14:00 | Rajshahi-230 | 134 | 06:00 | 115 | 09:00
Dhamrai | 133 | 00:00 | 127 | 12:00 | Ramganj | 123 | 07:00 | 110 | 23:00
Dhanmondi | 137 | 06:00 | 131 | 15:00 | Rampur | 134 | 05:00 | 129 | 12:00
Dohazari | 130 | 09:00 | 124 | 13:00 | Rampura | 136 | 06:00 | 130 | 17:00
Faridpur | 132 | 06:00 | 125 | 23:00 | Rangamati | 134 | 06:00 | 129 | 13:00
Fatullah | 136 | 06:00 | 131 | 00:00 | Rangpur | 128 | 02:00 | 121 | 09:00
Fenchuganj | 134 | 06:00 | 130 | 22:00 | Ruppur | 136 | 10:00 | 129 | 22:00
Feni | 125 | 10:00 | 116 | 00:00 | Saidpur | 130 | 03:00 | 118 | 16:00
Ghatail | 128 | 05:00 | 120 | 13:00 | Satkhira | 133 | 06:00 | 116 | 23:00
Ghorashal | 137 | 19:30 | 133 | 14:00 | Satmasjid | 138 | 06:00 | 133 | 00:00
Goalpara | 137 | 07:00 | 123 | 22:00 | Savar | 136 | 06:00 | 131 | 00:00
Gollamari | 137 | 06:00 | 125 | 23:00 | SevenRings | 137 | 06:00 | 133 | 13:00
Gopalganj | 137 | 06:00 | 125 | 23:00 | ShahCement | 134 | 06:00 | 130 | 00:00
Gopalganj-400 | 139 | 06:00 | 131 | 22:00 | Shahjadpur | 135 | 01:00 | 132 | 00:00
Gulshan | 136 | 06:00 | 130 | 05:00 | Shahjibazar | 132 | 08:00 | 124 | 22:00
Halishahar | 133 | 04:00 | 131 | 01:00 | Shahmirpur | 136 | 09:00 | 130 | 12:00
Haripur | 135 | 06:00 | 130 | 01:00 | Shariatpur | 136 | 05:00 | 126 | 23:00
HaripurSBU | 134 | 08:00 | 131 | 00:00 | Sherpur | 133 | 00:00 | 121 | 13:00
Hasnabad | 135 | 03:00 | 132 | 00:00 | Shikalbaha | 126 | 06:00 | 119 | 12:00
Hathazari | 137 | 04:00 | 132 | 18:30 | Shikalbaha-230 | 137 | 08:00 | 131 | 12:00
Ishurdi | 137 | 06:00 | 130 | 17:00 | Shitalakhya | 135 | 06:00 | 130 | 00:00
Jaldhaka | 129 | 01:00 | 116 | 11:00 | Sholosohor | 136 | 07:00 | 130 | 13:00
Jamalpur | 138 | 19:30 | 126 | 10:00 | Shyampur | 135 | 06:00 | 130 | 00:00
Jashore | 132 | 05:00 | 117 | 23:00 | Shyampur-230 | 136 | 09:00 | 130 | 15:00
Jhenaidah | 134 | 06:00 | 121 | 22:00 | Siddhirganj | 135 | 03:00 | 131 | 12:00
Jhenaidah-230 | 135 | 06:00 | 120 | 22:00 | Sirajganj | 130 | 05:00 | 124 | 17:00
Joydebpur | 133 | 19:30 | 127 | 01:00 | Sonargaon | 133 | 19:30 | 128 | 15:00
Joypurhat | 123 | 05:00 | 115 | 17:00 | Sreemongol | 132 | 08:00 | 126 | 00:00
Juldah | 135 | 05:00 | 130 | 13:00 | Sreepur | 129 | 06:00 | 125 | 12:00
Kabirpur | 135 | 05:00 | 128 | 11:00 | Srinagar | 136 | 07:00 | 131 | 00:00
Kachua | 128 | 09:00 | 118 | 15:00 | SSM | 140 | 08:00 | 132 | 12:00
Kaliakoir | 134 | 01:00 | 130 | 12:00 | Sunamganj | 130 | 08:00 | 122 | 19:00
Kallyanpur | 137 | 07:00 | 133 | 15:00 | Sylhet | 132 | 07:00 | 127 | 17:00
Kalurghat | 136 | 08:00 | 131 | 01:00 | Sylhet-132 | 132 | 06:00 | 128 | 18:30
Kamrangirchar | 136 | 07:00 | 130 | 00:00 | Tangail | 128 | 07:00 | 120 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 136 | 18:30 | 112 | 11:00
Kasba | 128 | 06:00 | 121 | 13:00 | TK | 136 | 05:00 | 131 | 12:00
Kazla | 134 | 05:00 | 131 | 13:00 | Tongi | 138 | 07:00 | 134 | 00:00
Keranigonj | 137 | 07:00 | 131 | 00:00 | Ullahpara | 132 | 05:00 | 127 | 17:00
Khagrachori | 134 | 06:00 | 129 | 12:00 | Ullon | 136 | 06:00 | 130 | 15:00
Khulna | 133 | 05:00 | 123 | 19:00 | Uttara | 138 | 06:00 | 131 | 15:00
Khulna(S) | 137 | 06:00 | 125 | 19:00 | UttaraNew | 137 | 06:00 | 132 | 00:00
Khulshi | 134 | 07:00 | 128 | 13:00 | Zigatola | 137 | 06:00 | 131 | 00:00
Kishoreganj | 127 | 08:00 | 119 | 22:00
Kodda | 134 | 19:30 | 124 | 11:00
KSRM | 135 | 09:00 | 130 | 15:00
Kulaura | 132 | 04:00 | 129 | 18:30
Kurigram | 128 | 06:00 | 116 | 11:00
Kushtia | 134 | 06:00 | 124 | 22:00
Lalbag | 136 | 06:00 | 130 | 00:00
Lalmonirhat | 126 | 14:00 | 119 | 22:00
Madanganj | 134 | 07:00 | 129 | 00:00
Madaripur | 138 | 07:00 | 128 | 23:00
Madartek | 136 | 06:00 | 132 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division