## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-03-2025 | [28 empty] | Date: | 29-03-2025 | [28 empty] | Date: | 29-03-2025 | [28 empty] | Date: | 29-03-2025 | [28 empty] | Date: | 29-03-2025 | [17 empty] | Date: | 29-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 86 | 384 | 0 | 0 | 0 | 17 | 0 | 34 | 92 | 0 | 0 | 17 | 72 | 24 | 102 | 450 | 296 | 583 | 0 | 0 | 32 | 330 | 99 | 0 | 0 | 108 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 95 | 24 | 0 | 46 | 34 | 42 | 575 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 147 | 0 | 360 | 285 | 47 | 198 | 35 | 19 | 50 | 178 | 5 | 20 | 114 | 32 | 25 | 0 | 30 | 300 | 320 | 350 | 40 | 38 | 5 | 153 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 97 | 184 | 101 | 0 | 0 | 11 | 8503.5 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 53 | 1352 | 0 | 0 | 60 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 170 | 0 | 153 | 0 | 184 | 0 | 180 | 0 | 0 | 5.5 | 161 | 53 | 93 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1240 | 0 | 6026.5 | 14530 | 85.16
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 99 | 355 | 0 | 0 | 0 | 17 | 0 | 34 | 108 | 0 | 0 | 17 | 72 | 24 | 50 | 450 | 287 | 583 | 0 | 0 | 32 | 328 | 99 | 0 | 0 | 108 | 12.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 17 | 0 | 0 | 95 | 12 | 0 | 46 | 34 | 42 | 575 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 122 | 107 | 0 | 360 | 285 | 48 | 216 | 35 | 17 | 50 | 196 | 0 | 20 | 114 | 38 | 25 | 0 | 30 | 280 | 320 | 290 | 40 | 38 | 5 | 134 | 24 | 0 | 83 | 30 | 0 | 18 | 116 | 0 | 48 | 58 | 100 | 0 | 0 | 12 | 7993.8 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 35 | 1360 | 0 | 0 | 60 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 143 | 0 | 174 | 0 | 319 | 0 | 0 | 5.5 | 159 | 55 | 62 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 180 | 0 | 0 | 1120 | 0 | 5951.5 | 13945.3 | 85.15
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 99 | 336 | 0 | 0 | 0 | 17 | 0 | 34 | 108 | 0 | 0 | 0 | 35 | 24 | 50 | 450 | 279 | 500 | 0 | 0 | 32 | 330 | 99 | 0 | 0 | 108 | 12.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 17 | 0 | 0 | 95 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1105 | 0 | 51 | 50 | 107 | 0 | 360 | 285 | 48 | 183 | 35 | 17 | 50 | 197 | 0 | 20 | 114 | 38 | 25 | 0 | 30 | 290 | 320 | 290 | 40 | 38 | 5 | 131 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 48 | 58 | 101 | 0 | 0 | 12 | 7691.8 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 35 | 1370 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 145 | 0 | 187 | 0 | 319 | 0 | 0 | 5.5 | 166 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 180 | 0 | 0 | 1098 | 0 | 5820.5 | 13512.3 | 85.15
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 100 | 324 | 0 | 0 | 0 | 17 | 0 | 41 | 140 | 0 | 0 | 0 | 35 | 24 | 50 | 450 | 286 | 500 | 0 | 0 | 32 | 330 | 100 | 0 | 0 | 125 | 12.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 95 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1104 | 0 | 51 | 20 | 107 | 0 | 360 | 285 | 49 | 183 | 35 | 17 | 50 | 183 | 0 | 20 | 114 | 38 | 25 | 0 | 31 | 290 | 320 | 310 | 40 | 38 | 5 | 133 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 49 | 88 | 101 | 0 | 0 | 12 | 7756.8 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 35 | 1361 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 146 | 0 | 190 | 0 | 320 | 0 | 0 | 5.5 | 166 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 0 | 1100 | 0 | 5858.5 | 13615.3 | 85.14
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 100 | 332 | 0 | 0 | 0 | 0 | 0 | 52 | 130 | 0 | 0 | 0 | 0 | 24 | 16 | 450 | 279 | 500 | 0 | 0 | 32 | 332 | 100 | 0 | 0 | 125 | 12.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 82 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 0 | 51 | 0 | 107 | 0 | 360 | 165 | 48 | 182 | 35 | 45 | 50 | 180 | 0 | 20 | 114 | 30 | 25 | 0 | 31 | 280 | 320 | 350 | 40 | 38 | 5 | 151 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 68 | 136 | 102 | 0 | 0 | 12 | 7590.8 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 35 | 1357 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 201 | 0 | 186 | 0 | 319 | 0 | 0 | 5.5 | 168 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1082 | 0 | 5860.5 | 13451.3 | 85.14
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 100 | 320 | 0 | 0 | 0 | 0 | 0 | 26 | 80 | 0 | 0 | 0 | 0 | 24 | 0 | 350 | 258 | 500 | 0 | 0 | 32 | 332 | 98 | 0 | 0 | 108 | 12.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 82 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1007 | 0 | 51 | 0 | 107 | 0 | 360 | 125 | 48 | 182 | 35 | 51 | 50 | 180 | 0 | 20 | 114 | 30 | 25 | 0 | 0 | 290 | 320 | 350 | 40 | 38 | 5 | 151 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 69 | 136 | 104 | 0 | 0 | 12 | 7211.8 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 1376 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 153 | 0 | 181 | 0 | 320 | 0 | 0 | 5.5 | 170 | 55 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 10 | 108 | 220 | 0 | 0 | 995 | 0 | 5547.5 | 12759.3 | 85.13
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 100 | 293 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 350 | 271 | 500 | 0 | 0 | 32 | 335 | 101 | 0 | 0 | 108 | 12.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 82 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 0 | 51 | 0 | 107 | 0 | 360 | 155 | 49 | 182 | 35 | 31 | 50 | 179 | 0 | 20 | 88 | 28 | 8 | 0 | 0 | 270 | 320 | 290 | 40 | 38 | 5 | 132 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 69 | 136 | 104 | 0 | 0 | 12 | 6833.8 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1145 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 153 | 0 | 180 | 0 | 318 | 0 | 0 | 5.5 | 167 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 108 | 220 | 0 | 0 | 800 | 0 | 4816.5 | 11650.3 | 85.13
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 274 | 500 | 0 | 0 | 32 | 335 | 101 | 0 | 4 | 90 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804 | 2 | 51 | 0 | 107 | 0 | 360 | 155 | 48 | 182 | 35 | 17 | 50 | 181 | 0 | 20 | 37 | 30 | 0 | 9 | 0 | 280 | 320 | 290 | 40 | 38 | 5 | 131 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 69 | 136 | 103 | 0 | 3.6 | 12 | 6675.6 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.56 | 376 | 0 | 1006 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 7.32 | 164 | 0 | 154 | 0 | 182 | 0 | 319 | 0 | 0.6 | 5.5 | 166 | 55 | 0 | 3 | 0 | 0 | 0 | 0.6 | 20 | 0.07 | 0 | 150 | 9 | 108 | 220 | 0 | 0 | 792 | 0 | 4731.65 | 11407.25 | 85.13
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 321 | 0 | 0 | 17 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 350 | 294 | 500 | 0 | 0 | 32 | 328 | 99 | 0 | 12 | 17 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 82 | 0 | 1 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 817 | 7 | 51 | 0 | 107 | 0 | 355 | 155 | 49 | 188 | 35 | 16 | 50 | 155 | 0 | 20 | 34 | 24 | 0 | 23 | 0 | 290 | 320 | 292 | 40 | 38 | 5 | 131 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 8 | 160 | 122 | 1 | 9.83 | 12 | 6682.83 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.33 | 375 | 0 | 859.97 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 25.33 | 165 | 0 | 156 | 0 | 198 | 0 | 321 | 0 | 2.05 | 5.5 | 164 | 54 | 0 | 9 | 0 | 0 | 0 | 1.8 | 60 | 0.17 | 0 | 150 | 9 | 108 | 220 | 0 | 0 | 700 | 0 | 4614.15 | 11296.98 | 85.12
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 380 | 0 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 350 | 294 | 500 | 0 | 0 | 32 | 325 | 99 | 0 | 21 | 17 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 2 | 46 | 0 | 12 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 14 | 51 | 0 | 107 | 0 | 354 | 155 | 47 | 199 | 35 | 17 | 50 | 136 | 0 | 20 | 34 | 24 | 0 | 30 | 0 | 310 | 320 | 313 | 40 | 38 | 5 | 133 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 8 | 165 | 113 | 2 | 30.3 | 12 | 6809.3 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.2 | 374 | 0 | 854.83 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 42.84 | 169 | 0 | 167 | 0 | 212 | 0 | 339 | 0 | 3.72 | 5.5 | 168 | 54 | 0 | 16 | 0 | 0 | 0 | 2.2 | 109 | 0.25 | 0 | 150 | 8 | 120 | 220 | 0 | 0 | 696 | 0 | 4763.54 | 11572.84 | 85.11
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 403 | 0 | 0 | 35 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 350 | 298 | 500 | 0 | 0 | 32 | 324 | 97 | 0 | 28 | 35 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 48 | 0 | 3 | 46 | 0 | 20 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 51 | 0 | 108 | 0 | 348 | 160 | 46 | 200 | 31 | 17 | 50 | 136 | 0 | 20 | 34 | 32 | 0 | 38 | 0 | 315 | 320 | 311 | 40 | 38 | 5 | 134 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 8 | 165 | 129 | 0 | 40.51 | 12 | 6866.51 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 374 | 0 | 877.42 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 55.87 | 166 | 0 | 174 | 0 | 209 | 0 | 340 | 0 | 4.8 | 5.5 | 168 | 55 | 0 | 24 | 0 | 0 | 0 | 3.8 | 149 | 0.51 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 703 | 0 | 4988.9 | 11855.41 | 85.11
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 402 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 350 | 291 | 583 | 0 | 0 | 32 | 315 | 96 | 0 | 32 | 35 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 30 | 0 | 4 | 46 | 0 | 33 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 107 | 0 | 344 | 180 | 43 | 194 | 34 | 17 | 50 | 136 | 0 | 20 | 34 | 26 | 0 | 57 | 0 | 310 | 320 | 356 | 40 | 39 | 5 | 137 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 8 | 115 | 144 | 0 | 48.84 | 12 | 6944.84 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 374 | 0 | 858.62 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 63.9 | 165 | 0 | 177 | 0 | 155 | 0 | 392 | 0 | 5.59 | 5.5 | 168 | 55 | 0 | 29 | 0 | 0 | 0 | 5 | 186 | 0.6 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 705 | 0 | 5050.21 | 11995.05 | 85.1
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 401 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 296 | 583 | 0 | 0 | 32 | 313 | 94 | 0 | 32 | 35 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 33 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 16 | 51 | 0 | 107 | 0 | 331 | 200 | 40 | 208 | 30 | 23 | 50 | 136 | 0 | 20 | 34 | 36 | 0 | 41 | 0 | 295 | 320 | 389 | 39 | 39 | 5 | 143 | 24 | 0 | 81 | 30 | 0 | 18 | 118 | 0 | 18 | 115 | 143 | 2 | 47.97 | 12 | 7042.97 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 375 | 0 | 861.62 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 65.95 | 163 | 0 | 194 | 0 | 179 | 0 | 407 | 0 | 5.82 | 5.5 | 165 | 56 | 0 | 36 | 0 | 0 | 0 | 2.4 | 200 | 0.59 | 0 | 207 | 9 | 120 | 220 | 0 | 0 | 723 | 0 | 5162.88 | 12205.85 | 85.1
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 401 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 298 | 583 | 0 | 0 | 28 | 313 | 94 | 0 | 30 | 35 | 10 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 36 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 18 | 51 | 0 | 97 | 0 | 323 | 210 | 40 | 202 | 32 | 34 | 50 | 136 | 0 | 17 | 45 | 34 | 0 | 62 | 0 | 310 | 320 | 353 | 39 | 38 | 5 | 154 | 24 | 0 | 80 | 30 | 0 | 18 | 117 | 0 | 45 | 115 | 136 | 2 | 46.26 | 12 | 7105.26 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 374 | 0 | 870.51 | 0 | 0 | 55 | 0 | 0 | 8.9 | 0 | 0 | 0 | 103 | 0 | 62.07 | 162 | 0 | 187 | 0 | 205 | 0 | 399 | 0 | 5.36 | 5.5 | 166 | 56 | 0 | 36 | 0 | 0 | 0 | 3.6 | 195 | 0.57 | 0 | 307 | 9 | 120 | 220 | 0 | 0 | 886 | 0 | 5433.51 | 12538.77 | 85.09
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 400 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 298 | 583 | 0 | 0 | 28 | 312 | 95 | 0 | 27 | 64 | 10 | 10 | 0 | 0 | 0 | 0 | 7 | 0 | 10 | 0 | 0 | 0 | 12 | 0 | 3 | 46 | 0 | 36 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 16 | 51 | 0 | 105 | 0 | 340 | 220 | 40 | 183 | 31 | 34 | 50 | 145 | 0 | 17 | 96 | 38 | 0 | 55 | 0 | 300 | 174 | 352 | 39 | 38 | 5 | 151 | 24 | 0 | 82 | 30 | 0 | 18 | 118 | 0 | 45 | 119 | 141 | 2 | 42.7 | 12 | 7125.7 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 509 | 0 | 1102.68 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 53.81 | 160 | 0 | 184 | 0 | 205 | 0 | 332 | 0 | 4.72 | 5.5 | 165 | 56 | 24 | 32 | 16 | 0 | 0 | 4.1 | 172 | 0.53 | 0 | 307 | 9 | 120 | 220 | 0 | 0 | 1130 | 0 | 5942.34 | 13068.04 | 85.09
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 401 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 288 | 583 | 0 | 0 | 26 | 312 | 94 | 0 | 21 | 90 | 15 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 36 | 0 | 2 | 46 | 0 | 34 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 12 | 51 | 0 | 132 | 0 | 340 | 220 | 36 | 186 | 28 | 34 | 50 | 200 | 0 | 20 | 96 | 40 | 0 | 42 | 1 | 305 | 0 | 352 | 39 | 38 | 5 | 151 | 24 | 0 | 81 | 30 | 0 | 18 | 118 | 0 | 45 | 150 | 140 | 2 | 33.49 | 12 | 7175.49 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 510 | 0 | 1110 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 42.16 | 156 | 0 | 186 | 0 | 203 | 0 | 376 | 0 | 3.71 | 0 | 165 | 57 | 35 | 25 | 34 | 0 | 0 | 3.8 | 138 | 0.4 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1225 | 0 | 6023.07 | 13198.56 | 85.08
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 399 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 293 | 583 | 0 | 0 | 26 | 310 | 94 | 0 | 15 | 90 | 10 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 13 | 0 | 0 | 0 | 36 | 0 | 2 | 46 | 0 | 34 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 7 | 51 | 0 | 132 | 0 | 340 | 220 | 38 | 188 | 31 | 39 | 50 | 200 | 0 | 20 | 97 | 40 | 0 | 25 | 31 | 300 | 0 | 360 | 39 | 38 | 5 | 150 | 24 | 0 | 80 | 30 | 0 | 18 | 118 | 0 | 45 | 151 | 140 | 1 | 22.99 | 12 | 7177.99 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 551 | 0 | 1118 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 25.71 | 143 | 0 | 184 | 0 | 203 | 0 | 373 | 0 | 2.3 | 0 | 165 | 58 | 35 | 17 | 34 | 0 | 0 | 2.4 | 86 | 0.26 | 0 | 278 | 10 | 116 | 220 | 0 | 0 | 1160 | 0 | 5832.67 | 13010.66 | 85.08
17:00 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 81 | 401 | 0 | 0 | 17 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 293 | 583 | 0 | 0 | 26 | 311 | 94 | 0 | 6 | 90 | 10 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 11 | 0 | 0 | 0 | 36 | 0 | 1 | 46 | 0 | 34 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 3 | 51 | 0 | 160 | 0 | 340 | 220 | 38 | 196 | 31 | 68 | 50 | 200 | 0 | 20 | 97 | 44 | 0 | 9 | 30 | 300 | 0 | 357 | 39 | 38 | 5 | 150 | 24 | 0 | 81 | 30 | 0 | 18 | 118 | 0 | 50 | 151 | 142 | 0 | 8.63 | 12 | 7234.63 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 613 | 6 | 1122 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 10.11 | 143 | 0 | 182 | 0 | 203 | 0 | 389 | 0 | 0.98 | 8 | 165 | 58 | 35 | 7 | 34 | 0 | 0 | 1 | 32 | 0.11 | 0 | 307 | 10 | 116 | 220 | 0 | 0 | 1200 | 0 | 5858.2 | 13092.83 | 85.07
18:00 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 81 | 401 | 0 | 0 | 35 | 0 | 0 | 15 | 22 | 0 | 0 | 6 | 35 | 22 | 0 | 450 | 298 | 583 | 0 | 17 | 29 | 317 | 95 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 8 | 0 | 1 | 0 | 70 | 24 | 0 | 46 | 4 | 34 | 565 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 1107 | 0 | 51 | 16 | 160 | 0 | 342 | 220 | 40 | 197 | 32 | 68 | 50 | 200 | 11 | 20 | 113 | 42 | 0 | 1 | 30 | 305 | 0 | 351 | 39 | 37 | 5 | 152 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 104 | 169 | 145 | 0 | 0.57 | 12 | 7679.57 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 617 | 27 | 1123 | 0 | 0 | 55 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.79 | 144 | 0 | 180 | 0 | 205 | 0 | 396 | 0 | 0.08 | 8 | 164 | 58 | 110 | 1 | 104 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 250 | 10 | 116 | 220 | 0 | 0 | 1150 | 0 | 5851.98 | 13531.55 | 85.07
19:00 | 0 | 52 | 0 | 0 | 0 | 100 | 0 | 81 | 404 | 0 | 0 | 35 | 0 | 0 | 38 | 60 | 0 | 0 | 27 | 90 | 22 | 16 | 370 | 274 | 500 | 0 | 35 | 29 | 317 | 98 | 0 | 0 | 148 | 10 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 5 | 0 | 40 | 0 | 98 | 24 | 0 | 46 | 17 | 35 | 565 | 0 | 0 | 0 | 1 | 43 | 0 | 0 | 0 | 0 | 1216 | 0 | 51 | 55 | 170 | 0 | 355 | 235 | 41 | 183 | 33 | 69 | 50 | 200 | 28 | 20 | 113 | 38 | 0 | 0 | 30 | 295 | 0 | 350 | 40 | 38 | 5 | 144 | 24 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 106 | 171 | 150 | 0 | 0 | 12 | 8074 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 83 | 1364 | 0 | 0 | 55 | 54 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 170 | 0 | 208 | 0 | 375 | 0 | 0 | 8 | 165 | 58 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1160 | 0 | 6236 | 14310 | 85.06
19:30 | 0 | 52 | 0 | 0 | 0 | 120 | 0 | 81 | 403 | 0 | 0 | 0 | 0 | 0 | 33 | 46 | 0 | 0 | 17 | 17 | 22 | 30 | 370 | 276 | 583 | 0 | 17 | 30 | 319 | 97 | 0 | 0 | 150 | 10.5 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 0 | 44 | 0 | 98 | 24 | 0 | 46 | 23 | 35 | 565 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | 0 | 0 | 1215 | 0 | 51 | 100 | 170 | 0 | 360 | 235 | 41 | 183 | 33 | 69 | 50 | 200 | 37 | 20 | 114 | 38 | 0 | 0 | 30 | 280 | 0 | 351 | 40 | 38 | 5 | 152 | 24 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 106 | 174 | 151 | 0 | 0 | 12 | 8119.5 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 83 | 1369 | 0 | 0 | 60 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 173 | 0 | 210 | 0 | 319 | 0 | 0 | 8 | 162 | 58 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1200 | 0 | 6177 | 14296.5
20:00 | 0 | 34 | 0 | 0 | 0 | 120 | 0 | 81 | 403 | 0 | 0 | 0 | 0 | 0 | 37 | 32 | 0 | 0 | 0 | 17 | 22 | 35 | 370 | 303 | 583 | 0 | 0 | 30 | 321 | 96 | 0 | 0 | 160 | 11 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 52 | 0 | 98 | 24 | 0 | 46 | 17 | 35 | 565 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 172 | 0 | 350 | 230 | 46 | 199 | 33 | 70 | 50 | 200 | 34 | 20 | 114 | 32 | 0 | 0 | 30 | 290 | 0 | 385 | 40 | 38 | 5 | 152 | 24 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 85 | 174 | 152 | 0 | 0 | 12 | 8051 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 84 | 1360 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 174 | 0 | 209 | 0 | 343 | 0 | 0 | 8 | 165 | 58 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1200 | 0 | 6113 | 14164 | 85.06
21:00 | 0 | 34 | 0 | 0 | 0 | 120 | 0 | 81 | 403 | 0 | 0 | 0 | 0 | 0 | 33 | 32 | 0 | 0 | 0 | 17 | 22 | 16 | 450 | 304 | 583 | 0 | 0 | 31 | 324 | 97 | 0 | 0 | 160 | 11 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 56 | 0 | 98 | 24 | 0 | 46 | 17 | 35 | 565 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 172 | 0 | 353 | 230 | 46 | 201 | 35 | 68 | 50 | 200 | 38 | 20 | 114 | 40 | 0 | 0 | 30 | 315 | 0 | 381 | 40 | 38 | 5 | 155 | 24 | 0 | 84 | 30 | 0 | 18 | 117 | 0 | 85 | 174 | 152 | 0 | 0 | 12 | 8108 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 105 | 1369.65 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 193 | 0 | 208 | 0 | 414 | 0 | 0 | 8 | 165 | 58 | 54 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 220 | 0 | 0 | 1232 | 0 | 6242.65 | 14350.65 | 85.05
22:00 | 0 | 34 | 0 | 0 | 0 | 120 | 0 | 81 | 400 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 22 | 16 | 450 | 298 | 583 | 0 | 0 | 31 | 326 | 97 | 0 | 0 | 142 | 11 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 17 | 35 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 172 | 0 | 358 | 235 | 47 | 189 | 35 | 68 | 50 | 200 | 38 | 20 | 114 | 38 | 0 | 0 | 31 | 300 | 0 | 360 | 40 | 38 | 5 | 151 | 24 | 0 | 85 | 30 | 0 | 18 | 117 | 0 | 65 | 174 | 152 | 0 | 0 | 12 | 7997 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 105 | 1361.91 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 179 | 0 | 210 | 0 | 387 | 0 | 0 | 8 | 164 | 58 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 220 | 0 | 0 | 1240 | 0 | 6213.91 | 14210.91 | 85.05
23:00 | 0 | 34 | 0 | 0 | 0 | 115 | 0 | 77 | 372 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 293 | 583 | 0 | 0 | 32 | 327 | 98 | 0 | 0 | 142 | 11 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 10 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 17 | 37 | 575 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 173 | 0 | 360 | 240 | 49 | 186 | 35 | 70 | 50 | 200 | 30 | 20 | 114 | 36 | 0 | 0 | 31 | 305 | 0 | 351 | 40 | 38 | 5 | 151 | 24 | 0 | 85 | 30 | 0 | 18 | 117 | 0 | 65 | 175 | 172 | 0 | 0 | 12 | 7969 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 105 | 1368.56 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 179 | 0 | 180 | 0 | 386 | 0 | 0 | 5.5 | 163 | 58 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1240 | 0 | 6180.06 | 14149.06 | 85.04
Total KWH | 0 | 387840 | 53760 | 0 | 0 | 790250 | 0 | 2142136.37 | 8989200 | 0 | 0 | 308520 | 145080 | 0 | 590544 | 825600 | 0 | 0 | 82344 | 384480 | 496080 | 417600 | 9660500 | 6938473 | 12916364 | 0 | 63940 | 720700 | 7795958 | 2478000 | 0 | 229410 | 2302800 | 279600 | 334800 | 0 | 0 | 0 | 0 | 133440 | 0 | 156480 | 76874 | 379517 | 0 | 1621440 | 236160 | 26738 | 1094100 | 189018 | 895200 | 13665454.55 | 0 | 0 | 0 | 44247.6 | 283527 | 11374 | 0 | 0 | 0 | 24365452 | 86940 | 1041340 | 439927 | 3077818 | 0 | 8762900 | 5162000 | 1073760 | 4698000 | 807912 | 976320 | 1188880 | 4284480 | 193200 | 458760 | 2115840 | 823680 | 150864 | 412536 | 403152 | 7258000 | 4521000 | 8453000 | 941000 | 898560 | 109008 | 3458782 | 552288 | 0 | 1996800 | 712992 | 0 | 432000 | 2517760 | 7560 | 1312800 | 3364800 | 3018240 | 11400 | 342970 | 298320 | 178878590.52 | 21853818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657360 | 12516360 | 744000 | 27946993 | 0 | 0 | 1365000 | 136032 | 0 | 67792 | 0 | 0 | 0 | 803580 | 15863 | 457496 | 3813818 | 0 | 4326809 | 0 | 4904209 | 0 | 8544290 | 0 | 39480 | 137394 | 4055000 | 1294690 | 831852 | 236726 | 1035504 | 0 | 0 | 30759.12 | 1357920 | 4320 | 0 | 6393000 | 230242 | 2660000 | 5164760 | 0 | 0 | 25245090.91 | 0 | 136870158.03 | 315748748.55

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-03-2025 | during | 30-03-2025 | during | 30-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 120 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 98 | 81 | 97.7 | 97.7 | 97.7 | 97.7 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 304 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 94 | 97 | 208.13 | 208.13 | 105 | 105 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 324 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 11 | 11 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 10 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 32 | 31 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 33 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2411 | 2728 | 5268.9 | 5237.9 | 3884.01 | 3853.01
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 56 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 98 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 33 | 35 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.79 | 0 | 3.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 800 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 0 | 4 | 2 | 4 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 565 | 565 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1486 | 2102 | 3316.51 | 3293.72 | 3316.51 | 3293.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 208 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 331 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 200 | 230 | 250 | 250 | 250 | 250 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 46 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 107 | 172 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 30 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 23 | 68 | 115 | 115 | 23 | 68 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1307 | 1648 | 2370.99 | 2310.99 | 2139.05 | 2124.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-03-2025 | during | 30-03-2025 | during | 30-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 143 | 152 | 210 | 210 | 145 | 145 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 174 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 85 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.97 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 337.97 | 423 | 653.5 | 601.5 | 588.5 | 536.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 40 | 41 | 41 | 39 | 39 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 155 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 118 | 117 | 115 | 115 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 381 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 0 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1501 | 1207 | 1564 | 1564 | 1543 | 1543
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 859 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 375 | 618 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1375 | 1582 | 3609.2 | 3514.2 | 1912.02 | 1817.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 9 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 112 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 723 | 1232 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 207 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1279.59 | 1881 | 2172.12 | 2171.12 | 2120.12 | 2119.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 55 | 60 | 55 | 55 | 55 | 55 | machine running
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 163 | 143 | 214 | 214 | 214 | 214 | GT air intake filter DP high.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 193 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 208 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 407 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 8 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.82 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 861.62 | 1369.65 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.95 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2048.89 | 2395.65 | 3165.28 | 2998.53 | 3079.49 | 2912.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 58 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 165 | 165 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 54 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 190 | 0 | 190 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 459.4 | 384 | 713.4 | 487 | 679.42 | 453.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 12205.85 | 14350.65 | 22833.9 | 22178.96 | 19262.12 | 18652.18
Forecast Scenario (30-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13770 |  | 0 |  | 13770
|  |  |  | 1:00 | 13190 |  | 0 |  | 13190
|  |  |  | 2:00 | 12760 |  | 0 |  | 12760
|  |  |  | 3:00 | 12890 |  | 0 |  | 12890
|  |  |  | 4:00 | 12690 |  | 0 |  | 12690
|  |  |  | 5:00 | 11980 |  | 0 |  | 11980
|  |  |  | 6:00 | 10870 |  | 0 |  | 10870
|  |  |  | 7:00 | 10600 |  | 0 |  | 10600
|  |  |  | 8:00 | 10490 |  | 0 |  | 10490
|  |  |  | 9:00 | 10770 |  | 0 |  | 10770
|  |  |  | 10:00 | 11050 |  | 0 |  | 11050
|  |  |  | 11:00 | 11190 |  | 0 |  | 11190
|  |  |  | 12:00 | 11400 |  | 0 |  | 11400
|  |  |  | 13:00 | 11730 |  | 0 |  | 11730
|  |  |  | 14:00 | 12280 |  | 0 |  | 12280
|  |  |  | 15:00 | 12470 |  | 0 |  | 12470
|  |  |  | 16:00 | 12270 |  | 0 |  | 12270
|  |  |  | 17:00 | 12350 |  | 0 |  | 12350
|  |  |  | 18:00 | 12730 |  | 0 |  | 12730
|  |  |  | 18:30 | 13100 |  | 0 |  | 13100
|  |  |  | 19:00 | 13530 |  | 0 |  | 13530
|  |  |  | 19:30 | 13510 |  | 0 |  | 13510
|  |  |  | 20:00 | 13360 |  | 0 |  | 13360
|  |  |  | 21:00 | 13550 |  | 0 |  | 13550
|  |  |  | 22:00 | 13410 |  | 0 |  | 13410
|  |  |  | 23:00 | 13000 |  | 0 |  | 13000
Probable Maximum Temperature: |  |  | 37.80°C
Probable Maximum Demand at Day Peak: |  |  | 11400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13550.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 294.33 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:06 hrs on 30-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12205.85 | MW | 12:00 Hr. | Energy Generated |  |  | 315.7487 |  | MKWHr.
| Day Peak Demand |  |  | 12205.85 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.532 |  | MKWHr.
| Evening Peak Generation |  |  | 14350.65 | MW | 21:00 Hr. | Energy Demand |  |  | 316.2807 |  | MKWHr.
| Evening Peak Demand |  |  | 14350.65 | MW | 21:00 Hr. | Maximum Temperature |  |  | 37.8 |  | °C
| Minimum Generation of the Day |  |  | 11296.98 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1106.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 14530 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.929 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 53.5421 | 0 | 5.5625 | 0 | 0 | 0.22941 | 0 | 0 | 59.334 | Gas | 146.736 | Gas | 485695635.5595
| Chattogram Zone |  |  | 0.90657 | 38.0309 | 2.9642 | 0 | 1.0941 | 0.11368 | 0 | 0.15648 | 43.266 | Coal | 87.535 | Coal | 621770599.5123
| Cumilla Zone |  |  | 26.2714 | 0 | 8.5638 | 0 | 0 | 0.41254 | 0.82368 | 0 | 36.0714 | HFO | 24.905 | HFO | 420834550.872
| Mymensingh Zone |  |  | 3.0182 | 0 | 4.9835 | 0 | 0 | 0.35437 | 0 | 0 | 8.3561 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.8512 | Hydro | 1.0941 | Hydro | 109410
| Khulna Zone |  |  | 0 | 12.5164 | 0.744 | 0 | 0 | 0.65736 | 21.8538 | 0 | 35.7715 | Solar | 4.6976 | Solar | 76653989.9832
| Barishal Zone |  |  | 8.055 | 31.6381 | 0 | 0 | 0 | 0.00432 | 0 | 0 | 39.6974 | Import | 50.6245 | Import | 264732156.42
| Rajshahi Zone |  |  | 23.0915 | 0 | 0.21969 | 0 | 0 | 1.3006 | 27.947 | 0 | 52.5588 | Wind | 0.15648 | Wind | 2290867.2
| Rangpur Zone |  |  | 0 | 5.3497 | 1.8674 | 0 | 0 | 1.6254 | 0 | 0 | 8.8425
| Total |  |  | 146.736 | 87.535 | 24.905 | 0 | 1.0941 | 4.6976 | 50.6245 | 0.15648 | 315.7487
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 485695635.5595 |  | Hydro | 109410
|  |  |  | Coal | 621770599.5123 |  | Solar | 76653989.9832
|  |  |  | HFO | 420834550.872 |  | Import | 264732156.42
|  |  |  | HSD | 0 |  | Wind | 2290867.2
[5 empty] | Total: | 187,20,87,209 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8538 | Peak Hr Flow | 859.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 23767309.13 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.947 | Peak Hr Flow | 1369.65 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 492 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.82368 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 728 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.6245 | Peak Hr Flow | 2268.65 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4208
|  |  |  | Chattogram |  | 0 |  | 1435
|  |  |  | Cumilla |  | 0 |  | 1499
|  |  |  | Mymensingh |  | 0 |  | 1291
|  |  |  | Sylhet |  | 0 |  | 614
|  |  |  | Khulna |  | 0 |  | 1838
|  |  |  | Barishal |  | 0 |  | 500
|  |  |  | Rajshahi |  | 0 |  | 1563
|  |  |  | Rangpur |  | 0 |  | 855
|  |  |  | Total |  | 0 |  | 13803
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Jangalia 52 MW PP (Lakdanavi) |  |  | 52.2
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 487.29
|  |  |  | Total Unavailable Capacity |  |  |  | 1147.29
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 12:47 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to By the
instruction of ALDC, Khulna
| 08:34 | 10:10 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to PDB incoming DS maintenance
| 08:35 | 10:10 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to PDB incoming DS maintenance
|  | 09:28 | Siddhirganj 132/33kV S/S T-2 HT is restored.
|  | 09:29 | Siddhirganj 132/33kV S/S T-2 LT is restored.
| 09:30 | 12:40 | Chowmuhani 132/33kV S/S TR1 Forced S/D Due to 33KV Tr-01 Bus Shut Down for 33KV incoming | [7 empty] | 20.0MW load
|  |  | Isulator B-Phase abnormal sound Maintenance work | [7 empty] | interrup.
|  | 09:35 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
|  | 09:35 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 09:46 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
| 10:21 | 11:38 | Sunamganj 132/33kV S/S Tr-1 HT Forced S/D Due to Red Hot Maintenance. | [7 empty] | 4.0MW load
interrup.
| 10:22 | 10:40 | Sunamganj 132/33kV S/S Tr-1 LT Forced S/D Due to Red Hot Manintenance. | [7 empty] | 4.0MW load
interrup.
| 10:26 | 11:41 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to High
temperature maintenance of main bus DS Y phase
|  | 11:06 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT is restored.
|  | 11:06 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
| 11:08 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to B-Bus high
temperature works
| 11:08 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D
|  | 11:44 | Mymensingh-Netrokona 132kV Ckt-2 is restored.
| 11:45 |  | Mymensingh-Netrokona 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end.
| 12:00 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 12:17 | 12:50 | Ishwardi-Natore 132kV Ckt-2 Tripped from Ishurdi 132/33kV end showing LZ-32 relays Due
to Here reconductoring work in progress in Natore ckt-1. Contractor's(KEC) labour
dropped earth wire onto the natore ckt -2 conductor.
| 12:22 | 16:26 | Meghnaghat-Shyampur 230kV Ckt-1 Forced S/D from Meghnaghat 400/230kV end Due to
Emergency maintenance purpose
| 12:40 | 12:50 | Ishwardi-Natore 132kV Ckt-2 Tripped from Natore 132/33kV end showing General Trip, Z2
Trip, Block AR, Sync. Fail relays.
|  | 12:47 | Goalpara- Khulna (C) 132kV Ckt-1 is restored.
| 12:57 | 15:20 | Chowmuhani 132/33kV S/S TR3 Forced S/D Due to 33KV CT B-Phase Oil Leakage Check.
| 12:58 |  | Ghorasal Repowered CCPP Unit-4 Tripped with remarks:- trip
| 14:23 |  | Bibiyana South 400 MW Shutdown with remarks:- GT
| 15:01 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 15:28 |  | Ghorasal Repowered CCPP Unit-4 Tripped
| 18:30 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 23:42 |  | Sikalbaha 225MW GT was sync.
| 06:44 | 07:58 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) LT Forced S/D Due to Emergency Maintenance | [7 empty] | 13.0MW load
|  |  | for over temperature in 33kv Bus. | [7 empty] | interrup.
| 06:45 | 07:59 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) LT Forced S/D Due to Emergency Maintenance | [7 empty] | 13.0MW load
|  |  | for over temperature in 33kv Bus. | [7 empty] | interrup.
| 06:45 | 07:56 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) HT Forced S/D Due to Emergency Maintenance | [7 empty] | 13.0MW load
|  |  | for over temperature in 33kv Bus. | [7 empty] | interrup.
| 06:46 | 07:57 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) HT Forced S/D Due to Emergency Maintenance | [7 empty] | 13.0MW load
|  |  | for over temperature in 33kv Bus. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation is 10793 MW
| 07:39 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 120 | 790250 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 81 | 2142136.37 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 8989200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9660500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 6938473 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 2478000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7795958 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 308520 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 825600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 82344 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 63940 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 279600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 10 | 334800 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 496080 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 31 | 720700 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 53760 | Line Overload
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 33 | 590544 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 387840 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 417600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 384480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 229410 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 145080 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 12916364 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2302800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2728 | 59333979.37
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 44247.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 86940 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1094100 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 11374 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 283527 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 56 | 379517 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 76874 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 98 | 1621440 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 895200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 133440 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26738 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 189018 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 236160 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 24365452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 156480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 565 | 13665454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2102 | 43265962.15
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 4698000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8762900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 230 | 5162000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 807912 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1073760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 172 | 3077818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1041340 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 439927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 30 | 403152 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1188880 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4284480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 823680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 150864 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 458760 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2115840 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 193200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 976320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 412536 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1648 | 36071369
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 152 | 3018240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 174 | 3364800 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1312800 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 342970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298320 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 7560 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 423 | 8356090
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 941000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 898560 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3458782 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 109008 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 712992 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1996800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 117 | 2517760 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 552288 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7258000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 8453000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 4521000 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1207 | 31851190
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 859 | 21853818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 744000 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 657360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 618 | 12516360 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1582 | 35771538
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 230242 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 112 | 2660000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 25245090.91 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5164760 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6393000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4320 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1881 | 39697412.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 60 | 1365000 | -
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 143 | 3813818 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4326809 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 208 | 4904209 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8544290 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 15863 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8 | 137394 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 67792 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 136032 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1369.65 | 27946993 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 457496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 803580 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2395.65 | 52558756
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1294690 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 4055000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1035504 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30759.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 54 | 831852 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 236726 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1357920 | -
Rangpur Area Total |  |  |  |  | 950 | 384 | 8842451.12
Eastern Grid Total |  |  |  |  | 16921.242 | 8108 | 178878590.52
Western Grid Total |  |  |  |  | 11614.5 | 6242.65 | 136870158.03
National Grid Total |  |  |  |  | 28535.742 | 14350.65 | 315748748.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-03-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9046.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4755.7 | MW
i) Dhaka area |  |  | 4207.64 |  | MW | i) Khulna area |  |  |  | 1838.2 | MW
ii) Chattogram area |  |  | 1435 |  | MW | ii) Barishal area |  |  |  | 499.5 | MW
iii) Cumilla area |  |  | 1499 |  | MW | iii) Rajshahi area |  |  |  | 1563 | MW
iv) Mymensingh area |  |  | 1291 |  | MW | iv) Rangpur area |  |  |  | 855 | MW
v) Sylhet area |  |  | 614 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13802.34 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 21:00 | 67 | Jaldhaka | 80 | 18:30 | 133 | Payra | 32 | 22:00
2 | AKSML | 122 | 00:00 | 68 | Jamalpur | 151 | 18:00 | 134 | Postogola | 48 | 00:00
3 | Aftabnagar | 32 | 18:00 | 69 | Jashore | 152 | 21:00 | 135 | Purbachal | 17 | 00:00
4 | Agargaon | 98 | 19:00 | 70 | Jhenaidah | 137 | 19:00 | 136 | Purbasadipur | 119 | 15:00
5 | Agrabad | 82 | 00:00 | 71 | Joydebpur | 131 | 01:00 | 137 | Rahanpur | 28 | 00:00
6 | Amnura | 56 | 14:00 | 72 | Joypurhat | 70 | 00:00 | 138 | Rahim | 1 | 01:00
7 | Ashuganj | 96 | 22:00 | 73 | Juldah | 14.5 | 16:00 | 139 | Rajbari | 80 | 03:00
8 | BSRM | 208 | 07:00 | 74 | KSRM | 11 | 16:00 | 140 | Rajendrapur | 109 | 00:00
9 | Bagerhat | 83 | 00:00 | 75 | Kabirpur | 171 | 00:00 | 141 | Rajshahi | 98 | 00:00
10 | Bajitpur | 55 | 18:30 | 76 | Kachua | 100 | 18:30 | 142 | Rajshahi-230 | 85 | 21:00
11 | Bakulia | 90 | 19:00 | 77 | Kallyanpur | 102 | 13:00 | 143 | Ramganj | 120 | 04:00
12 | Banani | 30 | 20:00 | 78 | Kalurghat | 32 | 06:00 | 144 | Rampur | 38 | 00:00
13 | Bangabhaban | 5 | 10:00 | 79 | Kamrangirchar | 49.5 | 00:00 | 145 | Rangamati | 16 | 18:30
14 | Barapukuria | 67 | 03:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 147 | 18:00
15 | Barguna | 24 | 22:00 | 81 | Kasba | 43 | 22:00 | 147 | Ruppur | 5 | 15:00
16 | Barishal | 113 | 23:00 | 82 | Kazla | 86 | 00:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 110 | 21:00 | 83 | Keranigonj | 69 | 00:00 | 149 | Saidpur | 105 | 17:00
18 | Baroaulia | 50 | 00:00 | 84 | Khagrachori | 34 | 18:30 | 150 | Satkhira | 146 | 19:30
19 | Baroirhat | 65 | 19:00 | 85 | Khulna | 87 | 20:00 | 151 | Satmasjid | 96 | 19:00
20 | Bashundhara | 160 | 19:00 | 86 | Khulshi | 165 | 00:00 | 152 | Savar | 148 | 01:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kishoreganj | 160 | 21:00 | 153 | SevenRings | 3.73 | 13:00
22 | Beanibazar | 74 | 18:30 | 88 | Kodda | 214 | 00:00 | 154 | ShahCement | 7 | 19:30
23 | Benapole | 72 | 19:00 | 89 | Kulaura | 52 | 18:30 | 155 | Shahjadpur | 88 | 20:00
24 | Bhaluka | 139 | 18:00 | 90 | Kurigram | 73 | 18:00 | 156 | Shahjibazar | 133 | 22:00
25 | Bhandaria | 56 | 22:00 | 91 | Kushtia | 130 | 19:00 | 157 | Shahmirpur | 45.6 | 23:00
26 | Bhangura | 44 | 03:00 | 92 | Lalbag | 48 | 01:00 | 158 | Shariatpur | 96 | 21:00
27 | Bheramara(GK) | 56 | 19:00 | 93 | Lalmonirhat | 66 | 18:00 | 159 | Sherpur | 168 | 18:00
28 | Bhulta | 208 | 00:00 | 94 | MI_Cement | 17.1 | 16:00 | 160 | Shikalbaha | 22 | 18:30
29 | Bog-Sherpur | 70 | 03:00 | 95 | Madanganj | 40 | 21:00 | 161 | Shitalakhya | 69.8 | 15:00
30 | Bogura | 177 | 21:00 | 96 | Madaripur | 126 | 22:00 | 162 | Sholosohor | 35 | 00:00
31 | Borhanuddin | 94 | 23:00 | 97 | Madartek | 82.74 | 00:00 | 163 | Shyampur | 132 | 05:00
32 | Brahmanbaria | 150 | 22:00 | 98 | Madunaghat | 52 | 19:00 | 164 | Siddhirganj | 91 | 00:00
33 | Cantonment | 107 | 19:00 | 99 | Magura | 70 | 19:00 | 165 | Sirajganj | 114 | 03:00
34 | Chandpur | 78 | 18:30 | 100 | Mahasthangarh | 78 | 00:00 | 166 | Sonargaon | 77 | 00:00
35 | Chandraghona | 37 | 18:30 | 101 | Manikganj | 114 | 20:00 | 167 | Sreemongol | 71 | 22:00
36 | Chapai | 67 | 00:00 | 102 | Maniknagar | 55 | 19:00 | 168 | Sreepur | 56 | 00:00
37 | Charsaidpur | 27 | 09:00 | 103 | Matarbari | 50 | 23:00 | 169 | Srinagar | 51.91 | 22:00
38 | Chauddagram | 83 | 18:30 | 104 | Matuail | 53 | 00:00 | 170 | Sunamganj | 59 | 21:00
39 | Chhatak | 35 | 18:30 | 105 | Millgate | 52 | 00:00 | 171 | Sylhet | 35 | 19:00
40 | Chowmuhani | 238 | 20:00 | 106 | Mirpur | 122 | 19:00 | 172 | Sylhet-132 | 122 | 20:00
41 | Chuadanga | 116 | 03:00 | 107 | Mirsorai | 7 | 00:00 | 173 | TK | 23 | 22:00
42 | Coxsbazar | 133 | 18:30 | 108 | Mirzapur | 49 | 19:00 | 174 | Tangail | 202 | 19:00
43 | Cumilla(N) | 184 | 18:00 | 109 | Mithapukur | 66 | 17:00 | 175 | Thakurgaon | 96 | 19:00
44 | Cumilla(S) | 151 | 18:30 | 110 | Modern | N/A | N/A | 176 | Tongi | 98 | 00:00
45 | Daudkandi | 140 | 22:00 | 111 | Mogbazar | 110 | 19:00 | 177 | Ullahpara | 33 | 19:00
46 | Dhaka | 32 | 13:00 | 112 | Mongla | 45 | 00:00 | 178 | Ullon | 46 | 00:00
47 | Dhamrai | 106 | 06:00 | 113 | Motijheel | 30 | 19:00 | 179 | Uttara | 81 | 19:00
48 | Dhanmondi | 111 | 19:00 | 114 | Muktagacha | 45 | 18:00 | 180 | UttaraNew | 43 | 00:00
49 | Dohazari | 117 | 19:00 | 115 | Munshiganj | 114 | 00:00 | 181 | Zigatola | 62 | 19:30
50 | Faridpur | 158 | 00:00 | 116 | Muradnagar | 32 | 18:30
51 | Fatullah | 66 | 00:00 | 117 | Mymensingh | 214 | 18:00
52 | Fenchuganj | 41 | 18:30 | 118 | Naogaon | 135 | 22:00
53 | Feni | 128 | 18:30 | 119 | Narail | 64 | 19:30
54 | GPH | 96 | 00:00 | 120 | Narinda | 55 | 13:00
55 | Ghatail | 94 | 18:30 | 121 | Narshingdi | 179 | 00:00
56 | Ghorashal | 15 | 07:00 | 122 | Natore | 162 | 19:30
57 | Ghorashal-230 | 84 | 01:00 | 123 | Nawabganj | 62.6 | 21:00
58 | Goalpara | 32 | 00:00 | 124 | Netrakona | 142 | 22:00
59 | Gollamari | 72 | 00:00 | 125 | New | 57 | 00:00
60 | Gopalganj | 120.8 | 23:00 | 126 | Niamatpur | 115 | 22:00
61 | Gulshan | 86 | 19:00 | 127 | Noapara | 46 | 19:00
62 | Halishahar | 36 | 09:00 | 128 | PHP | 2 | 04:00
63 | HaripurSBU | 128 | 00:00 | 129 | Pabna | 114 | 03:00
64 | Hasnabad | 73 | 00:00 | 130 | Palashbari | 126 | 18:30
65 | Hathazari | 85 | 20:00 | 131 | Panchagarh | 53 | 18:00
66 | Ishurdi | 69 | 19:30 | 132 | Patuakhali | 83.5 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14530 | 45 |  | 14577.03
1:00 | 13945.3 | 50 |  | 13997.3
2:00 | 13512.3 | 50 |  | 13564.3
3:00 | 13615.3 | 75 |  | 13693.3
4:00 | 13451.3 | 40 |  | 13493.3
5:00 | 12759.3 | 26 |  | 12786.3
6:00 | 11650.3 | 26 |  | 11677.3
7:00 | 11407.25 | 0 |  | 11407.25
8:00 | 11296.98 | 0 |  | 11296.98
9:00 | 11572.84 | 0 |  | 11572.84
10:00 | 11855.41 | 0 |  | 11855.41
11:00 | 11995.05 | 0 |  | 11995.05
12:00 | 12205.85 | 0 |  | 12205.85
13:00 | 12538.77 | 0 |  | 12538.77
14:00 | 13068.04 | 15 |  | 13084.04
15:00 | 13198.56 | 71 |  | 13272.56
16:00 | 13010.66 | 59 |  | 13072.66
17:00 | 13092.83 | 56 |  | 13151.83
18:00 | 13531.55 | 0 |  | 13531.55
19:00 | 14310 | 19 |  | 14330
19:30 | 14296.5 | 18 |  | 14315.5
20:00 | 14164 | 0 |  | 14164
21:00 | 14350.65 | 0 |  | 14350.65
22:00 | 14210.91 | 0 |  | 14210.91
23:00 | 14149.06 | 0 |  | 14149.06
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8503.5 | 6026.5 | 14530 | DAILY GENERATION CURVE
00:30 | 8248.65 | 5989 | 14237.65
01:00 | 7993.8 | 5951.5 | 13945.3 | 29-03-2025
01:30 | 7842.8 | 5886 | 13728.8
02:00 | 7691.8 | 5820.5 | 13512.3
02:30 | 7724.3 | 5839.5 | 13563.8
03:00 | 7756.8 | 5858.5 | 13615.3
03:30 | 7673.8 | 5859.5 | 13533.3
04:00 | 7590.8 | 5860.5 | 13451.3
04:30 | 7401.3 | 5704 | 13105.3
05:00 | 7211.8 | 5547.5 | 12759.3
05:30 | 7022.8 | 5182 | 12204.8
06:00 | 6833.8 | 4816.5 | 11650.3
06:30 | 6754.7 | 4774.075 | 11528.775
07:00 | 6675.6 | 4731.65 | 11407.25
07:30 | 6679.215 | 4672.9 | 11352.115
08:00 | 6682.83 | 4614.15 | 11296.98
08:30 | 6746.065 | 4688.845 | 11434.91
09:00 | 6809.3 | 4763.54 | 11572.84
09:30 | 6837.905 | 4876.22 | 11714.125
10:00 | 6866.51 | 4988.9 | 11855.41
10:30 | 6905.675 | 5019.555 | 11925.23
11:00 | 6944.84 | 5050.21 | 11995.05
11:30 | 6993.905 | 5106.545 | 12100.45
12:00 | 7042.97 | 5162.88 | 12205.85
12:30 | 7074.115 | 5298.195 | 12372.31
13:00 | 7105.26 | 5433.51 | 12538.77
13:30 | 7115.48 | 5687.925 | 12803.405
14:00 | 7125.7 | 5942.34 | 13068.04
14:30 | 7150.595 | 5982.705 | 13133.3
15:00 | 7175.49 | 6023.07 | 13198.56
15:30 | 7176.74 | 5927.87 | 13104.61
16:00 | 7177.99 | 5832.67 | 13010.66
16:30 | 7206.31 | 5845.435 | 13051.745
17:00 | 7234.63 | 5858.2 | 13092.83
17:30 | 7457.1 | 5855.09 | 13312.19
18:00 | 7679.57 | 5851.98 | 13531.55
18:30 | 7876.785 | 6043.99 | 13920.775
19:00 | 8074 | 6236 | 14310
19:30 | 8119.5 | 6177 | 14296.5
20:00 | 8051 | 6113 | 14164
20:30 | 8079.5 | 6177.825 | 14257.325 |  | Executive Engineer
21:00 | 8108 | 6242.65 | 14350.65 |  | Network Operation Division
21:30 | 8052.5 | 6228.28 | 14280.78
22:00 | 7997 | 6213.91 | 14210.91
22:30 | 7983 | 6196.985 | 14179.985
23:00 | 7969 | 6180.06 | 14149.06

## En-Curve
QF-LDC-12
Date | 29-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3592 | 2606 | 920 | 0 | 32 | 1352 | 46 | 4179 | 0 | 311 | 1475 | 0 | 0 | 17 | 45 | DAILY ENERGY CURVE
00:30 | 3629 | 2549.15 | 919.5 | 0 | 35 | 1356 | 46 | 4057 | 0 | 299.5 | 1331.5 | 0 | 0 | 15 | 47.5 | 29-03-2025
01:00 | 3666 | 2492.3 | 919 | 0 | 38 | 1360 | 46 | 3935 | 0 | 288 | 1188 | 0 | 0 | 13 | 50
01:30 | 3634.5 | 2450.3 | 919 | 0 | 38 | 1365 | 46 | 3930.5 | 0 | 288 | 1044 | 0 | 0 | 13.5 | 50 | Energy Generated | 315.7487 |  | MKWHr
02:00 | 3603 | 2408.3 | 919 | 0 | 38 | 1370 | 46 | 3926 | 0 | 288 | 900 | 0 | 0 | 14 | 50 | Energy not Served | 0.532 |  | MKWHr
02:30 | 3610 | 2433.8 | 919 | 0 | 38 | 1365.5 | 46 | 3926.5 | 0 | 313 | 897 | 0 | 0 | 15 | 62.5 | Total Energy Requirement | 316.2807 |  | MKWHr
03:00 | 3617 | 2459.3 | 919 | 0 | 38 | 1361 | 46 | 3927 | 0 | 338 | 894 | 0 | 0 | 16 | 75
03:30 | 3622 | 2459.3 | 912.5 | 0 | 34 | 1359 | 46 | 3882 | 0 | 333 | 877.5 | 0 | 0 | 8 | 57.5
04:00 | 3627 | 2459.3 | 906 | 0 | 30 | 1357 | 46 | 3837 | 0 | 328 | 861 | 0 | 0 | 0 | 40
04:30 | 3569.5 | 2403.8 | 906 | 0 | 30 | 1366.5 | 46 | 3711 | 0 | 270.5 | 801.5 | 0 | 0 | 0.5 | 33
05:00 | 3512 | 2348.3 | 906 | 0 | 30 | 1376 | 46 | 3585 | 0 | 213 | 742 | 0 | 0 | 1 | 26
05:30 | 3483 | 2335.8 | 905.5 | 0 | 29 | 1260.5 | 46 | 3271 | 0 | 181 | 688 | 0 | 0 | 5 | 26
06:00 | 3454 | 2323.3 | 905 | 0 | 28 | 1145 | 46 | 2957 | 0 | 149 | 634 | 0 | 0 | 9 | 26
06:30 | 3455 | 2324.9 | 908.5 | 0 | 29 | 1075.5 | 46 | 2937.5 | 35.875 | 128 | 584 | 0 | 0 | 4.5 | 13
07:00 | 3456 | 2326.5 | 912 | 0 | 30 | 1006 | 46 | 2918 | 71.75 | 107 | 534 | 0 | 0 | 0 | 0
07:30 | 3486.5 | 2340.5 | 909 | 0 | 27 | 932.985 | 46 | 2876.5 | 144.13 | 62 | 527 | 0 | 0 | 0.5 | 0
08:00 | 3517 | 2354.5 | 906 | 0 | 24 | 859.97 | 46 | 2835 | 216.51 | 17 | 520 | 0 | 0 | 1 | 0
08:30 | 3585.5 | 2350.5 | 884 | 0 | 24 | 857.4 | 46 | 2831 | 310.01 | 17 | 529 | 0 | 0 | 0.5 | 0
09:00 | 3654 | 2346.5 | 862 | 0 | 24 | 854.83 | 46 | 2827 | 403.51 | 17 | 538 | 0 | 0 | 0 | 0
09:30 | 3670 | 2355 | 883.5 | 0 | 28 | 866.125 | 46 | 2856 | 458.5 | 26 | 522.5 | 0 | 0 | 2.5 | 0
10:00 | 3686 | 2363.5 | 905 | 0 | 32 | 877.42 | 46 | 2885 | 513.49 | 35 | 507 | 0 | 0 | 5 | 0
10:30 | 3715 | 2403.5 | 905.5 | 0 | 29 | 868.02 | 46 | 2876 | 570.71 | 35 | 472 | 0 | 0 | 4.5 | 0
11:00 | 3744 | 2443.5 | 906 | 0 | 26 | 858.62 | 46 | 2867 | 627.93 | 35 | 437 | 0 | 0 | 4 | 0
11:30 | 3792.5 | 2489.5 | 906 | 0 | 31 | 860.12 | 46 | 2879 | 643.83 | 35 | 410.5 | 0 | 0 | 7 | 0
12:00 | 3841 | 2535.5 | 906 | 0 | 36 | 861.62 | 46 | 2891 | 659.73 | 35 | 384 | 0 | 0 | 10 | 0
12:30 | 3822.5 | 2542.5 | 906 | 0 | 35 | 866.065 | 46 | 3037.5 | 659.295 | 39.45 | 408.5 | 0 | 0 | 9.5 | 0
13:00 | 3804 | 2549.5 | 906 | 0 | 34 | 870.51 | 46 | 3184 | 658.86 | 43.9 | 433 | 0 | 0 | 9 | 0
13:30 | 3698 | 2538.5 | 906 | 0 | 36 | 986.595 | 46 | 3418 | 622.86 | 53.95 | 488 | 0 | 0 | 9.5 | 7.5
14:00 | 3592 | 2527.5 | 906 | 0 | 38 | 1102.68 | 46 | 3652 | 586.86 | 64 | 543 | 0 | 0 | 10 | 15
14:30 | 3524.5 | 2535.75 | 907 | 0 | 39 | 1106.34 | 46 | 3746.5 | 525.21 | 77.5 | 614.5 | 0 | 0 | 11 | 43
15:00 | 3457 | 2544 | 908 | 0 | 40 | 1110 | 46 | 3841 | 463.56 | 91 | 686 | 0 | 0 | 12 | 71
15:30 | 3450.5 | 2541.5 | 908 | 0 | 40 | 1114 | 46 | 3815 | 381.61 | 106 | 689.5 | 0 | 0 | 12.5 | 65
16:00 | 3444 | 2539 | 908 | 0 | 40 | 1118 | 46 | 3789 | 299.66 | 121 | 693 | 0 | 0 | 13 | 59
16:30 | 3456 | 2557.5 | 908 | 0 | 42 | 1120 | 46 | 3854.5 | 208.245 | 134.5 | 713 | 0 | 0 | 12 | 57.5
17:00 | 3468 | 2576 | 908 | 0 | 44 | 1122 | 46 | 3920 | 116.83 | 148 | 733 | 0 | 0 | 11 | 56
17:30 | 3478 | 2585.5 | 908 | 0 | 43 | 1122.5 | 46 | 3915.5 | 62.19 | 188 | 954 | 0 | 0 | 9.5 | 28
18:00 | 3488 | 2595 | 908 | 0 | 42 | 1123 | 46 | 3911 | 7.55 | 228 | 1175 | 0 | 0 | 8 | 0
18:30 | 3533.5 | 2499 | 883.5 | 0 | 40 | 1243.5 | 46 | 3999.5 | 3.775 | 303.5 | 1362 | 0 | 0 | 6.5 | 9.5
19:00 | 3579 | 2403 | 859 | 0 | 38 | 1364 | 46 | 4088 | 0 | 379 | 1549 | 0 | 0 | 5 | 19
19:30 | 3559 | 2482.5 | 859 | 0 | 38 | 1369 | 46 | 4124 | 0 | 371 | 1447 | 0 | 0 | 1 | 18
20:00 | 3632 | 2527 | 859 | 0 | 32 | 1360 | 46 | 4135 | 0 | 308 | 1265 | 0 | 0 | 0 | 0
20:30 | 3675.5 | 2582 | 859 | 0 | 36 | 1364.825 | 46 | 4152 | 0 | 310 | 1232 | 0 | 0 | 0 | 0
21:00 | 3719 | 2637 | 859 | 0 | 40 | 1369.65 | 46 | 4169 | 0 | 312 | 1199 | 0 | 0 | 0 | 0
21:30 | 3687.5 | 2625.5 | 883 | 0 | 39 | 1365.78 | 46 | 4177.5 | 0 | 295.5 | 1160.5 | 0 | 0 | 0.5 | 0
22:00 | 3656 | 2614 | 907 | 0 | 38 | 1361.91 | 46 | 4186 | 0 | 279 | 1122 | 0 | 0 | 1 | 0
22:30 | 3630 | 2613.75 | 906 | 0 | 37 | 1365.235 | 46 | 4186 | 0 | 279 | 1111.5 | 0 | 0 | 5.5 | 0
23:00 | 3604 | 2613.5 | 905 | 0 | 36 | 1368.56 | 46 | 4186 | 0 | 279 | 1101 | 0 | 0 | 10 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 07:00 | 386 | 21:00 | Payra | 419 | 06:00 | 408 | 22:00
Ashuganj | 413 | 6:00 | 393 | 13:00 | Rahanpur | 395 | 07:00 | 383 | 21:00
Bhulta | 407 | 06:00 | 393 | 14:00 | Rampal | 409 | 07:00 | 389 | 21:00
Bibiana | 398 | 06:00 | 388 | 13:00
BIPTC | 395 | 06:00 | 385 | 16:00
Bogura | 383 | 07:00 | 372 | 00:00
Gopalganj | 409 | 07:00 | 391 | 21:00
Kaliakoir | 375 | 05:00 | 362 | 14:00
Madunaghat | 403 | 08:00 | 392 | 15:00
Meghnaghat | 407 | 08:00 | 392 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 07:00 | 226 | 14:00 | Keranigonj | 234 | 07:00 | 225 | 13:00
AKSML | 234 | 05:00 | 226 | 14:00 | Khulna(S) | 232 | 06:00 | 219 | 00:00
Aminbazar | 233 | 06:00 | 227 | 14:00 | Madunaghat | 237 | 08:00 | 228 | 14:00
Ashuganj | 235 | 06:00 | 229 | 14:00 | Madunaghat-400 | 238 | 07:00 | 229 | 15:00
Ashuganj-400 | 235 | 06:00 | 229 | 14:00 | Maniknagar | 230 | 06:00 | 224 | 14:00
Baghabari | 235 | 05:00 | 226 | 21:00 | Meghnaghat | 240 | 07:00 | 231 | 21:00
Barapukuria | 221 | 06:00 | 215 | 12:00 | Meghnaghat-400 | 235 | 08:00 | 2 | 01:00
Barapukuria-230 | 221 | 06:00 | 215 | 12:00 | Mirsorai | 233 | 08:00 | 223 | 21:00
Barishal | 237 | 07:00 | 226 | 23:00 | Rajshahi | 234 | 05:00 | 219 | 21:00
Bheramara | 235 | 04:00 | 223 | 22:00 | Rampal | 233 | 06:00 | 218 | 21:00
Bhulta | 232 | 07:00 | 223 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 05:00 | 222 | 21:00 | Rampura | 230 | 06:00 | 222 | 13:00
BIPTC | 236 | 04:00 | 223 | 21:00 | Shikalbaha | 234 | 07:00 | 225 | 14:00
Bogura | 233 | 06:00 | 227 | 03:00 | Shyampur | 234 | 08:00 | 225 | 13:00
Bogura-400 | 233 | 06:00 | 227 | 00:00 | Siddhirganj | 234 | 07:00 | 226 | 13:00
Borhanuddin | 241 | 07:00 | 233 | 22:00 | Sirajgonj | 241 | 07:00 | 236 | 00:00
BSRM | 233 | 08:00 | 222 | 21:00 | Sreepur | 236 | 07:00 | 227 | 14:00
Cumilla(N) | 229 | 06:00 | 220 | 14:00 | Tongi | 229 | 04:00 | 220 | 13:00
Faridpur | 236 | 07:00 | 224 | 21:00
Fenchuganj | 232 | 07:00 | 227 | 00:00
Ghorashal | 232 | 00:00 | 230 | 06:00
Ghorashal-230 | 232 | 07:00 | 224 | 13:00
Gopalganj | 235 | 07:00 | 224 | 21:00
GPH | 234 | 07:00 | 225 | 14:00
Haripur | 230 | 06:00 | 223 | 13:00
Hasnabad | 233 | 07:00 | 224 | 14:00
Hathazari | 237 | 09:00 | 229 | 23:00
Ishurdi | 236 | 04:00 | 225 | 21:00
Jhenaidah | 228 | 05:00 | 213 | 00:00
Kaliakoir | 234 | 06:00 | 225 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 07:00 | 131 | 13:00 | Madunaghat | 136 | 07:00 | 129 | 14:00
Agargaon | 139 | 06:00 | 133 | 20:00 | Magura | 131 | 06:00 | 118 | 21:00
Agrabad | 135 | 06:00 | 127 | 14:00 | Mahasthangarh | 128 | 05:00 | 122 | 12:00
AKS | 132 | 07:00 | 126 | 14:00 | Manikganj | 131 | 05:00 | 123 | 11:00
Aminbazar | 136 | 06:00 | 131 | 14:00 | Maniknagar | 135 | 05:00 | 132 | 13:00
Amnura | 135 | 06:00 | 122 | 00:00 | Matarbari | 123 | 07:00 | 108 | 21:00
Ashuganj | 137 | 07:00 | 133 | 17:00 | Matuail | 135.7 | 07:00 | 131 | 15:00
Bagerhat | 130 | 07:00 | 118 | 00:00 | Millgate | 140 | 06:00 | 133 | 13:00
Bajitpur | 131 | 06:00 | 124 | 16:00 | Mirpur | 137 | 06:00 | 130 | 08:00
Bakulia | 136 | 07:00 | 129 | 14:00 | Mirzapur | 131 | 05:00 | 122 | 13:00
Banani | 138 | 06:00 | 130 | 20:00 | Mithapukur | 128 | 05:00 | 118 | 12:00
Bangabhaban | 136 | 06:00 | 132 | 13:00 | MI_Cement | 135.6 | 08:00 | 131 | 14:00
Barapukuria | 135 | 00:00 | 129 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 08:00 | 129 | 00:00 | Mogbazar | 139 | 05:00 | 132 | 13:00
Barishal | 133 | 08:00 | 123 | 22:00 | Mongla | 130 | 08:00 | 119 | 00:00
Barishal-230 | 133 | 07:00 | 123 | 23:00 | Motijheel | 136 | 06:00 | 132 | 13:00
Baroaulia | 135 | 09:00 | 129 | 14:00 | Muktagacha | 134 | 03:00 | 117 | 13:00
Baroirhat | 124 | 08:00 | 119 | 19:00 | Munshiganj | 135 | 07:00 | 130 | 13:00
Bashundhara | 138 | 01:00 | 131 | 06:00 | Muradnagar | 129 | 08:00 | 122 | 14:00
BashundharaCement | 135 | 01:00 | 130 | 00:00 | Mymensingh | 136 | 06:00 | 111 | 17:00
Beanibazar | 129 | 07:00 | 123 | 21:00 | Naogaon | 125 | 05:00 | 118 | 14:00
Benapole | 127 | 06:00 | 115 | 19:00 | Narail | 132 | 06:00 | 116 | 21:00
Bhaluka | 129 | 06:00 | 120 | 17:00 | Narinda | 135 | 9:00 | 132 | 13:00
Bhandaria | 127 | 07:00 | 113 | 23:00 | Narshingdi | 131 | 06:00 | 119 | 00:00
Bhangura | 132 | 03:00 | 127 | 00:00 | Natore | 131 | 05:00 | 123 | 21:00
Bheramara | 133 | 04:00 | 126 | 21:00 | Nawabganj | 137 | 06:00 | 130 | 14:00
Bheramara(GK) | 134 | 05:00 | 126 | 21:00 | Netrakona | 121 | 06:00 | 110 | 00:00
Bhulta | 130 | 06:00 | 126 | 00:00 | New | 140 | 06:00 | 134 | 13:00
Bog-Sherpur | 130 | 06:00 | 124 | 17:00 | Niamatpur | 132 | 06:00 | 127 | 19:30
Bogura | 131 | 06:00 | 125 | 14:00 | Noapara | 131 | 07:00 | 121 | 21:00
Bogura-230 | 131 | 05:00 | 126 | 17:00 | Pabna | 133 | 05:00 | 126 | 17:00
Brahmanbaria | 130 | 09:00 | 124 | 00:00 | Palashbari | 124 | 04:00 | 115 | 17:00
Cantonment | 145 | 01:00 | 133 | 14:00 | Panchagarh | 136 | 19:30 | 115 | 12:00
Chandpur | 125 | 08:00 | 119 | 00:00 | Patuakhali | 135 | 09:00 | 130 | 21:00
Chandraghona | 136 | 07:00 | 132 | 19:30 | Payra | 138 | 08:00 | 134 | 00:00
Chapai | 129 | 07:00 | 124 | 00:00 | PHP | 124 | 06:00 | 117 | 23:00
Charsaidpur | 136 | 06:00 | 131 | 14:00 | Postogola | 139 | 07:00 | 133 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 125 | 05:00 | 120 | 00:00 | Purbachal | 139 | 06:00 | 131 | 13:00
Chhatak | 130 | 08:00 | 121 | 21:00 | Purbasadipur | 130 | 00:00 | 114 | 12:00
Chowmuhani | 117 | 11:00 | 110 | 14:00 | Rahanpur | 135 | 05:00 | 129 | 21:00
Chuadanga | 130 | 05:00 | 116 | 14:00 | Rahanpur-400 | 134 | 06:00 | 130 | 00:00
Coxsbazar | 121 | 08:00 | 109 | 18:00 | Rahim | 135 | 06:00 | 131 | 14:00
Cumilla(N) | 130 | 07:00 | 124 | 21:00 | Rajbari | 131 | 08:00 | 123 | 00:00
Cumilla(S) | 133 | 05:00 | 121 | 14:00 | Rajendrapur | 131 | 04:00 | 124 | 00:00
Daudkandi | 129 | 08:00 | 121 | 14:00 | Rajshahi | 133 | 05:00 | 125 | 21:00
Dhaka | 139 | 05:00 | 131 | 13:00 | Rajshahi-230 | 134 | 05:00 | 116 | 21:00
Dhamrai | 133 | 08:00 | 128 | 14:00 | Ramganj | 119 | 10:00 | 111 | 01:00
Dhanmondi | 138 | 06:00 | 132 | 13:00 | Rampur | 135 | 06:00 | 129 | 12:00
Dohazari | 131 | 07:00 | 121 | 21:00 | Rampura | 137 | 03:00 | 131 | 13:00
Faridpur | 133 | 08:00 | 126 | 00:00 | Rangamati | 135 | 06:00 | 128 | 13:00
Fatullah | 137 | 08:00 | 132 | 00:00 | Rangpur | 128 | 02:00 | 116 | 17:00
Fenchuganj | 135 | 05:00 | 130 | 00:00 | Ruppur | 136 | 06:00 | 128 | 21:00
Feni | 123 | 16:00 | 118 | 14:00 | Saidpur | 131 | 03:00 | 118 | 09:00
Ghatail | 130 | 05:00 | 115 | 14:00 | Satkhira | 130 | 06:00 | 116 | 21:00
Ghorashal | 138 | 06:00 | 133 | 13:00 | Satmasjid | 139 | 07:00 | 133 | 13:00
Goalpara | 136 | 06:00 | 125 | 00:00 | Savar | 135 | 06:00 | 129 | 23:00
Gollamari | 136 | 06:00 | 125 | 21:00 | SevenRings | 139 | 07:00 | 133 | 13:00
Gopalganj | 135 | 06:00 | 126 | 00:00 | ShahCement | 136 | 06:00 | 131 | 14:00
Gopalganj-400 | 138 | 06:00 | 131 | 21:00 | Shahjadpur | 136 | 05:00 | 131 | 16:00
Gulshan | 137 | 06:00 | 131 | 13:00 | Shahjibazar | 132 | 08:00 | 125 | 00:00
Halishahar | 134 | 10:00 | 128 | 14:00 | Shahmirpur | 137 | 07:00 | 130 | 14:00
Haripur | 136 | 06:00 | 132 | 13:00 | Shariatpur | 136 | 07:00 | 126 | 21:00
HaripurSBU | 136 | 07:00 | 132 | 00:00 | Sherpur | 135 | 06:00 | 110 | 13:00
Hasnabad | 138 | 07:00 | 133 | 00:00 | Shikalbaha | 125 | 06:00 | 118 | 14:00
Hathazari | 135 | 08:00 | 132 | 01:00 | Shikalbaha-230 | 137 | 07:00 | 130 | 10:00
Ishurdi | 136 | 04:00 | 129 | 21:00 | Shitalakhya | 135.6 | 08:00 | 131 | 14:00
Jaldhaka | 128 | 01:00 | 115 | 12:00 | Sholosohor | 135 | 05:00 | 130 | 14:00
Jamalpur | 137 | 06:00 | 116 | 12:00 | Shyampur | 136 | 06:00 | 130 | 00:00
Jashore | 129 | 06:00 | 117 | 21:00 | Shyampur-230 | 137 | 06:00 | 130 | 00:00
Jhenaidah | 132 | 05:00 | 120 | 21:00 | Siddhirganj | 136 | 06:00 | 132 | 13:00
Jhenaidah-230 | 132 | 07:00 | 120 | 00:00 | Sirajganj | 130 | 05:00 | 123 | 21:00
Joydebpur | 134 | 06:00 | 127 | 14:00 | Sonargaon | 134 | 08:00 | 128 | 15:00
Joypurhat | 122 | 06:00 | 114 | 14:00 | Sreemongol | 132 | 06:00 | 125 | 22:00
Juldah | 136 | 07:00 | 130 | 14:00 | Sreepur | 133 | 07:00 | 125 | 17:00
Kabirpur | 135 | 02:00 | 125 | 14:00 | Srinagar | 137 | 07:00 | 131 | 00:00
Kachua | 124 | 07:00 | 119 | 00:00 | SSM | 140 | 06:00 | 130 | 15:00
Kaliakoir | 136 | 05:00 | 126 | 13:00 | Sunamganj | 128 | 08:00 | 119 | 21:00
Kallyanpur | 136 | 04:00 | 132 | 15:00 | Sylhet | 131 | 06:00 | 125 | 21:00
Kalurghat | 134 | 09:00 | 130 | 22:00 | Sylhet-132 | 131 | 09:00 | 127 | 18:30
Kamrangirchar | 137 | 06:00 | 131 | 14:00 | Tangail | 129 | 05:00 | 117 | 14:00
Kaptai | 138 | 7:00 | 133 | 15:00 | Thakurgaon | 134 | 18:30 | 112 | 12:00
Kasba | 128 | 08:00 | 121 | 13:00 | TK | 136 | 10:00 | 130 | 17:00
Kazla | 136 | 06:00 | 131 | 00:00 | Tongi | 139 | 04:00 | 136 | 00:00
Keranigonj | 137 | 06:00 | 131 | 13:00 | Ullahpara | 132 | 01:00 | 126 | 17:00
Khagrachori | 135 | 06:00 | 128 | 14:00 | Ullon | 137 | 05:00 | 131 | 15:00
Khulna | 133 | 06:00 | 123 | 22:00 | Uttara | 138 | 06:00 | 132 | 13:00
Khulna(S) | 135 | 06:00 | 126 | 00:00 | UttaraNew | 136 | 07:00 | 131 | 16:00
Khulshi | 134 | 05:00 | 127 | 13:00 | Zigatola | 137 | 06:00 | 130 | 01:00
Kishoreganj | 131 | 07:00 | 120 | 17:00
Kodda | 132 | 03:00 | 123 | 14:00
KSRM | 135 | 10:00 | 129 | 14:00
Kulaura | 134 | 07:00 | 128 | 21:00
Kurigram | 128 | 05:00 | 114 | 12:00
Kushtia | 133 | 06:00 | 123 | 21:00
Lalbag | 137 | 07:00 | 131 | 14:00
Lalmonirhat | 128 | 23:00 | 116 | 17:00
Madanganj | 135 | 07:00 | 130 | 00:00
Madaripur | 137 | 07:00 | 128 | 00:00
Madartek | 136 | 04:00 | 130 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division