## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
|  | Forecasted Generation & Demand of National Grid | [11 empty] | Eid Mubarak
| Date : | 31-03-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-03-2025 | during | 31-03-2025 | during | 31-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 140 | 140 | 150 | 150 | 150 | 150 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 81 | 81 | 97.7 | 97.7 | 97.7 | 97.7 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 361 | 409 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 258 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 38 | 40 | 208.13 | 208.13 | 105 | 105 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 322 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 7.5 | 8 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 15 | 15 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 8 | 8 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 17 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 10 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 70 | 125 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 500 | 520 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2323.5 | 2470 | 5189.9 | 5251.9 | 4619 | 4681
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 145 | 151 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 56 | 72 | 56 | 72 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 20 | 42 | 40 | 40 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 3.95 | 0 | 3.95 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 842 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 0 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 409 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1479 | 1937 | 3551.67 | 3542.72 | 3436.67 | 3427.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 180 | 235 | 250 | 250 | 250 | 250 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 46 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 107 | 162 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 37 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 170 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 69 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 41 | 0 | 41 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1294 | 1589 | 2351.99 | 2310.99 | 2212.05 | 2171.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-03-2025 | during | 31-03-2025 | during | 31-03-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 188 | 195 | 210 | 210 | 210 | 210 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 150 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 75 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.74 | 0 | 49.8 | 0 | 49.8 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 337.74 | 432 | 653.6 | 601.5 | 653.6 | 601.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 40 | 40 | 40 | 39 | 39 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 139 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 118 | 118 | 115 | 115 | 115 | 115 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 270 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 350 | 380 | 380 | 352 | 352 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1204 | 1109 | 1243 | 1243 | 1173 | 1173
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 859 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.01 | 0.01 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 382 | 472 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1373 | 1383 | 3610.2 | 3515.2 | 1913.02 | 1818.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 9 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 602 | 1089 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 276 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1101.65 | 1705 | 2171.12 | 2171.12 | 2119.12 | 2119.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 55 | 60 | 60 | 60 | 60 | 60 | machine running
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 138 | 138 | 214 | 214 | 214 | 214 | GT air intake filter DP high.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 209 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 207 | 211 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 376 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.75 | 0 | 5.72 | 0 | 5.72 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 818.72 | 1018.07 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.73 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2006.7 | 2017.57 | 3170.25 | 3003.53 | 3084.46 | 2917.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 61 | 57 | 57 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 157 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 74 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 20 | 0 | 0 | 0 | 0 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 313 | 399 | 525.4 | 489 | 489.42 | 453.02
System Total |  |  |  |  | 27566.2 | 28535.742 | 11432.59 | 13041.57 | 22467.13 | 22128.96 | 19700.34 | 19362.17
Forecast Scenario (31-03-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12270 |  | 0 |  | 12270
|  |  |  | 1:00 | 11860 |  | 0 |  | 11860
|  |  |  | 2:00 | 11380 |  | 0 |  | 11380
|  |  |  | 3:00 | 10840 |  | 0 |  | 10840
|  |  |  | 4:00 | 10340 |  | 0 |  | 10340
|  |  |  | 5:00 | 10200 |  | 0 |  | 10200
|  |  |  | 6:00 | 9930 |  | 0 |  | 9930
|  |  |  | 7:00 | 10220 |  | 0 |  | 10220
|  |  |  | 8:00 | 9800 |  | 0 |  | 9800
|  |  |  | 9:00 | 9090 |  | 0 |  | 9090
|  |  |  | 10:00 | 9060 |  | 0 |  | 9060
|  |  |  | 11:00 | 9260 |  | 0 |  | 9260
|  |  |  | 12:00 | 9550 |  | 0 |  | 9550
|  |  |  | 13:00 | 9850 |  | 0 |  | 9850
|  |  |  | 14:00 | 10050 |  | 0 |  | 10050
|  |  |  | 15:00 | 10040 |  | 0 |  | 10040
|  |  |  | 16:00 | 9700 |  | 0 |  | 9700
|  |  |  | 17:00 | 9420 |  | 0 |  | 9420
|  |  |  | 18:00 | 9360 |  | 0 |  | 9360
|  |  |  | 18:30 | 10200 |  | 0 |  | 10200
|  |  |  | 19:00 | 11190 |  | 0 |  | 11190
|  |  |  | 19:30 | 11490 |  | 0 |  | 11490
|  |  |  | 20:00 | 11490 |  | 0 |  | 11490
|  |  |  | 21:00 | 11730 |  | 0 |  | 11730
|  |  |  | 22:00 | 11750 |  | 0 |  | 11750
|  |  |  | 23:00 | 11550 |  | 0 |  | 11550
Probable Maximum Temperature: |  |  | 36.80°C
Probable Maximum Demand at Day Peak: |  |  | 9550.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11730.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11730.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 249.93 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:55 hrs on 31-03-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-03-2025 | [28 empty] | Date: | 30-03-2025 | [28 empty] | Date: | 30-03-2025 | [28 empty] | Date: | 30-03-2025 | [28 empty] | Date: | 30-03-2025 | [17 empty] | Date: | 30-03-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 111 | 0 | 80 | 353 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 289 | 583 | 0 | 0 | 32 | 330 | 99 | 0 | 0 | 142 | 11.3 | 10 | 0 | 0 | 0 | 0 | 13 | 0 | 8 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 17 | 37 | 575 | 0 | 0 | 0 | 8 | 17 | 60 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 173 | 0 | 360 | 240 | 49 | 184 | 35 | 63 | 51 | 200 | 0 | 20 | 114 | 38 | 0 | 0 | 31 | 300 | 0 | 289 | 40 | 39 | 5 | 146 | 24 | 0 | 85 | 30 | 0 | 18 | 118 | 7 | 65 | 175 | 179 | 0 | 0 | 12 | 7916.3 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 53 | 1367.38 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 175 | 0 | 175 | 0 | 320 | 0 | 0 | 5.5 | 162 | 58 | 55 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1240 | 0 | 6052.88 | 13969.18 | 85.04
01:00 | 0 | 17 | 0 | 0 | 0 | 110 | 0 | 80 | 337 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 22 | 45 | 450 | 287 | 583 | 0 | 0 | 32 | 330 | 99 | 0 | 0 | 125 | 11.5 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 7 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 17 | 41 | 575 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 173 | 0 | 360 | 240 | 48 | 182 | 35 | 24 | 50 | 200 | 0 | 20 | 114 | 38 | 0 | 0 | 31 | 295 | 0 | 289 | 41 | 39 | 5 | 132 | 24 | 0 | 85 | 30 | 0 | 18 | 118 | 17 | 65 | 66 | 173 | 0 | 0 | 12 | 7753.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 53 | 1368.17 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 168 | 0 | 174 | 0 | 319 | 0 | 0 | 5.5 | 165 | 58 | 35 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 10 | 96 | 220 | 0 | 0 | 1100 | 0 | 5747.67 | 13501.17 | 85.03
02:00 | 0 | 17 | 0 | 0 | 0 | 110 | 0 | 80 | 346 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 22 | 48 | 450 | 289 | 583 | 0 | 0 | 32 | 327 | 39 | 0 | 0 | 125 | 11.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 173 | 0 | 360 | 240 | 48 | 184 | 35 | 17 | 50 | 200 | 0 | 20 | 114 | 46 | 0 | 0 | 25 | 300 | 0 | 291 | 40 | 39 | 5 | 132 | 24 | 0 | 85 | 30 | 0 | 18 | 117 | 17 | 65 | 67 | 177 | 0 | 0 | 12 | 7607.5 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 53 | 1268.16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 173 | 0 | 170 | 0 | 320 | 0 | 0 | 5.5 | 165 | 58 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 90 | 180 | 0 | 0 | 1050 | 0 | 5475.66 | 13083.16 | 85.03
03:00 | 0 | 17 | 0 | 0 | 0 | 110 | 0 | 80 | 352 | 0 | 0 | 0 | 0 | 0 | 19 | 64 | 0 | 0 | 0 | 0 | 22 | 65 | 450 | 298 | 583 | 0 | 0 | 32 | 327 | 98 | 0 | 0 | 125 | 11.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 173 | 0 | 358 | 235 | 49 | 173 | 35 | 17 | 50 | 200 | 0 | 20 | 114 | 44 | 0 | 0 | 31 | 310 | 0 | 307 | 40 | 39 | 5 | 132 | 24 | 0 | 85 | 30 | 0 | 18 | 118 | 17 | 65 | 133 | 179 | 0 | 0 | 12 | 7821.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 53 | 1267.5 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 180 | 0 | 175 | 0 | 340 | 0 | 0 | 5.5 | 165 | 58 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 90 | 220 | 0 | 0 | 1048 | 0 | 5545 | 13366.5 | 85.02
04:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 80 | 350 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 22 | 34 | 450 | 301 | 583 | 0 | 0 | 32 | 328 | 98 | 0 | 0 | 70 | 11.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 56 | 0 | 95 | 24 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 108 | 0 | 358 | 235 | 48 | 214 | 35 | 46 | 50 | 196 | 0 | 0 | 114 | 40 | 0 | 0 | 32 | 315 | 0 | 315 | 40 | 39 | 5 | 136 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 17 | 65 | 136 | 183 | 0 | 0 | 12 | 7674.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 53 | 1115.95 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 191 | 0 | 188 | 0 | 348 | 0 | 0 | 5.5 | 166 | 56 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 88 | 220 | 0 | 0 | 1043 | 0 | 5319.45 | 12993.95 | 85.02
05:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 75 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 279 | 583 | 0 | 0 | 32 | 329 | 100 | 0 | 0 | 52 | 11.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 16 | 0 | 60 | 0 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1009 | 0 | 51 | 0 | 108 | 0 | 360 | 240 | 49 | 219 | 35 | 51 | 50 | 197 | 0 | 0 | 98 | 40 | 0 | 0 | 0 | 290 | 0 | 289 | 40 | 39 | 5 | 131 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 17 | 45 | 45 | 190 | 0 | 0 | 12 | 7196.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 1018.18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 173 | 0 | 164 | 0 | 319 | 0 | 0 | 5.5 | 166 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 90 | 220 | 0 | 0 | 1036 | 0 | 4990.68 | 12187.18 | 85.01
06:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 75 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 272 | 583 | 0 | 0 | 32 | 280 | 38 | 0 | 0 | 35 | 11.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 501 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 871 | 0 | 51 | 0 | 108 | 0 | 360 | 240 | 49 | 182 | 35 | 34 | 50 | 170 | 0 | 18 | 70 | 34 | 0 | 0 | 0 | 280 | 0 | 290 | 40 | 39 | 5 | 131 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 8 | 24 | 193 | 0 | 0.01 | 0 | 6516.51 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 920.48 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 170 | 0 | 156 | 0 | 319 | 0 | 0.01 | 5.5 | 164 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 90 | 220 | 0 | 0 | 850 | 0 | 4645.99 | 11162.5 | 85.01
07:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 70 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 286 | 583 | 0 | 0 | 15 | 280 | 39 | 0 | 4 | 17 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 42 | 405 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 860 | 2 | 51 | 0 | 108 | 0 | 360 | 180 | 49 | 182 | 35 | 17 | 50 | 155 | 0 | 18 | 34 | 34 | 0 | 11 | 0 | 285 | 0 | 290 | 40 | 39 | 5 | 131 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 8 | 24 | 191 | 0 | 5.93 | 0 | 6283.93 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.08 | 381 | 0 | 815.65 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 7.65 | 137 | 0 | 151 | 0 | 118 | 0 | 320 | 0 | 0.37 | 5.5 | 166 | 56 | 0 | 4 | 0 | 0 | 0 | 0.6 | 4 | 0.05 | 0 | 200 | 10 | 90 | 220 | 0 | 0 | 850 | 0 | 4517.9 | 10801.83 | 85
08:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 71 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 296 | 583 | 0 | 0 | 14 | 280 | 38 | 0 | 12 | 17 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 42 | 405 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 806 | 8 | 51 | 0 | 108 | 0 | 360 | 190 | 49 | 192 | 35 | 17 | 50 | 136 | 0 | 20 | 34 | 36 | 0 | 11 | 0 | 300 | 0 | 295 | 40 | 39 | 5 | 132 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 27 | 35 | 201 | 1 | 9.87 | 0 | 6293.87 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.61 | 380 | 0 | 819.14 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 21.51 | 137 | 0 | 127 | 0 | 111 | 0 | 331 | 0 | 1.48 | 5.5 | 163 | 56 | 0 | 12 | 0 | 0 | 0 | 2.5 | 8 | 0.14 | 0 | 200 | 10 | 90 | 220 | 0 | 0 | 755 | 0 | 4443.88 | 10737.75 | 85
09:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 73 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 292 | 583 | 0 | 0 | 8 | 280 | 39 | 0 | 20 | 17 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 37 | 409 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 800 | 14 | 51 | 0 | 108 | 0 | 356 | 190 | 48 | 189 | 35 | 17 | 50 | 136 | 0 | 20 | 63 | 36 | 0 | 42 | 0 | 315 | 0 | 303 | 40 | 39 | 5 | 134 | 24 | 0 | 83 | 30 | 0 | 18 | 117 | 0 | 35 | 35 | 200 | 1 | 25.57 | 0 | 6411.57 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 380 | 0 | 817.8 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 38.54 | 137 | 0 | 125 | 0 | 116 | 0 | 325 | 0 | 3.25 | 5.5 | 161 | 55 | 0 | 21 | 0 | 0 | 0 | 4.3 | 13 | 0.47 | 0 | 200 | 9 | 90 | 220 | 0 | 0 | 750 | 0 | 4520.86 | 10932.43 | 84.99
10:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 78 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 287 | 500 | 0 | 0 | 8 | 280 | 39 | 0 | 26 | 17 | 6 | 7 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 10 | 408 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 820 | 0 | 51 | 0 | 108 | 0 | 353 | 180 | 45 | 187 | 34 | 17 | 50 | 85 | 0 | 20 | 70 | 40 | 0 | 48 | 0 | 300 | 0 | 300 | 40 | 39 | 5 | 132 | 24 | 0 | 85 | 30 | 0 | 18 | 118 | 0 | 35 | 35 | 195 | 2 | 43.34 | 0 | 6319.34 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 380 | 0 | 815.25 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 50.02 | 137 | 0 | 142 | 0 | 146 | 0 | 322 | 0 | 4.26 | 2.5 | 165 | 55 | 0 | 28 | 34 | 0 | 0 | 5.9 | 17 | 0.37 | 0 | 150 | 9 | 90 | 220 | 0 | 0 | 632 | 0 | 4537.3 | 10856.64 | 84.98
11:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 80 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 296 | 500 | 0 | 0 | 8 | 280 | 38 | 0 | 30 | 35 | 6 | 7 | 0 | 70 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 20 | 409 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 823 | 0 | 51 | 0 | 107 | 0 | 300 | 180 | 43 | 204 | 33 | 22 | 50 | 85 | 0 | 20 | 70 | 36 | 0 | 63 | 0 | 310 | 0 | 335 | 40 | 39 | 5 | 135 | 24 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 45 | 55 | 194 | 2 | 46.63 | 0 | 6392.63 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 379 | 0 | 819.47 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 56.63 | 138 | 0 | 202 | 0 | 174 | 0 | 414 | 0 | 4.67 | 2.5 | 160 | 55 | 0 | 33 | 34 | 0 | 0 | 6.7 | 19 | 0.51 | 0 | 150 | 9 | 100 | 220 | 0 | 0 | 602 | 0 | 4720.48 | 11113.11 | 84.97
12:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 420 | 295 | 500 | 0 | 0 | 8 | 315 | 38 | 0 | 31 | 35 | 7.5 | 7 | 0 | 70 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 20 | 409 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 842 | 9 | 51 | 0 | 107 | 0 | 300 | 180 | 44 | 207 | 33 | 36 | 50 | 85 | 0 | 20 | 70 | 42 | 0 | 69 | 0 | 315 | 0 | 385 | 39 | 39 | 5 | 147 | 24 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 45 | 55 | 188 | 2 | 47.74 | 0 | 6638.24 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 382 | 0 | 818.72 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 59.73 | 138 | 0 | 205 | 0 | 207 | 0 | 414 | 0 | 4.75 | 2.5 | 160 | 56 | 0 | 36 | 34 | 0 | 0 | 7 | 20 | 0.65 | 0 | 150 | 9 | 120 | 220 | 0 | 0 | 602 | 0 | 4794.35 | 11432.59 | 84.96
13:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 450 | 300 | 583 | 0 | 0 | 8 | 317 | 96 | 0 | 29 | 52 | 7 | 7 | 0 | 105 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 34 | 496 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 802 | 16 | 51 | 0 | 107 | 0 | 344 | 235 | 47 | 192 | 33 | 36 | 50 | 86 | 0 | 20 | 70 | 50 | 0 | 66 | 0 | 315 | 0 | 357 | 39 | 38 | 5 | 152 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 45 | 55 | 188 | 2 | 45.76 | 0 | 7048.76 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 412 | 0 | 817.11 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 56.9 | 143 | 0 | 203 | 0 | 206 | 0 | 384 | 0 | 4.82 | 5.5 | 158 | 56 | 0 | 35 | 34 | 0 | 0 | 6.8 | 20 | 0.41 | 0 | 255 | 7 | 112 | 220 | 0 | 0 | 650 | 0 | 4929.54 | 11978.3 | 84.95
14:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 450 | 300 | 583 | 0 | 0 | 8 | 313 | 96 | 0 | 26 | 52 | 7 | 7 | 0 | 80 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 38 | 576 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 900 | 16 | 51 | 0 | 107 | 0 | 346 | 220 | 46 | 188 | 32 | 56 | 50 | 127 | 0 | 20 | 98 | 42 | 0 | 58 | 7 | 310 | 0 | 350 | 39 | 38 | 5 | 149 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 45 | 55 | 188 | 2 | 41.11 | 0 | 7253.11 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 410 | 0 | 816.97 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 51.01 | 143 | 0 | 203 | 0 | 205 | 0 | 326 | 0 | 4.42 | 5.5 | 154 | 57 | 35 | 31 | 70 | 0 | 0 | 6 | 19 | 0.56 | 0 | 307 | 10 | 110 | 220 | 0 | 0 | 840 | 0 | 5152.46 | 12405.57 | 84.94
15:00 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 81 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 450 | 292 | 583 | 0 | 0 | 8 | 315 | 95 | 0 | 19 | 52 | 8 | 7 | 0 | 65 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 32 | 0 | 3 | 46 | 0 | 38 | 575 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 900 | 13 | 51 | 0 | 107 | 0 | 340 | 220 | 46 | 188 | 30 | 69 | 50 | 170 | 0 | 17 | 98 | 36 | 0 | 37 | 38 | 305 | 0 | 357 | 39 | 38 | 5 | 132 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 45 | 55 | 188 | 2 | 30.57 | 0 | 7273.57 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 412 | 0 | 810.53 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 39.14 | 143 | 0 | 203 | 0 | 205 | 0 | 328 | 0 | 3.5 | 5.5 | 154 | 60 | 35 | 27 | 70 | 0 | 0 | 4.4 | 14 | 0.42 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 882 | 0 | 5127.49 | 12401.06 | 84.93
16:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 401 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 450 | 277 | 583 | 0 | 0 | 8 | 315 | 95 | 0 | 10 | 35 | 8 | 7 | 0 | 120 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 36 | 0 | 1 | 46 | 0 | 41 | 575 | 0 | 0 | 0 | 2 | 0 | 146 | 0 | 0 | 0 | 900 | 8 | 51 | 0 | 107 | 0 | 350 | 225 | 45 | 182 | 31 | 69 | 50 | 170 | 0 | 20 | 105 | 34 | 0 | 25 | 37 | 300 | 0 | 340 | 39 | 38 | 5 | 132 | 24 | 0 | 83 | 30 | 0 | 18 | 118 | 0 | 55 | 85 | 190 | 1 | 18.61 | 1 | 7300.61 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 410 | 0 | 811.47 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 22.34 | 140 | 0 | 204 | 0 | 206 | 0 | 320 | 0 | 1.95 | 5.5 | 158 | 60 | 35 | 18 | 70 | 0 | 0 | 2.8 | 9 | 0.27 | 0 | 307 | 10 | 88 | 180 | 0 | 0 | 884 | 0 | 4976.33 | 12276.94 | 84.92
17:00 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 81 | 402 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 450 | 295 | 583 | 0 | 0 | 8 | 315 | 95 | 0 | 4 | 35 | 8 | 7 | 0 | 125 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 36 | 12 | 1 | 46 | 0 | 40 | 575 | 0 | 0 | 0 | 16 | 0 | 146 | 0 | 0 | 0 | 902 | 2.76 | 51 | 0 | 107 | 0 | 343 | 220 | 44 | 200 | 32 | 69 | 50 | 170 | 0 | 20 | 114 | 36 | 0 | 9 | 37 | 295 | 0 | 290 | 39 | 38 | 5 | 132 | 24 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 55 | 125 | 188 | 0 | 7.08 | 8 | 7370.84 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 412 | 0 | 822.55 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8.1 | 139 | 0 | 204 | 0 | 207 | 0 | 344 | 0 | 0.72 | 5.5 | 157 | 61 | 35 | 8 | 70 | 0 | 0 | 1.1 | 4 | 0.76 | 0 | 307 | 10 | 88 | 180 | 0 | 0 | 878 | 0 | 4934.73 | 12305.57 | 84.91
18:00 | 0 | 17 | 17 | 0 | 0 | 140 | 0 | 81 | 404 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 450 | 288 | 583 | 0 | 0 | 8 | 319 | 96 | 0 | 0 | 70 | 8 | 7 | 0 | 125 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 36 | 12 | 0 | 46 | 0 | 40 | 575 | 0 | 0 | 0 | 16 | 0 | 149 | 0 | 0 | 0 | 932 | 0 | 51 | 0 | 135 | 0 | 347 | 230 | 45 | 182 | 32 | 69 | 50 | 170 | 5 | 20 | 114 | 34 | 0 | 0 | 37 | 295 | 0 | 290 | 39 | 38 | 5 | 132 | 16 | 0 | 84 | 30 | 0 | 18 | 118 | 0 | 75 | 179 | 191 | 0 | 0.49 | 12 | 7546.49 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 461 | 17 | 940.65 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 139 | 0 | 205 | 0 | 207 | 0 | 323 | 0 | 0.06 | 5.5 | 158 | 61 | 35 | 1 | 107 | 0 | 0 | 0 | 0 | 0.01 | 0 | 307 | 10 | 88 | 220 | 0 | 0 | 890 | 0 | 5138.51 | 12685 | 84.9
19:00 | 0 | 10 | 0 | 0 | 0 | 140 | 0 | 81 | 409 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 420 | 258 | 520 | 0 | 0 | 8 | 322 | 40 | 0 | 0 | 90 | 8 | 7 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 17 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 162 | 0 | 360 | 235 | 46 | 181 | 33 | 69 | 50 | 170 | 27 | 20 | 114 | 34 | 0 | 0 | 37 | 270 | 0 | 350 | 40 | 38 | 5 | 139 | 16 | 0 | 85 | 30 | 0 | 18 | 118 | 0 | 75 | 150 | 195 | 0 | 0 | 12 | 7537 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 52 | 1018.07 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 209 | 0 | 211 | 0 | 376 | 0 | 0 | 5.5 | 157 | 61 | 74 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 10 | 110 | 220 | 0 | 0 | 1089 | 0 | 5504.57 | 13041.57 | 84.89
19:30 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 415 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 420 | 269 | 520 | 0 | 0 | 8 | 322 | 39 | 0 | 0 | 90 | 8 | 7 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 12 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 17 | 0 | 151 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 170 | 0 | 355 | 235 | 46 | 181 | 33 | 69 | 50 | 136 | 27 | 20 | 98 | 34 | 0 | 0 | 37 | 295 | 0 | 350 | 39 | 37 | 5 | 152 | 16 | 0 | 85 | 30 | 0 | 18 | 118 | 0 | 55 | 150 | 195 | 0 | 0 | 12 | 7505 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 52 | 966.22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 209 | 0 | 211 | 0 | 378 | 0 | 0 | 5.5 | 153 | 61 | 35 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 110 | 220 | 0 | 0 | 1090 | 0 | 5333.72 | 12838.72
20:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 420 | 296 | 520 | 0 | 0 | 8 | 322 | 97 | 0 | 0 | 70 | 8 | 7 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 12 | 0 | 46 | 0 | 42 | 576 | 0 | 0 | 0 | 17 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 173 | 0 | 350 | 230 | 46 | 188 | 33 | 69 | 50 | 136 | 26 | 20 | 114 | 34 | 0 | 0 | 37 | 290 | 0 | 365 | 39 | 37 | 5 | 151 | 16 | 0 | 85 | 30 | 0 | 18 | 118 | 0 | 45 | 150 | 195 | 0 | 0 | 12 | 7469 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 17 | 969.04 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 209 | 0 | 211 | 0 | 393 | 0 | 0 | 5.5 | 150 | 61 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 116 | 220 | 0 | 0 | 1050 | 0 | 5201.54 | 12670.54 | 84.88
21:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 420 | 302 | 583 | 0 | 0 | 8 | 322 | 97 | 0 | 0 | 70 | 8 | 7 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 42 | 575 | 0 | 0 | 0 | 17 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 175 | 0 | 355 | 230 | 45 | 192 | 34 | 69 | 50 | 120 | 27 | 20 | 114 | 34 | 0 | 0 | 37 | 300 | 0 | 368 | 39 | 38 | 5 | 151 | 16 | 0 | 85 | 30 | 0 | 18 | 118 | 0 | 45 | 115 | 194 | 0 | 0 | 12 | 7507 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 17 | 966 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 208 | 0 | 210 | 0 | 394 | 0 | 0 | 5.5 | 160 | 61 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 116 | 220 | 0 | 0 | 950 | 0 | 5121.5 | 12628.5 | 84.87
22:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 450 | 305 | 583 | 0 | 0 | 8 | 322 | 97 | 0 | 0 | 70 | 8 | 7 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 42 | 565 | 0 | 0 | 0 | 17 | 0 | 150 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 177 | 0 | 349 | 230 | 47 | 203 | 33 | 57 | 50 | 139 | 28 | 20 | 114 | 36 | 0 | 0 | 37 | 315 | 0 | 387 | 39 | 38 | 5 | 156 | 16 | 0 | 85 | 30 | 0 | 18 | 118 | 0 | 45 | 115 | 194 | 0 | 0 | 12 | 7586 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 17 | 968 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 208 | 0 | 210 | 0 | 414 | 0 | 0 | 5.5 | 161 | 61 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 0 | 950 | 0 | 5124.5 | 12710.5 | 84.86
23:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 450 | 302 | 583 | 0 | 0 | 8 | 324 | 98 | 0 | 0 | 70 | 9 | 7 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 42 | 565 | 0 | 0 | 0 | 17 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 177 | 0 | 352 | 230 | 48 | 202 | 34 | 20 | 50 | 192 | 28 | 20 | 114 | 36 | 0 | 0 | 37 | 320 | 0 | 388 | 39 | 39 | 5 | 156 | 16 | 0 | 85 | 30 | 0 | 18 | 118 | 9 | 45 | 95 | 196 | 0 | 0 | 0 | 7629 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 17 | 967 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 210 | 0 | 212 | 0 | 414 | 0 | 0 | 5.5 | 160 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 0 | 945 | 0 | 5073.5 | 12702.5 | 84.85
Total KWH | 0 | 102720 | 35040 | 0 | 0 | 3001031 | 0 | 1817000.01 | 9374400 | 0 | 0 | 0 | 0 | 0 | 181872 | 119520 | 0 | 0 | 11295 | 14400 | 394560 | 310080 | 9879000 | 6945164 | 13466818 | 0 | 0 | 363900 | 7523303 | 1955000 | 0 | 208869 | 1519200 | 221400 | 211680 | 0 | 1635909.09 | 0 | 0 | 15360 | 0 | 80640 | 233333 | 273648 | 0 | 1010880 | 162240 | 25840 | 1085460 | 28400 | 929760 | 12465454.55 | 0 | 0 | 0 | 144846 | 35127 | 3345185 | 0 | 0 | 0 | 22319998 | 104085 | 1081608 | 0 | 3194909 | 0 | 8753900 | 5346000 | 1119360 | 4660000 | 811368 | 986880 | 1190650 | 3797760 | 151200 | 409510 | 2238960 | 906240 | 0 | 451636 | 506816 | 7358000 | 0 | 8194000 | 932000 | 908640 | 107760 | 3351518 | 488688 | 0 | 2005440 | 718944 | 0 | 432000 | 3561350 | 128520 | 1188000 | 2059200 | 4458240 | 14050 | 327280 | 139200 | 173532044.65 | 21712000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622080 | 10152730 | 417120 | 22992662 | 0 | 0 | 1390000 | 0 | 0 | 0 | 5664 | 0 | 0 | 715140 | 0 | 411752 | 3366364 | 0 | 4688945 | 0 | 4664573 | 0 | 8499127 | 0 | 34440 | 126108 | 3907000 | 1364945 | 490085 | 257649 | 1066924 | 0 | 0 | 48441.72 | 146880 | 3934.5 | 0 | 5890000 | 235789 | 2415000 | 5230550 | 0 | 0 | 22306909.09 | 0 | 123162812.31 | 296694856.96

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
|  |  |  | System Summary Report | [7 empty] | Eid Mubarak
|  | Date : | 30-03-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11432.59 | MW | 12:00 Hr. | Energy Generated |  |  | 296.6949 |  | MKWHr.
| Day Peak Demand |  |  | 11432.59 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.04 |  | MKWHr.
| Evening Peak Generation |  |  | 13041.57 | MW | 19:00 Hr. | Energy Demand |  |  | 296.7349 |  | MKWHr.
| Evening Peak Demand |  |  | 13041.57 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35.9 |  | °C
| Minimum Generation of the Day |  |  | 10737.75 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1178.6 |  | MMCFD
| Maximum Generation of the Day |  |  | 13969.18 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.5283 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 56.7892 | 0 | 2.2941 | 0 | 0 | 0.20887 | 0 | 0 | 59.2922 | Gas | 150.7645 | Gas | 505002566.4088
| Chattogram Zone |  |  | 4.2749 | 34.7855 | 1.9038 | 0 | 1.0855 | 0.12993 | 0 | 0.08064 | 42.2603 | Coal | 78.407 | Coal | 557704606.4657
| Cumilla Zone |  |  | 26.5673 | 0 | 7.6816 | 0 | 0 | 0.45164 | 0.90624 | 0 | 35.6068 | HFO | 17.3743 | HFO | 296893284.52
| Mymensingh Zone |  |  | 4.4582 | 0 | 3.5149 | 0 | 0 | 0.34133 | 0 | 0 | 8.3145 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.0583 | Hydro | 1.0855 | Hydro | 108546
| Khulna Zone |  |  | 0 | 10.1527 | 0.41712 | 0 | 0 | 0.62208 | 21.712 | 0 | 32.9039 | Solar | 3.3721 | Solar | 52717523.2042
| Barishal Zone |  |  | 7.8813 | 28.1969 | 0 | 0 | 0 | 0.0039345 | 0 | 0 | 36.0822 | Import | 45.6109 | Import | 226599026
| Rajshahi Zone |  |  | 22.7351 | 0 | 0.005664 | 0 | 0 | 1.1613 | 22.9927 | 0 | 46.8948 | Wind | 0.08064 | Wind | 1180569.6
| Rangpur Zone |  |  | 0 | 5.2719 | 1.557 | 0 | 0 | 0.45297 | 0 | 0 | 7.2819
| Total |  |  | 150.7645 | 78.407 | 17.3743 | 0 | 1.0855 | 3.3721 | 45.6109 | 0.08064 | 296.6949
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 505002566.4088 |  | Hydro | 108546
|  |  |  | Coal | 557704606.4657 |  | Solar | 52717523.2042
|  |  |  | HFO | 296893284.52 |  | Import | 226599026
|  |  |  | HSD | 0 |  | Wind | 1180569.6
[5 empty] | Total: | 164,02,06,122 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.712 | Peak Hr Flow | 859.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 1267927.29 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.9927 | Peak Hr Flow | 1018.07 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 492 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.90624 | Peak Hr Flow | 34.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 728 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.6109 | Peak Hr Flow | 1911.07 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3593
|  |  |  | Chattogram |  | 0 |  | 1211
|  |  |  | Cumilla |  | 0 |  | 1420
|  |  |  | Mymensingh |  | 0 |  | 1258
|  |  |  | Sylhet |  | 0 |  | 597
|  |  |  | Khulna |  | 0 |  | 1723
|  |  |  | Barishal |  | 0 |  | 476
|  |  |  | Rajshahi |  | 0 |  | 1401
|  |  |  | Rangpur |  | 0 |  | 906
|  |  |  | Total |  | 0 |  | 12585
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Jangalia 52 MW PP (Lakdanavi) |  |  | 52.2
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 990 |  |  |  | Total | 487.29
|  |  |  | Total Unavailable Capacity |  |  |  | 1477.29
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:34 | 13:36 | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to
Insulator disc replacement at T#23 R Phase and from Meghnaghat 400/230kV end Due to
Maintenance Work
| 09:38 | 11:24 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Forced S/D Due to 33 KV Incomer CT -B
phase Red hot
| 09:39 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- GT-synchronized at
09:39 hrs.
| 09:39 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 11:59 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- ST synchronized at
11:59 hrs.
| 11:59 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 12:00 |  | Day Peak Gen. 11432 MW
| 13:56 | 16:46 | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to | [7 empty] | 230.0MW load
|  |  | Request by NLDC and from Shyampur 230/132kV end Due to Disc insulator cleaning work. | [7 empty] | interrup.
Meghnaghat
400/230kV end
| 06:58 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing Distance
Protection relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-03-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 140 | 3001031 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 81 | 1817000.01 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 409 | 9374400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9879000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 258 | 6945164 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 40 | 1955000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7523303 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 119520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 11295 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 221400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 211680 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 15 | 394560 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 8 | 363900 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 35040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 181872 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 10 | 102720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 310080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 14400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208869 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 125 | 1635909.09 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 520 | 13466818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1519200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2470 | 59292161.1
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 144846 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104085 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1085460 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 151 | 3345185 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 35127 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 273648 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 233333 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 1010880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 929760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 15360 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 28400 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 162240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 22319998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 80640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12465454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1937 | 42260256.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4660000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8753900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 235 | 5346000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 811368 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1119360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 162 | 3194909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1081608 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 37 | 506816 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1190650 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3797760 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 34 | 906240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 409510 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2238960 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 151200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 986880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 451636 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1589 | 35606797
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 195 | 4458240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 2059200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 1188000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 327280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 139200 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 128520 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 432 | 8314490
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 40 | 932000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 908640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 139 | 3351518 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 107760 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718944 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2005440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 118 | 3561350 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 488688 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7358000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8194000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1109 | 28058340
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 859 | 21712000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 417120 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 622080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 472 | 10152730 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1383 | 32903930
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 235789 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2415000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1089 | 22306909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5230550 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 5890000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3934.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1705 | 36082182.59
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 60 | 1390000 | machine running
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 138 | 3366364 | GT air intake filter DP high.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 209 | 4688945 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 211 | 4664573 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 376 | 8499127 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 126108 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 5664 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1018.07 | 22992662 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 411752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 715140 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2017.57 | 46894775
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 61 | 1364945 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3907000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1066924 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48441.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 74 | 490085 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 257649 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 146880 | -
Rangpur Area Total |  |  |  |  | 950 | 399 | 7281924.72
Eastern Grid Total |  |  |  |  | 16921.242 | 7537 | 173532044.65
Western Grid Total |  |  |  |  | 11614.5 | 5504.57 | 123162812.31
National Grid Total |  |  |  |  | 28535.742 | 13041.57 | 296694856.96
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-03-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8078.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4506.7 | MW
i) Dhaka area |  |  | 3592.7 |  | MW | i) Khulna area |  |  |  | 1723 | MW
ii) Chattogram area |  |  | 1211 |  | MW | ii) Barishal area |  |  |  | 476.5 | MW
iii) Cumilla area |  |  | 1420 |  | MW | iii) Rajshahi area |  |  |  | 1401.2 | MW
iv) Mymensingh area |  |  | 1258 |  | MW | iv) Rangpur area |  |  |  | 906 | MW
v) Sylhet area |  |  | 597 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12585.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 16:00 | 67 | Jaldhaka | 84 | 18:00 | 133 | Payra | 32 | 00:00
2 | AKSML | 96 | 06:00 | 68 | Jamalpur | 144 | 18:00 | 134 | Postogola | 46 | 00:00
3 | Aftabnagar | 32 | 00:00 | 69 | Jashore | 148 | 00:00 | 135 | Purbachal | 17 | 00:00
4 | Agargaon | 96 | 19:00 | 70 | Jhenaidah | 137 | 23:00 | 136 | Purbasadipur | 113 | 14:00
5 | Agrabad | 78 | 00:00 | 71 | Joydebpur | 119 | 00:00 | 137 | Rahanpur | 28 | 00:00
6 | Amnura | 52 | 13:00 | 72 | Joypurhat | 69 | 00:00 | 138 | Rahim | 1 | 01:00
7 | Ashuganj | 87 | 02:00 | 73 | Juldah | 15 | 00:00 | 139 | Rajbari | 76 | 19:00
8 | BSRM | 202 | 02:00 | 74 | KSRM | 11 | 00:00 | 140 | Rajendrapur | 109 | 00:00
9 | Bagerhat | 79 | 00:00 | 75 | Kabirpur | 136 | 00:00 | 141 | Rajshahi | 92 | 00:00
10 | Bajitpur | 59 | 18:30 | 76 | Kachua | 95 | 23:00 | 142 | Rajshahi-230 | 81 | 00:00
11 | Bakulia | 85 | 00:00 | 77 | Kallyanpur | 99 | 00:00 | 143 | Ramganj | 122 | 00:00
12 | Banani | 28 | 19:00 | 78 | Kalurghat | 22 | 00:00 | 144 | Rampur | 37 | 00:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kamrangirchar | 39.9 | 05:00 | 145 | Rangamati | 17 | 19:00
14 | Barapukuria | 63 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 135 | 18:00
15 | Barguna | 24 | 00:00 | 81 | Kasba | 41 | 21:00 | 147 | Ruppur | 6.2 | 11:00
16 | Barishal | 110 | 00:00 | 82 | Kazla | 85 | 00:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 106 | 00:00 | 83 | Keranigonj | 62 | 00:00 | 149 | Saidpur | 96 | 14:00
18 | Baroaulia | 45 | 00:00 | 84 | Khagrachori | 32 | 19:00 | 150 | Satkhira | 144 | 19:00
19 | Baroirhat | 63 | 14:00 | 85 | Khulna | 86 | 00:00 | 151 | Satmasjid | 89 | 00:00
20 | Bashundhara | 150 | 00:00 | 86 | Khulshi | 163 | 00:00 | 152 | Savar | 124 | 00:00
21 | BashundharaCement | 0 | 00:00 | 87 | Kishoreganj | 158 | 02:00 | 153 | SevenRings | 1.82 | 00:00
22 | Beanibazar | 74 | 18:30 | 88 | Kodda | 168 | 00:00 | 154 | ShahCement | 10 | 16:00
23 | Benapole | 74 | 22:00 | 89 | Kulaura | 50 | 18:30 | 155 | Shahjadpur | 75 | 03:00
24 | Bhaluka | 127 | 00:00 | 90 | Kurigram | 66 | 03:00 | 156 | Shahjibazar | 133 | 00:00
25 | Bhandaria | 59 | 23:00 | 91 | Kushtia | 116 | 00:00 | 157 | Shahmirpur | 46 | 04:00
26 | Bhangura | 42 | 03:00 | 92 | Lalbag | 32 | 00:00 | 158 | Shariatpur | 96 | 23:00
27 | Bheramara(GK) | 52 | 19:00 | 93 | Lalmonirhat | 64 | 16:00 | 159 | Sherpur | 178 | 18:00
28 | Bhulta | 174 | 00:00 | 94 | MI_Cement | 15 | 08:00 | 160 | Shikalbaha | 22 | 23:00
29 | Bog-Sherpur | 68 | 03:00 | 95 | Madanganj | 38 | 00:00 | 161 | Shitalakhya | 61.2 | 00:00
30 | Bogura | 160 | 00:00 | 96 | Madaripur | 122 | 00:00 | 162 | Sholosohor | 33 | 19:00
31 | Borhanuddin | 90 | 19:00 | 97 | Madartek | 81.79 | 00:00 | 163 | Shyampur | 124 | 04:00
32 | Brahmanbaria | 153 | 18:30 | 98 | Madunaghat | 49 | 00:00 | 164 | Siddhirganj | 80 | 01:00
33 | Cantonment | 100 | 00:00 | 99 | Magura | 70 | 19:00 | 165 | Sirajganj | 112 | 03:00
34 | Chandpur | 76 | 18:30 | 100 | Mahasthangarh | 76 | 00:00 | 166 | Sonargaon | 63 | 00:00
35 | Chandraghona | 37 | 18:30 | 101 | Manikganj | 115 | 21:00 | 167 | Sreemongol | 78 | 18:30
36 | Chapai | 68 | 01:00 | 102 | Maniknagar | 52 | 00:00 | 168 | Sreepur | 46 | 00:00
37 | Charsaidpur | 9 | 00:00 | 103 | Matarbari | 50 | 02:00 | 169 | Srinagar | 51.6 | 23:00
38 | Chauddagram | 83 | 22:00 | 104 | Matuail | 40 | 02:00 | 170 | Sunamganj | 58 | 22:00
39 | Chhatak | 34 | 18:30 | 105 | Millgate | 48 | 00:00 | 171 | Sylhet | 41 | 19:00
40 | Chowmuhani | 232 | 21:00 | 106 | Mirpur | 115 | 00:00 | 172 | Sylhet-132 | 113 | 17:00
41 | Chuadanga | 110 | 03:00 | 107 | Mirsorai | 7 | 00:00 | 173 | TK | 24 | 22:00
42 | Coxsbazar | 132 | 13:00 | 108 | Mirzapur | 45 | 19:00 | 174 | Tangail | 192 | 19:00
43 | Cumilla(N) | 187 | 21:00 | 109 | Mithapukur | 66 | 03:00 | 175 | Thakurgaon | 96 | 14:00
44 | Cumilla(S) | 150 | 02:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 89 | 00:00
45 | Daudkandi | 138 | 22:00 | 111 | Mogbazar | 104.9 | 00:00 | 177 | Ullahpara | 32 | 03:00
46 | Dhaka | 22 | 11:00 | 112 | Mongla | 42 | 00:00 | 178 | Ullon | 46 | 00:00
47 | Dhamrai | 94 | 00:00 | 113 | Motijheel | 30 | 00:00 | 179 | Uttara | 74 | 00:00
48 | Dhanmondi | 98 | 00:00 | 114 | Muktagacha | 43 | 18:00 | 180 | UttaraNew | 42 | 00:00
49 | Dohazari | 123 | 19:30 | 115 | Munshiganj | 110 | 00:00 | 181 | Zigatola | 60 | 00:00
50 | Faridpur | 159 | 23:00 | 116 | Muradnagar | 32 | 23:00
51 | Fatullah | 52 | 01:00 | 117 | Mymensingh | 210 | 18:00
52 | Fenchuganj | 41 | 19:00 | 118 | Naogaon | 137 | 03:00
53 | Feni | 124 | 18:30 | 119 | Narail | 65 | 02:00
54 | GPH | 57 | 00:00 | 120 | Narinda | 48 | 00:00
55 | Ghatail | 94 | 18:00 | 121 | Narshingdi | 174 | 00:00
56 | Ghorashal | 14 | 00:00 | 122 | Natore | 166 | 03:00
57 | Ghorashal-230 | 80 | 01:00 | 123 | Nawabganj | 64.2 | 23:00
58 | Goalpara | 32 | 00:00 | 124 | Netrakona | 144 | 11:00
59 | Gollamari | 72 | 00:00 | 125 | New | 43 | 00:00
60 | Gopalganj | 115.2 | 23:00 | 126 | Niamatpur | 113 | 14:00
61 | Gulshan | 78 | 19:00 | 127 | Noapara | 44 | 00:00
62 | Halishahar | 36 | 01:00 | 128 | PHP | 2 | 06:00
63 | HaripurSBU | 96 | 01:00 | 129 | Pabna | 109 | 03:00
64 | Hasnabad | 72 | 00:00 | 130 | Palashbari | 128 | 20:00
65 | Hathazari | 86 | 09:00 | 131 | Panchagarh | 51 | 18:00
66 | Ishurdi | 58 | 03:00 | 132 | Patuakhali | 83 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-03-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13969.18 | 0 |  | 13969.18
1:00 | 13501.17 | 0 |  | 13501.17
2:00 | 13083.16 | 0 |  | 13083.16
3:00 | 13366.5 | 0 |  | 13366.5
4:00 | 12993.95 | 0 |  | 12993.95
5:00 | 12187.18 | 0 |  | 12187.18
6:00 | 11162.5 | 0 |  | 11162.5
7:00 | 10801.83 | 40 |  | 10843.63
8:00 | 10737.75 | 0 |  | 10737.75
9:00 | 10932.43 | 0 |  | 10932.43
10:00 | 10856.64 | 0 |  | 10856.64
11:00 | 11113.11 | 0 |  | 11113.11
12:00 | 11432.59 | 0 |  | 11432.59
13:00 | 11978.3 | 0 |  | 11978.3
14:00 | 12405.57 | 0 |  | 12405.57
15:00 | 12401.06 | 0 |  | 12401.06
16:00 | 12276.94 | 0 |  | 12276.94
17:00 | 12305.57 | 0 |  | 12305.57
18:00 | 12685 | 0 |  | 12685
19:00 | 13041.57 | 0 |  | 13041.57
19:30 | 12838.72 | 0 |  | 12838.72
20:00 | 12670.54 | 0 |  | 12670.54
21:00 | 12628.5 | 0 |  | 12628.5
22:00 | 12710.5 | 0 |  | 12710.5
23:00 | 12702.5 | 0 |  | 12702.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-03-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7916.3 | 6052.88 | 13969.18 | DAILY GENERATION CURVE
00:30 | 7834.9 | 5900.275 | 13735.175
01:00 | 7753.5 | 5747.67 | 13501.17 | 30-03-2025
01:30 | 7680.5 | 5611.665 | 13292.165
02:00 | 7607.5 | 5475.66 | 13083.16
02:30 | 7714.5 | 5510.33 | 13224.83
03:00 | 7821.5 | 5545 | 13366.5
03:30 | 7748 | 5432.225 | 13180.225
04:00 | 7674.5 | 5319.45 | 12993.95
04:30 | 7435.5 | 5155.065 | 12590.565
05:00 | 7196.5 | 4990.68 | 12187.18
05:30 | 6856.505 | 4818.335 | 11674.84
06:00 | 6516.51 | 4645.99 | 11162.5
06:30 | 6400.22 | 4581.945 | 10982.165
07:00 | 6283.93 | 4517.9 | 10801.83
07:30 | 6288.9 | 4480.89 | 10769.79
08:00 | 6293.87 | 4443.88 | 10737.75
08:30 | 6352.72 | 4482.37 | 10835.09
09:00 | 6411.57 | 4520.86 | 10932.43
09:30 | 6365.455 | 4529.08 | 10894.535
10:00 | 6319.34 | 4537.3 | 10856.64
10:30 | 6355.985 | 4628.89 | 10984.875
11:00 | 6392.63 | 4720.48 | 11113.11
11:30 | 6515.435 | 4757.415 | 11272.85
12:00 | 6638.24 | 4794.35 | 11432.59
12:30 | 6843.5 | 4861.945 | 11705.445
13:00 | 7048.76 | 4929.54 | 11978.3
13:30 | 7150.935 | 5041 | 12191.935
14:00 | 7253.11 | 5152.46 | 12405.57
14:30 | 7263.34 | 5139.975 | 12403.315
15:00 | 7273.57 | 5127.49 | 12401.06
15:30 | 7287.09 | 5051.91 | 12339
16:00 | 7300.61 | 4976.33 | 12276.94
16:30 | 7335.725 | 4955.53 | 12291.255
17:00 | 7370.84 | 4934.73 | 12305.57
17:30 | 7458.665 | 5036.62 | 12495.285
18:00 | 7546.49 | 5138.51 | 12685
18:30 | 7541.745 | 5321.54 | 12863.285
19:00 | 7537 | 5504.57 | 13041.57
19:30 | 7505 | 5333.72 | 12838.72
20:00 | 7469 | 5201.54 | 12670.54
20:30 | 7488 | 5161.52 | 12649.52 |  | Executive Engineer
21:00 | 7507 | 5121.5 | 12628.5 |  | Network Operation Division
21:30 | 7546.5 | 5123 | 12669.5
22:00 | 7586 | 5124.5 | 12710.5
22:30 | 7607.5 | 5099 | 12706.5
23:00 | 7629 | 5073.5 | 12702.5

## En-Curve
QF-LDC-12
Date | 30-03-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3517 | 2602.8 | 906 | 0 | 38 | 1367.38 | 46 | 4184 | 0 | 279 | 1021 | 0 | 0 | 8 | 0 | DAILY ENERGY CURVE
00:30 | 3538 | 2593.9 | 906 | 0 | 38 | 1367.775 | 46 | 4024 | 0 | 262 | 952 | 0 | 0 | 7.5 | 0 | 30-03-2025
01:00 | 3559 | 2585 | 906 | 0 | 38 | 1368.17 | 46 | 3864 | 0 | 245 | 883 | 0 | 0 | 7 | 0
01:30 | 3532 | 2569 | 906.5 | 0 | 42 | 1318.165 | 46 | 3788 | 0 | 242 | 843 | 0 | 0 | 5.5 | 0 | Energy Generated | 296.6949 |  | MKWHr
02:00 | 3505 | 2553 | 907 | 0 | 46 | 1268.16 | 46 | 3712 | 0 | 239 | 803 | 0 | 0 | 4 | 0 | Energy not Served | 0.04 |  | MKWHr
02:30 | 3554 | 2583 | 906.5 | 0 | 45 | 1267.83 | 46 | 3709 | 0 | 266 | 843 | 0 | 0 | 4.5 | 0 | Total Energy Requirement | 296.7349 |  | MKWHr
03:00 | 3603 | 2613 | 906 | 0 | 44 | 1267.5 | 46 | 3706 | 0 | 293 | 883 | 0 | 0 | 5 | 0
03:30 | 3643.5 | 2575 | 906 | 0 | 42 | 1191.725 | 46 | 3654 | 0 | 233.5 | 885.5 | 0 | 0 | 3 | 0
04:00 | 3684 | 2537 | 906 | 0 | 40 | 1115.95 | 46 | 3602 | 0 | 174 | 888 | 0 | 0 | 1 | 0
04:30 | 3656 | 2509 | 906 | 0 | 40 | 1067.065 | 46 | 3537 | 0 | 121 | 706.5 | 0 | 0 | 2 | 0
05:00 | 3628 | 2481 | 906 | 0 | 40 | 1018.18 | 46 | 3472 | 0 | 68 | 525 | 0 | 0 | 3 | 0
05:30 | 3555 | 2444 | 906 | 0 | 37 | 969.33 | 46 | 3248 | 0.01 | 51.5 | 415.5 | 0 | 0 | 2.5 | 0
06:00 | 3482 | 2407 | 906 | 0 | 34 | 920.48 | 46 | 3024 | 0.02 | 35 | 306 | 0 | 0 | 2 | 0
06:30 | 3423.5 | 2404.75 | 906 | 0 | 34 | 868.065 | 46 | 2971 | 27.85 | 26 | 272 | 0 | 0 | 3 | 20
07:00 | 3365 | 2402.5 | 906 | 0 | 34 | 815.65 | 46 | 2918 | 55.68 | 17 | 238 | 0 | 0 | 4 | 40
07:30 | 3372.5 | 2401.5 | 883.5 | 0 | 35 | 817.395 | 46 | 2841.5 | 108.895 | 17 | 243.5 | 0 | 0 | 3 | 20
08:00 | 3380 | 2400.5 | 861 | 0 | 36 | 819.14 | 46 | 2765 | 162.11 | 17 | 249 | 0 | 0 | 2 | 0
08:30 | 3390 | 2400.5 | 861 | 0 | 36 | 818.47 | 46 | 2760 | 237.62 | 17 | 267.5 | 0 | 0 | 1 | 0
09:00 | 3400 | 2400.5 | 861 | 0 | 36 | 817.8 | 46 | 2755 | 313.13 | 17 | 286 | 0 | 0 | 0 | 0
09:30 | 3410 | 2366.5 | 883 | 0 | 38 | 816.525 | 46 | 2682.5 | 354.01 | 17 | 281 | 0 | 0 | 0 | 0
10:00 | 3420 | 2332.5 | 905 | 0 | 40 | 815.25 | 46 | 2610 | 394.89 | 17 | 276 | 0 | 0 | 0 | 0
10:30 | 3497.5 | 2347.5 | 905.5 | 0 | 38 | 817.36 | 46 | 2594 | 417.515 | 26 | 293.5 | 0 | 0 | 2 | 0
11:00 | 3575 | 2362.5 | 906 | 0 | 36 | 819.47 | 46 | 2578 | 440.14 | 35 | 311 | 0 | 0 | 4 | 0
11:30 | 3650 | 2407.25 | 906 | 0 | 39 | 819.095 | 46 | 2589.5 | 458.005 | 35 | 318 | 0 | 0 | 5 | 0
12:00 | 3725 | 2452 | 906 | 0 | 42 | 818.72 | 46 | 2601 | 475.87 | 35 | 325 | 0 | 0 | 6 | 0
12:30 | 3784.5 | 2539.25 | 906.5 | 0 | 46 | 817.915 | 46 | 2715 | 471.78 | 43.5 | 327.5 | 0 | 0 | 7.5 | 0
13:00 | 3844 | 2626.5 | 907 | 0 | 50 | 817.11 | 46 | 2829 | 467.69 | 52 | 330 | 0 | 0 | 9 | 0
13:30 | 3799.5 | 2613 | 907 | 0 | 46 | 817.04 | 46 | 3036.5 | 445.895 | 55.5 | 416 | 0 | 0 | 9.5 | 0
14:00 | 3755 | 2599.5 | 907 | 0 | 42 | 816.97 | 46 | 3244 | 424.1 | 59 | 502 | 0 | 0 | 10 | 0
14:30 | 3751 | 2576 | 906.5 | 0 | 39 | 813.75 | 46 | 3267 | 373.565 | 74.5 | 546 | 0 | 0 | 10 | 0
15:00 | 3747 | 2552.5 | 906 | 0 | 36 | 810.53 | 46 | 3290 | 323.03 | 90 | 590 | 0 | 0 | 10 | 0
15:30 | 3731.5 | 2552.5 | 906 | 0 | 35 | 811 | 46 | 3292 | 259 | 81 | 618 | 0 | 0 | 7 | 0
16:00 | 3716 | 2552.5 | 906 | 0 | 34 | 811.47 | 46 | 3294 | 194.97 | 72 | 646 | 0 | 0 | 4 | 0
16:30 | 3706 | 2561 | 906.5 | 0 | 35 | 817.01 | 46 | 3293 | 138.245 | 89 | 694.5 | 0 | 0 | 5 | 0
17:00 | 3696 | 2569.5 | 907 | 0 | 36 | 822.55 | 46 | 3292 | 81.52 | 106 | 743 | 0 | 0 | 6 | 0
17:30 | 3693 | 2596.5 | 906.5 | 0 | 35 | 881.6 | 46 | 3338 | 42.685 | 140.5 | 811.5 | 0 | 0 | 4 | 0
18:00 | 3690 | 2623.5 | 906 | 0 | 34 | 940.65 | 46 | 3384 | 3.85 | 175 | 880 | 0 | 0 | 2 | 0
18:30 | 3752 | 2568.5 | 882.5 | 0 | 34 | 979.36 | 46 | 3507 | 1.925 | 173 | 918 | 0 | 0 | 1 | 0
19:00 | 3814 | 2513.5 | 859 | 0 | 34 | 1018.07 | 46 | 3630 | 0 | 171 | 956 | 0 | 0 | 0 | 0
19:30 | 3814 | 2570.5 | 859 | 0 | 34 | 966.22 | 46 | 3550 | 0 | 161 | 838 | 0 | 0 | 0 | 0
20:00 | 3899 | 2594.5 | 859 | 0 | 34 | 969.04 | 46 | 3365 | 0 | 141 | 763 | 0 | 0 | 0 | 0
20:30 | 3904 | 2639.5 | 882 | 0 | 34 | 967.52 | 46 | 3321 | 0 | 141 | 714.5 | 0 | 0 | 0 | 0
21:00 | 3909 | 2684.5 | 905 | 0 | 34 | 966 | 46 | 3277 | 0 | 141 | 666 | 0 | 0 | 0 | 0
21:30 | 3932 | 2713 | 905.5 | 0 | 35 | 967 | 46 | 3273 | 0 | 141 | 657 | 0 | 0 | 0 | 0
22:00 | 3955 | 2741.5 | 906 | 0 | 36 | 968 | 46 | 3269 | 0 | 141 | 648 | 0 | 0 | 0 | 0
22:30 | 3962.5 | 2761 | 906 | 0 | 36 | 967.5 | 46 | 3264 | 0 | 141 | 622.5 | 0 | 0 | 0 | 0
23:00 | 3970 | 2780.5 | 906 | 0 | 36 | 967 | 46 | 3259 | 0 | 141 | 597 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-03-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 17:00 | 390 | 00:00 | Payra | 420 | 08:00 | 409 | 00:00
Ashuganj | 410 | 6:00 | 390 | 16:00 | Rahanpur | 399 | 06:00 | 386 | 00:00
Bhulta | 411 | 06:00 | 397 | 00:00 | Rampal | 408 | 06:00 | 391 | 00:00
Bibiana | 399 | 10:00 | 390 | 00:00
BIPTC | 398 | 09:00 | 390 | 16:00
Bogura | 391 | 06:00 | 375 | 00:00
Gopalganj | 410 | 10:00 | 392 | 00:00
Kaliakoir | 378 | 08:00 | 369 | 23:00
Madunaghat | 403 | 10:00 | 393 | 00:00
Meghnaghat | 407 | 07:00 | 393 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 06:00 | 227 | 00:00 | Keranigonj | 235 | 07:00 | 226 | 00:00
AKSML | 235 | 09:00 | 228 | 00:00 | Khulna(S) | 233 | 10:00 | 219 | 00:00
Aminbazar | 235 | 17:00 | 229 | 00:00 | Madunaghat | 237 | 09:00 | 232 | 01:00
Ashuganj | 237 | 09:00 | 230 | 00:00 | Madunaghat-400 | 237 | 08:00 | 230 | 00:00
Ashuganj-400 | 236 | 6:00 | 224 | 0:00 | Maniknagar | 234 | 10:00 | 224 | 00:00
Baghabari | 236 | 07:00 | 227 | 00:00 | Meghnaghat | 241 | 10:00 | 231 | 00:00
Barapukuria | 225 | 05:00 | 212 | 13:00 | Meghnaghat-400 | 236 | 08:00 | 228 | 00:00
Barapukuria-230 | 225 | 6:00 | 214 | 14:00 | Mirsorai | 233 | 10:00 | 225 | 00:00
Barishal | 237 | 06:00 | 226 | 00:00 | Rajshahi | 234 | 05:00 | 220 | 23:00
Bheramara | 236 | 05:00 | 223 | 14:00 | Rampal | 232 | 06:00 | 220 | 00:00
Bhulta | 234 | 07:00 | 225 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 08:00 | 223 | 00:00 | Rampura | 232 | 08:00 | 224 | 00:00
BIPTC | 236 | 05:00 | 222 | 23:00 | Shikalbaha | 234 | 08:00 | 227 | 00:00
Bogura | 238 | 06:00 | 228 | 13:00 | Shyampur | 234 | 06:00 | 227 | 00:00
Bogura-400 | 237 | 05:00 | 228 | 13:00 | Siddhirganj | 236 | 06:00 | 231 | 04:00
Borhanuddin | 240 | 10:00 | 233 | 00:00 | Sirajgonj | 242 | 05:00 | 237 | 00:00
BSRM | 233 | 10:00 | 224 | 01:00 | Sreepur | 235 | 07:00 | 229 | 00:00
Cumilla(N) | 229 | 09:00 | 221 | 00:00 | Tongi | 234 | 10:00 | 225 | 00:00
Faridpur | 237 | 10:00 | 224 | 00:00
Fenchuganj | 233 | 07:00 | 227 | 00:00
Ghorashal | 238 | 01:00 | 230 | 00:00
Ghorashal-230 | 233 | 07:00 | 226 | 00:00
Gopalganj | 235 | 07:00 | 225 | 00:00
GPH | 234 | 10:00 | 227 | 00:00
Haripur | 234 | 10:00 | 226 | 00:00
Hasnabad | 235 | 10:00 | 227 | 00:00
Hathazari | 236 | 11:00 | 229 | 00:00
Ishurdi | 236 | 05:00 | 225 | 22:00
Jhenaidah | 229 | 07:00 | 211 | 23:00
Kaliakoir | 236 | 07:00 | 230 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 09:00 | 130 | 11:00 | Madunaghat | 136 | 08:00 | 132 | 01:00
Agargaon | 140 | 06:00 | 134 | 00:00 | Magura | 130 | 06:00 | 118 | 22:00
Agrabad | 134 | 07:00 | 130 | 00:00 | Mahasthangarh | 131 | 05:00 | 122 | 13:00
AKS | 130 | 01:00 | 124 | 18:00 | Manikganj | 130 | 07:00 | 125 | 21:00
Aminbazar | 139 | 21:00 | 132 | 00:00 | Maniknagar | 138 | 06:00 | 132 | 00:00
Amnura | 136 | 05:00 | 125 | 01:00 | Matarbari | 119 | 07:00 | 111 | 00:00
Ashuganj | 137 | 09:00 | 135 | 00:00 | Matuail | 137 | 08:00 | 127 | 10:00
Bagerhat | 132 | 10:00 | 117 | 00:00 | Millgate | 140 | 07:00 | 133 | 15:00
Bajitpur | 139 | 05:00 | 125 | 13:00 | Mirpur | 137 | 07:00 | 132 | 00:00
Bakulia | 135 | 07:00 | 130 | 00:00 | Mirzapur | 131 | 04:00 | 124 | 14:00
Banani | 138 | 06:00 | 130 | 15:00 | Mithapukur | 131 | 05:00 | 117 | 13:00
Bangabhaban | 138 | 07:00 | 132 | 00:00 | MI_Cement | 137 | 07:00 | 131 | 00:00
Barapukuria | 138 | 05:00 | 126 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 16:00 | 129 | 00:00 | Mogbazar | 140 | 08:00 | 131 | 23:00
Barishal | 132 | 07:00 | 123 | 00:00 | Mongla | 131 | 08:00 | 119 | 00:00
Barishal-230 | 132 | 06:00 | 123 | 00:00 | Motijheel | 138 | 07:00 | 132 | 00:00
Baroaulia | 134 | 09:00 | 132 | 01:00 | Muktagacha | 132 | 03:00 | 121 | 13:00
Baroirhat | 123 | 06:00 | 118 | 14:00 | Munshiganj | 136 | 06:00 | 131 | 00:00
Bashundhara | 148 | 08:00 | 129 | 18:30 | Muradnagar | 128 | 06:00 | 122 | 00:00
BashundharaCement | 137 | 10:00 | 131 | 00:00 | Mymensingh | 132 | 00:00 | 111 | 18:00
Beanibazar | 129 | 07:00 | 124 | 18:30 | Naogaon | 128 | 07:00 | 119 | 03:00
Benapole | 128 | 07:00 | 113 | 23:00 | Narail | 129 | 06:00 | 118 | 00:00
Bhaluka | 128 | 07:00 | 120 | 17:00 | Narinda | 138 | 6:00 | 132 | 0:00
Bhandaria | 126 | 09:00 | 113 | 00:00 | Narshingdi | 134 | 08:00 | 124 | 00:00
Bhangura | 133 | 05:00 | 128 | 13:00 | Natore | 133 | 06:00 | 125 | 00:00
Bheramara | 134 | 05:00 | 126 | 23:00 | Nawabganj | 138 | 06:00 | 130 | 23:00
Bheramara(GK) | 134 | 05:00 | 126 | 22:00 | Netrakona | 122 | 07:00 | 110 | 13:00
Bhulta | 132 | 08:00 | 126 | 00:00 | New | 141 | 07:00 | 134 | 15:00
Bog-Sherpur | 132 | 05:00 | 126 | 00:00 | Niamatpur | 136 | 06:00 | 128 | 00:00
Bogura | 134 | 05:00 | 126 | 14:00 | Noapara | 131 | 08:00 | 121 | 00:00
Bogura-230 | 134 | 05:00 | 127 | 13:00 | Pabna | 134 | 05:00 | 127 | 22:00
Brahmanbaria | 133 | 07:00 | 125 | 00:00 | Palashbari | 130 | 06:00 | 118 | 09:00
Cantonment | 140 | 06:00 | 133 | 22:00 | Panchagarh | 135 | 00:00 | 115 | 13:00
Chandpur | 121 | 16:00 | 116 | 13:00 | Patuakhali | 135 | 06:00 | 130 | 00:00
Chandraghona | 136 | 07:00 | 131 | 00:00 | Payra | 138 | 08:00 | 134 | 00:00
Chapai | 135 | 07:00 | 125 | 00:00 | PHP | 122 | 10:00 | 117 | 00:00
Charsaidpur | 137 | 07:00 | 131 | 00:00 | Postogola | 139 | 11:00 | 133 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 122 | 09:00 | 117 | 00:00 | Purbachal | 141 | 07:00 | 130 | 14:00
Chhatak | 128 | 06:00 | 122 | 00:00 | Purbasadipur | 134 | 03:00 | 112 | 13:00
Chowmuhani | 115 | 09:00 | 110 | 01:00 | Rahanpur | 136 | 03:00 | 130 | 00:00
Chuadanga | 128 | 06:00 | 113 | 23:00 | Rahanpur-400 | 136 | 05:00 | 131 | 00:00
Coxsbazar | 121 | 21:00 | 111 | 00:00 | Rahim | 137 | 10:00 | 131 | 00:00
Cumilla(N) | 130 | 09:00 | 124 | 00:00 | Rajbari | 130 | 06:00 | 123 | 00:00
Cumilla(S) | 132 | 03:00 | 121 | 12:00 | Rajendrapur | 131 | 08:00 | 125 | 00:00
Daudkandi | 128 | 09:00 | 122 | 00:00 | Rajshahi | 132 | 04:00 | 127 | 00:00
Dhaka | 138 | 06:00 | 130 | 23:00 | Rajshahi-230 | 135 | 05:00 | 118 | 00:00
Dhamrai | 136 | 07:00 | 131 | 00:00 | Ramganj | 114 | 05:00 | 109 | 13:00
Dhanmondi | 139 | 06:00 | 134 | 00:00 | Rampur | 135 | 08:00 | 130 | 00:00
Dohazari | 130 | 08:00 | 123 | 00:00 | Rampura | 138 | 06:00 | 130 | 18:00
Faridpur | 132 | 06:00 | 126 | 00:00 | Rangamati | 134 | 08:00 | 130 | 00:00
Fatullah | 138 | 06:00 | 133 | 01:00 | Rangpur | 130 | 05:00 | 120 | 07:00
Fenchuganj | 134 | 07:00 | 130 | 00:00 | Ruppur | 136 | 05:00 | 129 | 00:00
Feni | 122 | 19:30 | 114 | 13:00 | Saidpur | 132 | 04:00 | 116 | 13:00
Ghatail | 128 | 00:00 | 118 | 14:00 | Satkhira | 130 | 09:00 | 116 | 00:00
Ghorashal | 139 | 09:00 | 135 | 00:00 | Satmasjid | 140 | 06:00 | 133 | 14:00
Goalpara | 134 | 06:00 | 124 | 23:00 | Savar | 137 | 10:00 | 130 | 00:00
Gollamari | 135 | 06:00 | 125 | 00:00 | SevenRings | 139 | 06:00 | 135 | 00:00
Gopalganj | 135 | 09:00 | 126 | 00:00 | ShahCement | 137 | 07:00 | 131 | 00:00
Gopalganj-400 | 138 | 06:00 | 131 | 00:00 | Shahjadpur | 136 | 08:00 | 132 | 04:00
Gulshan | 138 | 07:00 | 130 | 15:00 | Shahjibazar | 133 | 10:00 | 126 | 00:00
Halishahar | 134 | 04:00 | 130 | 00:00 | Shahmirpur | 135 | 04:00 | 131 | 00:00
Haripur | 137 | 07:00 | 132 | 00:00 | Shariatpur | 136 | 10:00 | 125 | 00:00
HaripurSBU | 137 | 08:00 | 132 | 00:00 | Sherpur | 130 | 00:00 | 110 | 13:00
Hasnabad | 139 | 07:00 | 134 | 00:00 | Shikalbaha | 124 | 04:00 | 119 | 14:00
Hathazari | 137 | 20:00 | 132 | 00:00 | Shikalbaha-230 | 138 | 06:00 | 131 | 14:00
Ishurdi | 136 | 05:00 | 129 | 23:00 | Shitalakhya | 137 | 07:00 | 131 | 00:00
Jaldhaka | 131 | 05:00 | 113 | 13:00 | Sholosohor | 135 | 06:00 | 131 | 14:00
Jamalpur | 133 | 00:00 | 115 | 13:00 | Shyampur | 138 | 09:00 | 135 | 13:00
Jashore | 128 | 06:00 | 116 | 23:00 | Shyampur-230 | 138 | 10:00 | 132 | 00:00
Jhenaidah | 131 | 05:00 | 120 | 23:00 | Siddhirganj | 138 | 10:00 | 132 | 00:00
Jhenaidah-230 | 132 | 06:00 | 120 | 22:00 | Sirajganj | 131 | 07:00 | 125 | 02:00
Joydebpur | 134 | 08:00 | 130 | 22:00 | Sonargaon | 135 | 11:00 | 129 | 00:00
Joypurhat | 125 | 05:00 | 115 | 13:00 | Sreemongol | 132 | 09:00 | 126 | 00:00
Juldah | 134 | 03:00 | 132 | 00:00 | Sreepur | 131 | 07:00 | 126 | 17:00
Kabirpur | 138 | 08:00 | 129 | 14:00 | Srinagar | 139 | 07:00 | 131 | 00:00
Kachua | 123 | 05:00 | 117 | 13:00 | SSM | 139 | 09:00 | 134 | 00:00
Kaliakoir | 137 | 08:00 | 131 | 08:00 | Sunamganj | 127 | 10:00 | 120 | 00:00
Kallyanpur | 138 | 07:00 | 132 | 00:00 | Sylhet | 130 | 07:00 | 126 | 00:00
Kalurghat | 135 | 09:00 | 130 | 00:00 | Sylhet-132 | 131 | 07:00 | 127 | 00:00
Kamrangirchar | 139 | 08:00 | 132 | 00:00 | Tangail | 127 | 00:00 | 119 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 134 | 02:00 | 111 | 13:00
Kasba | 128 | 06:00 | 121 | 00:00 | TK | 136 | 10:00 | 131 | 00:00
Kazla | 138 | 07:00 | 132 | 00:00 | Tongi | 142 | 09:00 | 135 | 12:00
Keranigonj | 139 | 07:00 | 132 | 00:00 | Ullahpara | 133 | 05:00 | 128 | 00:00
Khagrachori | 133 | 06:00 | 129 | 00:00 | Ullon | 139 | 07:00 | 130 | 14:00
Khulna | 133 | 07:00 | 122 | 00:00 | Uttara | 139 | 06:00 | 133 | 13:00
Khulna(S) | 135 | 10:00 | 125 | 00:00 | UttaraNew | 138 | 07:00 | 131 | 00:00
Khulshi | 133 | 09:00 | 128 | 14:00 | Zigatola | 139 | 08:00 | 132 | 22:00
Kishoreganj | 127 | 06:00 | 120 | 18:00
Kodda | 132 | 17:00 | 126 | 14:00
KSRM | 134 | 06:00 | 130 | 11:00
Kulaura | 133 | 07:00 | 129 | 00:00
Kurigram | 130 | 06:00 | 111 | 13:00
Kushtia | 133 | 05:00 | 123 | 23:00
Lalbag | 138 | 06:00 | 132 | 00:00
Lalmonirhat | 129 | 00:00 | 115 | 13:00
Madanganj | 137 | 10:00 | 131 | 00:00
Madaripur | 136 | 08:00 | 128 | 00:00
Madartek | 138 | 06:00 | 130 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division