## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-04-2025 | during | 03-04-2025 | during | 03-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 150 | 150 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 341 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 268 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9.5 | 7 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 25 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 90 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 574 | 400 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 106 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2536.5 | 2803 | 5156.9 | 5218.9 | 4233.32 | 4295.32
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 20 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 151 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 82 | 82 | 82 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 65 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 96 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 42 | 29 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.15 | 0 | 3.15 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 650 | 1150 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 0 | 2 | 6 | 2 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 363 | 222 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1270 | 1827 | 3463.87 | 3445.72 | 3463.87 | 3445.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 210 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 325 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 164 | 165 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 70 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 26 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 170 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 22 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 97 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 38 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 37 | 73 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 41 | 0 | 41 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1135 | 1402 | 2101.99 | 2060.99 | 1962.05 | 1921.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-04-2025 | during | 03-04-2025 | during | 03-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 100 | 64 | 210 | 210 | 145 | 145 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 142 | 171 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 104 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 17.01 | 0 | 34.94 | 0 | 34.94 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 338.01 | 351 | 638.54 | 601.5 | 573.54 | 536.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 36 | 35 | 35 | 39 | 39 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 39 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 135 | 143 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 118 | 117 | 120 | 120 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | shutdown due to maintenance work on gas field
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 474 | 489 | 858 | 858 | 514 | 514
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 852 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 30 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 80 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 410 | 585 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1391 | 1467 | 3607.2 | 3515.2 | 2581 | 2489
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 9 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 126 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 1150 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 163 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1168.47 | 1707 | 2172.12 | 2171.12 | 2160.12 | 2159.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 60 | 0 | 71 | 71 | 60 | 60 | M/C running
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 185 | 214 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 169 | 169 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 167 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 400 | 319 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.94 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 912 | 1348.03 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.54 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2046.48 | 2419.03 | 3180.68 | 3014.53 | 3083.89 | 2917.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 57 | 58 | 58 | 58 | 58 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 158 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 73 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 165 | 0 | 167.35 | 0 | 167.35 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 564.4 | 438 | 691.75 | 490 | 691.75 | 490
System Total |  |  |  |  | 27566.2 | 28535.742 | 10923.86 | 12903.03 | 21871.05 | 21375.96 | 19263.54 | 18768.45
Forecast Scenario (03-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13040 |  | 0 |  | 13040
|  |  |  | 1:00 | 12600 |  | 0 |  | 12600
|  |  |  | 2:00 | 12240 |  | 0 |  | 12240
|  |  |  | 3:00 | 12030 |  | 0 |  | 12030
|  |  |  | 4:00 | 11730 |  | 0 |  | 11730
|  |  |  | 5:00 | 11520 |  | 0 |  | 11520
|  |  |  | 6:00 | 11200 |  | 0 |  | 11200
|  |  |  | 7:00 | 11040 |  | 0 |  | 11040
|  |  |  | 8:00 | 11220 |  | 0 |  | 11220
|  |  |  | 9:00 | 11190 |  | 0 |  | 11190
|  |  |  | 10:00 | 11100 |  | 0 |  | 11100
|  |  |  | 11:00 | 11070 |  | 0 |  | 11070
|  |  |  | 12:00 | 11520 |  | 0 |  | 11520
|  |  |  | 13:00 | 12020 |  | 0 |  | 12020
|  |  |  | 14:00 | 12350 |  | 0 |  | 12350
|  |  |  | 15:00 | 12220 |  | 0 |  | 12220
|  |  |  | 16:00 | 11920 |  | 0 |  | 11920
|  |  |  | 17:00 | 11630 |  | 0 |  | 11630
|  |  |  | 18:00 | 11240 |  | 0 |  | 11240
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13200 |  | 0 |  | 13200
|  |  |  | 19:30 | 13500 |  | 0 |  | 13500
|  |  |  | 20:00 | 13475 |  | 0 |  | 13475
|  |  |  | 21:00 | 13480 |  | 0 |  | 13480
|  |  |  | 22:00 | 13700 |  | 0 |  | 13700
|  |  |  | 23:00 | 13600 |  | 0 |  | 13600
Probable Maximum Temperature: |  |  | 35.80°C
Probable Maximum Demand at Day Peak: |  |  | 11520.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 290.335 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:13 hrs on 03-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-04-2025 | [28 empty] | Date: | 02-04-2025 | [28 empty] | Date: | 02-04-2025 | [28 empty] | Date: | 02-04-2025 | [28 empty] | Date: | 02-04-2025 | [17 empty] | Date: | 02-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 290 | 583 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 70 | 8 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 386 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 8 | 0 | 355 | 235 | 50 | 200 | 34 | 72 | 50 | 136 | 18 | 20 | 80 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 38 | 0 | 139 | 24 | 0 | 85 | 30 | 0 | 17 | 119 | 0 | 75 | 164 | 146 | 0 | 0 | 12 | 6739 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 0 | 1360.36 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 179 | 0 | 402 | 0 | 0 | 0 | 160 | 57 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 10 | 120 | 220 | 0 | 0 | 1230 | 0 | 5902.36 | 12641.36 | 84.36
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 290 | 500 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 52 | 8.5 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 38 | 575 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 8 | 0 | 355 | 240 | 50 | 196 | 34 | 60 | 45 | 146 | 16 | 20 | 70 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 137 | 23 | 0 | 85 | 30 | 0 | 17 | 119 | 0 | 55 | 130 | 146 | 0 | 0 | 12 | 6741.5 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 0 | 1213.62 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 189 | 0 | 160 | 0 | 404 | 0 | 0 | 0 | 160 | 55 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 116 | 220 | 0 | 0 | 1100 | 0 | 5463.62 | 12205.12 | 84.35
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 287 | 500 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 52 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 565 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 8 | 0 | 355 | 240 | 50 | 192 | 34 | 18 | 45 | 200 | 15 | 20 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 132 | 20 | 0 | 85 | 30 | 0 | 17 | 119 | 0 | 55 | 100 | 145 | 0 | 0 | 12 | 6583 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 1217.22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 182 | 0 | 154 | 0 | 395 | 0 | 0 | 0 | 160 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 116 | 220 | 0 | 0 | 1000 | 0 | 5257.22 | 11840.22 | 84.34
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 270 | 500 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 565 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 110 | 0 | 354 | 0 | 51 | 183 | 34 | 16 | 45 | 200 | 0 | 20 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 133 | 20 | 0 | 85 | 30 | 0 | 17 | 119 | 0 | 55 | 100 | 145 | 0 | 0 | 12 | 6401 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 1214.1 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 181 | 0 | 152 | 0 | 384 | 0 | 0 | 0 | 158 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 220 | 0 | 0 | 1000 | 0 | 5229.1 | 11630.1 | 84.33
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 291 | 500 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 35 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 42 | 500 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 157 | 0 | 355 | 0 | 51 | 199 | 34 | 17 | 45 | 180 | 0 | 20 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 147 | 20 | 0 | 85 | 30 | 0 | 17 | 110 | 0 | 55 | 65 | 145 | 0 | 0 | 12 | 6291 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1111.45 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 178 | 0 | 150 | 0 | 410 | 0 | 0 | 0 | 159 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 220 | 0 | 0 | 1000 | 0 | 5045.45 | 11336.45 | 84.32
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 287 | 500 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 42 | 500 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 157 | 0 | 354 | 0 | 51 | 190 | 34 | 17 | 50 | 180 | 0 | 20 | 80 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 151 | 20 | 0 | 85 | 30 | 0 | 17 | 108 | 0 | 55 | 65 | 138 | 0 | 0 | 0 | 6129 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 1013.36 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 186 | 0 | 151 | 0 | 395 | 0 | 0 | 0 | 158 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 116 | 220 | 0 | 0 | 950 | 0 | 4997.36 | 11126.36 | 84.31
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 282 | 500 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 42 | 500 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 725 | 0 | 51 | 0 | 157 | 0 | 355 | 0 | 51 | 186 | 34 | 17 | 50 | 180 | 0 | 20 | 80 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 152 | 0 | 0 | 85 | 30 | 0 | 17 | 115 | 0 | 55 | 65 | 138 | 0 | 0.27 | 0 | 5937.27 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 1015.07 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 179 | 0 | 148 | 0 | 386 | 0 | 0.02 | 0 | 160 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 108 | 220 | 0 | 0 | 800 | 0 | 4866.09 | 10803.36 | 84.3
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 288 | 500 | 0 | 0 | 0 | 333 | 0 | 0 | 2 | 17 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 42 | 500 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 709 | 3 | 51 | 0 | 157 | 0 | 355 | 0 | 51 | 192 | 34 | 17 | 50 | 120 | 1 | 20 | 80 | 22 | 0 | 6 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 154 | 0 | 0 | 85 | 30 | 0 | 17 | 115 | 0 | 75 | 105 | 108 | 0 | 5.38 | 0 | 5906.38 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.33 | 413 | 0 | 915.73 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 4.49 | 214 | 0 | 168 | 0 | 142 | 0 | 404 | 0 | 0.58 | 0 | 159 | 55 | 0 | 1 | 0 | 0 | 0 | 0.8 | 19 | 0.08 | 0 | 200 | 9 | 128 | 200 | 0 | 0 | 720 | 0 | 4733.01 | 10639.39 | 84.29
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 280 | 583 | 0 | 0 | 0 | 280 | 0 | 0 | 10 | 17 | 9 | 7 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 42 | 500 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 705 | 9 | 51 | 0 | 157 | 0 | 355 | 0 | 50 | 185 | 34 | 17 | 50 | 100 | 9 | 20 | 80 | 22 | 0 | 28 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 150 | 16 | 0 | 85 | 30 | 0 | 17 | 115 | 0 | 85 | 142 | 112 | 0 | 8.55 | 1 | 6010.55 | 852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.97 | 415 | 0 | 909 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 9.54 | 214 | 0 | 172 | 0 | 141 | 0 | 320 | 0 | 0.75 | 0 | 156 | 55 | 0 | 5 | 34 | 0 | 0 | 0.8 | 25 | 0.21 | 0 | 200 | 9 | 108 | 180 | 0 | 0 | 700 | 0 | 4617.27 | 10627.82 | 84.28
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 273 | 583 | 0 | 0 | 0 | 280 | 0 | 0 | 18 | 17 | 9 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 42 | 450 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 709 | 14 | 51 | 0 | 164 | 0 | 355 | 0 | 50 | 182 | 34 | 27 | 50 | 85 | 9 | 20 | 34 | 20 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 40 | 0 | 132 | 16 | 0 | 85 | 30 | 0 | 17 | 116 | 0 | 75 | 133 | 113 | 1 | 15.06 | 10 | 5843.06 | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.12 | 414 | 0 | 910 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 15.68 | 202 | 0 | 173 | 0 | 172 | 0 | 321 | 0 | 1.01 | 0 | 157 | 55 | 50 | 18 | 67 | 0 | 0 | 2.6 | 56 | 0.42 | 0 | 200 | 9 | 108 | 180 | 0 | 0 | 675 | 0 | 4752.83 | 10595.89 | 84.27
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 278 | 500 | 0 | 0 | 0 | 280 | 0 | 0 | 25 | 17 | 8 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 655 | 17 | 51 | 0 | 154 | 0 | 300 | 0 | 49 | 182 | 34 | 34 | 50 | 85 | 9 | 20 | 17 | 22 | 0 | 59 | 0 | 0 | 0 | 0 | 35 | 40 | 0 | 132 | 16 | 0 | 85 | 30 | 0 | 17 | 118 | 0 | 65 | 133 | 108 | 1 | 10.76 | 12 | 5607.76 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 408 | 0 | 900 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 32.95 | 173 | 0 | 180 | 0 | 171 | 0 | 319 | 0 | 3.28 | 0 | 158 | 56 | 70 | 26 | 70 | 0 | 0 | 4.8 | 119 | 0.5 | 0 | 150 | 9 | 108 | 180 | 0 | 0 | 650 | 0 | 4898.53 | 10506.29 | 84.27
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 301 | 500 | 0 | 0 | 0 | 280 | 0 | 0 | 29 | 17 | 7 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 42 | 361 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 650 | 19 | 51 | 0 | 162 | 0 | 300 | 0 | 48 | 210 | 34 | 34 | 45 | 85 | 9 | 20 | 17 | 22 | 0 | 63 | 0 | 0 | 0 | 0 | 35 | 40 | 0 | 133 | 16 | 0 | 85 | 30 | 0 | 17 | 118 | 0 | 65 | 124 | 107 | 2 | 12.01 | 12 | 5511.01 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 410 | 0 | 908 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 41.96 | 181 | 0 | 163 | 0 | 166 | 0 | 354 | 0 | 4.12 | 0 | 158 | 56 | 73 | 29 | 70 | 0 | 0 | 4.1 | 131 | 0.33 | 0 | 150 | 9 | 108 | 180 | 0 | 0 | 650 | 0 | 4960.51 | 10471.52 | 84.26
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 294 | 583 | 0 | 0 | 0 | 321 | 0 | 0 | 30 | 17 | 9.5 | 7 | 0 | 574 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 42 | 363 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 650 | 19 | 51 | 0 | 164 | 0 | 325 | 0 | 48 | 210 | 33 | 37 | 45 | 85 | 13 | 20 | 17 | 22 | 0 | 65 | 0 | 0 | 0 | 0 | 35 | 38 | 0 | 135 | 16 | 0 | 85 | 30 | 0 | 17 | 118 | 0 | 65 | 142 | 100 | 2 | 17.01 | 12 | 5753.51 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 410 | 0 | 912 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 51.54 | 185 | 0 | 169 | 0 | 169 | 0 | 400 | 0 | 4.94 | 0 | 160 | 56 | 73 | 34 | 70 | 0 | 0 | 6.4 | 165 | 0.47 | 0 | 163 | 9 | 126 | 220 | 0 | 0 | 650 | 0 | 5170.35 | 10923.86 | 84.26
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 293 | 583 | 0 | 0 | 0 | 322 | 0 | 0 | 29 | 17 | 9.5 | 7 | 0 | 568 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 29 | 363 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 750 | 18 | 51 | 0 | 165 | 0 | 350 | 0 | 41 | 196 | 33 | 41 | 45 | 98 | 13 | 20 | 38 | 24 | 0 | 60 | 0 | 0 | 0 | 0 | 37 | 38 | 0 | 152 | 22 | 0 | 84 | 30 | 0 | 17 | 118 | 0 | 67 | 127 | 68 | 2 | 26.32 | 12 | 5986.82 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 409 | 0 | 915 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 47.55 | 179 | 0 | 194 | 0 | 178 | 0 | 401 | 0 | 2.35 | 0 | 160 | 56 | 73 | 31 | 70 | 0 | 0 | 6.3 | 160 | 0.53 | 0 | 270 | 10 | 126 | 220 | 0 | 0 | 785 | 0 | 5433.73 | 11420.55 | 84.25
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 278 | 583 | 0 | 0 | 0 | 321 | 0 | 0 | 25 | 21 | 9 | 7 | 0 | 563 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 29 | 363 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 800 | 17 | 51 | 0 | 165 | 0 | 355 | 0 | 41 | 181 | 33 | 55 | 50 | 120 | 9 | 20 | 70 | 26 | 0 | 52 | 0 | 0 | 0 | 0 | 32 | 40 | 0 | 153 | 22 | 0 | 84 | 30 | 0 | 17 | 118 | 0 | 67 | 127 | 68 | 2 | 21.94 | 12 | 6094.94 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 459 | 0 | 1010.7 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 48.37 | 198 | 0 | 191 | 0 | 190 | 0 | 374 | 0 | 4.14 | 0 | 160 | 55 | 73 | 29 | 70 | 0 | 0 | 6 | 156 | 0.45 | 0 | 259 | 10 | 110 | 220 | 0 | 0 | 930 | 0 | 5659.66 | 11754.6 | 84.25
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 296 | 583 | 0 | 0 | 0 | 320 | 0 | 0 | 20 | 52 | 11 | 7 | 0 | 566 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 835 | 13 | 51 | 0 | 165 | 0 | 348 | 0 | 43 | 196 | 32 | 55 | 50 | 120 | 13 | 20 | 70 | 24 | 0 | 41 | 0 | 0 | 0 | 0 | 32 | 37 | 0 | 152 | 22 | 0 | 84 | 30 | 0 | 17 | 116 | 0 | 67 | 133 | 71 | 1 | 30.75 | 12 | 6162.75 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 456 | 0 | 1020.02 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 35.33 | 184 | 0 | 178 | 0 | 176 | 0 | 393 | 0 | 3.2 | 0 | 158 | 55 | 35 | 19 | 70 | 0 | 0 | 4.4 | 73 | 0.39 | 0 | 150 | 10 | 126 | 220 | 0 | 0 | 1038 | 0 | 5462.34 | 11625.09 | 84.24
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 287 | 500 | 0 | 0 | 0 | 322 | 0 | 0 | 11 | 52 | 13 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 24 | 0 | 1 | 46 | 0 | 29 | 272 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 900 | 8 | 51 | 0 | 165 | 0 | 349 | 0 | 44 | 182 | 32 | 55 | 50 | 120 | 18 | 20 | 70 | 24 | 0 | 22 | 0 | 0 | 0 | 0 | 32 | 37 | 0 | 152 | 22 | 0 | 84 | 30 | 0 | 17 | 116 | 0 | 76 | 128 | 72 | 1 | 18.2 | 12 | 5880.2 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 456 | 0 | 1113.39 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25.25 | 209 | 0 | 174 | 0 | 169 | 0 | 374 | 0 | 2.01 | 0 | 165 | 55 | 35 | 16 | 49 | 0 | 0 | 3.8 | 60 | 0.23 | 0 | 150 | 10 | 108 | 220 | 0 | 0 | 1036 | 0 | 5444.68 | 11324.88 | 84.24
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 282 | 500 | 0 | 0 | 0 | 324 | 0 | 0 | 4 | 52 | 12 | 7 | 0 | 400 | 0 | 0 | 0 | 30 | 4 | 0 | 0 | 0 | 24 | 0 | 1 | 46 | 0 | 29 | 273 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 900 | 3 | 51 | 0 | 165 | 0 | 354 | 0 | 45 | 183 | 33 | 55 | 50 | 120 | 17 | 20 | 70 | 24 | 0 | 8 | 0 | 0 | 0 | 0 | 37 | 37 | 0 | 138 | 22 | 0 | 84 | 30 | 0 | 17 | 116 | 0 | 77 | 142 | 72 | 0 | 7.46 | 12 | 5827.46 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 402 | 0 | 1110.55 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 8.08 | 209 | 0 | 161 | 0 | 162 | 0 | 375 | 0 | 0.66 | 0 | 159 | 55 | 35 | 2 | 49 | 0 | 0 | 0.7 | 21 | 0.09 | 0 | 150 | 9 | 108 | 220 | 0 | 0 | 1000 | 0 | 5207.08 | 11034.54 | 84.23
18:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 300 | 500 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 55 | 8 | 7 | 0 | 400 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 29 | 222 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 920 | 0 | 51 | 0 | 165 | 0 | 320 | 0 | 45 | 198 | 33 | 58 | 50 | 120 | 21 | 20 | 70 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 37 | 0 | 132 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 85 | 143 | 71 | 0 | 0.49 | 12 | 5669.49 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.54 | 410 | 0 | 1110.91 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.55 | 150 | 0 | 158 | 0 | 161 | 0 | 345 | 0 | 0.05 | 0 | 160 | 55 | 35 | 1 | 56 | 0 | 0 | 0 | 1 | 0.01 | 0 | 150 | 9 | 94 | 180 | 0 | 0 | 950 | 0 | 4973.06 | 10642.55 | 84.23
19:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 24 | 14 | 0 | 12 | 37 | 0 | 0 | 27 | 90 | 0 | 10 | 450 | 255 | 500 | 0 | 17 | 0 | 325 | 0 | 0 | 0 | 80 | 7 | 7 | 0 | 400 | 0 | 0 | 0 | 20 | 0 | 34 | 0 | 0 | 92 | 36 | 0 | 46 | 0 | 29 | 235 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1157 | 0 | 51 | 20 | 165 | 0 | 349 | 0 | 46 | 181 | 33 | 72 | 50 | 138 | 31 | 20 | 97 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 36 | 37 | 0 | 144 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 104 | 171 | 65 | 0 | 0 | 12 | 6643 | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 16 | 1358.83 | 0 | 0 | 0 | 41 | 0 | 82 | 0 | 0 | 0 | 0 | 22 | 0 | 186 | 0 | 177 | 0 | 176 | 0 | 379 | 0 | 0 | 0 | 162 | 57 | 92 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 10 | 108 | 220 | 0 | 0 | 1115 | 26 | 5960.83 | 12603.83 | 84.22
19:30 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 0 | 0 | 48 | 0 | 0 | 35 | 90 | 0 | 25 | 450 | 268 | 500 | 0 | 35 | 0 | 327 | 0 | 0 | 0 | 106 | 7 | 7 | 0 | 400 | 0 | 0 | 0 | 20 | 0 | 65 | 0 | 0 | 96 | 48 | 0 | 46 | 0 | 29 | 222 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1150 | 0 | 51 | 70 | 165 | 0 | 355 | 0 | 47 | 181 | 33 | 73 | 50 | 170 | 38 | 20 | 97 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 36 | 39 | 0 | 143 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 104 | 171 | 64 | 0 | 0 | 12 | 6872 | 852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 30 | 1348.03 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 22 | 0 | 214 | 0 | 169 | 0 | 167 | 0 | 319 | 0 | 0 | 0 | 158 | 57 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 110 | 220 | 0 | 0 | 1150 | 17 | 6031.03 | 12903.03
20:00 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 0 | 48 | 0 | 0 | 17 | 72 | 0 | 0 | 450 | 303 | 500 | 0 | 17 | 0 | 324 | 0 | 0 | 0 | 108 | 7 | 7 | 0 | 400 | 0 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 98 | 12 | 0 | 46 | 0 | 30 | 224 | 0 | 0 | 0 | 3 | 0 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 165 | 0 | 353 | 0 | 47 | 201 | 33 | 72 | 50 | 170 | 37 | 20 | 97 | 26 | 0 | 0 | 21 | 0 | 0 | 0 | 36 | 39 | 0 | 133 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 104 | 171 | 63 | 0 | 0 | 12 | 6842 | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 28 | 1358.77 | 0 | 0 | 0 | 35 | 0 | 87 | 0 | 0 | 0 | 0 | 22 | 0 | 214 | 0 | 175 | 0 | 171 | 0 | 356 | 0 | 0 | 0 | 159 | 57 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 10 | 120 | 220 | 0 | 0 | 1150 | 0 | 6032.77 | 12874.77 | 84.22
21:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 32 | 0 | 0 | 17 | 35 | 0 | 0 | 450 | 283 | 500 | 0 | 17 | 0 | 329 | 0 | 0 | 0 | 90 | 8 | 7 | 0 | 400 | 0 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 70 | 12 | 0 | 46 | 0 | 42 | 227 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 55 | 165 | 0 | 355 | 0 | 47 | 181 | 34 | 73 | 50 | 170 | 31 | 20 | 98 | 26 | 0 | 0 | 21 | 0 | 0 | 0 | 36 | 39 | 0 | 133 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 103 | 173 | 63 | 0 | 0 | 12 | 6713 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 33 | 1360.59 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 214 | 0 | 179 | 0 | 170 | 0 | 319 | 0 | 0 | 0 | 163 | 57 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1210 | 0 | 6173.59 | 12886.59 | 84.21
22:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 32 | 0 | 0 | 17 | 35 | 0 | 0 | 450 | 300 | 500 | 0 | 17 | 0 | 326 | 0 | 0 | 0 | 90 | 8 | 7 | 0 | 400 | 0 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 70 | 12 | 0 | 46 | 0 | 42 | 224 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 40 | 173 | 0 | 355 | 0 | 49 | 195 | 34 | 62 | 50 | 170 | 28 | 20 | 98 | 28 | 0 | 0 | 21 | 0 | 0 | 0 | 36 | 39 | 0 | 132 | 22 | 0 | 85 | 30 | 0 | 17 | 118 | 0 | 104 | 163 | 62 | 0 | 0 | 12 | 6711 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 34 | 1360.39 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 213 | 0 | 181 | 0 | 171 | 0 | 338 | 0 | 0 | 0 | 164 | 58 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 116 | 220 | 0 | 0 | 1244 | 0 | 6238.39 | 12949.39 | 84.21
23:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 32 | 0 | 0 | 17 | 35 | 0 | 0 | 450 | 305 | 500 | 0 | 17 | 0 | 327 | 0 | 0 | 0 | 90 | 8 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 70 | 12 | 0 | 46 | 0 | 42 | 233 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 40 | 175 | 0 | 355 | 0 | 49 | 196 | 34 | 38 | 45 | 178 | 29 | 20 | 98 | 28 | 0 | 0 | 21 | 0 | 0 | 0 | 35 | 39 | 0 | 132 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 103 | 173 | 64 | 0 | 0 | 12 | 6698 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 35 | 1351.32 | 0 | 0 | 0 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 22 | 0 | 213 | 0 | 186 | 0 | 161 | 0 | 345 | 0 | 0 | 0 | 163 | 58 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1240 | 0 | 6233.32 | 12931.32 | 84.2
Total KWH | 0 | 355200 | 7680 | 0 | 0 | 0 | 0 | 0 | 9230400 | 0 | 0 | 136476 | 43200 | 0 | 18720 | 203520 | 0 | 0 | 135819 | 299520 | 0 | 27456 | 10177000 | 6953193 | 12512273 | 0 | 118085 | 0 | 7663394 | 0 | 0 | 202407 | 115200 | 225000 | 178200 | 0 | 12090454 | 0 | 0 | 0 | 100000 | 50880 | 343871 | 0 | 0 | 744960 | 93120 | 27164 | 1087200 | 0 | 916320 | 8814545.45 | 0 | 0 | 0 | 46972.8 | 0 | 3611534 | 0 | 0 | 0 | 22161816 | 140130 | 1104104 | 356290 | 3479273 | 0 | 8684500 | 608000 | 1144320 | 4687000 | 811224 | 978240 | 1170400 | 3431520 | 354480 | 462710 | 1681500 | 591360 | 0 | 438882 | 116752 | 0 | 0 | 0 | 832000 | 901008 | 0 | 3392918 | 426600 | 0 | 2027520 | 713378 | 0 | 417000 | 2540930 | 0 | 1792800 | 3057600 | 2257920 | 12600 | 180840 | 250080 | 147735459.25 | 21562909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570960 | 11694550 | 178080 | 26808364 | 0 | 0 | 1025000 | 271584 | 0 | 372560 | 0 | 0 | 0 | 590190 | 112537 | 320248 | 4133727 | 0 | 4509073 | 0 | 4168045 | 0 | 8835345 | 0 | 27000 | 0 | 3944000 | 1324800 | 1103406 | 204060 | 1436160 | 0 | 0 | 38523.72 | 1017360 | 3810 | 0 | 5062000 | 233406 | 2684000 | 4954060 | 0 | 0 | 23754181.82 | 51600 | 130991539.54 | 278726998.79

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10923.86 | MW | 12:00 Hr. | Energy Generated |  |  | 278.727 |  | MKWHr.
| Day Peak Demand |  |  | 10923.86 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12903.03 | MW | 19:30 Hr. | Energy Demand |  |  | 278.727 |  | MKWHr.
| Evening Peak Demand |  |  | 12903.03 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 10471.52 | MW | 11:00 Hr. | Total Gas Supplied |  |  | 944.02 |  | MMCFD
| Maximum Generation of the Day |  |  | 12949.39 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 5.8244 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 59.0299 | 0 | 1.4609 | 0 | 0 | 0.20241 | 0 | 0 | 60.6932 | Gas | 129.8612 | Gas | 423708024.14
| Chattogram Zone |  |  | 4.6279 | 30.9764 | 1.2289 | 0 | 1.0872 | 0.16729 | 0 | 0.05088 | 38.1385 | Coal | 76.7559 | Coal | 548803831.5476
| Cumilla Zone |  |  | 22.1515 | 0 | 6.9188 | 0 | 0 | 0.43888 | 0.59136 | 0 | 30.1006 | HFO | 18.235 | HFO | 336052769.536
| Mymensingh Zone |  |  | 2.2579 | 0 | 5.1005 | 0 | 0 | 0.19344 | 0 | 0 | 7.5518 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 11.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2514 | Hydro | 1.0872 | Hydro | 108720
| Khulna Zone |  |  | 0 | 11.6945 | 0.17808 | 0 | 0 | 0.57096 | 21.5629 | 0 | 34.0065 | Solar | 3.7742 | Solar | 60818743.5392
| Barishal Zone |  |  | 7.8715 | 28.8162 | 0.0516 | 0 | 0 | 0.00381 | 0 | 0 | 36.7431 | Import | 48.9626 | Import | 253178839.91
| Rajshahi Zone |  |  | 22.6712 | 0 | 0.75668 | 0 | 0 | 0.93744 | 26.8084 | 0 | 51.1737 | Wind | 0.05088 | Wind | 744883.2
| Rangpur Zone |  |  | 0 | 5.2688 | 2.5396 | 0 | 0 | 1.2599 | 0 | 0 | 9.0683
| Total |  |  | 129.8612 | 76.7559 | 18.235 | 0 | 1.0872 | 3.7742 | 48.9626 | 0.05088 | 278.727
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 423708024.14 |  | Hydro | 108720
|  |  |  | Coal | 548803831.5476 |  | Solar | 60818743.5392
|  |  |  | HFO | 336052769.536 |  | Import | 253178839.91
|  |  |  | HSD | 0 |  | Wind | 744883.2
[5 empty] | Total: | 162,34,15,811 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5629 | Peak Hr Flow | 852.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 19908727.31 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.8084 | Peak Hr Flow | 1348.03 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 508 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.59136 | Peak Hr Flow | 26.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 674 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.9626 | Peak Hr Flow | 2226.03 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3165
|  |  |  | Chattogram |  | 0 |  | 1286
|  |  |  | Cumilla |  | 0 |  | 1404
|  |  |  | Mymensingh |  | 0 |  | 1272
|  |  |  | Sylhet |  | 0 |  | 567
|  |  |  | Khulna |  | 0 |  | 1722
|  |  |  | Barishal |  | 0 |  | 438
|  |  |  | Rajshahi |  | 0 |  | 1578
|  |  |  | Rangpur |  | 0 |  | 967
|  |  |  | Total |  | 0 |  | 12399
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Jangalia 52 MW PP (Lakdanavi) |  |  | 52.2
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 990 |  |  |  | Total | 487.29
|  |  |  | Total Unavailable Capacity |  |  |  | 1477.29
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:13 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 09:14 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
| 09:15 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 09:16 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:- Now the issue is solved
| 09:33 | 11:45 | Bogura 230/132kV S/S T-04 LT Scheduled S/D Due to Bogura132 kv ckt-02, Q2 DS Finger
Change,
| 09:34 | 11:44 | Bogura 230/132kV S/S T-04 HT Scheduled S/D Due to Bogura132 kv ckt-02, Q2 DS Finger
Change,
| 09:37 | 11:19 | Bogura 230/132kV S/S 132KV Main 2 Scheduled S/D Due to Bogura132 kv ckt-02, Q2 DS Finger
Change,
| 09:45 | 11:30 | Bogura-Bogura (New)) 132 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to
Bogura132 kv ckt-02, Q2 DS Finger Change,
| 09:52 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 09:57 | 11:40 | Bogura-Bogura (New)) 132 kV Ckt-2 Forced S/D from Bogura 132/33kV end Due to Red Hot
maintenance work.
| 16:08 |  | Raozan Unit-2 was sync.
| 17:28 | 17:49 | Kishoreganj-Mymensingh 132kV Ckt-2 Forced S/D from Kishoreganj 132/33kV end Due to due
to dry tree branches falling on the structure above the line
| 19:30 |  | Evening peak Generation is 12903 MW
| 22:35 |  | Raozan Unit-2 was shutdown.
| 00:07 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 00:51 |  | Unique Meghnaghat Power Limited (UMPL) Tripped with remarks:- ST
| 02:58 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 06:11 |  | Unique Meghnaghat Power 584 MW CCPP ST was sync.
| 06:43 | 06:58 | Dhamrai 132/33kV S/S Transformer-2 LT Tripped showing Over current and earth fault. 86 | [7 empty] | 30.0MW load
|  |  | relay Operate. relays. | [7 empty] | interrup.
| 06:43 | 06:58 | Dhamrai 132/33kV S/S Transformer-1 LT Tripped showing Over current and earth fault. 86 | [7 empty] | 30.0MW load
|  |  | relay operate. relays. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 10696 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9230400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10177000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 268 | 6953193 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7663394 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 136476 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 203520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 135819 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 118085 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 7 | 225000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 178200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 7680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 18720 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 355200 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 25 | 27456 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 299520 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 202407 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 43200 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 12090454 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 500 | 12512273 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 106 | 115200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2803 | 60693197
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 20 | 100000 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 46972.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 140130 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1087200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 151 | 3611534 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 65 | 343871 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 96 | 744960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 916320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 27164 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 93120 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 22161816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 50880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 222 | 8814545.45 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1827 | 38138513.25
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4687000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8684500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 608000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 811224 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1144320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 3479273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1104104 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 356290 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 26 | 116752 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1170400 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3431520 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 26 | 591360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 462710 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1681500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 354480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 978240 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 438882 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1402 | 30100555
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 64 | 2257920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 171 | 3057600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1792800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 180840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 250080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 351 | 7551840
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 832000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 901008 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3392918 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 713378 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2027520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 117 | 2540930 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 417000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 426600 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to maintenance work on gas field
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2368.568 | 489 | 11251354
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 852 | 21562909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 30 | 178080 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 570960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 585 | 11694550 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1467 | 34006499
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 233406 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2684000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1150 | 23754181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4954060 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 51600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 5062000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3810 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1707 | 36743057.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 1025000 | M/C running
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 214 | 4133727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 169 | 4509073 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 167 | 4168045 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 319 | 8835345 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 112537 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 372560 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 271584 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1348.03 | 26808364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 320248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 590190 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2419.03 | 51173673
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1324800 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3944000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 1436160 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38523.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1103406 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 204060 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1017360 | -
Rangpur Area Total |  |  |  |  | 950 | 438 | 9068309.72
Eastern Grid Total |  |  |  |  | 16921.242 | 6872 | 147735459.25
Western Grid Total |  |  |  |  | 11614.5 | 6031.03 | 130991539.54
National Grid Total |  |  |  |  | 28535.742 | 12903.03 | 278726998.79
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7693.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4705.2 | MW
i) Dhaka area |  |  | 3164.53 |  | MW | i) Khulna area |  |  |  | 1721.9 | MW
ii) Chattogram area |  |  | 1286 |  | MW | ii) Barishal area |  |  |  | 438.5 | MW
iii) Cumilla area |  |  | 1404 |  | MW | iii) Rajshahi area |  |  |  | 1577.8 | MW
iv) Mymensingh area |  |  | 1272 |  | MW | iv) Rangpur area |  |  |  | 967 | MW
v) Sylhet area |  |  | 567 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12398.73 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 22:00 | 67 | Jaldhaka | 84 | 19:00 | 133 | Payra | 32 | 00:00
2 | AKSML | 123 | 09:00 | 68 | Jamalpur | 146 | 19:00 | 134 | Postogola | 36 | 00:00
3 | Aftabnagar | 26 | 00:00 | 69 | Jashore | 143 | 19:30 | 135 | Purbachal | 14 | 00:00
4 | Agargaon | 83 | 18:30 | 70 | Jhenaidah | 142 | 19:00 | 136 | Purbasadipur | 116 | 13:00
5 | Agrabad | 64 | 19:30 | 71 | Joydebpur | 71 | 23:00 | 137 | Rahanpur | 30 | 00:00
6 | Amnura | 56 | 00:00 | 72 | Joypurhat | 74 | 19:00 | 138 | Rahim | 1 | 01:00
7 | Ashuganj | 79 | 00:00 | 73 | Juldah | 13 | 00:00 | 139 | Rajbari | 82 | 23:00
8 | BSRM | 178 | 20:00 | 74 | KSRM | 11 | 17:00 | 140 | Rajendrapur | 95 | 19:30
9 | Bagerhat | 77 | 19:30 | 75 | Kabirpur | 120 | 18:30 | 141 | Rajshahi | 108 | 23:00
10 | Bajitpur | 55 | 19:00 | 76 | Kachua | 90 | 18:30 | 142 | Rajshahi-230 | 86 | 23:00
11 | Bakulia | 69 | 23:00 | 77 | Kallyanpur | 84 | 23:00 | 143 | Ramganj | 120 | 18:30
12 | Banani | 24 | 17:00 | 78 | Kalurghat | 20 | 00:00 | 144 | Rampur | 34 | 00:00
13 | Bangabhaban | 4 | 18:00 | 79 | Kamrangirchar | 29.82 | 00:00 | 145 | Rangamati | 18 | 19:00
14 | Barapukuria | 69 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 136 | 19:00
15 | Barguna | 22 | 23:00 | 81 | Kasba | 40 | 21:00 | 147 | Ruppur | 5.4 | 16:00
16 | Barishal | 99 | 21:00 | 82 | Kazla | 57 | 22:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 94 | 22:00 | 83 | Keranigonj | 52 | 23:00 | 149 | Saidpur | 99 | 13:00
18 | Baroaulia | 47 | 20:00 | 84 | Khagrachori | 34 | 19:00 | 150 | Satkhira | 142 | 19:30
19 | Baroirhat | 63 | 20:00 | 85 | Khulna | 73 | 20:00 | 151 | Satmasjid | 69 | 19:30
20 | Bashundhara | 121 | 19:30 | 86 | Khulshi | 140 | 01:00 | 152 | Savar | 113 | 19:00
21 | BashundharaCement | 0 | 00:00 | 87 | Kishoreganj | 149 | 20:00 | 153 | SevenRings | 0.71 | 20:00
22 | Beanibazar | 68 | 18:30 | 88 | Kodda | 139 | 22:00 | 154 | ShahCement | 8 | 09:00
23 | Benapole | 76 | 00:00 | 89 | Kulaura | 46 | 18:30 | 155 | Shahjadpur | 87 | 23:00
24 | Bhaluka | 116 | 19:00 | 90 | Kurigram | 72 | 19:00 | 156 | Shahjibazar | 128 | 23:00
25 | Bhandaria | 56 | 23:00 | 91 | Kushtia | 120 | 19:00 | 157 | Shahmirpur | 42 | 21:00
26 | Bhangura | 45 | 19:00 | 92 | Lalbag | 15 | 13:00 | 158 | Shariatpur | 90 | 22:00
27 | Bheramara(GK) | 61 | 21:00 | 93 | Lalmonirhat | 70 | 19:00 | 159 | Sherpur | 174 | 19:00
28 | Bhulta | 99 | 21:00 | 94 | MI_Cement | 1.3 | 18:30 | 160 | Shikalbaha | 21 | 23:00
29 | Bog-Sherpur | 64 | 19:00 | 95 | Madanganj | 29 | 00:00 | 161 | Shitalakhya | 46.6 | 23:00
30 | Bogura | 161 | 20:00 | 96 | Madaripur | 113 | 00:00 | 162 | Sholosohor | 28 | 00:00
31 | Borhanuddin | 90 | 23:00 | 97 | Madartek | 65.77 | 23:00 | 163 | Shyampur | 42 | 00:00
32 | Brahmanbaria | 137 | 00:00 | 98 | Madunaghat | 45 | 21:00 | 164 | Siddhirganj | 66 | 18:30
33 | Cantonment | 80 | 18:30 | 99 | Magura | 70 | 19:00 | 165 | Sirajganj | 110 | 19:00
34 | Chandpur | 74 | 21:00 | 100 | Mahasthangarh | 86 | 00:00 | 166 | Sonargaon | 54 | 21:00
35 | Chandraghona | 37 | 19:00 | 101 | Manikganj | 116 | 19:30 | 167 | Sreemongol | 73 | 19:00
36 | Chapai | 66 | 21:00 | 102 | Maniknagar | 43 | 23:00 | 168 | Sreepur | 63 | 19:30
37 | Charsaidpur | 8 | 23:00 | 103 | Matarbari | 50 | 18:30 | 169 | Srinagar | 48.68 | 22:00
38 | Chauddagram | 80 | 00:00 | 104 | Matuail | 35 | 23:00 | 170 | Sunamganj | 56 | 19:30
39 | Chhatak | 34 | 21:00 | 105 | Millgate | 38 | 22:00 | 171 | Sylhet | 39 | 19:00
40 | Chowmuhani | 231 | 19:00 | 106 | Mirpur | 85 | 22:00 | 172 | Sylhet-132 | 94 | 19:30
41 | Chuadanga | 115 | 19:30 | 107 | Mirsorai | 6 | 10:00 | 173 | TK | 26 | 20:00
42 | Coxsbazar | 132 | 20:00 | 108 | Mirzapur | 44 | 19:00 | 174 | Tangail | 202 | 19:00
43 | Cumilla(N) | 185 | 20:00 | 109 | Mithapukur | 70 | 19:00 | 175 | Thakurgaon | 97 | 19:00
44 | Cumilla(S) | 131 | 22:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 74 | 23:00
45 | Daudkandi | 132 | 19:00 | 111 | Mogbazar | 81.5 | 18:30 | 177 | Ullahpara | 43 | 21:00
46 | Dhaka | 16 | 00:00 | 112 | Mongla | 27 | 00:00 | 178 | Ullon | 36 | 22:00
47 | Dhamrai | 68 | 22:00 | 113 | Motijheel | 22 | 00:00 | 179 | Uttara | 59 | 19:00
48 | Dhanmondi | 69 | 19:00 | 114 | Muktagacha | 41 | 21:00 | 180 | UttaraNew | 34 | 00:00
49 | Dohazari | 120 | 20:00 | 115 | Munshiganj | 101 | 23:00 | 181 | Zigatola | 50 | 00:00
50 | Faridpur | 153 | 22:00 | 116 | Muradnagar | 31 | 22:00
51 | Fatullah | 44 | 00:00 | 117 | Mymensingh | 195 | 20:00
52 | Fenchuganj | 39 | 19:00 | 118 | Naogaon | 141 | 23:00
53 | Feni | 110 | 00:00 | 119 | Narail | 62.5 | 19:30
54 | GPH | 10 | 23:00 | 120 | Narinda | 35 | 00:00
55 | Ghatail | 90 | 18:30 | 121 | Narshingdi | 139 | 23:00
56 | Ghorashal | 12 | 00:00 | 122 | Natore | 173 | 19:30
57 | Ghorashal-230 | 68 | 20:00 | 123 | Nawabganj | 60.2 | 22:00
58 | Goalpara | 28 | 00:00 | 124 | Netrakona | 142 | 18:30
59 | Gollamari | 66 | 00:00 | 125 | New | 33.2 | 00:00
60 | Gopalganj | 109.4 | 19:30 | 126 | Niamatpur | 123 | 19:00
61 | Gulshan | 64 | 18:00 | 127 | Noapara | 38 | 00:00
62 | Halishahar | 33 | 20:00 | 128 | PHP | 3 | 16:00
63 | HaripurSBU | 62 | 21:00 | 129 | Pabna | 114 | 21:00
64 | Hasnabad | 58 | 23:00 | 130 | Palashbari | 136 | 19:00
65 | Hathazari | 82 | 19:00 | 131 | Panchagarh | 47 | 18:30
66 | Ishurdi | 68 | 21:00 | 132 | Patuakhali | 78 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12641.36 | 0 |  | 12641.36
1:00 | 12205.12 | 0 |  | 12205.12
2:00 | 11840.22 | 0 |  | 11840.22
3:00 | 11630.1 | 0 |  | 11630.1
4:00 | 11336.45 | 0 |  | 11336.45
5:00 | 11126.36 | 0 |  | 11126.36
6:00 | 10803.36 | 0 |  | 10803.36
7:00 | 10639.39 | 0 |  | 10639.39
8:00 | 10627.82 | 0 |  | 10627.82
9:00 | 10595.89 | 0 |  | 10595.89
10:00 | 10506.29 | 0 |  | 10506.29
11:00 | 10471.52 | 0 |  | 10471.52
12:00 | 10923.86 | 0 |  | 10923.86
13:00 | 11420.55 | 0 |  | 11420.55
14:00 | 11754.6 | 0 |  | 11754.6
15:00 | 11625.09 | 0 |  | 11625.09
16:00 | 11324.88 | 0 |  | 11324.88
17:00 | 11034.54 | 0 |  | 11034.54
18:00 | 10642.55 | 0 |  | 10642.55
19:00 | 12603.83 | 0 |  | 12603.83
19:30 | 12903.03 | 0 |  | 12903.03
20:00 | 12874.77 | 0 |  | 12874.77
21:00 | 12886.59 | 0 |  | 12886.59
22:00 | 12949.39 | 0 |  | 12949.39
23:00 | 12931.32 | 0 |  | 12931.32
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6739 | 5902.36 | 12641.36 | DAILY GENERATION CURVE
00:30 | 6740.25 | 5682.99 | 12423.24
01:00 | 6741.5 | 5463.62 | 12205.12 | 02-04-2025
01:30 | 6662.25 | 5360.42 | 12022.67
02:00 | 6583 | 5257.22 | 11840.22
02:30 | 6492 | 5243.16 | 11735.16
03:00 | 6401 | 5229.1 | 11630.1
03:30 | 6346 | 5137.275 | 11483.275
04:00 | 6291 | 5045.45 | 11336.45
04:30 | 6210 | 5021.405 | 11231.405
05:00 | 6129 | 4997.36 | 11126.36
05:30 | 6033.135 | 4931.725 | 10964.86
06:00 | 5937.27 | 4866.09 | 10803.36
06:30 | 5921.825 | 4799.55 | 10721.375
07:00 | 5906.38 | 4733.01 | 10639.39
07:30 | 5958.465 | 4675.14 | 10633.605
08:00 | 6010.55 | 4617.27 | 10627.82
08:30 | 5926.805 | 4685.05 | 10611.855
09:00 | 5843.06 | 4752.83 | 10595.89
09:30 | 5725.41 | 4825.68 | 10551.09
10:00 | 5607.76 | 4898.53 | 10506.29
10:30 | 5559.385 | 4929.52 | 10488.905
11:00 | 5511.01 | 4960.51 | 10471.52
11:30 | 5632.26 | 5065.43 | 10697.69
12:00 | 5753.51 | 5170.35 | 10923.86
12:30 | 5870.165 | 5302.04 | 11172.205
13:00 | 5986.82 | 5433.73 | 11420.55
13:30 | 6040.88 | 5546.695 | 11587.575
14:00 | 6094.94 | 5659.66 | 11754.6
14:30 | 6128.845 | 5561 | 11689.845
15:00 | 6162.75 | 5462.34 | 11625.09
15:30 | 6021.475 | 5453.51 | 11474.985
16:00 | 5880.2 | 5444.68 | 11324.88
16:30 | 5853.83 | 5325.88 | 11179.71
17:00 | 5827.46 | 5207.08 | 11034.54
17:30 | 5748.475 | 5090.07 | 10838.545
18:00 | 5669.49 | 4973.06 | 10642.55
18:30 | 6156.245 | 5466.945 | 11623.19
19:00 | 6643 | 5960.83 | 12603.83
19:30 | 6872 | 6031.03 | 12903.03
20:00 | 6842 | 6032.77 | 12874.77
20:30 | 6777.5 | 6103.18 | 12880.68 |  | Executive Engineer
21:00 | 6713 | 6173.59 | 12886.59 |  | Network Operation Division
21:30 | 6712 | 6205.99 | 12917.99
22:00 | 6711 | 6238.39 | 12949.39
22:30 | 6704.5 | 6235.855 | 12940.355
23:00 | 6698 | 6233.32 | 12931.32

## En-Curve
QF-LDC-12
Date | 02-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3095 | 2571 | 906 | 0 | 28 | 1360.36 | 46 | 3830 | 0 | 87 | 718 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3080.5 | 2526.25 | 903.5 | 0 | 28 | 1286.99 | 46 | 3818 | 0 | 78 | 656 | 0 | 0 | 0 | 0 | 02-04-2025
01:00 | 3066 | 2481.5 | 901 | 0 | 28 | 1213.62 | 46 | 3806 | 0 | 69 | 594 | 0 | 0 | 0 | 0
01:30 | 3052.5 | 2478.25 | 901 | 0 | 27 | 1215.42 | 46 | 3660.5 | 0 | 69 | 573 | 0 | 0 | 0 | 0 | Energy Generated | 278.727 |  | MKWHr
02:00 | 3039 | 2475 | 901 | 0 | 26 | 1217.22 | 46 | 3515 | 0 | 69 | 552 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2915.5 | 2518.5 | 901 | 0 | 26 | 1215.66 | 46 | 3500 | 0 | 69 | 543.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 278.727 |  | MKWHr
03:00 | 2792 | 2562 | 901 | 0 | 26 | 1214.1 | 46 | 3485 | 0 | 69 | 535 | 0 | 0 | 0 | 0
03:30 | 2816 | 2603 | 900 | 0 | 26 | 1162.775 | 46 | 3404.5 | 0 | 52 | 473 | 0 | 0 | 0 | 0
04:00 | 2840 | 2644 | 899 | 0 | 26 | 1111.45 | 46 | 3324 | 0 | 35 | 411 | 0 | 0 | 0 | 0
04:30 | 2869.5 | 2644 | 898.5 | 0 | 26 | 1062.405 | 46 | 3249 | 0 | 26 | 410 | 0 | 0 | 0 | 0
05:00 | 2899 | 2644 | 898 | 0 | 26 | 1013.36 | 46 | 3174 | 0 | 17 | 409 | 0 | 0 | 0 | 0
05:30 | 2909.5 | 2632 | 898.5 | 0 | 25 | 1014.215 | 46 | 3013 | 0.645 | 17 | 409 | 0 | 0 | 0 | 0
06:00 | 2920 | 2620 | 899 | 0 | 24 | 1015.07 | 46 | 2852 | 1.29 | 17 | 409 | 0 | 0 | 0 | 0
06:30 | 2917.5 | 2613.5 | 898.5 | 0 | 23 | 965.4 | 46 | 2804 | 32.975 | 17 | 403.5 | 0 | 0 | 0 | 0
07:00 | 2915 | 2607 | 898 | 0 | 22 | 915.73 | 46 | 2756 | 64.66 | 17 | 398 | 0 | 0 | 0 | 0
07:30 | 2837.5 | 2640 | 875 | 0 | 22 | 912.365 | 46 | 2743.5 | 107.24 | 17 | 433 | 0 | 0 | 0 | 0
08:00 | 2760 | 2673 | 852 | 0 | 22 | 909 | 46 | 2731 | 149.82 | 17 | 468 | 0 | 0 | 0 | 0
08:30 | 2780 | 2622 | 852.5 | 0 | 21 | 909.5 | 46 | 2695.5 | 189.355 | 17 | 479 | 0 | 0 | 0 | 0
09:00 | 2800 | 2571 | 853 | 0 | 20 | 910 | 46 | 2660 | 228.89 | 17 | 490 | 0 | 0 | 0 | 0
09:30 | 2778 | 2526 | 877 | 0 | 21 | 905 | 46 | 2548.5 | 340.09 | 17 | 492.5 | 0 | 0 | 0 | 0
10:00 | 2756 | 2481 | 901 | 0 | 22 | 900 | 46 | 2437 | 451.29 | 17 | 495 | 0 | 0 | 0 | 0
10:30 | 2748 | 2451 | 900.5 | 0 | 22 | 904 | 46 | 2436 | 472.405 | 17 | 492 | 0 | 0 | 0 | 0
11:00 | 2740 | 2421 | 900 | 0 | 22 | 908 | 46 | 2435 | 493.52 | 17 | 489 | 0 | 0 | 0 | 0
11:30 | 2802.5 | 2519.25 | 900.5 | 0 | 22 | 910 | 46 | 2443.5 | 533.94 | 17 | 501.5 | 0 | 0 | 1.5 | 0
12:00 | 2865 | 2617.5 | 901 | 0 | 22 | 912 | 46 | 2452 | 574.36 | 17 | 514 | 0 | 0 | 3 | 0
12:30 | 2898 | 2646 | 901 | 0 | 23 | 913.5 | 46 | 2622.5 | 570.205 | 17 | 526.5 | 0 | 0 | 8.5 | 0
13:00 | 2931 | 2674.5 | 901 | 0 | 24 | 915 | 46 | 2793 | 566.05 | 17 | 539 | 0 | 0 | 14 | 0
13:30 | 2917.5 | 2679.75 | 901 | 0 | 25 | 962.85 | 46 | 2909.5 | 542.975 | 19 | 571 | 0 | 0 | 13 | 0
14:00 | 2904 | 2685 | 901 | 0 | 26 | 1010.7 | 46 | 3026 | 519.9 | 21 | 603 | 0 | 0 | 12 | 0
14:30 | 2903 | 2692.5 | 900.5 | 0 | 25 | 1015.36 | 46 | 3034 | 435.985 | 36.5 | 589 | 0 | 0 | 12 | 0
15:00 | 2902 | 2700 | 900 | 0 | 24 | 1020.02 | 46 | 3042 | 352.07 | 52 | 575 | 0 | 0 | 12 | 0
15:30 | 2888 | 2577 | 900 | 0 | 24 | 1066.705 | 46 | 3038 | 292.28 | 52 | 581 | 0 | 0 | 10 | 0
16:00 | 2874 | 2454 | 900 | 0 | 24 | 1113.39 | 46 | 3034 | 232.49 | 52 | 587 | 0 | 0 | 8 | 0
16:30 | 2881 | 2419 | 899.5 | 0 | 24 | 1111.97 | 46 | 2986.5 | 159.74 | 52 | 594 | 0 | 0 | 6 | 0
17:00 | 2888 | 2384 | 899 | 0 | 24 | 1110.55 | 46 | 2939 | 86.99 | 52 | 601 | 0 | 0 | 4 | 0
17:30 | 2788 | 2343.5 | 899.5 | 0 | 23 | 1110.73 | 46 | 2903 | 45.815 | 64.5 | 612.5 | 0 | 0 | 2 | 0
18:00 | 2688 | 2303 | 900 | 0 | 22 | 1110.91 | 46 | 2867 | 4.64 | 77 | 624 | 0 | 0 | 0 | 0
18:30 | 2763 | 2357 | 876.5 | 0 | 24 | 1234.87 | 46 | 3183 | 2.32 | 200 | 936.5 | 0 | 0 | 0 | 0
19:00 | 2838 | 2411 | 853 | 0 | 26 | 1358.83 | 46 | 3499 | 0 | 323 | 1249 | 0 | 0 | 0 | 0
19:30 | 2800 | 2424 | 852 | 0 | 26 | 1348.03 | 46 | 3522 | 0 | 391 | 1494 | 0 | 0 | 0 | 0
20:00 | 2869 | 2450 | 853 | 0 | 26 | 1358.77 | 46 | 3608 | 0 | 391 | 1273 | 0 | 0 | 0 | 0
20:30 | 2841 | 2446.5 | 873 | 0 | 26 | 1359.68 | 46 | 3708 | 0 | 363 | 1217.5 | 0 | 0 | 0 | 0
21:00 | 2813 | 2443 | 893 | 0 | 26 | 1360.59 | 46 | 3808 | 0 | 335 | 1162 | 0 | 0 | 0 | 0
21:30 | 2833 | 2456 | 893.5 | 0 | 27 | 1360.49 | 46 | 3823.5 | 0 | 335 | 1143.5 | 0 | 0 | 0 | 0
22:00 | 2853 | 2469 | 894 | 0 | 28 | 1360.39 | 46 | 3839 | 0 | 335 | 1125 | 0 | 0 | 0 | 0
22:30 | 2844.5 | 2472.5 | 893.5 | 0 | 28 | 1355.855 | 46 | 3842 | 0 | 335.5 | 1122.5 | 0 | 0 | 0 | 0
23:00 | 2836 | 2476 | 893 | 0 | 28 | 1351.32 | 46 | 3845 | 0 | 336 | 1120 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 406 | 09:00 | 392 | 00:00 | Payra | 421 | 09:00 | 410 | 22:00
Ashuganj | 415 | 6:00 | 391 | 23:00 | Rahanpur | 400 | 10:00 | 387 | 00:00
Bhulta | 406 | 09:00 | 390 | 23:00 | Rampal | 410 | 09:00 | 390 | 00:00
Bibiana | 390 | 09:00 | 372 | 23:00
BIPTC | 398 | 08:00 | 387 | 15:00
Bogura | 389 | 10:00 | 374 | 00:00
Gopalganj | 412 | 09:00 | 394 | 00:00
Kaliakoir | 377 | 09:00 | 359 | 23:00
Madunaghat | 404 | 10:00 | 394 | 01:00
Meghnaghat | 407 | 09:00 | 396 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 07:00 | 229 | 00:00 | Keranigonj | 236 | 09:00 | 227 | 00:00
AKSML | 235 | 08:00 | 226 | 01:00 | Khulna(S) | 234 | 09:00 | 218 | 00:00
Aminbazar | 239 | 09:00 | 230 | 00:00 | Madunaghat | 236 | 07:00 | 229 | 09:00
Ashuganj | 234 | 09:00 | 225 | 00:00 | Madunaghat-400 | 237 | 09:00 | 231 | 00:00
Ashuganj-400 | 232 | 6:00 | 224 | 23:00 | Maniknagar | 234 | 08:00 | 226 | 23:00
Baghabari | 234 | 08:00 | 225 | 00:00 | Meghnaghat | 241 | 07:00 | 233 | 00:00
Barapukuria | 223 | 06:00 | 218 | 08:00 | Meghnaghat-400 | 237 | 09:00 | 229 | 00:00
Barapukuria-230 | 222 | 6:00 | 216 | 9:00 | Mirsorai | 234 | 08:00 | 224 | 00:00
Barishal | 240 | 09:00 | 229 | 00:00 | Rajshahi | 231 | 06:00 | 218 | 23:00
Bheramara | 235 | 04:00 | 222 | 20:00 | Rampal | 234 | 08:00 | 219 | 00:00
Bhulta | 234 | 08:00 | 225 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 09:00 | 215 | 23:00 | Rampura | 233 | 08:00 | 225 | 00:00
BIPTC | 237 | 04:00 | 221 | 20:00 | Shikalbaha | 233 | 10:00 | 226 | 00:00
Bogura | 236 | 10:00 | 227 | 00:00 | Shyampur | 236 | 09:00 | 227 | 00:00
Bogura-400 | 236 | 11:00 | 227 | 00:00 | Siddhirganj | 236 | 09:00 | 229 | 00:00
Borhanuddin | 243 | 08:00 | 236 | 00:00 | Sirajgonj | 240 | 06:00 | 234 | 00:00
BSRM | 233 | 09:00 | 224 | 00:00 | Sreepur | 232 | 09:00 | 225 | 00:00
Cumilla(N) | 229 | 09:00 | 220 | 00:00 | Tongi | 233 | 09:00 | 222 | 00:00
Faridpur | 238 | 09:00 | 225 | 00:00
Fenchuganj | 230 | 06:00 | 221 | 00:00
Ghorashal | 240 | 00:00 | 230 | 03:00
Ghorashal-230 | 232 | 08:00 | 223 | 23:00
Gopalganj | 236 | 09:00 | 226 | 00:00
GPH | 234 | 08:00 | 227 | 00:00
Haripur | 234 | 08:00 | 227 | 00:00
Hasnabad | 237 | 09:00 | 228 | 00:00
Hathazari | 237 | 09:00 | 230 | 00:00
Ishurdi | 235 | 03:00 | 223 | 20:00
Jhenaidah | 230 | 07:00 | 215 | 00:00
Kaliakoir | 235 | 09:00 | 225 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 129 | 00:00 | Madunaghat | 136 | 08:00 | 131 | 00:00
Agargaon | 138 | 08:00 | 132 | 00:00 | Magura | 130 | 06:00 | 118 | 20:00
Agrabad | 135 | 07:00 | 129 | 01:00 | Mahasthangarh | 128 | 06:00 | 123 | 00:00
AKS | 132 | 07:00 | 128 | 00:00 | Manikganj | 130 | 10:00 | 124 | 00:00
Aminbazar | 136 | 07:00 | 131 | 00:00 | Maniknagar | 135 | 06:00 | 131 | 00:00
Amnura | 134 | 03:00 | 121 | 00:00 | Matarbari | 119 | 16:00 | 110 | 00:00
Ashuganj | 137 | 08:00 | 133 | 00:00 | Matuail | 138 | 09:00 | 133 | 00:00
Bagerhat | 133 | 08:00 | 119 | 00:00 | Millgate | 136 | 08:00 | 131 | 00:00
Bajitpur | 128 | 05:00 | 122 | 00:00 | Mirpur | 136 | 10:00 | 130 | 00:00
Bakulia | 136 | 17:00 | 130 | 00:00 | Mirzapur | 130 | 10:00 | 122 | 07:00
Banani | 134 | 10:00 | 132 | 18:00 | Mithapukur | 130 | 10:00 | 15 | 01:00
Bangabhaban | 135 | 08:00 | 131 | 00:00 | MI_Cement | 138 | 06:00 | 133 | 00:00
Barapukuria | 137 | 06:00 | 132 | 08:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 136 | 07:00 | 130 | 00:00 | Mogbazar | 135 | 06:00 | 130 | 00:00
Barishal | 134 | 09:00 | 125 | 00:00 | Mongla | 134 | 10:00 | 120 | 00:00
Barishal-230 | 134 | 10:00 | 125 | 23:00 | Motijheel | 135 | 08:00 | 131 | 00:00
Baroaulia | 135 | 08:00 | 131 | 00:00 | Muktagacha | 131 | 11:00 | 124 | 14:00
Baroirhat | 126 | 18:00 | 117 | 01:00 | Munshiganj | 138 | 08:00 | 132 | 00:00
Bashundhara | 137 | 10:00 | 129 | 00:00 | Muradnagar | 129 | 08:00 | 122 | 00:00
BashundharaCement | 138 | 09:00 | 127 | 18:00 | Mymensingh | 133 | 00:00 | 112 | 00:00
Beanibazar | 131 | 08:00 | 122 | 22:00 | Naogaon | 125 | 18:00 | 118 | 00:00
Benapole | 128 | 10:00 | 115 | 00:00 | Narail | 132 | 08:00 | 117 | 19:00
Bhaluka | 124 | 10:00 | 120 | 00:00 | Narinda | 135 | 6:00 | 131 | 0:00
Bhandaria | 127 | 08:00 | 115 | 23:00 | Narshingdi | 135 | 07:00 | 123 | 00:00
Bhangura | 131 | 05:00 | 125 | 22:00 | Natore | 129 | 04:00 | 123 | 00:00
Bheramara | 133 | 03:00 | 125 | 22:00 | Nawabganj | 135 | 05:00 | 130 | 00:00
Bheramara(GK) | 133 | 06:00 | 125 | 22:00 | Netrakona | 117 | 10:00 | 109 | 14:00
Bhulta | 134 | 06:00 | 128 | 23:00 | New | 138 | 13:00 | 132 | 00:00
Bog-Sherpur | 130 | 18:00 | 124 | 00:00 | Niamatpur | 135 | 18:00 | 127 | 00:00
Bogura | 131 | 06:00 | 126 | 00:00 | Noapara | 133 | 07:00 | 120 | 00:00
Bogura-230 | 132 | 18:00 | 126 | 00:00 | Pabna | 133 | 09:00 | 124 | 23:00
Brahmanbaria | 132 | 08:00 | 124 | 00:00 | Palashbari | 124 | 04:00 | 119 | 11:00
Cantonment | 138 | 09:00 | 133 | 00:00 | Panchagarh | 140 | 21:00 | 125 | 08:00
Chandpur | 126 | 18:00 | 121 | 04:00 | Patuakhali | 136 | 10:00 | 131 | 00:00
Chandraghona | 135 | 08:00 | 131 | 00:00 | Payra | 138 | 09:00 | 134 | 00:00
Chapai | 130 | 01:00 | 125 | 00:00 | PHP | 124 | 18:00 | 115 | 01:00
Charsaidpur | 138 | 08:00 | 134 | 00:00 | Postogola | 140 | 09:00 | 135 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 124 | 07:00 | 116 | 00:00 | Purbachal | 137 | 06:00 | 129 | 00:00
Chhatak | 132 | 06:00 | 123 | 00:00 | Purbasadipur | 134 | 22:00 | 119 | 07:00
Chowmuhani | 119 | 18:00 | 108 | 01:00 | Rahanpur | 136 | 17:00 | 130 | 00:00
Chuadanga | 127 | 09:00 | 115 | 00:00 | Rahanpur-400 | 136 | 10:00 | 131 | 00:00
Coxsbazar | 119 | 09:00 | 110 | 00:00 | Rahim | 137 | 07:00 | 134 | 14:00
Cumilla(N) | 130 | 07:00 | 123 | 00:00 | Rajbari | 131 | 09:00 | 123 | 00:00
Cumilla(S) | 133 | 07:00 | 121 | 00:00 | Rajendrapur | 131 | 09:00 | 123 | 01:00
Daudkandi | 129 | 08:00 | 122 | 00:00 | Rajshahi | 132 | 06:00 | 125 | 00:00
Dhaka | 134 | 08:00 | 130 | 00:00 | Rajshahi-230 | 133 | 06:00 | 118 | 00:00
Dhamrai | 136 | 08:00 | 130 | 00:00 | Ramganj | 119 | 18:00 | 110 | 01:00
Dhanmondi | 138 | 06:00 | 134 | 00:00 | Rampur | 134 | 08:00 | 129 | 00:00
Dohazari | 130 | 03:00 | 122 | 00:00 | Rampura | 134 | 06:00 | 129 | 00:00
Faridpur | 133 | 09:00 | 126 | 00:00 | Rangamati | 134 | 08:00 | 128 | 02:00
Fatullah | 139 | 08:00 | 134 | 00:00 | Rangpur | 130 | 11:00 | 119 | 08:00
Fenchuganj | 133 | 09:00 | 128 | 00:00 | Ruppur | 135 | 04:00 | 120 | 23:00
Feni | 124 | 18:00 | 114 | 01:00 | Saidpur | 133 | 04:00 | 123 | 08:00
Ghatail | 128 | 11:00 | 117 | 07:00 | Satkhira | 133 | 10:00 | 118 | 00:00
Ghorashal | 138 | 05:00 | 134 | 00:00 | Satmasjid | 138 | 08:00 | 132 | 00:00
Goalpara | 136 | 11:00 | 122 | 00:00 | Savar | 136 | 19:00 | 130 | 00:00
Gollamari | 136 | 06:00 | 126 | 00:00 | SevenRings | 139 | 08:00 | 134 | 00:00
Gopalganj | 136 | 09:00 | 126 | 23:00 | ShahCement | 138 | 08:00 | 134 | 00:00
Gopalganj-400 | 139 | 09:00 | 132 | 00:00 | Shahjadpur | 136 | 09:00 | 130 | 00:00
Gulshan | 133 | 05:00 | 128 | 00:00 | Shahjibazar | 133 | 07:00 | 124 | 00:00
Halishahar | 134 | 04:00 | 130 | 15:00 | Shahmirpur | 135 | 09:00 | 131 | 00:00
Haripur | 138 | 09:00 | 133 | 00:00 | Shariatpur | 137 | 09:00 | 126 | 07:00
HaripurSBU | 138 | 09:00 | 133 | 01:00 | Sherpur | 129 | 00:00 | 117 | 06:00
Hasnabad | 139 | 03:00 | 136 | 00:00 | Shikalbaha | 124 | 07:00 | 118 | 00:00
Hathazari | 136 | 08:00 | 132 | 00:00 | Shikalbaha-230 | 136 | 08:00 | 131 | 00:00
Ishurdi | 136 | 09:00 | 128 | 20:00 | Shitalakhya | 138 | 06:00 | 133 | 00:00
Jaldhaka | 131 | 22:00 | 119 | 08:00 | Sholosohor | 134 | 06:00 | 130 | 00:00
Jamalpur | 132 | 00:00 | 122 | 05:00 | Shyampur | 139 | 08:00 | 134 | 00:00
Jashore | 131 | 10:00 | 117 | 00:00 | Shyampur-230 | 139 | 09:00 | 134 | 00:00
Jhenaidah | 132 | 10:00 | 120 | 00:00 | Siddhirganj | 138 | 07:00 | 134 | 00:00
Jhenaidah-230 | 132 | 06:00 | 121 | 22:00 | Sirajganj | 129 | 11:00 | 123 | 00:00
Joydebpur | 134 | 08:00 | 128 | 00:00 | Sonargaon | 136 | 09:00 | 130 | 00:00
Joypurhat | 121 | 18:30 | 112 | 00:00 | Sreemongol | 132 | 08:00 | 124 | 00:00
Juldah | 135 | 08:00 | 131 | 00:00 | Sreepur | 128 | 04:00 | 124 | 00:00
Kabirpur | 135 | 08:00 | 127 | 00:00 | Srinagar | 136 | 09:00 | 130 | 01:00
Kachua | 124 | 17:00 | 118 | 00:00 | SSM | 140 | 09:00 | 135 | 01:00
Kaliakoir | 137 | 09:00 | 124 | 09:00 | Sunamganj | 130 | 05:00 | 120 | 21:00
Kallyanpur | 136 | 07:00 | 131 | 00:00 | Sylhet | 131 | 08:00 | 124 | 23:00
Kalurghat | 135 | 07:00 | 131 | 00:00 | Sylhet-132 | 132 | 05:00 | 127 | 18:30
Kamrangirchar | 137 | 07:00 | 131 | 00:00 | Tangail | 128 | 10:00 | 120 | 07:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 22:00 | 121 | 08:00
Kasba | 128 | 08:00 | 121 | 00:00 | TK | 136 | 09:00 | 133 | 00:00
Kazla | 135 | 09:00 | 131 | 00:00 | Tongi | 138 | 04:00 | 132 | 23:00
Keranigonj | 137 | 09:00 | 130 | 00:00 | Ullahpara | 133 | 04:00 | 125 | 23:00
Khagrachori | 133 | 07:00 | 128 | 00:00 | Ullon | 133 | 06:00 | 129 | 00:00
Khulna | 135 | 09:00 | 123 | 00:00 | Uttara | 136 | 10:00 | 128 | 00:00
Khulna(S) | 137 | 10:00 | 125 | 00:00 | UttaraNew | 136 | 09:00 | 131 | 00:00
Khulshi | 133 | 07:00 | 129 | 00:00 | Zigatola | 136 | 09:00 | 130 | 00:00
Kishoreganj | 125 | 10:00 | 119 | 00:00
Kodda | 132 | 08:00 | 125 | 00:00
KSRM | 135 | 17:00 | 130 | 00:00
Kulaura | 132 | 07:00 | 126 | 23:00
Kurigram | 128 | 22:00 | 117 | 07:00
Kushtia | 132 | 06:00 | 122 | 22:00
Lalbag | 137 | 09:00 | 131 | 00:00
Lalmonirhat | 128 | 22:00 | 118 | 08:00
Madanganj | 138 | 09:00 | 133 | 00:00
Madaripur | 138 | 08:00 | 130 | 00:00
Madartek | 133 | 06:00 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division