## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-04-2025 | during | 04-04-2025 | during | 04-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 150 | 150 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 402 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 287 | 300 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 314 | 315 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 8 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 20 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 450 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 500 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2486 | 2717 | 5189.9 | 5251.9 | 4233.32 | 4295.32
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 150 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 40 | 82 | 82 | 82 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 70 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 27 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.06 | 0 | 4.06 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 12 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 18 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 950 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 6 | 0 | 6 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 313 | 314 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1487 | 1998 | 3468.78 | 3439.72 | 3468.78 | 3439.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 208 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 336 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 48 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 174 | 170 | 195 | 195 | 177 | 177 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 45 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 76 | 180 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 24 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52 | 52.2 | 52.2 | 40 | 40 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 8 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 18 | 113 | 113 | 9 | 18 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 32 | 90 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1170 | 1507 | 2125.99 | 2060.99 | 1843.35 | 1787.35
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-04-2025 | during | 04-04-2025 | during | 04-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 67 | 97 | 210 | 210 | 100 | 100 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 126 | 164 | 200 | 200 | 126 | 164 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 115 | 115 | 115 | 68 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 24.86 | 0 | 34.94 | 0 | 34.94 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 299.86 | 388 | 638.64 | 601.5 | 407.64 | 455.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 35 | 35 | 35 | 35 | 35 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 36 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 133 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 117 | 117 | 115 | 115 | 115 | 115 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | shutdown due to maintenance work on gas field
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 220 | 310 | 220 | 310 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 496 | 477 | 1453 | 1543 | 1077 | 1167
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 844 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 378 | 555 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1360 | 1450 | 3600.2 | 3515.2 | 2469.01 | 2384.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 10 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 876 | 1220 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 216 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.38 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1442.38 | 1877 | 2172.12 | 2171.12 | 2120.12 | 2119.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 169 | 160 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 202 | 160 | 220 | 220 | 198 | 198 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 160 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 406 | 320 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.34 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 966.66 | 1356 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.65 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2094.65 | 2256 | 3180.73 | 3014.53 | 3012.94 | 2846.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 58 | 60 | 60 | 58 | 58 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 162 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 33 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 17 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 160.5 | 0 | 160.5 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 487.4 | 448 | 668.9 | 472 | 666.9 | 470
System Total |  |  |  |  | 27566.2 | 28535.742 | 11323.29 | 13118 | 22498.26 | 22069.96 | 19299.06 | 18964.76
Forecast Scenario (04-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12770 |  | 0 |  | 12770
|  |  |  | 1:00 | 12460 |  | 0 |  | 12460
|  |  |  | 2:00 | 12100 |  | 0 |  | 12100
|  |  |  | 3:00 | 11790 |  | 0 |  | 11790
|  |  |  | 4:00 | 11490 |  | 0 |  | 11490
|  |  |  | 5:00 | 11320 |  | 0 |  | 11320
|  |  |  | 6:00 | 10790 |  | 0 |  | 10790
|  |  |  | 7:00 | 10730 |  | 0 |  | 10730
|  |  |  | 8:00 | 10720 |  | 0 |  | 10720
|  |  |  | 9:00 | 10660 |  | 0 |  | 10660
|  |  |  | 10:00 | 10820 |  | 0 |  | 10820
|  |  |  | 11:00 | 11020 |  | 0 |  | 11020
|  |  |  | 12:00 | 11320 |  | 0 |  | 11320
|  |  |  | 13:00 | 12300 |  | 0 |  | 12300
|  |  |  | 14:00 | 11500 |  | 0 |  | 11500
|  |  |  | 15:00 | 11400 |  | 0 |  | 11400
|  |  |  | 16:00 | 11300 |  | 0 |  | 11300
|  |  |  | 17:00 | 11360 |  | 0 |  | 11360
|  |  |  | 18:00 | 11010 |  | 0 |  | 11010
|  |  |  | 18:30 | 11900 |  | 0 |  | 11900
|  |  |  | 19:00 | 12850 |  | 0 |  | 12850
|  |  |  | 19:30 | 13110 |  | 0 |  | 13110
|  |  |  | 20:00 | 13070 |  | 0 |  | 13070
|  |  |  | 21:00 | 13030 |  | 0 |  | 13030
|  |  |  | 22:00 | 13100 |  | 0 |  | 13100
|  |  |  | 23:00 | 13100 |  | 0 |  | 13100
Probable Maximum Temperature: |  |  | 34.60°C
Probable Maximum Demand at Day Peak: |  |  | 11320.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13110.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13110.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 282.01 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:16 hrs on 04-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-04-2025 | [28 empty] | Date: | 03-04-2025 | [28 empty] | Date: | 03-04-2025 | [28 empty] | Date: | 03-04-2025 | [28 empty] | Date: | 03-04-2025 | [17 empty] | Date: | 03-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 48 | 0 | 0 | 17 | 35 | 0 | 0 | 450 | 300 | 450 | 0 | 17 | 0 | 328 | 0 | 0 | 0 | 90 | 8 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 95 | 12 | 0 | 46 | 0 | 42 | 213 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 40 | 175 | 0 | 355 | 0 | 49 | 190 | 34 | 21 | 40 | 176 | 18 | 20 | 98 | 28 | 0 | 0 | 21 | 0 | 0 | 0 | 35 | 39 | 0 | 141 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 47 | 115 | 65 | 0 | 0 | 7 | 6478 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 35 | 1362.51 | 0 | 0 | 0 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 20 | 0 | 214 | 0 | 197 | 0 | 170 | 0 | 324 | 0 | 0 | 0 | 165 | 58 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 180 | 0 | 0 | 1240 | 0 | 6196.51 | 12674.51 | 84.2
01:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 295 | 583 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 70 | 8 | 10 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 95 | 0 | 0 | 46 | 0 | 42 | 216 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 40 | 177 | 0 | 355 | 0 | 49 | 183 | 34 | 17 | 40 | 155 | 10 | 20 | 98 | 28 | 0 | 0 | 21 | 0 | 0 | 0 | 35 | 39 | 0 | 134 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 48 | 96 | 70 | 0 | 0 | 0 | 6298 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 17 | 1359.52 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 198 | 0 | 167 | 0 | 363 | 0 | 0 | 0 | 168 | 58 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 220 | 0 | 0 | 1240 | 0 | 6084.52 | 12382.52 | 84.19
02:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 307 | 583 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 70 | 8 | 10 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 46 | 0 | 42 | 216 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1215 | 0 | 51 | 0 | 177 | 0 | 355 | 0 | 50 | 181 | 34 | 16 | 40 | 155 | 9 | 20 | 98 | 26 | 0 | 0 | 21 | 0 | 0 | 0 | 35 | 39 | 0 | 152 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 48 | 97 | 70 | 0 | 0 | 1 | 6171 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1359.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 194 | 0 | 151 | 0 | 322 | 0 | 0 | 0 | 167 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1242 | 0 | 5861.32 | 12032.32 | 84.19
03:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 267 | 583 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 8 | 10 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 46 | 0 | 42 | 216 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1219 | 0 | 51 | 0 | 177 | 0 | 355 | 0 | 50 | 181 | 34 | 17 | 40 | 155 | 0 | 20 | 98 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 137 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 48 | 97 | 71 | 0 | 0 | 12 | 6014 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 1359.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 194 | 0 | 155 | 0 | 320 | 0 | 0 | 0 | 168 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 88 | 220 | 0 | 0 | 1120 | 0 | 5723.34 | 11737.34 | 84.18
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 265 | 500 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 8 | 10 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 42 | 216 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1200 | 0 | 51 | 0 | 177 | 0 | 355 | 0 | 50 | 181 | 34 | 17 | 50 | 155 | 0 | 20 | 98 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 133 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 48 | 97 | 71 | 0 | 0 | 12 | 5868 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1266.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 192 | 0 | 152 | 0 | 320 | 0 | 0 | 0 | 170 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 88 | 180 | 0 | 0 | 1097 | 0 | 5565.61 | 11433.61 | 84.18
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 256 | 583 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 52 | 8 | 10 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 46 | 0 | 42 | 282 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1101 | 0 | 51 | 0 | 177 | 0 | 354 | 0 | 50 | 181 | 34 | 17 | 50 | 155 | 0 | 20 | 98 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 133 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 48 | 97 | 71 | 0 | 0 | 12 | 5775 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 0 | 1261.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 178 | 0 | 149 | 0 | 321 | 0 | 0 | 0 | 170 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 88 | 180 | 0 | 0 | 1102 | 0 | 5494.37 | 11269.37 | 84.17
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 284 | 450 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 52 | 9 | 10 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 42 | 314 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1020 | 0 | 51 | 0 | 177 | 0 | 355 | 0 | 50 | 181 | 34 | 16 | 50 | 155 | 0 | 20 | 98 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 132 | 22 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 48 | 97 | 71 | 0 | 0.33 | 5 | 5590.33 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1261.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 174 | 0 | 143 | 0 | 321 | 0 | 0.01 | 0 | 167 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 10 | 88 | 180 | 0 | 0 | 1005 | 0 | 5158.32 | 10748.65 | 84.17
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 294 | 450 | 0 | 0 | 0 | 332 | 0 | 0 | 3 | 52 | 9 | 10 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 46 | 0 | 42 | 314 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 904 | 3 | 51 | 0 | 177 | 0 | 355 | 0 | 51 | 198 | 34 | 16 | 50 | 155 | 1 | 8 | 70 | 22 | 0 | 10 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 132 | 22 | 0 | 85 | 30 | 0 | 17 | 112 | 0 | 68 | 125 | 71 | 0 | 5.55 | 0 | 5764.55 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.22 | 375 | 0 | 1126.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 7.65 | 180 | 0 | 174 | 0 | 137 | 0 | 343 | 0 | 0.58 | 0 | 166 | 58 | 0 | 3 | 0 | 0 | 0 | 0.6 | 23 | 0.06 | 0 | 200 | 10 | 88 | 180 | 0 | 0 | 950 | 0 | 4935.91 | 10700.46 | 84.16
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 288 | 450 | 0 | 0 | 0 | 331 | 0 | 0 | 13 | 52 | 9 | 10 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 2 | 46 | 0 | 42 | 334 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 9 | 51 | 0 | 177 | 0 | 355 | 0 | 50 | 191 | 34 | 17 | 50 | 85 | 10 | 20 | 17 | 22 | 0 | 21 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 136 | 22 | 0 | 85 | 30 | 0 | 17 | 115 | 0 | 68 | 126 | 71 | 1 | 15.74 | 0 | 5756.74 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.69 | 378 | 0 | 1113.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 20.58 | 172 | 0 | 167 | 0 | 134 | 0 | 328 | 0 | 1.35 | 0 | 162 | 57 | 35 | 8 | 34 | 0 | 0 | 2.1 | 61 | 0.18 | 0 | 200 | 10 | 88 | 180 | 0 | 0 | 892 | 0 | 4937.35 | 10694.09 | 84.16
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 284 | 450 | 0 | 0 | 0 | 328 | 0 | 0 | 21 | 52 | 10 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 46 | 0 | 42 | 323 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 850 | 14 | 51 | 0 | 177 | 0 | 355 | 0 | 51 | 184 | 33 | 30 | 50 | 51 | 9 | 20 | 17 | 22 | 0 | 44 | 0 | 0 | 0 | 0 | 35 | 39 | 0 | 132 | 22 | 0 | 83 | 30 | 0 | 17 | 117 | 0 | 68 | 126 | 69 | 1 | 21.09 | 1 | 5686.09 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 378 | 0 | 1057.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 32.96 | 162 | 0 | 172 | 0 | 159 | 0 | 324 | 0 | 2.73 | 0 | 166 | 58 | 35 | 19 | 34 | 0 | 0 | 3.7 | 104 | 0.42 | 0 | 200 | 9 | 88 | 180 | 0 | 0 | 850 | 0 | 4976.67 | 10662.76 | 84.15
10:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 299 | 450 | 0 | 0 | 0 | 326 | 0 | 0 | 18 | 52 | 10 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 46 | 0 | 20 | 323 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 850 | 18 | 51 | 0 | 177 | 0 | 355 | 0 | 49 | 199 | 31 | 34 | 50 | 51 | 9 | 20 | 17 | 22 | 0 | 54 | 0 | 0 | 0 | 0 | 35 | 38 | 0 | 133 | 22 | 0 | 83 | 30 | 0 | 17 | 117 | 0 | 68 | 126 | 67 | 2 | 18.85 | 9 | 5767.85 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 378 | 0 | 955.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 46.27 | 165 | 0 | 190 | 0 | 181 | 0 | 334 | 0 | 3.78 | 0 | 166 | 58 | 0 | 27 | 34 | 0 | 0 | 5.2 | 142 | 0.53 | 0 | 200 | 8 | 88 | 180 | 0 | 0 | 843 | 0 | 5056.77 | 10824.62 | 84.15
11:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 293 | 450 | 0 | 0 | 0 | 320 | 0 | 0 | 30 | 52 | 10 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 28 | 323 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 850 | 15 | 51 | 0 | 175 | 0 | 350 | 0 | 48 | 196 | 33 | 34 | 50 | 56 | 9 | 17 | 34 | 22 | 0 | 62 | 0 | 0 | 0 | 0 | 35 | 38 | 0 | 135 | 22 | 0 | 83 | 30 | 0 | 17 | 117 | 0 | 68 | 126 | 67 | 2 | 36.1 | 12 | 5814.1 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 379 | 0 | 958.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 33.75 | 170 | 0 | 203 | 0 | 189 | 0 | 402 | 0 | 2.78 | 0 | 165 | 58 | 0 | 31 | 34 | 0 | 0 | 5.9 | 165 | 0.58 | 0 | 200 | 9 | 120 | 180 | 0 | 0 | 839 | 0 | 5213.39 | 11027.49 | 84.14
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 287 | 500 | 0 | 0 | 0 | 314 | 0 | 0 | 31 | 52 | 10 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 4 | 46 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 950 | 18 | 51 | 0 | 174 | 0 | 336 | 0 | 47 | 208 | 33 | 32 | 45 | 76 | 9 | 20 | 52 | 24 | 0 | 63 | 0 | 0 | 0 | 0 | 36 | 36 | 0 | 154 | 22 | 0 | 84 | 30 | 0 | 17 | 117 | 0 | 68 | 126 | 67 | 2 | 24.86 | 12 | 5938.86 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 378 | 0 | 966.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 57.65 | 169 | 0 | 202 | 0 | 192 | 0 | 406 | 0 | 4.34 | 0 | 161 | 58 | 17 | 33 | 33 | 0 | 0 | 6.4 | 179 | 0.38 | 0 | 216 | 10 | 120 | 220 | 0 | 0 | 876 | 0 | 5384.43 | 11323.29 | 84.14
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 293 | 500 | 0 | 0 | 0 | 310 | 0 | 0 | 28 | 52 | 8 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 36 | 0 | 4 | 46 | 0 | 13 | 315 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1012 | 18 | 43 | 0 | 175 | 0 | 341 | 0 | 43 | 202 | 32 | 32 | 50 | 98 | 8 | 20 | 70 | 26 | 0 | 59 | 0 | 0 | 0 | 0 | 35 | 38 | 0 | 155 | 22 | 0 | 84 | 30 | 0 | 17 | 117 | 0 | 68 | 126 | 66 | 1 | 33.66 | 12 | 6078.66 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 432 | 0 | 1067.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 55.27 | 192 | 0 | 201 | 0 | 201 | 0 | 360 | 0 | 4.64 | 0 | 160 | 57 | 35 | 32 | 4 | 0 | 0 | 6.2 | 171 | 0.61 | 0 | 279 | 9 | 120 | 220 | 0 | 0 | 972 | 0 | 5643.86 | 11722.52 | 84.13
14:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 296 | 500 | 0 | 0 | 0 | 310 | 0 | 0 | 25 | 70 | 8 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 36 | 0 | 3 | 46 | 0 | 15 | 315 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1100 | 17 | 43 | 0 | 164 | 0 | 340 | 0 | 43 | 191 | 32 | 49 | 50 | 110 | 9 | 20 | 88 | 24 | 0 | 51 | 0 | 0 | 0 | 0 | 37 | 38 | 0 | 151 | 22 | 0 | 84 | 30 | 0 | 17 | 118 | 0 | 67 | 124 | 61 | 2 | 29.42 | 12 | 6208.42 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 456 | 0 | 1115.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 42.89 | 206 | 0 | 201 | 0 | 204 | 0 | 389 | 0 | 4.64 | 0 | 152 | 57 | 35 | 30 | 0 | 0 | 0 | 5.3 | 159 | 0.53 | 0 | 307 | 10 | 116 | 220 | 0 | 0 | 1091 | 0 | 5815.22 | 12023.64 | 84.13
15:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 291 | 500 | 0 | 0 | 0 | 308 | 0 | 0 | 19 | 70 | 8 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 60 | 0 | 2 | 46 | 0 | 22 | 315 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1100 | 0 | 43 | 0 | 162 | 0 | 338 | 0 | 44 | 202 | 28 | 51 | 50 | 136 | 8 | 20 | 97 | 26 | 0 | 38 | 0 | 0 | 0 | 0 | 35 | 38 | 0 | 152 | 22 | 0 | 83 | 30 | 0 | 17 | 117 | 0 | 67 | 123 | 64 | 1 | 31.64 | 12 | 6237.64 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 405 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 39.72 | 206 | 0 | 201 | 0 | 204 | 0 | 360 | 0 | 3.52 | 0 | 154 | 57 | 35 | 21 | 34 | 0 | 0 | 4.2 | 129 | 0.23 | 0 | 307 | 10 | 116 | 220 | 0 | 0 | 1050 | 0 | 5685.67 | 11923.31 | 84.12
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 275 | 500 | 0 | 0 | 0 | 307 | 0 | 0 | 12 | 70 | 8 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 60 | 0 | 1 | 46 | 0 | 29 | 315 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1000 | 8 | 43 | 0 | 172 | 0 | 342 | 0 | 43 | 186 | 32 | 50 | 50 | 136 | 9 | 20 | 105 | 26 | 0 | 30 | 0 | 0 | 0 | 0 | 35 | 37 | 0 | 152 | 22 | 0 | 83 | 30 | 0 | 17 | 117 | 0 | 67 | 123 | 65 | 1 | 17.87 | 12 | 6100.87 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 410 | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 22.23 | 206 | 0 | 200 | 0 | 204 | 0 | 324 | 0 | 2.15 | 0 | 168 | 57 | 35 | 14 | 34 | 0 | 0 | 2.7 | 76 | 0.25 | 0 | 307 | 10 | 116 | 220 | 0 | 0 | 1053 | 0 | 5527.33 | 11628.2 | 84.12
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 289 | 500 | 0 | 0 | 0 | 311 | 0 | 0 | 6 | 70 | 8 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 60 | 0 | 1 | 46 | 0 | 29 | 315 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1000 | 3 | 43 | 0 | 172 | 0 | 347 | 0 | 44 | 188 | 32 | 51 | 50 | 136 | 8 | 20 | 105 | 26 | 16 | 9 | 0 | 0 | 0 | 0 | 35 | 37 | 0 | 152 | 22 | 0 | 83 | 30 | 0 | 17 | 117 | 0 | 76 | 123 | 69 | 0 | 7.78 | 12 | 6108.78 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 410 | 0 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 8.14 | 207 | 0 | 201 | 0 | 204 | 0 | 324 | 0 | 0.75 | 0 | 169 | 58 | 35 | 5 | 34 | 0 | 0 | 1.2 | 29 | 0.1 | 0 | 200 | 10 | 108 | 220 | 0 | 0 | 1000 | 0 | 5255.19 | 11363.97 | 84.11
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 301 | 450 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 8 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 27 | 315 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1035 | 0 | 43 | 0 | 172 | 0 | 300 | 0 | 45 | 198 | 32 | 72 | 50 | 136 | 10 | 20 | 105 | 26 | 34 | 1 | 0 | 0 | 0 | 0 | 35 | 37 | 0 | 136 | 22 | 0 | 84 | 30 | 0 | 17 | 117 | 0 | 105 | 160 | 69 | 0 | 0.26 | 12 | 5934.26 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 410 | 0 | 1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 209 | 0 | 203 | 0 | 207 | 0 | 343 | 0 | 0.04 | 0 | 162 | 58 | 35 | 1 | 34 | 0 | 0 | 0.1 | 3 | 0.01 | 0 | 200 | 10 | 120 | 180 | 0 | 0 | 900 | 0 | 5081.64 | 11015.9 | 84.11
19:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 15 | 0 | 0 | 0 | 48 | 0 | 0 | 23 | 100 | 0 | 7 | 360 | 251 | 500 | 0 | 35 | 0 | 311 | 0 | 0 | 0 | 108 | 8 | 7 | 0 | 450 | 0 | 15 | 0 | 0 | 0 | 51 | 48 | 0 | 70 | 48 | 0 | 46 | 7 | 27 | 314 | 0 | 0 | 0 | 0 | 20 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 40 | 180 | 0 | 355 | 0 | 47 | 182 | 33 | 89 | 50 | 158 | 18 | 8 | 114 | 26 | 52 | 0 | 33 | 0 | 0 | 0 | 35 | 37 | 0 | 150 | 23 | 0 | 84 | 30 | 0 | 17 | 117 | 0 | 115 | 162 | 84 | 0 | 0 | 12 | 7004 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 32 | 1360 | 0 | 0 | 0 | 51 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 185 | 0 | 160 | 0 | 320 | 0 | 0 | 0 | 167 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1025 | 0 | 5854 | 12858 | 84.1
19:30 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 0 | 48 | 0 | 0 | 17 | 54 | 0 | 20 | 400 | 300 | 500 | 0 | 17 | 0 | 315 | 0 | 0 | 0 | 108 | 8 | 7 | 0 | 450 | 0 | 12 | 0 | 0 | 0 | 51 | 40 | 0 | 70 | 12 | 0 | 46 | 18 | 27 | 314 | 0 | 0 | 0 | 0 | 34 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 170 | 0 | 355 | 0 | 48 | 182 | 33 | 90 | 45 | 180 | 18 | 8 | 114 | 26 | 52 | 0 | 35 | 0 | 0 | 0 | 35 | 38 | 0 | 133 | 23 | 0 | 84 | 30 | 0 | 17 | 117 | 0 | 115 | 164 | 97 | 0 | 0 | 12 | 7087 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 51 | 1356 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 160 | 0 | 320 | 0 | 0 | 0 | 162 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1220 | 0 | 6031 | 13118
20:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 0 | 0 | 31 | 0 | 0 | 17 | 54 | 0 | 0 | 400 | 301 | 500 | 0 | 17 | 0 | 318 | 0 | 0 | 0 | 108 | 8 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 70 | 12 | 0 | 46 | 17 | 27 | 364 | 0 | 0 | 0 | 6 | 17 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 173 | 0 | 355 | 0 | 48 | 185 | 33 | 90 | 46 | 182 | 17 | 8 | 114 | 28 | 52 | 0 | 36 | 0 | 0 | 0 | 35 | 38 | 0 | 139 | 23 | 0 | 85 | 30 | 0 | 17 | 117 | 0 | 115 | 164 | 97 | 0 | 0 | 12 | 7031 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 51 | 1359 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 188 | 0 | 166 | 0 | 373 | 0 | 0 | 0 | 163 | 60 | 74 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1230 | 0 | 6046 | 13077 | 84.1
21:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 35 | 0 | 0 | 400 | 292 | 500 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 108 | 8 | 10 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 0 | 70 | 12 | 0 | 46 | 17 | 27 | 421 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 182 | 0 | 355 | 0 | 48 | 196 | 34 | 90 | 45 | 181 | 18 | 8 | 114 | 28 | 52 | 0 | 36 | 0 | 0 | 0 | 35 | 38 | 0 | 153 | 23 | 0 | 85 | 28 | 0 | 17 | 117 | 0 | 85 | 164 | 98 | 0 | 0 | 12 | 6945 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 51 | 1357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 203 | 0 | 210 | 0 | 400 | 0 | 0 | 0 | 163 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 220 | 0 | 0 | 1230 | 0 | 6087 | 13032 | 84.09
22:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 17 | 0 | 0 | 400 | 304 | 500 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 108 | 8 | 10 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 0 | 70 | 12 | 0 | 46 | 17 | 34 | 420 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 184 | 0 | 355 | 0 | 48 | 202 | 34 | 52 | 45 | 157 | 18 | 8 | 114 | 28 | 52 | 0 | 28 | 0 | 0 | 0 | 35 | 38 | 0 | 156 | 23 | 0 | 85 | 28 | 0 | 17 | 117 | 0 | 85 | 170 | 101 | 0 | 0 | 12 | 6878 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 52 | 1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 206 | 0 | 209 | 0 | 410 | 0 | 0 | 0 | 164 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1230 | 0 | 6138 | 13016 | 84.09
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 17 | 0 | 0 | 400 | 300 | 500 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 108 | 8 | 10 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 0 | 70 | 12 | 0 | 46 | 17 | 35 | 422 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 184 | 0 | 354 | 0 | 48 | 196 | 34 | 34 | 50 | 181 | 18 | 8 | 114 | 28 | 52 | 0 | 28 | 0 | 0 | 0 | 35 | 39 | 0 | 154 | 23 | 0 | 85 | 28 | 0 | 17 | 109 | 0 | 85 | 175 | 101 | 0 | 0 | 12 | 6884 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 52 | 1361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 208 | 0 | 210 | 0 | 407 | 0 | 0 | 0 | 163 | 60 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1244 | 0 | 6185 | 13069 | 84.08
Total KWH | 0 | 785280 | 0 | 0 | 0 | 0 | 0 | 0 | 9313200 | 0 | 0 | 74520 | 0 | 0 | 0 | 498720 | 0 | 0 | 142455 | 299520 | 0 | 24000 | 9920500 | 6919738 | 11984545 | 0 | 74239 | 0 | 7708349 | 0 | 0 | 205651 | 1749600 | 205200 | 231480 | 0 | 8945909 | 0 | 17815 | 0 | 0 | 35520 | 286954 | 117504 | 0 | 1404480 | 105600 | 26719 | 1089720 | 117091 | 803520 | 7352727.27 | 0 | 0 | 0 | 60285.6 | 136327 | 3511898 | 0 | 0 | 0 | 25854543 | 135810 | 1026896 | 281018 | 4215273 | 0 | 8720900 | 0 | 1142400 | 4670000 | 799416 | 964800 | 1136430 | 3285240 | 225120 | 398370 | 2072520 | 601920 | 333365 | 432191 | 218992 | 0 | 0 | 0 | 829000 | 900960 | 0 | 3458782 | 509568 | 0 | 2016000 | 704736 | 0 | 414000 | 3547110 | 0 | 1693200 | 3024000 | 1728960 | 12600 | 252660 | 226080 | 149981926.87 | 21374545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607680 | 11767270 | 338880 | 28935636 | 0 | 0 | 0 | 176928 | 0 | 101680 | 0 | 0 | 0 | 640340 | 16079 | 370504 | 4809091 | 0 | 4822300 | 0 | 4571100 | 0 | 8477381 | 0 | 31440 | 0 | 4020000 | 1344872 | 743846 | 228478 | 956908 | 0 | 0 | 42767.64 | 1198800 | 4362 | 0 | 6480000 | 238868 | 2539000 | 5067570 | 0 | 0 | 25883636.36 | 0 | 135789962 | 285771888.87

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11323.29 | MW | 12:00 Hr. | Energy Generated |  |  | 285.7719 |  | MKWHr.
| Day Peak Demand |  |  | 11323.29 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.519 |  | MKWHr.
| Evening Peak Generation |  |  | 13118 | MW | 19:30 Hr. | Energy Demand |  |  | 286.2909 |  | MKWHr.
| Evening Peak Demand |  |  | 13118 | MW | 19:30 Hr. | Maximum Temperature |  |  | 36.6 |  | °C
| Minimum Generation of the Day |  |  | 10662.76 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 939.41 |  | MMCFD
| Maximum Generation of the Day |  |  | 13118 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.912 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 55.2289 | 0 | 3.6483 | 0 | 0 | 0.20565 | 0 | 0 | 59.0829 | Gas | 126.2884 | Gas | 410915453.02
| Chattogram Zone |  |  | 4.3154 | 33.2073 | 2.2461 | 0 | 1.0897 | 0.16253 | 0 | 0.03552 | 41.0565 | Coal | 82.703 | Coal | 589798479.5134
| Cumilla Zone |  |  | 22.1097 | 0 | 7.3811 | 0 | 0 | 0.43219 | 0.60192 | 0 | 30.5249 | HFO | 20.553 | HFO | 350478759.112
| Mymensingh Zone |  |  | 1.729 | 0 | 4.9433 | 0 | 0 | 0.26526 | 0 | 0 | 6.9375 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 12.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3802 | Hydro | 1.0897 | Hydro | 108972
| Khulna Zone |  |  | 0 | 11.7673 | 0.33888 | 0 | 0 | 0.60768 | 21.3745 | 0 | 34.0884 | Solar | 4.19 | Solar | 68130133.6204
| Barishal Zone |  |  | 7.8454 | 32.3636 | 0 | 0 | 0 | 0.004362 | 0 | 0 | 40.2134 | Import | 50.9121 | Import | 269532175.55
| Rajshahi Zone |  |  | 22.6799 | 0 | 0.29469 | 0 | 0 | 1.0423 | 28.9356 | 0 | 52.9525 | Wind | 0.03552 | Wind | 520012.8
| Rangpur Zone |  |  | 0 | 5.3649 | 1.7008 | 0 | 0 | 1.47 | 0 | 0 | 8.5357
| Total |  |  | 126.2884 | 82.703 | 20.553 | 0 | 1.0897 | 4.19 | 50.9121 | 0.03552 | 285.7719
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 410915453.02 |  | Hydro | 108972
|  |  |  | Coal | 589798479.5134 |  | Solar | 68130133.6204
|  |  |  | HFO | 350478759.112 |  | Import | 269532175.55
|  |  |  | HSD | 0 |  | Wind | 520012.8
[5 empty] | Total: | 168,94,83,985 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3745 | Peak Hr Flow | 844.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8145472.77 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.9356 | Peak Hr Flow | 1356.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 528 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.60192 | Peak Hr Flow | 26.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 704 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.9121 | Peak Hr Flow | 2226.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3277
|  |  |  | Chattogram |  | 0 |  | 1345
|  |  |  | Cumilla |  | 0 |  | 1442
|  |  |  | Mymensingh |  | 0 |  | 1275
|  |  |  | Sylhet |  | 0 |  | 578
|  |  |  | Khulna |  | 0 |  | 1726
|  |  |  | Barishal |  | 0 |  | 458
|  |  |  | Rajshahi |  | 0 |  | 1565
|  |  |  | Rangpur |  | 0 |  | 962
|  |  |  | Total |  | 0 |  | 12628
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 990 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1425.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:40 |  | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Taken by
DPDC
| 09:40 | 16:43 | Rampura-Ullon-2 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Taken by
DPDC
|  | 14:22 | Cumilla(S) 132/33kV S/S 53.2MW Lakthanavi is restored.
| 02:20 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 04:44 |  | Ashuganj CCPP 225 MW ST tripped at 04:44hrs. due to CW pump trip
| 04:44 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 04:44 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST trip-04:44 at 04.04.25
| 07:00 |  | Minimum Generation is 11009 MW
| 07:06 |  | Cantonment 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Painting work.
| 07:07 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 LT Scheduled S/D Due to Painting
work.
| 07:13 |  | Cantonment 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D Due to Painting work.
| 07:21 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 HT Scheduled S/D Due to Painting
work.
| 07:27 |  | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Red Hot remove at 33 kV busber | [7 empty] | 50.0MW load
|  |  | (Padma bowing) under 132 kV T1 Transformer. | [7 empty] | interrup.
| 07:28 |  | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Red hot remove at 33 kV busber | [7 empty] | 50.0MW load
|  |  | (Padma bowing) under 132 kV T1 Transformer. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9313200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9920500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6919738 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 7708349 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 74520 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 498720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 142455 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 74239 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 205200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 231480 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 785280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 20 | 24000 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 299520 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 205651 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 8945909 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 500 | 11984545 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1749600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2717 | 59082906
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 60285.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 135810 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1089720 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3511898 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 136327 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 40 | 117504 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 286954 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 1404480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 803520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 12 | 17815 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 18 | 117091 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 105600 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25854543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 35520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 314 | 7352727.27 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1998 | 41056513.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4670000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8720900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 799416 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1142400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 170 | 4215273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1026896 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 281018 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 35 | 218992 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1136430 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3285240 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 26 | 601920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52 | 333365 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 398370 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2072520 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 225120 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 964800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 432191 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1507 | 30524851
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 97 | 1728960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 3024000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1693200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 252660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 226080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 388 | 6937500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 35 | 829000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 900960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 133 | 3458782 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 704736 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2016000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 117 | 3547110 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 414000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 509568 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to maintenance work on gas field
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2368.568 | 477 | 12380156
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 844 | 21374545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 338880 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 607680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 555 | 11767270 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1450 | 34088375
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 238868 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 120 | 2539000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1220 | 25883636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5067570 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6480000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4362 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1877 | 40213436.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | M/C running
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4809091 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 160 | 4822300 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 160 | 4571100 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 320 | 8477381 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 16079 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 101680 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 176928 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1356 | 28935636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 370504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 640340 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2256 | 52952479
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1344872 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 4020000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 956908 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42767.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 743846 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 228478 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1198800 | -
Rangpur Area Total |  |  |  |  | 950 | 448 | 8535671.64
Eastern Grid Total |  |  |  |  | 16921.242 | 7087 | 149981926.87
Western Grid Total |  |  |  |  | 11614.5 | 6031 | 135789962
National Grid Total |  |  |  |  | 28535.742 | 13118 | 285771888.87
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7917.45 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4710.6 | MW
i) Dhaka area |  |  | 3277.45 |  | MW | i) Khulna area |  |  |  | 1726 | MW
ii) Chattogram area |  |  | 1345 |  | MW | ii) Barishal area |  |  |  | 458 | MW
iii) Cumilla area |  |  | 1442 |  | MW | iii) Rajshahi area |  |  |  | 1564.6 | MW
iv) Mymensingh area |  |  | 1275 |  | MW | iv) Rangpur area |  |  |  | 962 | MW
v) Sylhet area |  |  | 578 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12628.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 09:00 | 67 | Jaldhaka | 84 | 19:00 | 133 | Payra | 34 | 22:00
2 | AKSML | 135.4 | 14:00 | 68 | Jamalpur | 142 | 19:00 | 134 | Postogola | 36 | 00:00
3 | Aftabnagar | 28 | 23:00 | 69 | Jashore | 147 | 20:00 | 135 | Purbachal | 16 | 23:00
4 | Agargaon | 87 | 23:00 | 70 | Jhenaidah | 149 | 19:00 | 136 | Purbasadipur | 114 | 19:00
5 | Agrabad | 68 | 19:30 | 71 | Joydebpur | 75 | 21:00 | 137 | Rahanpur | 31 | 22:00
6 | Amnura | 56 | 21:00 | 72 | Joypurhat | 72 | 00:00 | 138 | Rahim | 1 | 00:00
7 | Ashuganj | 81 | 19:30 | 73 | Juldah | 14 | 23:00 | 139 | Rajbari | 83 | 23:00
8 | BSRM | 181 | 14:00 | 74 | KSRM | 12 | 11:00 | 140 | Rajendrapur | 99 | 22:00
9 | Bagerhat | 80 | 23:00 | 75 | Kabirpur | 122 | 21:00 | 141 | Rajshahi | 107 | 00:00
10 | Bajitpur | 53 | 21:00 | 76 | Kachua | 92 | 18:30 | 142 | Rajshahi-230 | 85 | 00:00
11 | Bakulia | 72 | 14:00 | 77 | Kallyanpur | 84 | 00:00 | 143 | Ramganj | 126 | 18:30
12 | Banani | 26.4 | 13:00 | 78 | Kalurghat | 22 | 00:00 | 144 | Rampur | 36 | 23:00
13 | Bangabhaban | 4 | 11:00 | 79 | Kamrangirchar | 31.5 | 23:00 | 145 | Rangamati | 18 | 19:00
14 | Barapukuria | 76 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 127 | 19:30
15 | Barguna | 22 | 22:00 | 81 | Kasba | 41 | 22:00 | 147 | Ruppur | 6.6 | 11:00
16 | Barishal | 106 | 21:00 | 82 | Kazla | 59 | 23:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 100 | 23:00 | 83 | Keranigonj | 53 | 22:00 | 149 | Saidpur | 105 | 14:00
18 | Baroaulia | 45 | 21:00 | 84 | Khagrachori | 34 | 19:00 | 150 | Satkhira | 142 | 21:00
19 | Baroirhat | 65 | 18:30 | 85 | Khulna | 75 | 23:00 | 151 | Satmasjid | 72 | 19:00
20 | Bashundhara | 128 | 21:00 | 86 | Khulshi | 151 | 19:00 | 152 | Savar | 108 | 21:00
21 | BashundharaCement | 0 | 00:00 | 87 | Kishoreganj | 156 | 21:00 | 153 | SevenRings | 4.67 | 19:30
22 | Beanibazar | 70 | 19:00 | 88 | Kodda | 148 | 18:30 | 154 | ShahCement | 1 | 00:00
23 | Benapole | 74 | 22:00 | 89 | Kulaura | 44 | 18:30 | 155 | Shahjadpur | 87 | 00:00
24 | Bhaluka | 122 | 19:00 | 90 | Kurigram | 72 | 19:00 | 156 | Shahjibazar | 128 | 00:00
25 | Bhandaria | 58 | 23:00 | 91 | Kushtia | 118 | 00:00 | 157 | Shahmirpur | 48 | 23:00
26 | Bhangura | 45 | 18:30 | 92 | Lalbag | 16 | 21:00 | 158 | Shariatpur | 91 | 22:00
27 | Bheramara(GK) | 60 | 00:00 | 93 | Lalmonirhat | 66 | 19:00 | 159 | Sherpur | 178 | 18:30
28 | Bhulta | 110 | 23:00 | 94 | MI_Cement | 1.5 | 20:00 | 160 | Shikalbaha | 21 | 18:00
29 | Bog-Sherpur | 66 | 19:30 | 95 | Madanganj | 28 | 00:00 | 161 | Shitalakhya | 48 | 23:00
30 | Bogura | 166 | 23:00 | 96 | Madaripur | 118 | 23:00 | 162 | Sholosohor | 30 | 23:00
31 | Borhanuddin | 92 | 23:00 | 97 | Madartek | 70.02 | 23:00 | 163 | Shyampur | 46 | 19:00
32 | Brahmanbaria | 148 | 22:00 | 98 | Madunaghat | 47 | 19:00 | 164 | Siddhirganj | 66 | 20:00
33 | Cantonment | 86 | 20:00 | 99 | Magura | 72 | 19:00 | 165 | Sirajganj | 112 | 19:30
34 | Chandpur | 75 | 20:00 | 100 | Mahasthangarh | 84 | 00:00 | 166 | Sonargaon | 52 | 00:00
35 | Chandraghona | 38 | 20:00 | 101 | Manikganj | 116 | 23:00 | 167 | Sreemongol | 78 | 21:00
36 | Chapai | 67 | 22:00 | 102 | Maniknagar | 49 | 22:00 | 168 | Sreepur | 65 | 19:00
37 | Charsaidpur | 8 | 00:00 | 103 | Matarbari | 50 | 18:30 | 169 | Srinagar | 49.33 | 22:00
38 | Chauddagram | 80 | 19:30 | 104 | Matuail | 34 | 00:00 | 170 | Sunamganj | 58 | 20:00
39 | Chhatak | 33 | 18:30 | 105 | Millgate | 40 | 21:00 | 171 | Sylhet | 41 | 19:00
40 | Chowmuhani | 232 | 20:00 | 106 | Mirpur | 89 | 23:00 | 172 | Sylhet-132 | 103 | 20:00
41 | Chuadanga | 116 | 22:00 | 107 | Mirsorai | 7 | 12:00 | 173 | TK | 24 | 00:00
42 | Coxsbazar | 137 | 18:30 | 108 | Mirzapur | 45 | 19:30 | 174 | Tangail | 198 | 19:00
43 | Cumilla(N) | 187 | 21:00 | 109 | Mithapukur | 68 | 19:00 | 175 | Thakurgaon | 102 | 19:00
44 | Cumilla(S) | 136 | 23:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 77 | 21:00
45 | Daudkandi | 138 | 21:00 | 111 | Mogbazar | 79.4 | 00:00 | 177 | Ullahpara | 44 | 19:00
46 | Dhaka | 18 | 12:00 | 112 | Mongla | 33 | 19:00 | 178 | Ullon | 37 | 23:00
47 | Dhamrai | 74 | 21:00 | 113 | Motijheel | 24 | 23:00 | 179 | Uttara | 63 | 20:00
48 | Dhanmondi | 73 | 18:30 | 114 | Muktagacha | 38 | 13:00 | 180 | UttaraNew | 37 | 23:00
49 | Dohazari | 124 | 19:00 | 115 | Munshiganj | 106 | 23:00 | 181 | Zigatola | 66 | 20:00
50 | Faridpur | 159 | 22:00 | 116 | Muradnagar | 32 | 20:00
51 | Fatullah | 45 | 23:00 | 117 | Mymensingh | 197 | 20:00
52 | Fenchuganj | 41 | 18:00 | 118 | Naogaon | 135 | 00:00
53 | Feni | 119 | 18:30 | 119 | Narail | 64 | 19:00
54 | GPH | 82 | 19:00 | 120 | Narinda | 36.5 | 20:00
55 | Ghatail | 92 | 19:00 | 121 | Narshingdi | 143 | 23:00
56 | Ghorashal | 14 | 11:00 | 122 | Natore | 167 | 20:00
57 | Ghorashal-230 | 98 | 01:00 | 123 | Nawabganj | 60.2 | 23:00
58 | Goalpara | 28 | 00:00 | 124 | Netrakona | 141 | 19:30
59 | Gollamari | 60 | 00:00 | 125 | New | 34.5 | 23:00
60 | Gopalganj | 112.6 | 23:00 | 126 | Niamatpur | 122 | 21:00
61 | Gulshan | 70 | 19:00 | 127 | Noapara | 40 | 19:00
62 | Halishahar | 35 | 20:00 | 128 | PHP | 3 | 09:00
63 | HaripurSBU | 71 | 23:00 | 129 | Pabna | 114 | 00:00
64 | Hasnabad | 62 | 23:00 | 130 | Palashbari | 134 | 19:00
65 | Hathazari | 82 | 18:30 | 131 | Panchagarh | 52 | 19:00
66 | Ishurdi | 65 | 00:00 | 132 | Patuakhali | 80.5 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12674.51 | 100 |  | 12779.01
1:00 | 12382.52 | 80 |  | 12466.52
2:00 | 12032.32 | 70 |  | 12105.32
3:00 | 11737.34 | 55 |  | 11794.34
4:00 | 11433.61 | 54 |  | 11489.61
5:00 | 11269.37 | 53 |  | 11324.37
6:00 | 10748.65 | 45 |  | 10795.65
7:00 | 10700.46 | 37 |  | 10739.13
8:00 | 10694.09 | 25 |  | 10720.09
9:00 | 10662.76 | 0 |  | 10662.76
10:00 | 10824.62 | 0 |  | 10824.62
11:00 | 11027.49 | 0 |  | 11027.49
12:00 | 11323.29 | 0 |  | 11323.29
13:00 | 11722.52 | 0 |  | 11722.52
14:00 | 12023.64 | 0 |  | 12023.64
15:00 | 11923.31 | 0 |  | 11923.31
16:00 | 11628.2 | 0 |  | 11628.2
17:00 | 11363.97 | 0 |  | 11363.97
18:00 | 11015.9 | 0 |  | 11015.9
19:00 | 12858 | 0 |  | 12858
19:30 | 13118 | 0 |  | 13118
20:00 | 13077 | 0 |  | 13077
21:00 | 13032 | 0 |  | 13032
22:00 | 13016 | 0 |  | 13016
23:00 | 13069 | 0 |  | 13069
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6478 | 6196.51 | 12674.51 | DAILY GENERATION CURVE
00:30 | 6388 | 6140.515 | 12528.515
01:00 | 6298 | 6084.52 | 12382.52 | 03-04-2025
01:30 | 6234.5 | 5972.92 | 12207.42
02:00 | 6171 | 5861.32 | 12032.32
02:30 | 6092.5 | 5792.33 | 11884.83
03:00 | 6014 | 5723.34 | 11737.34
03:30 | 5941 | 5644.475 | 11585.475
04:00 | 5868 | 5565.61 | 11433.61
04:30 | 5821.5 | 5529.99 | 11351.49
05:00 | 5775 | 5494.37 | 11269.37
05:30 | 5682.665 | 5326.345 | 11009.01
06:00 | 5590.33 | 5158.32 | 10748.65
06:30 | 5677.44 | 5047.115 | 10724.555
07:00 | 5764.55 | 4935.91 | 10700.46
07:30 | 5760.645 | 4936.63 | 10697.275
08:00 | 5756.74 | 4937.35 | 10694.09
08:30 | 5721.415 | 4957.01 | 10678.425
09:00 | 5686.09 | 4976.67 | 10662.76
09:30 | 5726.97 | 5016.72 | 10743.69
10:00 | 5767.85 | 5056.77 | 10824.62
10:30 | 5790.975 | 5135.08 | 10926.055
11:00 | 5814.1 | 5213.39 | 11027.49
11:30 | 5876.48 | 5298.91 | 11175.39
12:00 | 5938.86 | 5384.43 | 11323.29
12:30 | 6008.76 | 5514.145 | 11522.905
13:00 | 6078.66 | 5643.86 | 11722.52
13:30 | 6143.54 | 5729.54 | 11873.08
14:00 | 6208.42 | 5815.22 | 12023.64
14:30 | 6223.03 | 5750.445 | 11973.475
15:00 | 6237.64 | 5685.67 | 11923.31
15:30 | 6169.255 | 5606.5 | 11775.755
16:00 | 6100.87 | 5527.33 | 11628.2
16:30 | 6104.825 | 5391.26 | 11496.085
17:00 | 6108.78 | 5255.19 | 11363.97
17:30 | 6021.52 | 5168.415 | 11189.935
18:00 | 5934.26 | 5081.64 | 11015.9
18:30 | 6469.13 | 5467.82 | 11936.95
19:00 | 7004 | 5854 | 12858
19:30 | 7087 | 6031 | 13118
20:00 | 7031 | 6046 | 13077
20:30 | 6988 | 6066.5 | 13054.5 |  | Executive Engineer
21:00 | 6945 | 6087 | 13032 |  | Network Operation Division
21:30 | 6911.5 | 6112.5 | 13024
22:00 | 6878 | 6138 | 13016
22:30 | 6881 | 6161.5 | 13042.5
23:00 | 6884 | 6185 | 13069

## En-Curve
QF-LDC-12
Date | 03-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2819 | 2340 | 894 | 0 | 28 | 1362.51 | 46 | 3826 | 0 | 363 | 996 | 0 | 0 | 0 | 100 | DAILY ENERGY CURVE
00:30 | 2839 | 2368 | 893.5 | 0 | 28 | 1361.015 | 46 | 3828.5 | 0 | 287 | 877.5 | 0 | 0 | 0 | 90 | 03-04-2025
01:00 | 2859 | 2396 | 893 | 0 | 28 | 1359.52 | 46 | 3831 | 0 | 211 | 759 | 0 | 0 | 0 | 80
01:30 | 2814 | 2411.5 | 892 | 0 | 27 | 1359.42 | 46 | 3827 | 0 | 194 | 636.5 | 0 | 0 | 0 | 75 | Energy Generated | 285.7719 |  | MKWHr
02:00 | 2769 | 2427 | 891 | 0 | 26 | 1359.32 | 46 | 3823 | 0 | 177 | 514 | 0 | 0 | 0 | 70 | Energy not Served | 0.519 |  | MKWHr
02:30 | 2748 | 2389.5 | 891 | 0 | 26 | 1359.33 | 46 | 3765 | 0 | 148.5 | 511.5 | 0 | 0 | 0 | 62.5 | Total Energy Requirement | 286.2909 |  | MKWHr
03:00 | 2727 | 2352 | 891 | 0 | 26 | 1359.34 | 46 | 3707 | 0 | 120 | 509 | 0 | 0 | 0 | 55
03:30 | 2730 | 2287.5 | 891 | 0 | 25 | 1312.975 | 46 | 3687.5 | 0 | 102.5 | 503 | 0 | 0 | 0 | 54.5
04:00 | 2733 | 2223 | 891 | 0 | 24 | 1266.61 | 46 | 3668 | 0 | 85 | 497 | 0 | 0 | 0 | 54
04:30 | 2723.5 | 2186.5 | 891.5 | 0 | 24 | 1263.99 | 46 | 3626 | 0 | 93 | 497 | 0 | 0 | 0 | 53.5
05:00 | 2714 | 2150 | 892 | 0 | 24 | 1261.37 | 46 | 3584 | 0 | 101 | 497 | 0 | 0 | 0 | 53
05:30 | 2706 | 2099.5 | 891.5 | 0 | 24 | 1261.34 | 46 | 3397 | 0.67 | 101 | 482 | 0 | 0 | 0 | 49
06:00 | 2698 | 2049 | 891 | 0 | 24 | 1261.31 | 46 | 3210 | 1.34 | 101 | 467 | 0 | 0 | 0 | 45
06:30 | 2685.5 | 2180 | 891.5 | 0 | 23 | 1194.055 | 46 | 3088.5 | 40 | 101 | 475 | 0 | 0 | 0 | 41
07:00 | 2673 | 2311 | 892 | 0 | 22 | 1126.8 | 46 | 2967 | 78.66 | 101 | 483 | 0 | 0 | 0 | 37
07:30 | 2654.5 | 2345.5 | 868 | 0 | 22 | 1120.125 | 46 | 2945 | 141.65 | 93 | 461.5 | 0 | 0 | 0 | 31
08:00 | 2636 | 2380 | 844 | 0 | 22 | 1113.45 | 46 | 2923 | 204.64 | 85 | 440 | 0 | 0 | 0 | 25
08:30 | 2652.5 | 2374 | 844 | 0 | 22 | 1085.655 | 46 | 2874 | 283.77 | 85 | 411.5 | 0 | 0 | 0 | 12.5
09:00 | 2669 | 2368 | 844 | 0 | 22 | 1057.86 | 46 | 2825 | 362.9 | 85 | 383 | 0 | 0 | 0 | 0
09:30 | 2720.5 | 2363.5 | 867.5 | 0 | 22 | 1006.925 | 46 | 2821.5 | 430.765 | 93.5 | 371.5 | 0 | 0 | 0 | 0
10:00 | 2772 | 2359 | 891 | 0 | 22 | 955.99 | 46 | 2818 | 498.63 | 102 | 360 | 0 | 0 | 0 | 0
10:30 | 2829 | 2358.5 | 891 | 0 | 22 | 957.185 | 46 | 2816 | 531.87 | 102 | 372.5 | 0 | 0 | 0 | 0
11:00 | 2886 | 2358 | 891 | 0 | 22 | 958.38 | 46 | 2814 | 565.11 | 102 | 385 | 0 | 0 | 0 | 0
11:30 | 2880 | 2397 | 891 | 0 | 23 | 962.52 | 46 | 2883 | 588.37 | 93.5 | 411 | 0 | 0 | 0 | 0
12:00 | 2874 | 2436 | 891 | 0 | 24 | 966.66 | 46 | 2952 | 611.63 | 85 | 437 | 0 | 0 | 0 | 0
12:30 | 2865.5 | 2439 | 891 | 0 | 25 | 1016.9 | 46 | 3089.5 | 599.505 | 85 | 463 | 0 | 0 | 2.5 | 0
13:00 | 2857 | 2442 | 891 | 0 | 26 | 1067.14 | 46 | 3227 | 587.38 | 85 | 489 | 0 | 0 | 5 | 0
13:30 | 2871.5 | 2437.5 | 891 | 0 | 25 | 1091.5 | 46 | 3352.5 | 539.58 | 102.5 | 509.5 | 0 | 0 | 6.5 | 0
14:00 | 2886 | 2433 | 891 | 0 | 24 | 1115.86 | 46 | 3478 | 491.78 | 120 | 530 | 0 | 0 | 8 | 0
14:30 | 2873 | 2433.5 | 891 | 0 | 25 | 1115.43 | 46 | 3433 | 452.045 | 120 | 576.5 | 0 | 0 | 8 | 0
15:00 | 2860 | 2434 | 891 | 0 | 26 | 1115 | 46 | 3388 | 412.31 | 120 | 623 | 0 | 0 | 8 | 0
15:30 | 2837.5 | 2434 | 891.5 | 0 | 26 | 1107.5 | 46 | 3349 | 336.755 | 111.5 | 627 | 0 | 0 | 9 | 0
16:00 | 2815 | 2434 | 892 | 0 | 26 | 1100 | 46 | 3310 | 261.2 | 103 | 631 | 0 | 0 | 10 | 0
16:30 | 2820.5 | 2441.5 | 891.5 | 0 | 26 | 1104.5 | 46 | 3231 | 181.585 | 103 | 643.5 | 0 | 0 | 7 | 0
17:00 | 2826 | 2449 | 891 | 0 | 26 | 1109 | 46 | 3152 | 101.97 | 103 | 656 | 0 | 0 | 4 | 0
17:30 | 2783.5 | 2347 | 891 | 0 | 26 | 1111 | 46 | 3116 | 54.935 | 103 | 709.5 | 0 | 0 | 2 | 0
18:00 | 2741 | 2245 | 891 | 0 | 26 | 1113 | 46 | 3080 | 7.9 | 103 | 763 | 0 | 0 | 0 | 0
18:30 | 2751 | 2310.5 | 867.5 | 0 | 26 | 1236.5 | 46 | 3362 | 3.95 | 246.5 | 1087 | 0 | 0 | 0 | 0
19:00 | 2761 | 2376 | 844 | 0 | 26 | 1360 | 46 | 3644 | 0 | 390 | 1411 | 0 | 0 | 0 | 0
19:30 | 2738 | 2439 | 844 | 0 | 26 | 1356 | 46 | 3840 | 0 | 384 | 1445 | 0 | 0 | 0 | 0
20:00 | 2830 | 2450 | 844 | 0 | 28 | 1359 | 46 | 3908 | 0 | 301 | 1311 | 0 | 0 | 0 | 0
20:30 | 2898.5 | 2458.5 | 867.5 | 0 | 28 | 1358 | 46 | 3936.5 | 0 | 268.5 | 1193 | 0 | 0 | 0 | 0
21:00 | 2967 | 2467 | 891 | 0 | 28 | 1357 | 46 | 3965 | 0 | 236 | 1075 | 0 | 0 | 0 | 0
21:30 | 2984.5 | 2479 | 891 | 0 | 28 | 1360.5 | 46 | 3973 | 0 | 232 | 1030 | 0 | 0 | 0 | 0
22:00 | 3002 | 2491 | 891 | 0 | 28 | 1364 | 46 | 3981 | 0 | 228 | 985 | 0 | 0 | 0 | 0
22:30 | 3000 | 2488.5 | 891 | 0 | 28 | 1362.5 | 46 | 4008 | 0 | 228 | 990.5 | 0 | 0 | 0 | 0
23:00 | 2998 | 2486 | 891 | 0 | 28 | 1361 | 46 | 4035 | 0 | 228 | 996 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 06:00 | 390 | 22:00 | Payra | 419 | 07:00 | 409 | 00:00
Ashuganj | 408 | 6:00 | 392 | 21:00 | Rahanpur | 402 | 18:00 | 390 | 21:00
Bhulta | 405 | 07:00 | 392 | 22:00 | Rampal | 409 | 09:00 | 390 | 23:00
Bibiana | 388 | 07:00 | 373 | 21:00
BIPTC | 398 | 05:00 | 389 | 16:00
Bogura | 389 | 05:00 | 377 | 21:00
Gopalganj | 409 | 09:00 | 393 | 23:00
Kaliakoir | 374 | 07:00 | 359 | 13:00
Madunaghat | 405 | 18:00 | 395 | 14:00
Meghnaghat | 407 | 07:00 | 396 | 22:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 07:00 | 229 | 22:00 | Keranigonj | 236 | 07:00 | 227 | 22:00
AKSML | 235 | 18:00 | 226 | 00:00 | Khulna(S) | 234 | 09:00 | 219 | 20:00
Aminbazar | 239 | 05:00 | 230 | 22:00 | Madunaghat | 236 | 09:00 | 231 | 13:00
Ashuganj | 235 | 07:00 | 226 | 23:00 | Madunaghat-400 | 237 | 07:00 | 230 | 00:00
Ashuganj-400 | 235 | 07:00 | 226 | 23:00 | Maniknagar | 233 | 07:00 | 226 | 14:00
Baghabari | 233 | 09:00 | 225 | 18:30 | Meghnaghat | 241 | 15:00 | 235 | 00:00
Barapukuria | 223 | 00:00 | 217 | 13:00 | Meghnaghat-400 | 236 | 07:00 | 229 | 22:00
Barapukuria-230 | 223 | 00:00 | 217 | 13:00 | Mirsorai | 233 | 07:00 | 224 | 14:00
Barishal | 238 | 08:00 | 228 | 23:00 | Rajshahi | 232 | 06:00 | 219 | 20:00
Bheramara | 233 | 06:00 | 222 | 20:00 | Rampal | 232 | 06:00 | 219 | 23:00
Bhulta | 233 | 07:00 | 225 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 18:00 | 216 | 21:00 | Rampura | 232 | 07:00 | 225 | 13:00
BIPTC | 235 | 05:00 | 221 | 20:00 | Shikalbaha | 235 | 07:00 | 228 | 14:00
Bogura | 236 | 18:00 | 228 | 21:00 | Shyampur | 235 | 07:00 | 228 | 14:00
Bogura-400 | 236 | 05:00 | 229 | 21:00 | Siddhirganj | 235 | 05:00 | 230 | 00:00
Borhanuddin | 242 | 08:00 | 235 | 23:00 | Sirajgonj | 241 | 05:00 | 234 | 01:00
BSRM | 233 | 07:00 | 224 | 14:00 | Sreepur | 232 | 09:00 | 226 | 00:00
Cumilla(N) | 229 | 06:00 | 220 | 13:00 | Tongi | 232 | 04:00 | 223 | 13:00
Faridpur | 236 | 08:00 | 226 | 00:00
Fenchuganj | 229 | 07:00 | 221 | 23:00
Ghorashal | 235 | 00:00 | 230 | 01:00
Ghorashal-230 | 232 | 07:00 | 223 | 14:00
Gopalganj | 235 | 09:00 | 225 | 23:00
GPH | 234 | 07:00 | 227 | 14:00
Haripur | 233 | 07:00 | 227 | 14:00
Hasnabad | 235 | 07:00 | 228 | 13:00
Hathazari | 237 | 07:00 | 232 | 00:00
Ishurdi | 235 | 05:00 | 224 | 19:30
Jhenaidah | 228 | 05:00 | 212 | 19:30
Kaliakoir | 234 | 07:00 | 225 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 129 | 15:00 | Madunaghat | 135 | 05:00 | 132 | 00:00
Agargaon | 138 | 07:00 | 132 | 22:00 | Magura | 130 | 06:00 | 118 | 19:30
Agrabad | 134 | 06:00 | 130 | 12:00 | Mahasthangarh | 129 | 05:00 | 124 | 02:00
AKS | 131 | 06:00 | 120 | 06:00 | Manikganj | 130 | 11:00 | 124 | 22:00
Aminbazar | 137 | 06:00 | 131 | 13:00 | Maniknagar | 135 | 06:00 | 130 | 23:00
Amnura | 133 | 18:00 | 124 | 21:00 | Matarbari | 120 | 09:00 | 112 | 18:30
Ashuganj | 137 | 06:00 | 133 | 15:00 | Matuail | 137 | 07:00 | 133 | 00:00
Bagerhat | 132 | 10:00 | 120 | 00:00 | Millgate | 136 | 04:00 | 130 | 13:00
Bajitpur | 128 | 05:00 | 123 | 00:00 | Mirpur | 135 | 05:00 | 130 | 22:00
Bakulia | 135 | 17:00 | 130 | 12:00 | Mirzapur | 129 | 07:00 | 121 | 13:00
Banani | 133 | 06:00 | 128 | 22:00 | Mithapukur | 129 | 00:00 | 121 | 13:00
Bangabhaban | 135 | 07:00 | 130 | 23:00 | MI_Cement | 137.9 | 06:00 | 133 | 22:00
Barapukuria | 137 | 00:00 | 131 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 06:00 | 130 | 21:00 | Mogbazar | 135 | 06:00 | 130 | 00:00
Barishal | 133 | 07:00 | 126 | 00:00 | Mongla | 133 | 09:00 | 121 | 23:00
Barishal-230 | 133 | 08:00 | 125 | 00:00 | Motijheel | 135 | 07:00 | 130 | 23:00
Baroaulia | 135 | 05:00 | 132 | 00:00 | Muktagacha | 130 | 23:00 | 120 | 14:00
Baroirhat | 125 | 19:00 | 118 | 15:00 | Munshiganj | 137 | 06:00 | 132 | 22:00
Bashundhara | 137 | 06:00 | 128 | 13:00 | Muradnagar | 130 | 07:00 | 123 | 14:00
BashundharaCement | 137 | 04:00 | 133 | 13:00 | Mymensingh | 131 | 18:00 | 110 | 18:30
Beanibazar | 130 | 07:00 | 122 | 23:00 | Naogaon | 125 | 17:00 | 118 | 22:00
Benapole | 127 | 09:00 | 115 | 19:30 | Narail | 128 | 06:00 | 117 | 00:00
Bhaluka | 125 | 09:00 | 119 | 14:00 | Narinda | 135 | 06:00 | 130 | 23:00
Bhandaria | 127 | 09:00 | 115 | 22:00 | Narshingdi | 135 | 06:00 | 122 | 22:00
Bhangura | 131 | 07:00 | 126 | 00:00 | Natore | 131 | 05:00 | 123 | 00:00
Bheramara | 133 | 06:00 | 126 | 00:00 | Nawabganj | 135 | 05:00 | 129 | 22:00
Bheramara(GK) | 132 | 06:00 | 125 | 00:00 | Netrakona | 117 | 06:00 | 106 | 18:30
Bhulta | 132 | 07:00 | 127 | 22:00 | New | 138 | 07:00 | 131 | 22:00
Bog-Sherpur | 130 | 05:00 | 124 | 21:00 | Niamatpur | 134 | 05:00 | 129 | 21:00
Bogura | 132 | 05:00 | 127 | 21:00 | Noapara | 132 | 05:00 | 121 | 23:00
Bogura-230 | 132 | 05:00 | 127 | 21:00 | Pabna | 132 | 05:00 | 125 | 00:00
Brahmanbaria | 131 | 10:00 | 123 | 22:00 | Palashbari | 126 | 05:00 | 118 | 14:00
Cantonment | 137 | 05:00 | 132 | 22:00 | Panchagarh | 138 | 00:00 | 120 | 10:00
Chandpur | 127 | 18:00 | 117 | 12:00 | Patuakhali | 136 | 09:00 | 131 | 01:00
Chandraghona | 135 | 06:00 | 131 | 13:00 | Payra | 137 | 06:00 | 133 | 22:00
Chapai | 131 | 11:00 | 126 | 22:00 | PHP | 125 | 07:00 | 117 | 14:00
Charsaidpur | 138 | 05:00 | 133 | 22:00 | Postogola | 139 | 08:00 | 135 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 126 | 06:00 | 118 | 00:00 | Purbachal | 136 | 07:00 | 128 | 22:00
Chhatak | 130 | 06:00 | 122 | 19:30 | Purbasadipur | 133 | 00:00 | 120 | 10:00
Chowmuhani | 116 | 19:00 | 110 | 01:00 | Rahanpur | 136 | 05:00 | 130 | 23:00
Chuadanga | 129 | 05:00 | 114 | 20:00 | Rahanpur-400 | 137 | 09:00 | 132 | 21:00
Coxsbazar | 119 | 08:00 | 112 | 23:00 | Rahim | 137 | 06:00 | 133 | 22:00
Cumilla(N) | 130 | 06:00 | 124 | 13:00 | Rajbari | 131 | 08:00 | 122 | 23:00
Cumilla(S) | 135 | 05:00 | 121 | 14:00 | Rajendrapur | 131 | 06:00 | 123 | 14:00
Daudkandi | 129 | 06:00 | 123 | 00:00 | Rajshahi | 132 | 05:00 | 125 | 00:00
Dhaka | 135 | 06:00 | 128 | 13:00 | Rajshahi-230 | 133 | 06:00 | 119 | 00:00
Dhamrai | 137 | 07:00 | 127 | 16:00 | Ramganj | 121 | 18:00 | 110 | 02:00
Dhanmondi | 137.5 | 09:00 | 124 | 00:00 | Rampur | 135 | 06:00 | 129 | 14:00
Dohazari | 129 | 06:00 | 124 | 13:00 | Rampura | 134 | 07:00 | 129 | 13:00
Faridpur | 132 | 03:00 | 126 | 00:00 | Rangamati | 135 | 07:00 | 129 | 14:00
Fatullah | 138 | 06:00 | 134 | 22:00 | Rangpur | 130 | 00:00 | 120 | 13:00
Fenchuganj | 133 | 06:00 | 127 | 23:00 | Ruppur | 135 | 09:00 | 128 | 00:00
Feni | 124 | 18:00 | 114 | 14:00 | Saidpur | 133 | 02:00 | 120 | 14:00
Ghatail | 126 | 07:00 | 118 | 13:00 | Satkhira | 131 | 09:00 | 117 | 20:00
Ghorashal | 139 | 07:00 | 133 | 21:00 | Satmasjid | 137 | 06:00 | 132 | 14:00
Goalpara | 135 | 08:00 | 123 | 00:00 | Savar | 135 | 07:00 | 129 | 13:00
Gollamari | 135 | 06:00 | 126 | 23:00 | SevenRings | 139 | 06:00 | 133 | 22:00
Gopalganj | 136 | 09:00 | 127 | 00:00 | ShahCement | 138 | 05:00 | 133 | 22:00
Gopalganj-400 | 139 | 09:00 | 131 | 23:00 | Shahjadpur | 135 | 04:00 | 130 | 00:00
Gulshan | 133 | 06:00 | 128 | 15:00 | Shahjibazar | 131 | 07:00 | 123 | 23:00
Halishahar | 135 | 06:00 | 131 | 12:00 | Shahmirpur | 136 | 19:00 | 132 | 14:00
Haripur | 138 | 06:00 | 134 | 00:00 | Shariatpur | 136 | 09:00 | 126 | 23:00
HaripurSBU | 138 | 06:00 | 134 | 00:00 | Sherpur | 129 | 18:00 | 118 | 01:00
Hasnabad | 139 | 04:00 | 135 | 13:00 | Shikalbaha | 125 | 05:00 | 120 | 12:00
Hathazari | 136 | 04:00 | 134 | 00:00 | Shikalbaha-230 | 137 | 07:00 | 132 | 13:00
Ishurdi | 135 | 05:00 | 128 | 20:00 | Shitalakhya | 137.8 | 06:00 | 133 | 22:00
Jaldhaka | 131 | 00:00 | 118 | 14:00 | Sholosohor | 136 | 07:00 | 131 | 13:00
Jamalpur | 133 | 18:00 | 119 | 14:00 | Shyampur | 138 | 00:00 | 134 | 22:00
Jashore | 129 | 09:00 | 117 | 23:00 | Shyampur-230 | 138 | 06:00 | 134 | 13:00
Jhenaidah | 130 | 03:00 | 120 | 00:00 | Siddhirganj | 138 | 04:00 | 133 | 22:00
Jhenaidah-230 | 131 | 05:00 | 121 | 19:30 | Sirajganj | 129 | 09:00 | 123 | 00:00
Joydebpur | 132 | 02:00 | 127 | 21:00 | Sonargaon | 136 | 06:00 | 130 | 13:00
Joypurhat | 122 | 17:00 | 114 | 21:00 | Sreemongol | 131 | 05:00 | 124 | 22:00
Juldah | 135 | 09:00 | 131 | 01:00 | Sreepur | 128 | 05:00 | 124 | 14:00
Kabirpur | 135 | 06:00 | 128 | 13:00 | Srinagar | 135 | 07:00 | 130 | 21:00
Kachua | 126 | 18:00 | 117 | 15:00 | SSM | 140 | 05:00 | 136 | 00:00
Kaliakoir | 137 | 07:00 | 128 | 13:00 | Sunamganj | 128 | 07:00 | 119 | 23:00
Kallyanpur | 136 | 06:00 | 131 | 14:00 | Sylhet | 130 | 06:00 | 124 | 19:30
Kalurghat | 136 | 07:00 | 131 | 13:00 | Sylhet-132 | 131 | 06:00 | 126 | 23:00
Kamrangirchar | 137 | 05:00 | 130 | 13:00 | Tangail | 127 | 18:00 | 115 | 13:00
Kaptai | 135 | 6:00 | 123 | 19:00 | Thakurgaon | 137 | 00:00 | 117 | 10:00
Kasba | 129 | 07:00 | 122 | 14:00 | TK | 137 | 06:00 | 132 | 13:00
Kazla | 135 | 06:00 | 130 | 15:00 | Tongi | 137 | 04:00 | 132 | 00:00
Keranigonj | 136 | 07:00 | 130 | 14:00 | Ullahpara | 133 | 04:00 | 126 | 00:00
Khagrachori | 134 | 07:00 | 127 | 00:00 | Ullon | 134 | 07:00 | 128 | 22:00
Khulna | 134 | 09:00 | 124 | 00:00 | Uttara | 137 | 07:00 | 130 | 14:00
Khulna(S) | 136 | 09:00 | 126 | 20:00 | UttaraNew | 136 | 06:00 | 130 | 22:00
Khulshi | 135 | 07:00 | 122 | 14:00 | Zigatola | 136 | 07:00 | 130 | 22:00
Kishoreganj | 126 | 04:00 | 117 | 18:30
Kodda | 131 | 06:00 | 125 | 22:00
KSRM | 136 | 08:00 | 130 | 14:00
Kulaura | 131 | 06:00 | 126 | 23:00
Kurigram | 129 | 00:00 | 116 | 13:00
Kushtia | 131 | 05:00 | 122 | 20:00
Lalbag | 136 | 08:00 | 131 | 00:00
Lalmonirhat | 127 | 04:00 | 120 | 13:00
Madanganj | 137 | 04:00 | 133 | 13:00
Madaripur | 137 | 08:00 | 129 | 23:00
Madartek | 133 | 05:00 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division